## Sheet1
Region | Site | Id | Pim_Issue_Date | Source | IdBy | Type | Cornerstone_ | Significance | Title_ | EACaseNo | CrossCuttingAspect | TE | Docket | CornerstoneAttribute | Procedure | Introduction_
Region: IV | Arkansas Nuclear One | 23159 | 01/19/2017 01/19/2017 | 2016011-01 | NRC | NOV | Mitigating Systems | White | Failure to Ensure Adequate Lubrication for Emergency Diesel Generator Bearing | EA Case: 2016247 | H.5 - Work Management | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors reviewed a self-revealing finding that was preliminarily determined to have low to moderate safety significance (White) for the failure to perform maintenance activities in a manner that ensured adequate lubrication to Unit 2 emergency dies
Region: IV | Arkansas Nuclear One | 2273 | 08/01/2014 08/09/2014 | 2014009-01 | NRC | VIO | Mitigating Systems | Yellow | Inadequate Flood Protection for Auxiliary and Emergency Diesel Fuel Storage Buildings | EA Case: 2014088 | H.6 - Design Margins | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.01 | The inspectors identified a finding of preliminary substantial safety significance (Yellow) for the failure to design, construct, and maintain the Units 1 and 2 auxiliary and emergency diesel fuel storage buildings in accordance with the safety analysis r
Region: IV | Arkansas Nuclear One | 1880 | 02/10/2014 03/24/2014 | 2013012-04 | NRC | VIO | Initiating Events | Yellow | Unit 1 - Failure to Follow the Materials Handling Program during the Unit 1 Generator Stator Move | EA Case: 2014008 | H.2 Field Presence | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | Unit 1 Apparent Violation. The inspectors reviewed a self-revealing apparent violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," which states, in part, that "activities affecting quality shall be prescribed by documen
Region: IV | Arkansas Nuclear One | 1886 | 02/10/2014 03/24/2014 | 2013012-05 | NRC | VIO | Initiating Events | Yellow | Unit 2 - Failure to Follow the Materials Handling Program during the Unit 1 Generator Stator Move | EA Case: 2014008 | H.2 Field Presence | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Unit 2 Apparent Violation. The inspectors reviewed a self-revealing apparent violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," which states, in part, that "activities affecting quality shall be prescribed by documen
Region: I | Beaver Valley | 6889 | 08/22/2006 09/18/2006 | 2006009-01 | NRC | VIO | Emergency Preparedness | White | Inadequate dose assessment procedure. | EA Case: 2006215 |  | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71114.01 | During an NRC inspection conducted between June 26 and August 22, 2006, for which an exit meeting was held on August 22, 2006, and a Regulatory Conference was held on October 24, 2006, a violation of NRC requirements was identified. In accordance with the
Region: III | Braidwood | 5085 | 11/03/2009 11/30/2009 | 2009007-01 | NRC | VIO | Mitigating Systems | White | FAILURE OF CONTAINMENT SUMP SUCTION VALVE 1SI8811B TO STROKE OPEN | EA Case: 2009259 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000456 Braidwood 1 |  | NONE | The inspectors identified a finding of substantial safety significance and an associated apparent violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to prevent water from entering the motor operated valve actuator fo
Region: III | Braidwood | 4995 | 05/25/2006 05/25/2006 | 2006008-01 | NRC | VIO | Public Radiation Safety | White | Braidwood Tritium WHITE finding - failure to survey | EA Case: 2006081 |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7112201 | 10 CFR 20.1501 requires that each licensee make or cause to be made surveys that may be necessary for the licensee to comply with the regulations in Part 20 and that are reasonable under the circumstances to evaluate the extent of radiation levels, concen
Region: II | Browns Ferry | 24113 | 03/16/2018 08/09/2018 | 2018002-03 | Licensee - Identified | AV | Mitigating Systems | TBD | Failure to analyze for a Water Hammer event due to Spurious Operation of Residual Heat Removal Service Water (RHRSW) Valves during a Fire Event | EA Case: EA-18-101 |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71153 | The licensee identified an Apparent Violation (AV) of 10 CFR 50(c)(3)(ii). On February 19, 2016, at 1235 Central Standard Time (CST), BFN personnel discovered a failure to consider Residual Heat Removal (RHR) Service Water (SW) water hammer in Fire S
Region: II | Browns Ferry | 3601 | 12/31/2013 02/14/2014 | 2013005-02 | NRC | VIO | Emergency Preparedness | White | Failure to maintain emergency response staffing levels | EA Case: 2014005 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.11Q | The NRC identified an apparent violation of 10 CFR 50.54(q), Emergency Plans, for the licensee's failure to maintain plant staffing levels in accordance with NP-REP, Tennessee Valley Authority Nuclear Power Radiological Emergency Plan. Specifically, the l
Region: II | Browns Ferry | 3292 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | VIO | Initiating Events | White | Failure to follow operating procedure guidance resulted in Unit 2 reactor scram | EA Case: 2013118 | H.4(a) Human Error Prevention | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A self-revealing White Violation of Technical Specification 5.4.1 was identified for the licensee's failure to properly implement procedure 2-OI-99, Reactor Protection System (RPS) in that an operator failed to re-energize the 2B RPS Bus and inappropriate
Region: II | Browns Ferry | 3271 | 05/14/2012 05/28/2012 | 2012007-05 | NRC | VIO | Mitigating Systems | White | Failure to properly implement the requirements of the plant modifications and engineering change control procedure | EA Case: 2012133 | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | During an NRC inspection completed on March 1, 2012, a violation of NRC requirements was identified. In accordance with the NRC Enforcement Policy, the violation is listed below: 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawing
Region: II | Browns Ferry | 3221 | 10/23/2010 05/09/2011 | 2011008-01 | Self - Revealed | VIO | Mitigating Systems | Red | RHR subsystem inoperable beyond the TS allowed outage time | EA Case: 2011018 |  | TE?: N | 05000259 Browns Ferry 1 |  | NONE | Browns Ferry Nuclear Plant Unit 1 Technical Specification (TS) LCO 3.5.1, Emergency Core Cooling System (ECCS) - Operating, requires, in part, that each ECCS injection/spray subsystem shall be operable in Modes 1, 2 and 3. Action statement Condition A sta
Region: II | Browns Ferry | 3149 | 10/09/2009 01/20/2010 | 2009009-03 | NRC | VIO | Mitigating Systems | Yellow | Failure to Ensure One Train of Cables of Syatems Necessary to Achieve and/or Maintain Post-Fire safe Shutdown is Free of Fire Damage in Accordance With 10 CFR Part 50, Appendix R, Section III.G. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | Title 10 of the Code of Federal Regulations (10 CFR), Part 50.48(b)(1) requires that all nuclear power plants licensed to operate prior to January 1, 1979, must satisfy the applicable requirements of 10 CFR Part 50, Appendix R, Sections III.G, III.J, and
Region: II | Browns Ferry | 3155 | 10/09/2009 01/20/2010 | 2009009-05 | NRC | VIO | Mitigating Systems | White | Inadequate Safe Shutdown Instruction Entry Conditions for Appendix R Fire Events |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The team identified an apparent violation of Technical Specification 5.4.1.a., in that, the licensee's revision to the safe shutdown instruction entry conditions in December 2008 resulted in inadequate procedural guidance. Specifically, the revision to Pr
Region: II | Brunswick | 6543 | 11/21/2011 11/29/2011 | 2011012-01 | NRC | VIO | Mitigating Systems | White | Failure to Identify and Correct a Degraded Flood Barrier for the Emergency Diesel Generator Fuel Oil Tank Rooms | EA Case: 2011251 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.01 | (TBD) The inspectors identified an Apparent Violation (AV) of 10 CFR Part 50 Appendix B Criterion XVI, Corrective Action, for failure to identify and correct a condition adverse to quality associated with the entrance enclosures for the Emergency Diesel G
Region: II | Brunswick | 6518 | 09/17/2010 10/20/2010 | 2010007-01 | NRC | VIO | Emergency Preparedness | White | Failure to timely augment on-shift staffing | EA Case: 2010192 | P.3(a) Self-Assessment | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | NONE | An NRC-identified, low to moderate safety significance (White), apparent violation (AV) of 10 CFR 50.54(q) was identified in that the licensee failed to meet the requirements of 10 CFR 50.47(b)(2). The Technical Support Center (TSC), Operations Support Ce
Region: II | Brunswick | 6467 | 05/28/2009 06/17/2009 | 2009009-01 | NRC | VIO | Mitigating Systems | White | Inability to Operate the EDGs Locally as Required by the Safe Shutdown Analysis Report | EA Case: 2009121 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 93812 | A violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for failure to correctly translate the design basis into EC 66274 to replace control relays on all four EDGs. Specifically, termination points for linking control power to
Region: II | Brunswick | 6412 | 02/28/2007 02/28/2007 | 2007008-01 | NRC | VIO | Mitigating Systems | White | Failure to Meet TS 3.8.1, AC Sources-Operating | EA Case: 2007024 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000325 Brunswick 1 |  | 71153 | A preliminary White finding with an apparent violation (AV) of Technical Specification (TS) 3.8.1, AC Sources-Operating, was identified for Unit 1. The finding involved inadequate corrective actions to prevent a repeat failure of the #9 main crankshaft be
Region: III | Byron | 10890 | 02/07/2011 02/11/2011 | 2011011-01 | NRC | VIO | Mitigating Systems | White | Self-Revealing Failure of the 2A Diesel Generator Upper Lube Oil Cooler | EA Case: 2011014 | H.4(a) Human Error Prevention | TE?: N | 05000455 Byron 2 |  | 71111.12 | A finding of low to moderate safety significance (White) and a violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the 2A Diesel Generator (D/G) was required to be shutdown during routine
Region: III | Byron | 10798 | 02/14/2008 02/21/2008 | 2007009-03 | NRC | VIO | Initiating Events | White | Inadequate Design Margins for Continued Operation of SX Riser Pipes | EA Case: 2008046 | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 93812 | -White. The team identified a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to verify the adequacy of the methodology and design inputs used to support licensee decisions to accept the deg
Region: I | Calvert Cliffs | 18987 | 06/30/2014 08/08/2014 | 2014003-02 | NRC | VIO | Emergency Preparedness | White | Inaccurate EAL Threshold Values Incorporated into Site EAL Scheme Change | EA Case: 2014100 | H.12 Avoid Complacency | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.15 | -Preliminary White: The inspectors documented a licensee-identified apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2), which preliminarily has been determined to be of low to moderate safety significance (White). Speci
Region: I | Calvert Cliffs | 18419 | 04/30/2010 06/14/2010 | 2010006-02 | NRC | VIO | Mitigating Systems | White | Inadequate Preventive Maintenance Results in the Failure of the 2B Emergency Diesel Generator | EA Case: 2010080 | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000318 Calvert Cliffs 2 |  | 93812 | The NRC identified a violation of Technical Specifidcation 5.4.1 for the failure of Constellation to establish, implement, and maintain preventive maintenance requirements associated with safety related relays. The team identified that Constellation did n
Region: I | Calvert Cliffs | 18382 | 01/14/2009 02/26/2009 | 2008502-01 | Licensee - Identified | VIO | Emergency Preparedness | White | Failure to Maintain Emergency Plans | EA Case: 2008351 |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71114.04 | Constellation identified a violation associated with the failure to meet emergency preparedness planning standard 10 CFR 50.47(b)(4). For the period of August 31, 2005, until April 10, 2008, the emergency action level (EAL) table's fission product barrier
Region: I | Calvert Cliffs | 18308 | 08/16/2006 09/08/2006 | 2006012-01 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Adequately Control the Design of the Setpoints for "1A" EDG Feeder Breaker for Essential EDG Support Systems | EA Case: 2006198 |  | TE?: N | 05000317 Calvert Cliffs 1 |  | NONE | A violation of 10 CFR 50, Appendix B, Criterion III (Design Control) was identified involving the failure to ensure an adequate trip setpoint for the electrical circuit breaker that supplies the "1A" EDG support systems. An SDP Phase 3 risk analysis deter
Region: II | Catawba | 20269 | 07/12/2017 07/18/2017 | 2017011-01 | NRC | NOV | Mitigating Systems | White | Failure to adequately establish and adjust preventive maintenance for emergency diesel generator excitation system diodes. |  | P.5 Operating Experience | TE?: N | 05000414 Catawba 2 |  | 71111.15 | The inspectors identified an AV of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to adequately develop and adjust the preventive maintenance strategy for the emergency diesel generator (EDG) excitation system in accordance with
Region: II | Catawba | 19807 | 06/18/2012 07/25/2012 | 2012009-01 | NRC | VIO | Mitigating Systems | White | Failure to Provide Vendor with Accurate Design Information | EA Case: 2012153 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 |  | 93812 | Self-revealing findings were identified for the licensee's failure to follow EDM-141, Procurement Specifications for Services. The licensee did not identify the need for the blocking feature for the instantaneous underfrequency protective function in both
Region: III | Clinton | 125502 | 08/03/2018 07/31/2019 | 2018050-01 | Self - Revealed | NOV | Mitigating Systems | White | Failure to Follow Multiple Procedures | EA Case: EA-18-104 | H.2 - Field Presence | TE?: N | 05000461 Clinton |  | 95001 | On May 17, 2018, a To-Be-Determined (TBD) finding and an associated Apparent Violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” and Technical Specification 3.8.2, C
Region: III | Clinton | 23158 | 12/28/2017 01/26/2018 | 2017011-01 | Self - Revealed | NOV | Mitigating Systems | White | Failure to Correct an Identified Degraded Condition on the Division 3 Shutdown Service Water Pump | EA Case: EA-17-203 | P.2 - Evaluation | TE?: N | 05000461 Clinton |  | 71152 | A self-revealing finding and an apparent violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” with associated violations of Technical Specification (TS) 3.7.2 and TS 3.5.1 were identified on June 15, 2017, for the licensee’s failure to
Region: III | Clinton | 22394 | 08/14/2017 08/14/2017 | 2017009-01 | Self - Revealed | NOV | Mitigating Systems | White | FAILURE TO EVALUATE REPLACEMENT RELAY DROPOUT VOLTAGE | EA Case: 2017098 | H.11 Challenge the Unknown | TE?: N | 05000461 Clinton |  | 71111.15 | A self-revealed finding preliminarily determined to be of low to moderate safety significance, and an associated apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," was identifie
Region: III | Clinton | 21936 | 03/31/2015 05/13/2015 | 2015001-03 | Self - Revealed | VIO | Mitigating Systems | White | FAILURE OF THE DIVISION 3 SHUTDOWN SERVICE WATER PUMP DUE TO AN INADEQUATE BUSHING DESIGN | EA Case: 2015064 |  | TE?: N | 05000461 Clinton |  | 71153 | A self-revealed finding, determined to be of low to moderate safety significance (White) and an associated AV of 10 CFR 50 Appendix B, Criterion III, Design Control, was identified for the failure to review the suitability of application of the Division 3
Region: III | Clinton | 20509 | 08/12/2006 11/29/2006 | 2006011-01 | NRC | VIO | Mitigating Systems | White | HPCS OPERABILITY QUESTIONED DUE TO VORTEXING | EA Case: 2006291 |  | TE?: N | 05000461 Clinton |  | 7111121 | White. A finding of low to moderate safety significance was identified by the inspectors for a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" requirements. Specifically, the licensee failed to adequately address vortexing in the
Region: IV | Columbia Generating Station | 19438 | 03/17/2017 04/10/2017 | 2016009-01 | Self - Revealed | NOV | Public Radiation Safety | White | Shipment of a Typed B Quantity of Radioactive Material in a Type A Package | EA Case: EA-17-028 | H.14 Conservative Bias | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team reviewed a self-revealed finding and apparent violation of 49 CFR 173.427 associated with a shipment of low specific activity (LSA) material consisting of radioactive filters, irradiated components, and dry active waste. The licensee failed to en
Region: IV | Columbia Generating Station | 17012 | 06/27/2012 07/26/2012 | 2012502-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain Accurate EAL Thresholds |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71114.04 | 10 CFR 50.54(q)(2), requires, in part, that a holder of a license under Part 50 shall follow and maintain the effectiveness of an emergency plan that meets the requirements in Appendix E to Part 50 and, for nuclear power reactor licensees, the planning
Region: IV | Columbia Generating Station | 17013 | 06/27/2012 07/26/2012 | 2012502-02 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain Accurate Methods for Dose Assessment | EA Case: 2012092 |  | TE?: N | 05000397 Columbia Generating Station |  | 71114.05 | 10 CFR 50.47(b)(9) requires, in part, that nuclear power reactors have adequate methods for assessing and monitoring actual or potential offsite consequences of a radiological emergency condition in use. Contrary to the above, between April 2000 and
Region: IV | Comanche Peak | 28244 | 01/24/2008 02/29/2008 | 2007008-03 | Self - Revealed | VIO | Mitigating Systems | White | Painting Activities Result in Inoperability of Emergency Diesel Generator | EA Case: 2008028 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000445 Comanche Peak 1 |  | 93812 | A violation of Unit 1 Technical Specification 3.8.1, "AC Sources - Operating," was identified for the licensee's failure to satisfy Limiting Condition for Operation 3.8.1 in that painting activities conducted on the Unit 1 Train B EDG 1-02 resulted in pai
Region: IV | Cooper | 22641 | 08/11/2017 08/14/2017 | 2017011-01 | NRC | AV | Initiating Events | Preliminary White | Emergency Transformer Bus Failure due to Inadequate Inspection and Testing Activities | EA Case: EA-17-057 | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a preliminary low-to-moderate safety significance (White) finding with two NRC-identified apparent violations of Technical Specification 5.4.1.a, for the licensee’s failure to implement and maintain Maintenance Procedure 7.3.41,
Region: IV | Cooper | 24195 | 07/02/2011 06/10/2011 | 2011009-01 | NRC | VIO | Mitigating Systems | White | Untimely Corrective Action & Inadequate PFSSD Procedure | EA Case: 2011024 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.05T | A violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," and Criterion V, "Instructions, Procedures, and Drawings," was identified for failure to ensure that some steps contained in Emergency Procedures at the Cooper Nuclear Station
Region: IV | Cooper | 23904 | 03/14/2011 03/17/2011 | 2010006-01 | NRC | AV | Mitigating Systems | White | Inadequate Post-Fire Safe Shutdown Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.05T | An apparent violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," and Criterion XVI, "Corrective Action," with a preliminary white significance, was identified for failure to ensure that some steps contained in Em
Region: IV | Cooper | 23785 | 03/22/2008 05/06/2008 | 2008002-02 | NRC | VIO | Mitigating Systems | White | Failure to Establish Adequate Procedures for Maintenance of Emergency DG Electrical Connections | EA Case: 2008124 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.19 | Two examples of a self-revealing apparent violation of Technical Specification 5.4.1.a were identified regarding the licensee's failure to establish procedural controls for maintenance of electrical connections on essential equipment. In the first example
Region: IV | Cooper | 23795 | 03/18/2008 06/13/2008 | 2008008-01 | NRC | VIO | Mitigating Systems | White | Failure to ensure that some steps contained in emergency procedures would work as written | EA Case: 2007204 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.05T | White. A violation of 10 CFR Part 50, Appendix B, Criterion V, was identified for failure to ensure that some steps contained in emergency procedures at Cooper Nuclear Station would work as written. Inspectors identified that steps in Emergency Procedures
Region: IV | Cooper | 23438 | 04/24/2007 05/22/2007 | 2007007-01 | NRC | VIO | Mitigating Systems | White | Failure to Promptly Identify and Correct Defective Diesel Generator Voltage Regulator Components | EA Case: 2007090 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper 05000298 Cooper |  | 93812 | The team identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct a significant condition adverse to quality, and failed to assure that the cause of a significant
Region: I | Crystal River | 32337 | 07/15/2011 09/14/2011 | 2011501-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain a Standard EAL Scheme | EA Case: 2011208 | H.1(a) Systematic Process for Decisions | TE?: N | 05000302 Crystal River 3 |  | 71114.04 | TBD. An AV was identified for failure to follow and maintain in effect emergency plans which use a standard emergency classification and action level scheme. Specifically, the licensee's emergency plan emergency action level (EAL) 1.4, General Emergency -
Region: III | Davis-Besse | 23210 | 12/31/2017 02/14/2018 | 2017004-03 | Self - Revealed | NOV | Mitigating Systems | White | Failure to Prescribe Appropriate Work Instructions for an Activity Affecting Quality | EA Case: 2018-008 | H.11 - Challenge the Unknown | TE?: N | 05000346 Davis-Besse |  | 71152 | A self-revealed finding with an Apparent Violation (AV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” and an associated violation of technical specification (TS) 3.7.5, “Em
Region: III | Davis-Besse | 34268 | 11/23/2009 12/28/2009 | 2009503-01 | NRC | VIO | Emergency Preparedness | White | Failure to Use Classification Scheme for an Alert. | EA Case: 2009283 | H.1(a) Systematic Process for Decisions | TE?: N | 05000346 Davis-Besse |  | 71153 | A licensee identified finding and associated Apparent Violation (AV) of 10 CFR 50.54(q) and 10 CFR 50.47(b)(4) was identified for the failure to implement the emergency classification and action level scheme during an actual event to declare an Alert afte
Region: IV | Diablo Canyon | 7911 | 09/12/2016 10/03/2016 | 2016010-01 | NRC | VIO | Mitigating Systems | White | Failure to Establish Adequate Work Instructions for Installation of Namco Snap Lock Limit Switches | EA Case: 2016168 |  | TE?: N | 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a preliminary White finding associated with an apparent violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to develop adequate instructions for the installation, adjustment, and testing of Namc
Region: IV | Diablo Canyon | 7840 | 10/17/2014 12/01/2014 | 2014502-01 | NRC | VIO | Emergency Preparedness | White | Failure to Obtain Prior Approval for a Change Which Decreased the Effectiveness of the Emergency Plan | EA Case: 2014010 |  | TE?: Y SL-III-VIO | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | (Initial Entry) The inspectors identified an apparent Severity Level III violation of 10 CFR 50.54(q) and an associated preliminary finding of low to moderate significance (White) for failing to obtain prior approval for an emergency plan change which de
Region: III | Dresden | 9001 | 11/15/2016 12/05/2016 | 2016010-01 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Verify the Adequacy of Design for the Unit 3 HPCI AOP Motor Shunt Resistor Setting | EA Case: 2016236 | H.6 Design Margins | TE?: N | 05000249 Dresden 3 |  | 71153 | A self-revealing finding determined to be of low to moderate safety significance, and a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was associated with the licensee's failure to ensure that the applicable design basis for app
Region: III | Dresden | 8978 | 06/30/2015 08/07/2015 | 2015002-04 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Ensure Continued Operability of Unit 2 Electromatic Relief Valve 2-0203-3C (2C) Following Implementation of Extended Power Uprate Plant Conditions | EA Case: 2015115 | P.3 Resolution | TE?: N | 05000237 Dresden 2 |  | 71153 | A finding of low- to-moderate safety significance, and an associated Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control"; TS 3.4.3, "Safety and Relief Valves"; and TS 3.5.1, "ECCS Operating", was
Region: III | Dresden | 8965 | 12/31/2014 01/29/2015 | 2014005-02 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Ensure Continued Operability of Unit 3 Electromatic Relief Valve 3-0203-3E Following Implementation of Extended Power Uprate Plant Conditions | EA Case: 2015001 | P.5 Operating Experience | TE?: N | 05000249 Dresden 3 |  | 71111.15 | A violation (AV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, having a low to moderate safety significance, was self-revealed on November 6, 2014, following the discovery that one of the Unit 3 electromatic relief valves (ERVs) would not
Region: III | Dresden | 8924 | 03/31/2013 05/07/2013 | 2013002-02 | NRC | VIO | Mitigating Systems | White | Deficiency In Abnormal Operating Procedures for Site Response to External Flooding Events | EA Case: 2013079 | P.3(a) Self-Assessment | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | Technical Specification Section 5.4.1 requires, in part, that written procedures be established, implemented, and maintained covering the applicable procedures recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Regulatory Guide 1
Region: III | Dresden | 8332 | 07/15/2009 08/19/2009 | 2009009-01 | NRC | VIO | Mitigating Systems | White | Inadvertent Control Rod Movement While Shutdown | EA Case: 2009172 | P.2(b) Implementing Operating Experience | TE?: N | 05000249 Dresden 3 |  | NONE | A finding that has preliminarily been determined to be White, a finding with low to moderate safety significance, was self-revealed on November 3, 2008, when the licensee failed to prevent inadvertent and uncontrolled control rod withdrawal by non-license
Region: III | Duane Arnold | 10085 | 01/08/2015 02/19/2015 | 2014011-01 | Self - Revealed | VIO | Mitigating Systems | White | FAILURE TO INSTALL TORUS COATING IN ACCORDANCE WITH ESTABLISHED PROCESSESS. | EA Case: 2014237 | H.2 Field Presence | TE?: N | 05000331 Duane Arnold |  | 93812 | White. A violation of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion IX, "Control of Special Processes," was self-revealed for the failure to install the torus coating under suitable controlled conditions. Specifically, inadequate qua
Region: III | Duane Arnold | 10037 | 09/30/2013 11/14/2013 | 2013004-03 | Self - Revealed | VIO | Mitigating Systems | White | RCIC Turbine Overspeed Trip | EA Case: 2013223 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding and apparent violation of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3, Condition B was self-revealed for the licensee's failure to perform an immediate operability determination (IOD) in accordance with licensee pr
Region: III | Duane Arnold | 10036 | 09/05/2013 09/30/2013 | 2013010-01 | Self - Revealed | VIO | Mitigating Systems | White | 'A' Standby Diesel Generator Lube Oil Heat Exchanger Gasket Failure | EA Case: 2013182 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71111.12 | A finding and violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to prescribe a work instruction of a type appropriate to the circumstances for the re-assembly of the 'A
Region: III | Duane Arnold | 9703 | 04/17/2009 05/01/2009 | 2009009-01 | NRC | VIO | Mitigating Systems | White | FAILURE TO PROMPTLY IDENTIFY AND CORRECT A SIGNIFICANT CONDITION AVERSE TO QUALITY ASSOCIATED WITH THE 'B' EDG. | EA Case: 2009083 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | NONE | The inspectors identified a finding and associated apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to identify and correct the cause of 'B' EDG overspeed trip alarms, a condition
Region: III | Duane Arnold | 9652 | 12/05/2006 01/19/2007 | 2006009-01 | NRC | VIO | Emergency Preparedness | White | Failure of the licensee's exercise critique process | EA Case: 2007017 |  | TE?: N | 05000331 Duane Arnold |  | 71114.01 | The inspectors identified a finding when the licensee's critique presented to the NRC on October 19, 2006, failed to properly identify a weakness that was associated with a risk significant planning standard. The finding was more than minor because it
Region: II | Farley | 11069 | 12/31/2013 02/14/2014 | 2013005-01 | Licensee - Identified | VIO | Emergency Preparedness | White | Calculation Error Results in Significantly non-Conservative EAL Threshold Values | EA Case: 2014017 |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | White: A finding and associated violation of 10 CFR 50.54(q)(2) was identified by the licensee for the failure to follow and maintain the effectiveness of emergency plans which use a standard emergency classification and action level scheme. Specifically,
Region: II | Farley | 10525 | 05/02/2009 05/18/2009 | 2009502-02 | NRC | VIO | Emergency Preparedness | White | Failure to Establish Effective Means of Providing Early Notification (Inaccurate Tone Alert Radios Addresses) | EA Case: 2009103 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | NONE | An AV of 10 CFR 50.47(b)(5) was identified for a failure to maintain the means to provide alert and notification and clear instruction to all of the population within the plume exposure pathway emergency planning zone (EPZ). Specifically, in February 20
Region: II | Farley | 10505 | 08/01/2008 07/16/2008 | 2008011-01 | NRC | AV | Mitigating Systems | White | Inadequate Work Instructions Cause 1B EDG Exhaust Header Failure. | EA Case: 2008192 |  | TE?: N | 05000348 Farley 1 |  | NONE | A self-revealing finding and Apparent Violation of Technical Specification 5.4.1 was identified for inadequate work instructions which resulted in the 1B Emergency Diesel Generator (EDG) exhaust header not being installed in accordance with the vendor's i
Region: II | Farley | 10484 | 07/16/2007 08/17/2007 | 2007008-01 | NRC | FIN | Mitigating Systems | White | Parallel Performance Indicator White Finding |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 95001 | The NRC identified significant weakness regarding historical evaluations for safety-related breaker failures and the thoroughness of design modification reviews for the installation of new breakers. In accordance with NRC Inspection Manual Chapter (MC)
Region: II | Farley | 10486 | 07/03/2007 08/02/2007 | 2007009-01 | NRC | VIO | Mitigating Systems | Yellow | Failure to Promptly Identify and Correct a Condition Adverse to Quality for RHR Pump 2A Containment Sump Suction Valve | EA Case: 2007173 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000364 Farley 2 |  | 93812 | The inspectors identified an apparent violation (AV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly identify and correct a condition adverse to quality (CAQ) which resulted in a Unit 2 residual heat remo
Region: III | Fermi | 23165 | 02/24/2017 02/24/2017 | 2017009-01 | NRC | NOV | Emergency Preparedness | White | Failure to Maintain the Effectiveness of the Site’s Emergency Plan. | EA Case: EA-17-012 | NPP | TE?: N | 05000341 Fermi 2 |  | 71124.06 | An NRC identified finding preliminarily determined to be of low to moderate safety significance (White), and an associated apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2) and 10 CFR 50.47(b)(9) was identified for the
Region: IV | Fort Calhoun | 13123 | 10/16/2014 11/25/2014 | 2013018-01 | NRC | VIO | Mitigating Systems | White | Failure to Correctly Translate Design Requirements into Installed Plant Configuration | EA Case: 2014187 |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that applicable regulatory requirements and the design bases, as defined in 10 CFR 50.2 and as specified in th
Region: IV | Fort Calhoun | 13105 | 03/14/2014 04/25/2014 | 2013017-01 | NRC | VIO | Mitigating Systems | White | Failure to Ensure Tornado Missile Protection for Site Components | EA Case: 2013222 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified multiple examples of a violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," involving the failure to establish applicable tornado missile protection design requirements for components needed to ensure the capability to
Region: IV | Fort Calhoun | 12826 | 04/13/2012 04/10/2012 | 2012010-01 | NRC | VIO | Initiating Events | Red | Failure to Ensure that the 480 Vac Electrical Power Distribution System Design Requirements were Implemented and Maintained | EA Case: 2012023 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | NONE | The failure to ensure that the 480 Vac electrical power distribution system design requirements were properly implemented and maintained through proper maintenance, modification, and design activities led to a catastrophic fire in a switchgear impacting t
Region: IV | Fort Calhoun | 12805 | 12/16/2011 03/12/2012 | 2011014-01 | NRC | AV | Initiating Events | Red | Failure to Ensure the 480 Vac Electrical Power Distribution System Design Requirements were Implemented and Maintained | EA Case: 2012023 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 93812 | DRAFT The failure to ensure that the 480 Vac electrical power distribution system design requirements were properly implemented and maintained through proper maintenance, modification, and design activities led to a catastrophic fire in a switchgear im
Region: IV | Fort Calhoun | 12345 | 04/15/2011 05/06/2011 | 2011007-01 | NRC | VIO | Mitigating Systems | White | Failure to Correct a Degraded Contactor in the Reactor Protective System | EA Case: 2011025 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71152 | During an NRC inspection conducted from January 17 through April 15, 2011, one violation of NRC requirements was identified. In accordance with the NRC Enforcement Policy, the violation is listed below: Title 10 of the Code of Federal Regulations (10 CFR
Region: IV | Fort Calhoun | 12301 | 06/21/2010 07/15/2010 | 2010007-01 | NRC | VIO | Mitigating Systems | Yellow | Failure to Maintain External Flood Procedures | EA Case: 2010084 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | Yellow. The inspectors identified an apparent violation of Technical Specification 5.8.1.a, "Procedures," for failure to establish and maintain procedures that protect the intake structure and auxiliary building during external flooding events. The inspec
Region: IV | Fort Calhoun | 11657 | 08/31/2007 10/10/2007 | 2007011-02 | NRC | VIO | Mitigating Systems | White | Inadequate Emergency Diesel Generator Corrective Measures | EA Case: 2007194 | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified an apparent violation of 10 CFR 50, Appendix B, Criterion XVI (Corrective Actions), with two examples, for the failure to: 1) treat the February 14, 2007 emergency diesel generator failure as a significant condition adverse to qu
Region: IV | Fort Calhoun | 12184 | 08/31/2007 10/10/2007 | 2007011-03 | NRC | VIO | Mitigating Systems | White | Failure to Provide Procedure for Safety Related Maintenance Activity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified an apparent violation of Technical Specification 5.8.1.a (Procedures) because craftsmen used an unapproved wet lubricant on the emergency diesel generator field flash relay auxiliary contact sliding mechanisms without a procedure
Region: IV | Fort Calhoun | 11651 | 12/21/2006 03/02/2007 | 2006018-01 | NRC | VIO | Mitigating Systems | White | Containment Spray Train 'B' Inoperable in Excess of Technical Specifications due to Failure to Perform Adequate Maintenance and Testing | EA Case: 2007047 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | A violation of 10 CFR Part 50, Appendix B, Criterion V, was identified for the OPPD's failure to perform adequate maintenance and testing on containment spray header isolation Valve HCV-345. This issue was self revealed on September 13, 2006, when reactor
Region: I | Ginna | 14661 | 06/30/2016 08/18/2016 | 2016002-01 | NRC | VIO | Emergency Preparedness | White | Incorrect Emergency Action Level Table | EA Case: 2016128 | H.3 Change Management | TE?: N | 05000244 Ginna |  | 71114.04 | (Initial Entry) Preliminary White finding issued under inspection report 2016002 (ML16232A051). Exelon identified that they had inadvertently made a change to the Ginna Emergency Plan. The NRC determined that this error is a preliminary White finding unde
Region: I | Ginna | 14602 | 12/31/2013 02/14/2014 | 2013005-01 | NRC | VIO | Mitigating Systems | White | Failure to Identify and Correct Non-Hydrostatically Sealed Penetrations into Battery Room 'B' | EA Case: 2013247 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.01 | The inspectors identified a finding associated with an apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," for Constellation Energy Nuclear Group, LLC (CENG) staff's failure to ass
Region: I | Ginna | 33694 | 10/07/2009 11/12/2009 | 2009008-01 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Preclude Recurrence of a Significant Condition Adverse to Quality Associated with the Turbine-Driven Auxiliary Feedwater Pump Governor Control Valve | EA Case: 2009249 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000244 Ginna |  | 93812 | A self-revealing apparent violation (AV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure to preclude recurrence of a significant condition adverse to quality (SCAQ) associated with the turbine-driven auxiliary
Region: I | Ginna | 33676 | 03/31/2009 05/04/2009 | 2009002-01 | Self - Revealed | VIO | Mitigating Systems | White | Failure to Properly Lubricate Governor Linkage | EA Case: 2009045 | H.3(b) Work Activity Coordination | TE?: N | 05000244 Ginna |  | 71152 | The inspectors identified an violation of Technical Specification 5.4.1.a, "Procedures," for the failure of the licensee to implement an effective preventive maintenance (PM) program for the turbine-driven auxiliary feedwater (TDAFW) pump governor link
Region: IV | Grand Gulf | 23945 | 01/01/2017 12/06/2017 | 2017013-03 | NRC | FIN | Initiating Events | White | Parallel White Unplanned Scrams per 7000 Critical Hours PI Finding | EA Case: EA-17-184 |  | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | The NRC assigned a parallel performance indicator inspection finding with low-to-moderate safety significance (White) for the failure to adequately evaluate the causes and implement corrective actions sufficient to address the root and contributing causes
Region: II | Harris | 15254 | 06/30/2012 07/16/2012 | 2012007-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain an Adequate EOF to Support Emergency Response | EA Case: 2012132 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71152 | White: The inspectors identified multiple examples of a Violation (Vio) of 10 CFR 50.54(q) for the lack of facility oversight and control, coupled with component failures and removal of the Emergency Operations Facility (EOF) ventilation system from servi
Region: II | Hatch | 17714 | 12/31/2009 02/12/2010 | 2009005-02 | Self - Revealed | VIO | Mitigating Systems | White | Failure to establish appropriate preventative maintenance for electrolytic capacitors | EA Case: 2010009 | P.2(b) Implementing Operating Experience | TE?: N | 05000366 Hatch 2 |  | 71111.12 | -TBD A self-revealing apparent violation (AV) of TS 5.4, Procedures, was identified for failure to establish and perform preventive maintenance activities to replace electrolytic capacitors prior to their failure, specifically the electrolytic capacitors
Region: II | Hatch | 17687 | 03/10/2009 03/13/2009 | 2008009-01 | Self - Revealed | VIO | Mitigating Systems | White | 1B EDG Coupling Failure | EA Case: 2009054 |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | NONE | TBD. A self-revealing apparent violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for failure to promptly identify and correct a condition adverse to quality. Since 1988, the licensee had observed cracks in the glands of
Region: I | Hope Creek | 24392 | 09/30/2016 11/14/2016 | 2016003-01 | NRC | NOV | Mitigating Systems | White | Inadequate Implementation of Adverse Condition Monitoring Actions for the High Pressure Coolant Injection System | EA Case: 2016184 | H.14 - Conservative Bias | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing preliminary White finding and apparent violation (AV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," and Technical Specification (TS) 3.5.1.c, "Emergency C
Region: III | Kewaunee | 32969 | 02/14/2013 03/04/2013 | 2013007-01 | NRC | FIN | Mitigating Systems | White | Failure to Perform Announced Fire Drills in Accordance With Fire Protection Program Plan |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 71111.05A | EA-12-266 The NRC staff identified a preliminary finding of low-to-moderate safety significance for the licensee's failure to implement and maintain in effect all provisions of the approved Fire Protection Program as described in the licensee's Fire Prot
Region: III | Kewaunee | 32954 | 12/17/2012 01/24/2013 | 2012503-01 | NRC | VIO | Emergency Preparedness | White | Emergency Preparedness Degraded Emergency Action Level Scheme | EA Case: 2012272 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71114.05 | A finding having a significance of White with a violation of 10 CFR 50.54(q)(2) associated with risk-significant planning standard 10 CFR 50.47(b)(4) was identified by the NRC for the licensee's failure to follow and maintain the effectiveness of its emer
Region: III | Kewaunee | 31733 | 08/29/2008 09/23/2008 | 2008503-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain a Standard EAL Scheme | EA Case: 2008223 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71114.04 | An apparent violation was identified by the inspector for failure to follow and maintain in effect emergency plans which use a standard emergency classification and action level scheme. Specifically, the licensee's emergency plan Alert emergency action le
Region: III | Kewaunee | 30770 | 01/31/2007 03/02/2007 | 2007007-01 | NRC | VIO | Mitigating Systems | Yellow | Failure to Evaluate Operability of the "A" EDG When a Fuel Oil Leak Was Identified | EA Case: 2007058 | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71153 | A finding that was preliminarily determined to be of substantial safety significance (Yellow), and an associated apparent violation of Technical Specification 6.8, "Procedures," was identified for a fuel oil leak on the "A" emergency diesel generator (EDG
Region: III | LaSalle | 33880 | 09/30/2013 11/15/2013 | 2013004-01 | Self - Revealed | FIN | Initiating Events | White | Failure to Follow Procedures Led to Scram with Complications |  | H.14 Conservative Bias | TE?: N | 05000374 LaSalle 2 |  | NONE | A self-revealed finding was identified for the licensee's failure to follow procedure LOP-CW-10, "Dewatering the Circulating Water System," Revision 32, on Unit 2. Specifically, on April 25, 2013, while operating at 56 percent power, operators appointed t
Region: I | Limerick | 35965 | 09/30/2011 11/04/2011 | 2011004-04 | NRC | VIO | Mitigating Systems | White | Failure of Feedwater MOV Resulting in RCIC Inoperability for Longer than Allowed by Technical Specifications (Final Significance Determination) | EA Case: 2011221 | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000353 Limerick 2 |  | NONE | A self-revealing White finding and violation of Technical Specification (TS) 3.7.3, "Reactor Core Isolation Cooling System and TS 3.6.3, "Primary Containment Isolation Valves," was identified. The inspectors determined that the failure by Exelon to ensure
Region: II | McGuire | 36827 | 08/20/2008 10/27/2008 | 2008009-01 | NRC | VIO | Mitigating Systems | White | Failure to Take Adequate Corrective Action for Implementation of Safety-Related RN Strainer Backwash | EA Case: 2008220 |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71153 | 10 CFR 50 Appendix B Criterion XVI, Corrective Action, states that measures shall be established to assure that conditions adverse to quality, such as deficiencies, deviations, and non-conformances are promptly identified and corrected. In the case of s
Region: I | Millstone | 23692 | 07/21/2014 08/28/2014 | 2014008-02 | NRC | VIO | Mitigating Systems | White | Failure to Identify and Promptly Correct a Condition Adverse to Quality | EA Case: 2014092 | H.13 Consistent Process | TE?: N | 05000423 Millstone 3 |  | 93812 | The inspection team identified a self-revealing apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," involving Dominion's failure to promptly identify and correct a condition advers
Region: I | Millstone | 23608 | 04/29/2011 05/27/2011 | 2011008-01 | Self - Revealed | VIO | Initiating Events | White | VIO 05000336/2011008-01, Multiple Examples of Procedural Violations and Inadequate Procedures Relating to Control Room Crew Performance During a Plant Transient. | EA Case: 2011047 | H.1(a) Systematic Process for Decisions | TE?: N | 05000336 Millstone 2 |  | 93812 | White: A self-revealing violation (VIO) of low to moderate safety significance (White) was identified involving the failure of Millstone personnel to carry out their assigned roles and responsibilities and inadequate reactivity management during main turb
Region: III | Monticello | 27065 | 08/31/2016 09/15/2016 | 2016010-01 | NRC | VIO | Mitigating Systems | White | FAILURE TO PLAN AND PERFORM MAINTENANCE TO CORRECT HPCI OIL LEAK. | EA Case: 2016175 | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.15 | A self-revealing finding preliminarily determined to be of low to moderate safety significance (White), and an associated apparent violation of Technical Specification 5.4.1.a, were identified for the licensee's failure to plan and perform maintenance
Region: III | Monticello | 26749 | 05/15/2013 06/11/2013 | 2013008-01 | NRC | VIO | Mitigating Systems | Yellow | FAILURE TO MAINTAIN AN ADEQUATE FLOOD PLAN CONSISTENT WITH DESIGN REQUIREMENTS. | EA Case: 2013096 | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a Yellow finding with substantial safety significance and associated violation of Technical Specification 5.4.1 for the licensee's failure to maintain a flood plan to protect the site from external flooding events. Specifically,
Region: I | Nine Mile Point | 31703 | 10/16/2009 11/24/2009 | 2009009-02 | NRC | FIN | Mitigating Systems | White | Parallel Performance Indicator White Finding |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 95001 | The NRC identified a parallel White Performance Indicator (PI) inspection finding involving significant weaknesses identified in Constellation's causal evaluation and corrective actions for a White Cooling Water Systems PI. The inspectors identified si
Region: I | Nine Mile Point | 31644 | 01/18/2007 02/13/2007 | 2006011-01 | NRC | VIO | Mitigating Systems | White | Failure to Ensure Integrity of Unit 1 Examinations and Tests | EA Case: 2007001 | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.11B | White. A violation of 10 CFR 55.49, "Integrity of Examinations and Tests," was identified, concerning an apparent compromise of the 2005 and the 2006 annual operating exams at Unit 1. NRC inspectors identified practices that collectively had the impact of
Region: II | North Anna | 27330 | 12/31/2011 02/13/2012 | 2011005-02 | NRC | VIO | Mitigating Systems | White | Failure to Provide Adequate Guidance for Installation of 2H EDG Jacket Water Cooling Inlet Jumper | EA Case: 2012033 | P.2(b) Implementing Operating Experience | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152 | A self-revealing Apparent Violation of Technical Specifications 5.4.1.a was identified for the licensee's failure to establish and maintain emergency diesel generator (EDG) maintenance procedures as required by Regulatory Guide 1.33, Appendix A, Section 9
Region: II | Oconee | 36576 | 06/27/2014 06/26/2014 | 2014011-01 | NRC | VIO | Initiating Events | White | Failure to Identify and Correct Weld Cracking in HPI Nozzle | EA Case: 2014091 | H.7 Documentation | TE?: N | 05000269 Oconee 1 |  | NONE | A White violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the licensee failed to identify a crack in a weld located in the Unit 1 High Pressure Injection (HPI) system. In 2004, a procedure was developed for a
Region: II | Oconee | 36210 | 09/09/2011 09/07/2011 | 2011017-01 | NRC | VIO | Mitigating Systems | Yellow | Pressurizer Heater Breaker Installation That Would not have Functioned During Certain SSF-Credited Events | EA Case: 2011226 |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 93812 | A licensee-identified potentially greater than Green apparent violation (AV) of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified when the licensee failed to maintain design control of the Standby Shutdown Facility (SSF). Because the sa
Region: II | Oconee | 36175 | 03/30/2010 06/09/2010 | 2010007-01 | NRC | VIO | Mitigating Systems | White | Failure to promptly identify and correct an adverse condition affecting operability of the Unit 2 and Unit 3 standby shutdown facility | EA Case: 2010094 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | A NRC-identified White violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to promptly identify and correct a condition adverse to quality associated with a degraded condition on Unit 2 and Unit
Region: II | Oconee | 36177 | 03/30/2010 06/09/2010 | 2010007-03 | NRC | VIO | Mitigating Systems | Yellow | SSF reactor coolant makeup subsystem inoperable for greater than allowed by technical speciafications | EA Case: 2010094 |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | A self-revealing Yellow violation of Technical Specification 3.10.1 was identified when the Standby Shutdown Facility (SSF) Reactor Coolant Makeup (RCM) subsystem letdown line failed to pass the required flow. As a result, the SSF RCM subsystem was render
Region: II | Oconee | 36152 | 11/19/2008 11/21/2008 | 2008010-01 | Self - Revealed | FIN | Initiating Events | White | Failure to Implement an Adequate AVR Maintenance Procedure [EA-08-324] |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 |  | 71153 | A White Finding was identified for the failure to implement a main generator automatic voltage regulator (AVR) maintenance procedure that met the standards/expectations of Nuclear System Directive (NSD) 703, Administrative Instructions for Technical Proce
Region: II | Oconee | 36124 | 11/17/2006 02/13/2007 | 2007006-01 | Licensee - Identified | VIO | Mitigating Systems | White | Inadequate Foreign Material Exclusion Controls for the Unit 3, A and B Train Reactor Building Emergency Sump Suction Lines | EA Case: 2006294 |  | TE?: N | 05000287 Oconee 3 |  | NONE | Violation of Technical Specification 5.4.1, Procedures, and Section 9.e of referenced Regulatory Guide 1.33 for the failure to comply with Nuclear System Directive (NSD) 104, Material Condition/Housekeeping, Cleanliness/Foreign Material Exclusion and Seis
Region: II | Oconee | 36120 | 08/31/2006 11/22/2006 | 2006017-01 | NRC | VIO | Mitigating Systems | White | Inadequate Procedural Controls and Risk Management Associated with Breach in SSF Flood Protection Barrier | EA Case: 2006199 | H.3(a) Work Planning | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.06 | Contrary to Technical Specification 5.4.1 and 10 CFR 50.65(a)(4), the licensee failed to use adequate procedures to control maintenance activities (removal of a CO2 access cover from SSF flood barrier to facilitate installation of temporary electrical pow
Region: I | Oyster Creek | 35075 | 12/31/2016 01/26/2017 | 2016004-01 | NRC | AV | Mitigating Systems | White | 'E' EMRV Failure to Stroke Due to Incorrect Reassembly | EA Case: 16-241 | H.8 - Procedure Adherence | TE?: N | 05000219 Oyster Creek |  | 71152 | (Initial Entry) The NRC identified a preliminary White finding and associated apparent violation of Technical Specification 6.8.1, "Procedures and Programs," and Technical Specification 3.4.B, "Automatic Depressurization System," because Exelon faile
Region: I | Oyster Creek | 35068 | 03/31/2016 05/12/2016 | 2016001-03 | NRC | VIO | Mitigating Systems | White | Inadequate Instructions for the Flexible Coupling Hose Preventative Maintenance Resulting in an Inoperable Emergency Diesel Generator |  |  | TE?: N | 05000219 Oyster Creek |  | 71152 | (Initial Entry) The inspectors identified a preliminary White finding and associated apparent violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Exelon did not appropriately prescribe instructions or proced
Region: I | Oyster Creek | 35052 | 12/31/2014 02/11/2015 | 2014005-02 | NRC | VIO | Mitigating Systems | White | Inadequate Review of Change in Maintenance Process Results in Inoperable Emergency Diesel Generator |  |  | TE?: N | 05000219 Oyster Creek |  | 71152 | (Initial Entry) The inspectors identified a preliminary White finding and an associated apparent violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Exelon staff did not review the suitability of the application of a different ma
Region: I | Oyster Creek | 34477 | 12/31/2014 02/11/2015 | 2014009-01 | NRC | VIO | Mitigating Systems | Yellow | Inadequate Application of Materials, Parts, Equipment, and Processes Associated with the Electromatic Relief Valves |  |  | TE?: N | 05000219 Oyster Creek |  | 71152 | (Initial Entry) The NRC identified a preliminary Yellow finding and associated apparent violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," and Technical Specification 3.4.B, "Automatic Depressurization System," because the station did n
Region: III | Palisades | 37971 | 10/31/2014 02/23/2015 | 2015007-01 | NRC | VIO | Occupational Radiation Safety | White | Failure to Monitor the Highest Exposed Part of the Compartment When Using EDEX | EA Case: 2014168 | H.3 Change Management | TE?: N | 05000255 Palisades |  | NONE
Region: III | Palisades | 37946 | 10/30/2014 12/02/2014 | 2014010-01 | NRC | VIO | Occupational Radiation Safety | White | Failure to Monitor the Highest Exposed Part of the Compartment When Using EDEX | EA Case: 2014168 | H.3 Change Management | TE?: N | 05000255 Palisades |  | 71124.04 | The NRC identified one finding and two violations of NRC requirements associated with the replacement of Control Rod Drive (CRD) housings between February 6 and March 8, 2014. Specifically, the inspectors identified a violation of Title 10 of the Code of
Region: III | Palisades | 37799 | 10/28/2011 11/29/2011 | 2011014-02 | NRC | VIO | Initiating Events | Yellow | Failure to Have Adequate Work Instructions for Work Performed on Panel D11-2. | EA Case: 2011243 | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 93812 | A preliminary finding of substantial safety significance (Yellow) and an associated apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed on
Region: III | Palisades | 37795 | 10/28/2011 11/29/2011 | 2011016-01 | NRC | VIO | Initiating Events | White | Failure to Prevent Recurrence of a Significant Condition Adverse to Quality concerning Service Water Pump Couplings. | EA Case: 2011041 | P.2(b) Implementing Operating Experience | TE?: N | 05000255 Palisades |  | 93812 | A self revealed finding with a preliminary low to moderate safety significance and two associated apparent violations of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," and Criterion III, "Design Control," was self-revealed on August 9, 2
Region: III | Palisades | 37787 | 10/05/2011 10/28/2011 | 2011013-01 | NRC | VIO | Mitigating Systems | White | Improper Lubrication of Turbine Driven Auxiliary Feedwater Pump Linkages | EA Case: 2011227 | H.1(a) Systematic Process for Decisions | TE?: N | 05000255 Palisades |  | 71153 | A self-revealed finding of low to moderate safety significance and associated Apparent Violation (AV) of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," occurred for the licensee's failure to follow procedures for lubricat
Region: III | Palisades | 37686 | 11/09/2009 12/09/2009 | 2009008-01 | NRC | VIO | Initiating Events | White | Loss of Spent Fuel Pool Neutron Absorption Capability | EA Case: 2009269 |  | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding and associated violation of the Design Feature for fuel storage in Technical Specification 4.3.1 due to loss of neutron absorption capability in the spent fuel pool (SFP) racks. Over the life of the facility, the neutro
Region: III | Palisades | 37646 | 11/19/2008 12/19/2008 | 2008011-01 | NRC | VIO | Occupational Radiation Safety | White | Failure To Assess Dose To Three Workers After A Known Change In Radiological Conditions Near The Spent Fuel Pool | EA Case: 2008322 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 7112101 | The inspector identified a finding and associated Apparent Violation of 10 CFR 20.1501 for the failure to perform adequate radiological evaluations necessary to properly quantify the radiological hazards to assess the dose from the conditions that were id
Region: IV | Palo Verde | 38392 | 11/30/2006 12/06/2006 | 2006012-01 | NRC | VIO | Mitigating Systems | White | FAILURE TO ESTABLISH APPROPRIATE INSTRUCTIONS | EA Case: 2006296 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000530 Palo Verde 3 |  | 93812 | The team identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," states, in part, that activities affecting quality shall be prescribed by documented instructions, procedures, or drawings, of
Region: IV | Palo Verde | 38393 | 11/30/2006 12/06/2006 | 2006012-02 | NRC | VIO | Mitigating Systems | White | FAILURE TO IDENTIFY AND CORRECT A CONDITION ADVERSE TO QUALITY | EA Case: 2006296 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000530 Palo Verde 3 |  | 93812 | The team identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," states, in part, that for significant conditions adverse to quality, measures shall assure that the cause of the condition is determined and corre
Region: I | Peach Bottom | 125124 | 09/30/2018 06/27/2019 | 2018013-01 | NRC | NOV | Mitigating Systems | White | Inadequate Corrective Actions Result in the Failure of the E-3 Emergency Diesel Generator | EA Case: EA-18-107 | H.11 - Challenge the Unknown | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 | Equipment Performance | 95001 | The inspectors identified a self-revealing preliminary White finding associated with an apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” because Exelon did not perform adequate corrective actions on the E-3 EDG scaveng
Region: III | Perry | 16602 | 04/27/2017 06/05/2017 | 2017009-01 | NRC | NOV | Mitigating Systems | White | Division 2 Diesel Generator Failure to Start due to a Failed Diode in the 125 VDC Control Power Circuit | EA Case: 2017043 | NPP | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding preliminarily determined to be of low to moderate safety significance (White), and an associated apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Criterion III, "Design Control," for the li
Region: III | Perry | 16242 | 09/14/2012 12/28/2012 | 2012009-01 | NRC | FIN | Occupational Radiation Safety | White | Parallel White PI Finding (EA 2012-228) |  |  | TE?: N | 05000440 Perry 1 |  | 95002 | The inspectors identified a White parallel PI inspection finding for the failure to provide assurance that the corrective actions for performance issues associated with the Occupational Exposure Control Effectiveness PI were sufficient to address the root
Region: III | Perry | 16191 | 05/25/2011 06/30/2011 | 2011013-02 | NRC | VIO | Occupational Radiation Safety | White | The Licensee Failed to Appropriately Identify and Assess the Radiological Hazards when retracting a Source Range Monitor. (Section 4OA5.7) | EA Case: 2011148 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 93812 | The NRC identified a finding and three apparent violations of NRC requirements associated with the removal of a source range monitor from the reactor vessel. Specifically, the inspectors identified an apparent violation of Title 10 of the Code of Federal
Region: I | Pilgrim | 17884 | 03/20/2015 05/27/2015 | 2015007-02 | NRC | VIO | Mitigating Systems | White | Failure to Identify, Evaluate, and Correct 'A' SRV Failure to Open Upon Manual Actuation | EA Case: 2015081 | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 93812 | A self-revealing preliminary White findIing and Violation (VIO) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," and Technical Specification (TS) 3.5.E, "Automatic Depressurization System," was identified for the failure to identify, evaluate
Region: I | Pilgrim | 17876 | 07/01/2014 01/26/2015 | 2014008-04 | NRC | FIN | Initiating Events | White | Parallel White Unplanned Scrams with Complications PI Finding |  |  | TE?: N | 05000293 Pilgrim 1 |  | 95002 | The NRC assigned two parallel White PI inspection findings involving a significant weakness identified in Entergy's causal evaluation and corrective actions for the White Unplanned Scrams with Complications PI. In accordance with IP 95002 and NRC IMC 0
Region: I | Pilgrim | 17875 | 01/01/2014 01/26/2015 | 2014008-03 | NRC | FIN | Initiating Events | White | Parallel White Unplanned Scrams per 7000 Critical Hours PI Finding |  |  | TE?: N | 05000293 Pilgrim 1 |  | 95002 | The NRC assigned a parallel White PI inspection findings involving a significant weakness identified in Entergy's causal evaluation and corrective actions for the White Unplanned Scrams per 7000 Critical Hours PIs. In accordance with IP 95002 and NRC I
Region: I | Pilgrim | 17393 | 07/20/2011 09/01/2011 | 2011012-01 | Self - Revealed | VIO | Initiating Events | White | Failure to Implement Conduct of Operations and Reactivity Control Procedures during Reactor Startup | EA Case: 2011174 | H.4(a) Human Error Prevention | TE?: N | 05000293 Pilgrim 1 |  | 93812 | A self-revealing finding was identified involving the failure of Pilgrim personnel to implement conduct of operations and reactivity control standards and procedures during a reactor startup, which contributed to an unrecognized subcriticality followed by
Region: III | Point Beach | 20686 | 03/31/2013 05/13/2013 | 2013002-10 | NRC | VIO | Mitigating Systems | White | Failure to Establish an Adequate Procedure to Implement Wave Run-Up Design Features | EA Case: 2013125 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding and an apparent violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's lack of procedural requirements to appropriately implement external flooding wave
Region: III | Point Beach | 20603 | 10/29/2012 01/02/2013 | 2012010-01 | NRC | VIO | Mitigating Systems | White | Failure To Have Adequate Work Instructions And Procedures For Work Performed On The Turbine-Driven Auxiliary Feedwater Pump | EA Case: 2012220 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000266 Point Beach 1 |  | NONE | A finding of low to moderate safety significance and an associated Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed, in that, on November 8, 2011, the licensee failed to ensure that the work
Region: III | Point Beach | 20543 | 04/20/2012 06/01/2012 | 2012503-01 | NRC | VIO | Emergency Preparedness | White | Protective Action Recommendation Weakness | EA Case: 2012106 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71114.01 | An NRC identified finding with a preliminary low to moderate safety significance and one associated apparent violation of 10 CFR 50.47(b)(10) for failure to develop and put into place guidelines for the choice of protective actions during an emergency tha
Region: III | Prairie Island | 22134 | 12/18/2012 01/24/2013 | 2012504-01 | NRC | VIO | Emergency Preparedness | White | Emergency Preparedness Degraded Emergency Action Level Scheme | EA Case: 2012273 | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 |  | 71114.05 | Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2) requires that a holder of a nuclear power reactor operating license follow and maintain the effectiveness of an emergency plan that meets the requirements in Part 50, Appendix E and the plan
Region: III | Prairie Island | 21865 | 05/20/2011 06/09/2011 | 2011010-01 | NRC | VIO | Mitigating Systems | White | Failure to Ensure that the Train A and Train B DC Electrical Power Subsystems Remained Operable in Modes 1 through 4 (Section 4OA5.1) | EA Case: 2011110 |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | An apparent violation of Technical Specification (TS) 3.8.4 was identified by the inspectors due to the licensee's failure to maintain the train A and train B direct current electrical power subsystems operable while operating the reactor in Modes 1 throu
Region: III | Prairie Island | 21834 | 07/09/2009 08/05/2009 | 2009010-02 | NRC | VIO | Mitigating Systems | White | Failure to Ensure Design Measures Were Appropriately Established for The Unit 2 Component Cooling Water System | EA Case: 2009167 | H.1(a) Systematic Process for Decisions | TE?: N | 05000306 Prairie Island 2 |  | NONE | An inspector identified apparent violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified due to the licensee's failure to establish design control measures to ensure that the design basis for the Unit 2 CCW system was corr
Region: III | Prairie Island | 21744 | 01/21/2009 02/10/2009 | 2008009-01 | NRC | VIO | Public Radiation Safety | White | Radioactive Material Shipment Package radiation Levels Exceeded | EA Case: 2008349 | H.3(a) Work Planning | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112202 | A self-revealing finding with an apparent violation of regulatory requirements was identified involving a failure of the licensee to properly radiologically characterize, prepare, and ship a package containing radioactive material in a manner that assured
Region: III | Prairie Island | 21724 | 10/06/2008 11/07/2008 | 2008008-01 | Self - Revealed | VIO | Mitigating Systems | White | 11 TURBINE-DRIVEN AUXILIARY FEEDWATER PUMP INOPERABLE DUE TO FAILURE TO CONTROL POSITION OF VALVE THAT COULD ISOLATE THE DISCHARGE PRESSURE SWITCH | EA Case: 2008272 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 |  | 93812 | A self-revealing apparent violation of Technical Specifications was associated with the licensee's failure to adequately control the position of a valve that could isolate the 11 TDAFWP's discharge pressure switch. Because of the valve being closed, the 1
Region: III | Quad Cities | 26028 | 06/29/2006 06/29/2006 | 2006014-01 | NRC | VIO | Mitigating Systems | White | FAILURE TO ESTABLISH MEASURES TO ENSURE THAT THE UNIT 1 ERV ACTUATORS REMAINED SUITABLE FOR OPERATION WHILE OPERATING AT EPU POWER LEVELS | EA Case: 06 112 |  | TE?: N | 05000254 Quad Cities 1 |  | NONE | Title 10 CFR 50, Appendix B, Criterion III, Design Control, requires, in part, that measures be established for the selection and review for suitability of application of materials, parts, equipment, and processes that are essential to the safety-related
Region: III | Quad Cities | 26026 | 05/23/2006 05/30/2006 | 2006012-01 | NRC | AV | Mitigating Systems | White | FAILURE TO ESTABLISH MEASURES TO ENSURE THAT THE UNIT 1 ERV ACTUATORS REMAINED SUITABLE FOR OPERATION WHILE OPERATING AT EPU POWER LEVELS | EA Case: 06 112 |  | TE?: N | 05000254 Quad Cities 1 |  | 71152 | An apparent violation (AV) of 10 CFR 50, Appendix B, Criterion III, Design Control, having a preliminary low to moderate safety significance (White), was identified in January 2006 following the discovery that two of the Unit 1 electromatic relief valves
Region: IV | River Bend | 30623 | 06/29/2015 07/07/2015 | 2015009-05 | NRC | VIO | Mitigating Systems | White | Failure of the Plant-Referenced Simulator to Demonstrate Expected Plant Response | EA Case: 2015043 | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified an apparent violation of 10 CFR 55.46(c)(1), "Plant-Referenced Simulators," for the licensee's failure to maintain the simulator so it would demonstrate expected plant response to operator input and to normal, transient, and accident c
Region: II | Robinson | 32648 | 06/25/2013 07/01/2013 | 2013008-01 | NRC | VIO | Mitigating Systems | White | Failure to Perform Adequate Preventative Maintenance on the DSDG In accordance with Vendor Guidelines | EA Case: 2013129 |  | TE?: N | 05000261 Robinson 2 |  | 71111.12 | 10 CFR 50.63 (c)(2) states, in part, that the alternate AC power source, as defined in section 50.2, will constitute acceptable capability to withstand station blackout provided an analysis is performed which demonstrates that the plant has this capabilit
Region: II | Robinson | 31536 | 12/31/2010 12/27/2010 | 2010013-01 | NRC | VIO | Mitigating Systems | White | Failure to Comply with Conduct of Operations Procedure | EA Case: 2010257 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000261 Robinson 2 |  | 71153 | The inspectors identified a problem associated with the failure to implement requirements and standards of the fleet conduct of operations procedure, which involves an AV and four related violations for failure to meet Technical Specification (TS) 5.4.1,
Region: II | Robinson | 31510 | 08/26/2010 10/08/2010 | 2010006-02 | NRC | VIO | Mitigating Systems | White | Failure to Correct a Condition Adverse to Quality in "B" Emergency Diesel Generator Output Breaker 52/27B | EA Case: 2010205 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000261 Robinson 2 |  | 71152B | The NRC identified an apparent violation (AV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for the licensee's failure to promptly correct a condition adverse to quality involving the failure of the "B" Emergency Diesel Generator (EDG)
Region: II | Saint Lucie | 14943 | 12/19/2016 02/02/2017 | 2016012-01 | Self - Revealed | FIN | Initiating Events | White | Failure to Maintain Component Configuration Control Resulted in a Complicated Reactor Trip | EA Case: 17-013 | H.12 Avoid Complacency | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | (WHITE). A self-revealing finding was identified for the licensee's failure to maintain configuration control of the inadvertent energization lockout relay manual synchronization circuitry as required by licensee procedures MA-AA-100 and ADM-08.12, during
Region: II | Saint Lucie | 14829 | 09/24/2014 09/24/2014 | 2014009-01 | NRC | VIO | Mitigating Systems | White | Failure to Implement Measures to Ensure the Watertight Integrity of the Unit 1 Reactor Auxiliary Building | EA Case: 2014131 | H.6 Design Margins | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | Self-revealing apparent violations (AV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," and Criterion XVI, "Corrective Action," were identified for the failure to install internal flood barriers in conduits that penetrated the Unit 1 react
Region: II | Saint Lucie | 12701 | 12/03/2009 01/19/2010 | 2009006-06 | NRC | VIO | Mitigating Systems | Yellow | Failure to Identify and Correct a Condition Adverse to Quality | EA Case: 2009321 | H.1(a) Systematic Process for Decisions | TE?: N | 05000335 Saint Lucie 1 |  | 7111121 | The team identified an AV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to implement adequate corrective actions associated with the CCW air intrusion event that occurred in October, 2008. The corrective actions we
Region: IV | San Onofre | 10269 | 12/31/2012 09/20/2013 | 2012009-02 | NRC | AV | Initiating Events | White | Failure to Verify Adequacy of Thermal-Hydraulic and Flow-Induced Vibration Design for the Unit 3 Replacement Steam Generators |  |  | TE?: N | 05000362 San Onofre 3 |  | 92702 | The inspectors identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the thermal-hydraulic and flow-induced vibration design of the Unit 3 replacement steam generators, w
Region: IV | San Onofre | 9294 | 12/11/2008 12/19/2008 | 2008013-05 | NRC | VIO | Mitigating Systems | White | Failure to Establish Appropriate Instructions | EA Case: 2008296 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 93812 | The team identified a White violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to establish appropriate instructions for performing maintenance activities on safety-related 125 Vdc station
Region: I | Seabrook | 10674 | 04/17/2012 08/07/2012 | 2012504-01 | NRC | VIO | Emergency Preparedness | White | Final Significance Determination for a White Finding with Assessment Follow-up and Notice of Violation | EA Case: 2012093 |  | TE?: N | 05000443 Seabrook 1 |  | NONE | During an NRC inspection conducted at the NextEra Energy, LLC (NextEra) Seabrook Station (Seabrook) Unit 1 from April 17-19, 2012, and for which an exit meeting was held on April 19, 2012, a violation of NRC requirements was identified. In accordance with
Region: I | Seabrook | 10620 | 08/28/2009 09/01/2009 | 2009007-01 | NRC | VIO | Mitigating Systems | White | White Finding-The failure to establish adequate design control measures to modify a cooling water flange on the B emergency diesel generator (EDG) | EA Case: 2009145 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | 71111.18 | A self-revealing apparent violation of 10 CFR 50, Appendix B, Criterion III, Design Control was identified following a review of the identified causes for the failure of the B EDG jacket water cooling system on February 25, 2009. Specifically, NextEra's f
Region: I | Seabrook | 10619 | 03/31/2009 05/07/2009 | 2009002-01 | NRC | URI | Mitigating Systems | White | White Finding-B EDG Emergency Shutdown During Testing on 2/25/09 |  |  | TE?: N | 05000443 Seabrook 1 |  | NONE
Region: II | Sequoyah | 11910 | 03/08/2013 03/18/2013 | 2013404-01 | NRC | VIO | MISC | White | Failure to control vehicle access into the protected area | EA Case: 2013044 | H.1(a) Systematic Process for Decisions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | See Inspection Report 2013404 for Apparent Violation 2013407 for final significance determination 2013408 for 95001 and closure
Region: II | Sequoyah | 11909 | 02/28/2013 03/18/2013 | 2013010-01 | NRC | VIO | Mitigating Systems | White | Degraded Intake Pumping Station Flooding Barriers | EA Case: 2013045 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | The licensee failed to translate the design basis related to onsite flooding into specifications, drawings, procedures, and instructions. Specifically, Sequoyah's existing design documentation including current licensing documents and configuration contro
Region: II | Sequoyah | 11901 | 02/15/2013 03/12/2013 | 2013009-01 | NRC | VIO | Mitigating Systems | White | Inadequate abnormal operating procedure for flood mitigation strategy prior to installation of HESCO barriers. | EA Case: 2013023 |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.01 | Technical Specification 6.8.1, "Procedures and Programs," requires in part that written procedures shall be established, implemented, and maintained covering the activities recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Regul
Region: II | Summer | 16264 | 03/23/2007 05/05/2006 | 2006011-01 | Self - Revealed | VIO | Public Radiation Safety | White | White Finding Involving Failure to Properly Prepare a Radioactive Material Package for Shipment | EA Case: 2006046 |  | TE?: N | 05000395 Summer |  | NONE | See 05000395/2006009-01. 10 CFR 71.5 requires that NRC licensees ship radioactive materials in accordance with the applicable provisions of the Department of Transportation regulations found in 49 CFR 100-177. 49 CFR 173.441(a) requires that each p
Region: II | Summer | 16068 | 03/03/2006 03/09/2006 | 2006009-01 | Self - Revealed | VIO | Public Radiation Safety | White | Failure to Properly Prepare a Radioactive Material Package for Shipment | EA Case: 2006046 |  | TE?: N | 05000395 Summer |  | 7112202 | The inspectors identified an apparent self-revealing finding of low to moderate safety significance. The licensee failed to prepare a shipment of radioactive material to a waste processing facility in a manner such that, under conditions normally incident
Region: II | Surry | 17182 | 07/31/2006 07/25/2006 | 2006010-01 | NRC | VIO | Emergency Preparedness | White | White Finding Involving Failure to Identify a Weakness During an Emergency Exercise Critique Associated with an RSPS | EA Case: 2006071 |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71114.01 | See 05000280, 281/2006008-01. 10 CFR 50.47(b)(4) requires, in part, that a standard emergency classification and action level scheme, the bases of which include facility system and effluent parameters, is in use by the nuclear facility licensee, and St
Region: II | Surry | 17180 | 03/29/2006 05/05/2006 | 2006008-01 | NRC | VIO | Emergency Preparedness | White | Failure of Exercise Critique to identify a RSPS weakness as a DEP PI opportunity Failure | EA Case: 2006071 |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71114.01 | The NRC identified an apparent violation (AV) for failure of the licensee's exercise critique process to properly identify a weakness associated with a risk-significant planning standard (RSPS) that was determined to be a Drill/Exercise Performance (DEP)
Region: I | Susquehanna | 32282 | 03/18/2015 04/16/2015 | 2015503-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain a Standard EAL Scheme | EA Case: 2015022 | P.5 Operating Experience | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | White: The inspectors identified an apparent violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2), which has been determined to be of low to moderate safety significance (White). Specifically, 10 CFR 50.54(q)(2) requires a license
Region: I | Susquehanna | 31202 | 09/30/2010 11/12/2010 | 2010004-01 | Self - Revealed | FIN | Initiating Events | White | Procedural Inadequacies Result in Reactor Scram and Loss of Normal Heat Sink |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 |  | 71111.06 | A self-revealing preliminary White finding regarding procedure NDAP-QA-0008, "Procedure Writer's Guide," Revision 8, was identified following a July 16, 2010, flooding event in the Unit 1 condenser bay which resulted in a manual reactor scram and loss of
Region: I | Three Mile Island | 34051 | 12/31/2012 02/11/2013 | 2012005-03 | NRC | VIO | Mitigating Systems | White | Failure to Identify and Correct Missing Electrical Conduit Flood Seals in the Air Intake Tunnel | EA Case: 2013046 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000289 Three Mile Island 1 |  | NONE | TBD. The inspectors identified an apparent violation (AV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, was identified during the TI-187 flooding walkdowns for Exelon's failure to identify and correct an external flood barrier deficiency. S
Region: II | Turkey Point | 668 | 12/31/2011 01/26/2012 | 2011005-02 | NRC | VIO | Emergency Preparedness | White | Failure to maintain TSC habitability | EA Case: 2012001 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | NONE | The licensee identified an Apparent Violation (AV) of 10 CFR Part 50.54(q), which requires that adequate emergency facilities and equipment to support the emergency response are provided and maintained. During the periods from December 4, 2010 to July 13,
Region: II | Turkey Point | 34833 | 12/30/2009 01/28/2010 | 2009005-03 | NRC | VIO | Initiating Events | White | Violation of Technical Specification 5.5.1.1 regarding Unit 3 spent fuel storage with degrading Boraflex poison | EA Case: 2010037 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 |  | 71152 | The inspectors identified an apparent violation of Technical Specification 5.5.1.1 requirements regarding storage of fuel assemblies in the Unit 3 spent fuel pool when Keff limits for fuel configurations were not maintained using methods described in the
Region: II | Turkey Point | 34764 | 08/18/2006 08/24/2006 | 2006015-01 | NRC | VIO | Initiating Events | White | Failure to assess and manage maintenance risk during shutdown operations | EA Case: 2006200 | H.3(a) Work Planning | TE?: N | 05000250 Turkey Point 3 |  | NONE | A violation of 10 CFR Part 50.65(a)(4) was identified for failure to adequately assess and manage the increase in risk of performing maintenance on the A-train 480 volt 3C load center while Unit 3 was operating in decay heat removal mode with one operatin
Region: I | Vermont Yankee | 1687 | 10/06/2006 11/07/2006 | 2006011-01 | NRC | FIN | Public Radiation Safety | White | Radioactive Material Shipment Package Dose Rate Exceeded |  |  | TE?: N | 05000271 Vermont Yankee |  | 7112202 | The inspector identified a self-revealing finding, involving a failure to properly prepare and ship a package containing radioactive material in a manner that assured, under conditions normally incident to transport, conformance with Department of Transpo
Region: II | Vogtle | 1273 | 12/31/2014 01/22/2015 | 2014009-01 | Self - Revealed | VIO | Public Radiation Safety | White | Shipment of a Type B quantity of RAM in a Type A Container | EA Case: 2014158 | H.7 Documentation | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71124.08 | A self-revealing, preliminary White, AV of Technical Specification (TS) 5.4.1., Procedures, occurred on June 24, 2014, when a Type A shipping cask containing Type B radioactive waste (spent resin) was shipped by Southern Nuclear Operating Company (SNC)
Region: II | Vogtle | 1256 | 06/30/2014 08/06/2014 | 2014003-03 | Licensee - Identified | VIO | Emergency Preparedness | White | Calculation Error Results in Significantly Non-Conservative EAL Threshold Values | EA Case: 2014112 |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | White: A finding and associated violation of 10 CFR 50.54(q)(2) was identified by the licensee for the failure to follow and maintain the effectiveness of emergency plans which use a standard emergency classification and action level scheme. Specifically,
Region: II | Vogtle | 1119 | 08/31/2006 09/18/2006 | 2006011-01 | NRC | VIO | Emergency Preparedness | White | White Finding Involving Failure to Identify A Weakness During an Emergency Exercise Critique Associated with an RSPS. | EA Case: 0006132 |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71114.01 | The NRC identified a Violation for failure of the licensee's exercise critique process to properly identify a weakness associated with a risk-significant planning standard (RSPS) that was determined to be a Drill/Exercise Performance (DEP) Performance Ind
Region: II | Vogtle | 1510 | 02/08/2017 | 2017503-01 | NRC | UNKN | Emergency Preparedness | White | Transposition Results in Significantly Different EAL Threshold Values | EA Case: 2017014 | H.3 Change Management | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | The inspectors identified an apparent violation (AV) of Title 10 CFR Part 50.54(q)(2) for failure to follow and maintain the effectiveness of emergency plans which met the requirements of 10 CFR Part 50.47(b)(4) and Part 50 Appendix E, to have a standardi
Region: IV | Waterford | 3427 | 12/20/2013 01/30/2014 | 2013008-01 | NRC | VIO | Mitigating Systems | White | Failure to establish an adequate test program to demonstrate that the train B EDG exhaust fan would perform satisfactorily in service | EA Case: 2013233 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | NONE | A self-revealing apparent violation of 10 CFR Part 50, Appendix B, Criteria XI, Test Control, occurred because the licensee failed to establish an adequate test program to demonstrate that a safety related component associated with the Train B Emergency D
Region: IV | Waterford | 3019 | 08/10/2011 08/24/2011 | 2011009-01 | NRC | FIN | Occupational Radiation Safety | White | Failure To Use Effective Engineering Controls As Part Of Pre-Job Planning To Reduce Contamination And Subsequent Exposure |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71124.02 | The inspectors identified an apparent White finding because the licensee failed to use effective engineering controls as part of pre-job planning to reduce contamination and subsequent exposure. The primary reason for the dose overage was the licensee's f
Region: IV | Waterford | 2965 | 09/24/2009 11/06/2009 | 2009008-01 | Licensee - Identified | VIO | Mitigating Systems | White | Inoperable 125Vdc battery because electricians failed to follow work instructions | EA Case: 2009018 | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | NONE | Following a September 2, 2008 train B 125 Vdc battery failure, the licensee identified a violation of Technical Specification 6.8.1.a for the failure to follow plant procedures during corrective maintenance on the safety-related battery. Following the rep
Region: II | Watts Bar | 125752 | 12/31/2018 09/13/2019 | 2018004-05 | NRC | NOV | Emergency Preparedness | White | The failure to maintain the effectiveness of an emergency plan to meet the requirements of Title 10 CFR Part 50.47(b)(4) and Part 50 Appendix E to have a standardized emergency action level (EAL) scheme in use based on facility system and effluent paramet | EA Case: 18-182 | H.3 - Change Management | TE?: Y SL-NOV | 05000390 Watts Bar 1 05000391 Watts Bar 2 | Program & Process | 95001 | An Apparent Violation (AV) of 10 CFR Part 50.47(b)(4), (b)(9), and Part 50 Appendix E, for failure to maintain the effectiveness of the emergency plan and a standard emergency classification scheme which included facility effluent parameters. Specifically
Region: II | Watts Bar | 4242 | 01/18/2013 03/12/2013 | 2012009-01 | NRC | VIO | Mitigating Systems | White | Inadequate abnormal condition procedure for flood mitigation strategy prior to installation of HESCO barriers | EA Case: 2013018 |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The inspectors identified a Violation (VIO) of Technical Specification (TS) 5.7.1, Procedures, for the licensee's failure to establish an adequate procedure for mitigation of external events, specifically flooding prior to the installation of HESCO barrie
Region: II | Watts Bar | 4244 | 01/18/2013 03/12/2013 | 2012009-03 | NRC | VIO | Mitigating Systems | Yellow | Failure to maintain an adequate abnormal condition procedure to implement the flood mitigation strategy | EA Case: 2013018 | H.2(d) Facilities & Equipment | TE?: N | 05000390 Watts Bar 1 |  | NONE | The inspectors identified an violation (VIO) of Technical Specification 5.7.1, Procedures, for the licensee's inability to demonstrate that the required Stage I and Stage II activities could be performed within 27 hours as required by AOI-7.1, Maximum Pro
Region: II | Watts Bar | 3989 | 03/15/2006 04/07/2006 | 2006007-01 | NRC | FIN | Barrier Integrity | White | Failure to Implement Shutdown Procedures which Resulted in Pressurizer PORV Actuations |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | Technical Specification 5.7.1.1 requires that written procedures be implemented and maintained covering the activities in the applicable procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978, of which Part 2.j requires a p
Region: IV | Wolf Creek | 5716 | 06/29/2016 07/19/2016 | 2016008-01 | NRC | AV | Mitigating Systems | White | Failure to Adequately Establish and Adjust Preventive Maintenance for Emergency Diesel Generator Excitation System Diodes | EA Case: 2016069 | P.5 Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a preliminary White finding associated with an apparent violation of Technical Specification 5.4.1.a, for the licensee's failure to adequately develop and adjust preventive maintenance activities in accordance with Procedure AP 1
Region: IV | Wolf Creek | 5379 | 03/04/2014 04/02/2014 | 2014502-01 | NRC | VIO | Emergency Preparedness | White | Failure to Maintain Accurate Methods for Dose Assessment | EA Case: 2014024 | P.2 Evaluation | TE?: N | 05000482 Wolf Creek 1 |  | 71114.05 | (Initial Entry) An apparent violation of 10 CFR 50.54(q)(2) was identified involving the failure to maintain adequate methods for assessing the actual or potential consequences of a radiological emergency between September 2012 and November 2013, in acco
Region: IV | Wolf Creek | 5289 | 08/06/2012 08/06/2012 | 2012009-01 | NRC | VIO | Initiating Events | Yellow | Failure to provide adequate oversight of contractors during maintenance on the Startup Transformer | EA Case: 2012152 | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team reviewed a self-revealing apparent violation of Technical Specification 5.4.1.a and Regulatory Guide 1.33 for the failure to follow procedures. Specifically, the electrical penetration seal and wiring assembly associated with the H1/CT4 and H2/CT