## Sheet1
Region | Site | Id | Pim_Issue_Date | Source | IdBy | Type | Cornerstone_ | Significance | Title_ | EACaseNo | CrossCuttingAspect | TE | Docket | CornerstoneAttribute | Procedure | Introduction_
Region: I | Beaver Valley | 25912 | 12/31/2018 02/05/2019 | 2018004-01 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Service Water Header Pressure Reduction |  | H.12 - Avoid Complacency | TE?: N | 05000412 Beaver Valley 2 | Procedure Quality | 71111.15 | A self-revealed Green non-cited violation of technical specification 5.4.1, “Procedures,” was identified when FENOC failed to adequately implement procedure NOP-WM-1001, “Order Planning Process.” Specifically, the work order failed to identify how the wor
Region: I | Beaver Valley | 38859 | 12/31/2018 02/05/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to correct a degraded condition with the Unit 2 B safeguards area air conditioning unit |  | P.3 - Resolution | TE?: N | 05000412 Beaver Valley 2 | Equipment Performance | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” because FENOC did not promptly identify and correct a condition adverse to quality. Specifically, from August 24, 2015 to present, FEN
Region: I | Beaver Valley | 24690 | 09/30/2018 10/30/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Verification of Full Low Head Safety Injection Suction Piping |  | H.11 - Challenge the Unknown | TE?: N | 05000334 Beaver Valley 1 |  | 71111.15 | A self-revealed Green non-cited violation (NCV) of technical specification (TS) 5.4.1, Procedures, was identified when FENOC failed to adequately implement procedure 1OM-52.4.R.2.A, "Station Startup Mode 6 to Mode 1 Administrative and Local Actions," to v
Region: I | Beaver Valley | 24404 | 08/10/2018 09/20/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Duties of the Shift Technical Advisor for Control Room Evacuation during a Fire Event. |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71111.05XT | The inspectors identified a Green non-cited violation (NCV) of Technical Specification (TS) 5.4.1(a), Procedures, related to the duties of the Shift Technical Advisor (STA) in response to a serious fire requiring control room evacuation. Specifically, pro
Region: I | Beaver Valley | 23947 | 03/31/2018 05/02/2018 |  | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedure Adherence |  | NPP | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | A self-revealed Green finding was identified when the licensee failed to adequately implement procedure NOP-WM-1001, "Order Planning Process." Specifically, FENOC personnel that made a change to work order testing requirements did not receive concurrence
Region: I | Beaver Valley | 24353 | 02/23/2018 05/03/2018 | 2018010-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Diesel Fuel Oil Temperature Protection |  | H.7 - Documentation | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 2515/191 | The team identified a finding of very low safety significance (Green) for the failure to ensure that diesel powered Diverse and Flexible Coping Strategies (FLEX) equipment would be reliable to mitigate postulated beyond-design basis external events during
Region: I | Beaver Valley | 22677 | 12/31/2017 01/24/2018 | 2017004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Inadequate Control of Entry into High Radiation Areas |  | H.12 - Avoid Complacency | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 60855 | A self-revealing, very low safety significance (Green) NCV of Technical Specification (TS) 5.7.1 for failure to control a high radiation area (HRA) was identified. On November 8, 2017, during independent spent fuel storage installation (ISFSI) dry cask lo
Region: I | Beaver Valley | 23462 | 11/17/2017 12/18/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Differential Pressure Value Used in Low Head Safety Injection Motor-Operated Valve Design Analysis |  | NPP | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71111.21M | Green. The NRC team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, “Design Control,” because FENOC staff did not establish measures to assure that the design bases were
Region: I | Beaver Valley | 7308 | 12/31/2016 01/31/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in an Inoperable 'A' River Water Train |  | H.12 Avoid Complacency | TE?: N | 05000334 Beaver Valley 1 |  | 71111.15 | A self-revealing NCV of Title 10 of the Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for FENOC's failure to assure that activities affecting quality were accomplished in accordance
Region: I | Beaver Valley | 7306 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to Quality Leads to Inoperable Emergency Bus Degraded Voltage Relays |  | P.4 Trending | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, "Corrective Action," for FENOC's failure to assure that a condition adverse to quality was promptly identified and corrected. Specifically,
Region: I | Beaver Valley | 7295 | 06/30/2016 08/02/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Procedure Change Results in Failure to Maintain the Design Basis for the Service Water System |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 71111.15 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (CFR) 50, Appendix B, Criterion III, "Design Control," for FENOC's failure to assure that the regulatory requirements and design basis for the Unit 2 service water system were
Region: I | Beaver Valley | 7296 | 06/30/2016 08/02/2016 | 2016002-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Measures to Ensure the Effectiveness of an EAL |  | H.7 Documentation | TE?: N | 05000412 Beaver Valley 2 |  | 71152 | The inspectors identified a NCV of 10 CFR 50.54(q)(2) for FENOC's failure to follow and maintain the effectiveness of an emergency plan that meets the planning standards of 10 CFR 50.47(b)(4). Specifically, following the failure of the area radiation moni
Region: I | Beaver Valley | 7297 | 06/30/2016 08/02/2016 | 2016002-03 | NRC | FIN | Initiating Events | Green | Failure to Appropriately Utilize Multiple and Diverse Indications Results in Plant Transient |  | H.11 Challenge the Unknown | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | A self-revealing finding of NOP-OP-1002, "Conduct of Operations," was identified for FENOC's failure to adequately implement operator fundamentals. Specifically, operators did not appropriately utilize multiple and diverse indications when making the deci
Region: I | Beaver Valley | 7307 | 03/31/2016 05/04/2016 | 2016001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Evaluate Control Room Envelope Test Results |  | H.14 Conservative Bias | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71111.15 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XI, "Test Control," for FENOC's failure to properly evaluate the test results of the Control Room Envelope (CRE) unfiltered air in-leakag
Region: I | Beaver Valley | 7290 | 12/31/2015 03/29/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Rule Monitoring of the Auxiliary Feedwater System |  | H.12 Avoid Complacency | TE?: N | 05000334 Beaver Valley 1 |  | 71111.12 | Green. The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (CFR) 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," for FENOC's failure to monitor the performance of the Unit 1 auxili
Region: I | Beaver Valley | 7288 | 09/30/2015 11/10/2015 | 2015003-01 | NRC | FIN | Initiating Events | Green | Failure to Correct a Low Oil Level in the Condensate Pump Motor |  | H.13 Consistent Process | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | A self-revealing finding was identified for FENOC's failure to correct a low oil level in the lower motor bearing of the Unit 1 'A' condensate pump in accordance with NOP-LP-2001, "Corrective Action Program." Specifically, FENOC incorrectly cancelled the
Region: I | Beaver Valley | 7289 | 08/21/2015 09/30/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Unanalyzed Condition Resulting from Unfused Direct Current Control Circuits |  | H.1 Resources | TE?: N | 05000334 Beaver Valley 1 |  | 71111.05T | On April 30, 2014, FENOC identified a violation of very low safety significance of 10 CFR 50, Appendix R, Section III.G for BVPS Unit 1 in that unfused direct current (DC) control circuits for DC motors were routed from the turbine building through other
Region: I | Beaver Valley | 7285 | 06/30/2015 08/04/2015 | 2015002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Utilize Respiratory Protection as Specified by the Radiation Work Permit |  | H.14 Conservative Bias | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | NONE | - Green. The inspectors identified a self-revealing NCV of Technical Specification 5.4.1, "Procedures," for FENOC's failure to utilize respiratory protection, as required by the applicable radiation work permit (RWP), for entry into the 722-foot elevation
Region: I | Beaver Valley | 7287 | 06/30/2015 08/04/2015 | 2015002-02 | NRC | FIN | Initiating Events | Green | Failure to Perform Maintenance in Accordance with Licensee Maintenance Process |  | H.9 Training | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | - Green. A self-revealing finding was identified for FENOC's failure to perform maintenance on the Unit 2 feedwater heater drain system in accordance with FENOC's maintenance process, NOP-WM-4006, "Conduct of Maintenance." Specifically, FENOC did not adju
Region: I | Beaver Valley | 7286 | 06/26/2015 07/20/2015 | 2015008-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Initiate a Condition Report for an Adverse Condition |  | H.2 Field Presence | TE?: N | 05000334 Beaver Valley 1 |  | 71152B | Green. A Green self-revealing finding of NOP-LP-2001, "Corrective Action Program," was identified after FENOC failed to generate a condition report for a condition adverse to quality. Specifically, FENOC did not initiate a condition report when a lifted
Region: I | Beaver Valley | 7281 | 12/31/2014 02/04/2015 | 2014005-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO PROPERLY SHIP CATEGORY 2 RADIOACTIVE MATERIAL |  |  | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71124.08 | The inspectors identified an NCV of 10 CFR 71.5, "Transportation of licensed material," and 49 CFR 172, Subpart I, "Safety and Security Plans." Specifically, FENOC personnel shipped a category 2 radioactive material of concern (RAM-QC) on public highways
Region: I | Beaver Valley | 7282 | 12/04/2014 01/15/2015 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Green NCV |  |  | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 7111121 | The Commission has decided that specific information related to findings and performance indicators pertaining to security will not be publicy available to ensure that security information is not provided to a possible adversary. Other than the fact that
Region: I | Beaver Valley | 7283 | 11/17/2014 11/13/2014 | 2014004-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO PROPERLY SHIP CATEGORY 2 RADIOACTIVE MATERIAL |  |  | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | NONE | The inspectors identified an NCV of 10 CFR 71.5, "Transportation of licensed material," and 49 CFR 172, Subpart I, "Safety and Security Plans." Specifically, FENOC personnel shipped a category 2 radioactive material of concern (RAM-QC) on public highways
Region: I | Beaver Valley | 7280 | 10/13/2014 02/04/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY IMPLEMENT RISK MANAGEMENT ACTIONS |  | H.5 Work Management | TE?: N | 05000334 Beaver Valley 1 |  | 71111.13 | The inspectors identified an NCV of 10 CFR 50.65(a)(4), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," for FENOC's failure to implement adequate risk management actions (RMAs) associated with maintenance on the alt
Region: I | Beaver Valley | 7279 | 05/20/2014 11/13/2014 | 2014004-01 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PLANT STARTUP PROCEDURE LEADS TO MANUAL REACTOR TRIP |  | H.11 Challenge the Unknown | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for FENOC's failure to have an adequate plant startup procedure. Specifically, 2OM-52.4A, "Raising Power from 5% to Full Load Operation," d
Region: I | Beaver Valley | 7270 | 05/19/2014 08/13/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE RESULTS IN INOPERABLE SI ACCUMULATOR |  | H.12 Avoid Complacency | TE?: N | 05000412 Beaver Valley 2 |  | 71111.04Q | A self-revealing NCV of technical specification (TS) 5.4.1 was identified because the unit 2 'B' safety injection (SI) accumulator was made inoperable when FENOC operators did not follow procedural requirements to align nitrogen to the accumulator. Specif
Region: I | Beaver Valley | 7271 | 04/17/2014 08/13/2014 | 2014003-02 | NRC | NCV | Barrier Integrity | Green | REMOVAL OF MISSILE BARRIER RENDERS CONTAINMENT INOPERABLE |  | H.14 Conservative Bias | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71111.2 | The inspectors identified a Green non-cited violation of TS limiting condition for operation (LCO) 3.6.1, "Containment." Specifically, the inspectors determined that FENOC removed the missile barriers for the unit 1 and unit 2 containment equipment hatche
Region: I | Beaver Valley | 7277 | 03/31/2014 05/15/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Testing Procedures Resulted in TDAFW Pump Inoperability |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71111.19 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified because FENOC did not establish appropriate post maintenance test procedures for the Turbine Driven Auxiliary Feedwater (TDAFW) pump
Region: I | Beaver Valley | 7278 | 03/31/2014 05/15/2014 | 2014002-02 | NRC | FIN | Initiating Events | Green | Main Transformer Failure Due to Static Electrification |  | H.6 Design Margins | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | A self-revealing, Green finding was identified because FirstEnergy Nuclear Operating Company (FENOC) did not evaluate technical information provided in a vendor report as required by FENOC procedures: 1/2-ADM-2017, "Control of Vendor Technical Information
Region: I | Beaver Valley | 7264 | 12/31/2013 02/10/2014 | 2013005-01 | Self - Revealed | NCV | Initiating Events | Green | Moisture Separator Reheater Valve Misposition Results in Plant Transient |  | H.4(a) Human Error Prevention | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A self-revealing, Green NCV of TS 5.4.1 "Procedures" was identified when an operator did not correctly implement procedure 1OM-52.4.A, Raising Power from 5% to Full Load Operation, Revision 68, during the warm up the moisture separator reheaters. Specific
Region: I | Beaver Valley | 7269 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | NCV | Occupational Radiation Safety | Green | Insufficient VHRA Control UnderVessel |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 |  | 71124.01 | The inspectors identified a Green non-cited violation involving the failure to properly ensure that a device used to control access to a Very High Radiation Area was adequate to prevent an unauthorized entry into the area. Specifically, the licensee used
Region: I | Beaver Valley | 7265 | 12/06/2013 01/16/2014 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Untimely Problem Identification and Corrective Action for Degraded Auxiliary Feedwater Pump Steam Supply Valve |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000412 Beaver Valley 2 |  | 71152B | The inspectors identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, related to FENOC's problem identification and corrective action to address the November 2011 fa
Region: I | Beaver Valley | 7253 | 04/18/2013 07/30/2013 | 2013003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM A WRITTEN EVALUATION AS REQUIRED BY 50.59 |  | H.4(b) Procedural Compliance | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71111.11Q | The inspectors identified a Severity Level (SL) IV NCV and associated Green finding of 10 CFR 50.59, "Changes, Tests and Experiments," in that FENOC failed to perform a written evaluation for creation of an abnormal operating procedure (AOP) for response
Region: I | Beaver Valley | 7246 | 03/31/2013 05/09/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Manage Elevated Risk during Preventive Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000412 Beaver Valley 2 |  | 71111.13 | The inspectors identified a Green, NCV of 10 CFR 50.65(a)(4) "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because FENOC did not implement risk management actions to manage the risk associated with performance of
Region: I | Beaver Valley | 7238 | 12/04/2012 02/05/2013 | 2012005-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO USE A PROCEDURE TO OPERATE A CVCS VALVE |  | H.4(a) Human Error Prevention | TE?: N | 05000412 Beaver Valley 2 |  | 71111.2 | A self revealing, Green NCV of Technical Specification 5.4.1 "Procedures," was identified for FENOC's failure to use a procedure when operating chemical volume and control system (CVCS) valve 2CHS-FCV122 during troubleshooting, as required by the RG 1.33
Region: I | Beaver Valley | 7239 | 12/04/2012 02/05/2013 | 2012005-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO IDENTIFY AND CORRECT A CONDITION ADVERSE TO QUALITY |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 71111.2 | A self revealing, Green NCV was indentified for FENOC violating 10 CFR 50 Appendix B, Criterion XVI "Corrective Action," for failure to identify and correct a condition adverse to quality on the Controller Driver printed circuit board (NCD board) for the
Region: I | Beaver Valley | 7245 | 09/30/2012 11/07/2012 | 2012004-02 | Self - Revealed | FIN | Mitigating Systems | Green | REMEDIAL EXAMINATION FAILURE RATE EXCEEDS 10 PERCENT |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000334 Beaver Valley 1 |  | 71111.11Q | A self-revealing Green finding was identified when greater than 10 percent of reactor operators who failed the biennial written requalification examination subsequently failed the remediation examination. A performance deficiency existed since the re-exam
Region: I | Beaver Valley | 7244 | 08/01/2012 11/07/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | INEFFECTIVE CORRECTIVE ACTION RESULTS IN OPERABLE COMPONENT COOLING WATER HEAT EXCHANGER |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000412 Beaver Valley 2 |  | 71111.07A | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified in that FENOC failed to prevent further degradation of the 'A' component cooling water heat exchanger
Region: I | Beaver Valley | 7229 | 04/30/2012 08/03/2012 | 2012003-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE CONTAINMENT ISOLATION VALVE LEAKAGE TESTING PROCEDURE RESULTS IN RCS PIPING WATER HAMMER |  | H.3(b) Work Activity Coordination | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A self-revealing Green NCV of TS 5.4.1, "Procedures", for FENOC's failure to establish adequate procedural guidance for plant conditions for containment isolation valve leakage testing. Specifically, inadequate procedural guidance in BVT-1.47.11, Safety I
Region: I | Beaver Valley | 7228 | 04/15/2012 08/03/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE MAINTENANCE RESULTS IN LOW HEAD SAFETY INJECTION SYSTEM EXCEEDING OUTSIDE CONTAINMENT LEAKAGE RATE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A self-revealing Green NCV of License Condition 2.C.6.(2), Outside Containment Leakage Rate, was identified in FENOC's failure to perform adequate maintenance and restoration of the Unit 1 LHSI system. The inspectors determined the failure to adequately p
Region: I | Beaver Valley | 6980 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | FIN | Initiating Events | Green | FAILURE TO ADEQUATELY CONTROL LOOSE MATERIAL NEAR OFF-SITE POWER TRANSFORMER |  | P.2(b) Implementing Operating Experience | TE?: N | 05000334 Beaver Valley 1 |  | 71111.01 | The inspectors identified a Green finding (FIN) for FENOC's failure to adequately control loose materials near the 1B System Station Service Transformer (SSST) that provides off-site power. The inspectors determined the failure to secure loose material wa
Region: I | Beaver Valley | 6981 | 03/31/2012 04/30/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN AUXILIARY FEEDWATER OPERABLE DURING MAINTENANCE |  | H.3(a) Work Planning | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | The NRC inspectors identified a Green NCV of TS 3.7.5, in that FENOC performed maintenance on the Unit 1 auxiliary feed water (AFW) system that resulted in three inoperable AFW trains due to removing the auto-open feature of the AFW pumps discharge valves
Region: I | Beaver Valley | 6982 | 03/31/2012 04/30/2012 | 2012002-03 | NRC | NCV | Initiating Events | Green | EXPANSION JOINT DEGRADATION RESULTS IN RIVER WATER INOPERABILITY |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | The inspectors identified a Green NCV of TS 5.4.1 "Procedures" for FENOC's failure to adequately implement and maintain a replacement program for expansion joints installed in safety related systems. The inspectors determined the procedural inadequacy of
Region: I | Beaver Valley | 6973 | 10/25/2011 02/01/2012 | 2011005-01 | Self - Revealed | NCV | Emergency Preparedness | Green | UNANNOUNCED EMERGENCY RESPONSE ORGANIZATION ACTIVATION DRILL FAILURE |  | H.4(b) Procedural Compliance | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71114.06 | A Green, self-revealing non-cited violation (NCV) of 10 CFR 50.47(b)(2) to ensure timely augmentation of response capabilities is available was identified. Specifically, FENOC failed to fully staff two primary Emergency Response Organization (ERO) positio
Region: I | Beaver Valley | 6975 | 09/16/2011 10/27/2011 | 2011009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to lmplement Effective Corrective Actions to Prevent Recurrence of Socket-Weld Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71152B | The inspectors identified a Green, self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Action," in that FENOC failed to take adequate corrective actions to prevent recurrence of a significant condition adverse to quali
Region: I | Beaver Valley | 6974 | 09/16/2011 10/27/2011 | 2011009-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Corrective Actions for 2A Service Water Pump Motor Epoxy Vioding |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 71152B | The inspectors identified a Green , self-revealing, non-cited violation of 10CFR50, Appendix B, Criterion XVI, "Corrective Action," in that FENOC did not take corrective actions to prevent recurrence of a significant condition adverse to quality. Specific
Region: I | Beaver Valley | 6962 | 06/30/2011 08/02/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Recirculation Spray HXs in Chemical Wet Layup |  | H.3(b) Work Activity Coordination | TE?: N | 05000412 Beaver Valley 2 |  | 71111.07A | A Green, self-revealing non-cited violation (NCV) of TS 5.4.1, "Procedures", was identified in that the Unit 2 recirculation spray (RSS) HXs were not maintained in chemical wet layup, contrary to station procedures and industry guidance. Specifically, FEN
Region: I | Beaver Valley | 6963 | 06/30/2011 08/02/2011 | 2011003-02 | NRC | FIN | Public Radiation Safety | Green | Untimely Radiation Monitor Corrective Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71152 | A Green, NRC identified finding (FIN) was identified in that plans and actions to correct long-standing radiation monitor system instrumentation deficiencies were not accomplished in a timely manner, in accordance with FENOC CAP procedure NOP-LP-2001. Spe
Region: I | Beaver Valley | 6964 | 06/17/2011 08/01/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO VERIFY THE DESIGN REQUIREMENTS FOR THE FUEL OIL TRANSFER PUMPS |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited viotation (NCV) of 10 CFR 50, Appendix B, Criterion lll, "Design Control" because FENOC did not verify or check the adequacy of the Unit 1 emergency diesel generator (ED
Region: I | Beaver Valley | 6970 | 06/17/2011 08/01/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CALCULATIONS FOR PLACING SSST LTC IN MANUAL MODE |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited vioiation of 10 CFR 50, Appendix B, Criterion lll, "Design Control," because FENOC did not correctly translate the design basis of the electrical distribution system int
Region: I | Beaver Valley | 6972 | 06/17/2011 08/01/2011 | 2011007-04 | NRC | NCV | Mitigating Systems | Green | OFFSITE POWER NON-CONSERVATIVE POST TRANSIENT VOLTAGE CALCULATIONS |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion lll, "Design Control," because FENOC did not perform adequate voltage calculations to verify that vital bus voltage levels
Region: I | Beaver Valley | 6952 | 03/07/2011 05/13/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADVERTENT AUXILIARY FEEDWATER START DURING STEAM GENERATOR WATER LEVEL INSTRUMENT ADJUSTMENTS |  | H.3(b) Work Activity Coordination | TE?: N | 05000412 Beaver Valley 2 |  | 71111.2 | A Green, self-revealing non-cited violation (NCV) of TS 5.4.1, "Procedures", was identified in that technicians inadvertently caused an auxiliary feedwater actuation. Specifically, the procedure used was inadequately written to adjust steam generator wate
Region: I | Beaver Valley | 6950 | 12/31/2010 02/14/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE RESULTS IN MAIN FEEDWATER PIPING PRESSURIZATION |  | H.4(a) Human Error Prevention | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A self-revealing non-cited violation (NCV) was identified in that a chemical addition pump [1WT-P-15B] was misaligned to an isolated main feed water header, and upon starting caused an unexpected pressure transient, which affected the 'B' Fast Acting Main
Region: I | Beaver Valley | 6951 | 12/31/2010 02/14/2011 | 2010005-03 | Self - Revealed | NCV | Barrier Integrity | Green | MAX DIFFERENTIAL TEMPERATURE EXCEEDED FOR SPRAY NOZZLE DURING PRESSURIZER HEAT UP |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A self-revealing non-cited violation (NCV) of TS 5.4.1, "Procedures", was identified in that the shift technical advisor's (STA) failure to follow procedure resulted in the maximum differential temperature being exceed on the spray nozzle during pressuriz
Region: I | Beaver Valley | 6953 | 12/09/2010 05/13/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE SPRAY ADDITIVE SYSTEM SAMPLING PROCEDURES |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | A Green, self-revealing non-cited violation (NCV) of TS 5.4.1, "Procedures", was identified in that chemistry procedures failed to provide adequate detail to ensure timely completion of TS required sampling of the spray additive system. Specifically, FENO
Region: I | Beaver Valley | 6947 | 09/05/2010 10/27/2010 | 2010004-01 | Self - Revealed | FIN | Mitigating Systems | Green | INADEQUATE MAINTENANCE PROCEDURE RESULTS IN AUTO-DISASSEMBLY OF EDG INTAKE DAMPER |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000334 Beaver Valley 1 |  | 71111.19 | A Green, self-revealing finding (FIN) was identified in that an inadequate procedure resulted in a failure to adequately retain a 1-1 EDG room damper after louver adjustment. Specifically, the adjustment of the 1-1 EDG upper damper (1VS-D-22-2A) in April
Region: I | Beaver Valley | 6941 | 03/04/2010 04/23/2010 | 2010002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Human Performance Error Results in Disabling Control Room Annunciator |  | H.4(b) Procedural Compliance | TE?: N | 05000412 Beaver Valley 2 |  | 71152 | A self-revealing finding was identified for FENOC's failure to properly implement a station procedure. Specifically, work order instructions were not properly followed, as expected by NOP-WM-4006, "Conduct of Maintenance", causing leads to be inadvertentl
Region: I | Beaver Valley | 6938 | 11/24/2009 01/29/2010 | 2009005-02 | Self - Revealed | NCV | Initiating Events | Green | RHR PUMP SUCTION RELIEF LIFT DURING SYSTEM SHUTDOWN |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | A self-revealing NCV of TS 5.4.1, "Procedures", was identified in that procedures for securing Residual Heat Removal System (RHS) were not adequately maintained and did not contain relevant operating restrictions resulting in the inadvertent lifting of th
Region: I | Beaver Valley | 6937 | 11/11/2009 01/29/2010 | 2009005-01 | Self - Revealed | NCV | Barrier Integrity | Green | OVERPRESS OF THE ISOLATED B RCS LOOP |  | H.4(b) Procedural Compliance | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | A self-revealing NCV of TS 5.4.1, "Procedures", was identified in that operators failed to properly align and check the position of the "B" reactor coolant system (RCS) loop bypass valve [2RCS*45], as required by procedure. This deficiency caused an incor
Region: I | Beaver Valley | 6930 | 09/15/2009 10/15/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | PERSONNEL FAILURE TO DEMONSTRATE THAT 10CFR 50.65(a)(2) PERFORMANCE OF CONTAINMENT ISOLATION VALVE LIMIT SWITCHES WAS EFFECTIVELY CONTROLLED THROUGH PERFORMANCE OF APPROPRIATE PREVENTATIVE MAINTENANC |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71152B | The inspectors identified an NCV of very low significance (Green) of 10CFR 50.65 (a)(2), "Requirements for Monitoring the Effectiveness of Maintence at Nuclear Power Plants, " due to FENOC personnel's failure to demonstrate that the 10 CFR 50.65(a)(2) per
Region: I | Beaver Valley | 6924 | 06/30/2009 08/04/2009 | 2009003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post-Maintenance Testing Specified for Safety-Related River Water Check Valve |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000334 Beaver Valley 1 |  | 71111.19 | -Green. A non-cited violation (NCV) of 10CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for failure to specify and perform an adequate post-maintenance test (PMT) after replacing a safety-related river water
Region: I | Beaver Valley | 6929 | 06/30/2009 08/04/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Continuously Submerged Cables Design Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 71152 | -Green. The inspectors identified a non-cited violation (NCV) of 10CFR Part 50, Appendix B, Criterion III, "Design Control," in that FENOC failed to maintain safety-related cables in an environment for which they were designed. Since NRC Information Notic
Region: I | Beaver Valley | 6921 | 11/24/2008 11/24/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTION FOR POTENTIAL BLOCKAGE OF AFW PUMP LUBE OIL COOLING SYSTEM ORIFICES WHEN SUPPLIED BY RW/SW |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 05000412 Beaver Valley 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, in that FENOC did not take adequate corrective action following the identification of a conditio
Region: I | Beaver Valley | 6920 | 09/30/2008 11/13/2008 | 2008004-01 | Self - Revealed | NCV | Initiating Events | Green | Procedure Use Errors Result in Loss of an Electrical Bus |  | H.4(b) Procedural Compliance | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | A self-revealing NCV of TS 5.4.1.(a), "Procedures", was identified in that FENOC failed to properly implement procedures and required actions in planning, tagging, and electrical system operation. A series of procedural use errors in control of maintenanc
Region: I | Beaver Valley | 6917 | 06/30/2008 08/13/2008 | 2008003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure Results in Unexpected Terry Turbine Speed Increase |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000334 Beaver Valley 1 |  | 71111.15 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified in that the licensee failed to incorporate sufficient assembly detail into the maintenance procedure for the governor linkage on the Turbi
Region: I | Beaver Valley | 6918 | 06/30/2008 08/13/2008 | 2008003-02 | Self - Revealed | FIN | Initiating Events | Green | Deficient Control of Clearance Posting Interrupts Reactor Coolant Charging Path while Vessel Water Level Drained below the Flange. |  | H.3(b) Work Activity Coordination | TE?: N | 05000412 Beaver Valley 2 |  | 71111.2 | A self-revealing finding was identified for failure to properly coordinate clearance activities associated with testing for penetration 2X-46 during reduced reactor coolant system (RCS) level. A decision to post a clearance to support penetration testing
Region: I | Beaver Valley | 6919 | 06/30/2008 08/13/2008 | 2008003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Properly Implement Operating Procedure during Plant Startup |  | H.1(c) Communication of Decisions | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | A Green self-revealing NCV of TS 5.4.1.(a) was identified in that the licensee failed to take appropriate action to trip the main turbine as specified in 2OM-52.4.A, "Raising Power from 5% to Full Load Operation," Rev. 13 during an unexpected main turbine
Region: I | Beaver Valley | 6905 | 06/30/2008 08/13/2008 | 2008003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Implement Abnormal Operating Procedure During Plant Startup |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000412 Beaver Valley 2 |  | 71153 | A Green self-revealing NCV of TS 5.4.1.(a) was identified in that the licensee failed to properly enter and implement the appropriate abnormal operating procedure (AOP) for loss of main feedwater. The licensee has developed and implemented an operations d
Region: I | Beaver Valley | 6916 | 03/31/2008 04/28/2008 | 2008002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Incorrect performance of Test Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000412 Beaver Valley 2 |  | 71152 | A self-revealing, Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XI "Test Control," was identified for the failure to properly perform line starter testing for a Unit 2 safety-related battery exhaust fan (2HVZ-FN216B) in accordance with the writt
Region: I | Beaver Valley | 6902 | 12/31/2007 02/13/2008 | 2007005-01 | NRC | FIN | Mitigating Systems | Green | Ineffective Corrective Action for Preventing Postponing of Safety Related Heat Exchanger Cleaning |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000412 Beaver Valley 2 |  | 7111107B | The inspectors identified a green finding because FENOC failed to meet a commitment made in their Generic Letter (GL) 89-13 program. Specifically, after a self-assessment identified the potential for postponing the cleaning of safety related heat exchange
Region: I | Beaver Valley | 6904 | 12/31/2007 02/13/2008 | 2007005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Comply with TS 3.8.1 Required Actions for One Offsite Power Source Inoperable |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000334 Beaver Valley 1 |  | 71111.13 | A green self-revealing NCV of TS LCO 3.8.1, "Electrical Power Systems - AC Sources - Operating," was identified due to FENOC's failure to comply with the LCO actions for one required offsite power circuit inoperable within the specified allowed time requi
Region: I | Beaver Valley | 6910 | 12/31/2007 02/13/2008 | 2007005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Control Work Activities Results in Degraded 'C' Steam Generator Water Level Alarm Function |  | H.3(b) Work Activity Coordination | TE?: N | 05000334 Beaver Valley 1 |  | 71111.19 | A green self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified in that the licensee failed to properly implement and control work activities associated with the alarm and status relays for Unit 1
Region: I | Beaver Valley | 6911 | 12/31/2007 02/13/2008 | 2007005-05 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Inspection and Subsequent Failure of Fuel Transfer Up-Ender Cable |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | A green self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified, in that FENOC failed to properly establish and implement adequate work instructions and acceptance criteria to inspect the fuel tra
Region: I | Beaver Valley | 6912 | 12/31/2007 02/13/2008 | 2007005-06 | NRC | NCV | Mitigating Systems | Green | Inadequate 10 CFR 50.59 Review results in Condition Beyond Design Basis during Test |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | The inspectors identified that the licensee did not perform an adequate safety evaluation in accordance with 10 CFR 50.59 associated with changing the periodicity of IST testing of valves MOV-1SI-890 A&B in May 2006. The review did not identify that the c
Region: I | Beaver Valley | 6899 | 09/28/2007 11/14/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE AND MONITORING PROGRAM FOR TURBINE-DRIVEN AUXILIARY FEEDWATER PUMP TURBINE, 1FW-T-2 |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71152 | Green. (Section 4OA2) The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to specify post-maintenance acceptance criteria for important turbine parameters af
Region: I | Beaver Valley | 6898 | 08/07/2007 11/14/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | POST-FIRE SAFE SHUTDOWN CAPABILITY DEGRADED DUE TO AMMONIA GAS HAZARD |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000412 Beaver Valley 2 |  | 71111.05Q | Green. (Section 1R05) The inspectors identified a non-cited violation (NCV) of Unit 2 license condition 2.F for failure to maintain adequate protection of a post-fire safe-shutdown area. Ammonia gas migrated through a floor drain, and concentrated in an a
Region: I | Beaver Valley | 6896 | 03/31/2007 04/13/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to effect timely and adequate corrective actions related to deficiencies in a safety-related river water valve pit. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000334 Beaver Valley 1 |  | 71111.06 | Green. (Section 1R06) The inspectors identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, for inadequate and untimely corrective actions regarding deficiencies in a safety-related river water valve pit at Unit 1. Specifically, the NRC
Region: I | Beaver Valley | 6897 | 03/31/2007 04/13/2007 | 2007002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement and control chemical addition activities results in a degraded auxiliary feedwater pump |  | H.3(b) Work Activity Coordination | TE?: N | 05000412 Beaver Valley 2 |  | 71111.15 | Green. (Section 1R15) A self-revealing, Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, was identified in that the licensee failed to properly implement and control chemical additions to the Unit 2 Steam Generators, which resulted in a valve be
Region: I | Beaver Valley | 6888 | 08/18/2006 11/09/2006 | 2006004-03 | Self - Revealed | NCV | Initiating Events | Green | HOT WORK RESULTS IN FIRE IN UNIT 1 WEST CABLE VAULT |  | H.4(b) Procedural Compliance | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | A self-revealing non-cited violation (NCV) of License Condition DPR-66 Section 2.C.5, Fire Protection Program, was identified for failure to follow plant fire protection procedures related to hot work and ignition control. On August 18, 2006, failure to a
Region: I | Beaver Valley | 6880 | 07/19/2006 11/09/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO VERIFY THE ADEQUACY OF A TEMPORARY DESIGN MODIFICATION ASSOCIATED WITH THE UNIT 2 CHILLED WATER SYSTEM |  |  | TE?: N | 05000412 Beaver Valley 2 |  | 7111123 | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for failure to provide for verifying the adequacy of design associated with a temporary design modification installed on the Unit 2 chilled wat
Region: I | Beaver Valley | 6881 | 07/19/2006 11/09/2006 | 2006004-02 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTION TO RESOLVE SLEEVE BEARING SET SCREW POSITION |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 |  | 71153 | A self-revealing, non-cited violation of 10 CFR 50,Appendix B, Criterion XVI, "Corrective Action," was identified on July 17, 2006, when the Unit 1 '3B' motor-driven auxiliary feedwater (MDAFW) pump [1FW-P-3B] inboard motor bearing oil was sampled and det
Region: I | Beaver Valley | 6877 | 06/30/2006 07/28/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM AN ADEQUATE OPERABILITY DETERMINATION FOR CURRENT LEAKAGE PAST MAIN STEAM SAFETY, DUMP AND RESIDUAL RELEASE VALVES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000334 Beaver Valley 1 |  | 71111.12 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion 16, for failure to perform an adequate operability evaluations for degraded components to assure off-site dose consequences are bounded in the radiological safety analysis for a SGTR eve
Region: I | Beaver Valley | 6872 | 03/31/2006 05/09/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO SCOPE A SEISMIC, SAFETY-RELATED STRUCTURE INTO THE MAINTENANCE RULE STRUCTURAL MONITORING PROGRAM |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71111.06 | The inspectors identified a Non-Cited Violation for failure to include seismic, safety-related valve pits for Unit 1 in the structural monitoring program of the maintenance rule as required by 10 CFR 50.65 (b). FENOC's failure to monitor valve pit structu
Region: I | Beaver Valley | 6873 | 03/31/2006 05/09/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS TO RESOLVE MAIN STEAM SAFETY VALVE (MSSV) COMPONENT DEFICEINCIES THAT WERE THE SUBJECT OF INDUSTRY OPERATING EXPERIENCE |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71111.15 | The inspectors identified a self-revealing Non-Cited Violation against 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, for inadequate corrective actions to resolve main steam safety valve (MSSV) component deficiencies in Unit 1. Specifically, th
Region: I | Beaver Valley | 6874 | 03/31/2006 05/09/2006 | 2006002-03 | NRC | FIN | Mitigating Systems | Green | FAILURE TO CONSIDER EXTERNAL EVENTS DURING REACTOR COOLANT SYSTEM DRAIN-DOWN ACTIVITIES |  |  | TE?: N | 05000334 Beaver Valley 1 |  | 71111.2 | The inspectors identified a finding which involved the failure to adequately plan for entry into a reduced inventory condition during the Unit 1 refueling outage. This resulted in an increased exposure to a reduced "time to boil". Controls were not in pla
Region: I | Calvert Cliffs | 126558 | 12/31/2019 02/14/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Fire Brigade Performance During an Unannounced Fire Drill |  | P.3 - Resolution | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 | Protection Against External Factors | 71152 | The inspectors identified a Green non-cited violation of Calvert Cliffs Nuclear Power Plant Renewed Facility Operating License DPR-53, DRP-69, Condition E, for the licensee’s failure to identify, address, and document deficiencies associated with the perf
Region: I | Calvert Cliffs | 124816 | 03/31/2019 05/07/2019 | 2019001-01 | NRC | NCV | Barrier Integrity | Green | Technical Specification Required Shutdown Due to Inoperable Containment Personnel Air Lock Not Performed as Required |  | H.14 - Conservative Bias | TE?: N | 05000318 Calvert Cliffs 2 | Human Performance | 71111.15 | The inspectors identified a Green non-cited violation (NCV) of CCNPP Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.2.D when Exelon did not place Unit 2 in MODE 3 and subsequently MODE 5 within the required completion times. This
Region: I | Calvert Cliffs | 124820 | 03/31/2019 05/07/2019 | 2019001-02 | NRC | NCV | Barrier Integrity | Green | Condition Adverse to Quality not Identified and Corrected Resulting in Exceeding Licensed Thermal Power Limit |  | P.5 - Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 | Procedure Quality | 71152 | The inspectors identified a Green NCV of 10 Code of Federal Regulation (CFR) 50, Appendix B, Criterion XVI, “Corrective Action,” for Exelon not identifying and correcting a condition adverse to quality. Specifically, from December 1, 2017 to November 24,
Region: I | Calvert Cliffs | 124606 | 03/31/2019 05/07/2019 | 2019001-03 | NRC | NCV | Mitigating Systems | Green | Fairbanks Morse Emergency Diesel Generator Air Start System Design Does Not Meet Single Failure Criteria |  | NPP | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 | Design Control | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, “Design Control,” for Exelon’s failure to ensure the adequacy of the Emergency Diesel Generator (EDG) starting system original design to meet the single failure criteria with r
Region: I | Calvert Cliffs | 25913 | 12/31/2018 02/01/2019 |  | NRC | FIN | Mitigating Systems | Green | Failure to Store and Maintain FLEX Equipment Such that Reliable Starting is Reasonably Assured During Extreme Cold |  | P.3 - Resolution | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 | Protection Against External Factors | 71152 | The inspectors identified a Green finding (FIN) for Exelon’s failure to ensure that diesel powered Diverse and Flexible Coping Strategies (FLEX) equipment would be reliable to mitigate postulated beyond-design basis external events during extreme cold con
Region: I | Calvert Cliffs | 23524 | 03/31/2018 05/09/2018 | 2018001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Conduct Adequate Radiation Surveys and Evaluate Potential Radiological Hazards |  | H.11 - Challenge the Unknown | TE?: N | 05000317 Calvert Cliffs 1 |  | 71124.01 | A self-revealed Green non-cited violation (NCV) of Title 10 Code of Federal Regulations (10 CFR) 20.1501, “Surveys and Monitoring: General,” was identified when Exelon failed to perform adequate surveys of the 11 reactor coolant pump bay area following th
Region: I | Calvert Cliffs | 22687 | 12/31/2017 02/08/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Fire Brigade Performance During an Announced Fire Drill | EA Case: 18-011 | P.6 - Self-Assessment | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.05A | Green. An NRC-identified Green non-cited violation (NCV) of Calvert Cliffs Nuclear Power Plant Renewed Facility Operating License DPR-53, DRP-69, Condition E, was identified for Exelon’s failure to adequately assess the performance of the fire brigade
Region: I | Calvert Cliffs | 19051 | 12/31/2016 02/10/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Inspection of Caulking, Seals, and Expansion Barriers in the Auxiliary Building |  | H.8 Procedure Adherence | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | -Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR), Appendix B, Criterion XVI, Corrective Action, for Exelon's failure to identify conditions adverse to quality at CCNPP. Specifically, several safety rela
Region: I | Calvert Cliffs | 19048 | 09/30/2016 10/31/2016 | 2016003-01 | NRC | NCV | Barrier Integrity | Green | Deficient Design Control of Air Pressure Available for Unit 1 Component Cooling Water Air Operated Valves |  | H.7 Documentation | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.18 | -Green. The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," for Exelon's failure to establish measures to assure that the design basis wa
Region: I | Calvert Cliffs | 19041 | 06/30/2016 08/03/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Failure to Implement Engineering Change Procedures Results in Plant Trip |  | H.7 Documentation | TE?: N | 05000318 Calvert Cliffs 2 |  | 71152 | -Green. The inspectors documented a self-revealing, Green finding for Exelon's failure to implement procedures for engineering changes. Specifically, Exelon failed to address the full scope and critical parameters associated with a modification to a steam
Region: I | Calvert Cliffs | 19047 | 06/30/2016 08/03/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Scaffolding Impairs Fire Sprinkler Systems in Safety Related Fire Areas |  | H.8 Procedure Adherence | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.05Q | -Green. The inspectors identified a Green, NCV of CCNPP Renewed Facility Operating License for Units One and Two, paragraph 2.E for Exelon's failure to maintain in effect all provisions of the approved fire protection program as described in the Updated F
Region: I | Calvert Cliffs | 19022 | 12/31/2015 02/09/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedures for the Control of Hazard Barriers During Maintenance |  | H.5 Work Management | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.04Q | -Green. The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1.a for Exelon's failure to implement procedures as required by Regulatory Guide (RG) 1.33, Appendix A, Section 1, "Administrative Procedures," during replacement of the 11
Region: I | Calvert Cliffs | 19023 | 12/31/2015 02/09/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | AFAS Channel Inoperable due to Valve Miss-position |  | H.11 Challenge the Unknown | TE?: N | 05000317 Calvert Cliffs 1 |  | 71153 | -Green. The inspectors documented a self-revealing Green NCV of TS 5.4.1.a for Exelon's failure to implement procedures as required by RG 1.33, Appendix A, Section 8, "Procedures for Control of Metering and Testing Equipment and for Surveillance Tests, Pr
Region: I | Calvert Cliffs | 19024 | 12/02/2015 01/13/2016 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Offsite Power Operability Limit |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.21M | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," because Exelon did not ensure the operability of of
Region: I | Calvert Cliffs | 19033 | 12/02/2015 01/13/2016 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify AC Equipment Operability at Design Loading and Voltage Levels |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.21M | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Exelon failed to verify, in design basis calculations, that all required Class 1E
Region: I | Calvert Cliffs | 19020 | 10/09/2015 11/30/2015 | 2015010-01 | NRC | NCV | Mitigating Systems | Green | Untimely Actions to Test or Inspect DFO Check Valves Relied on for Safety |  | H.8 Procedure Adherence | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152B | Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not assure that conditions adverse to quality were promptly corrected. Specifically
Region: I | Calvert Cliffs | 19016 | 09/30/2015 11/03/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish and Maintain Procedures for the Operation of the Diesel Fuel Oil System |  | P.5 Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | -Green. The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1.a for Exelon's failure to adequately establish and maintain procedures as required by Regulatory Guide (RG) 1.33, Appendix A, Section 3, "Procedures for Startup, Operation
Region: I | Calvert Cliffs | 19007 | 06/30/2015 07/27/2015 | 2015002-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Properly Ship Category 2 Radioactive Material - Quantity of Concern |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71124.07 | -Green. The inspectors identified a Green NCV of 10 CFR 71.5, "Transportation of Licensed Material," and CFR 172, Subpart I, "Safety and Security Plans." Specifically, Exelon personnel shipped a Category 2 radioactive material quantity of concern (RAM-QC)
Region: I | Calvert Cliffs | 19015 | 06/30/2015 07/27/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Instructions for Replacement of the Units 1 and 2 Containment Air Cooler Starters |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | -Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to include appropriate quantitative acceptance criteria for determinin
Region: I | Calvert Cliffs | 18998 | 03/31/2015 04/27/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Component Cooling Operated in Unanalyzed Condition |  | H.6 Design Margins | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04Q | Green: The inspectors identified a Green NCV of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, "Component Cooling (CC) System," and 3.0.3, because Exelon operated Units 1 and 2 CC systems in an unanalyzed condition on 18 occasi
Region: I | Calvert Cliffs | 19006 | 03/31/2015 04/27/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Management Action for LOCI Sequencer Maintenance |  | H.5 Work Management | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.15 | Green: The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) because Exelon did not implement adequate risk management actions (RMA) during the replacement of the loss of coolant incident (LOCI) sequence
Region: I | Calvert Cliffs | 18997 | 12/31/2014 01/22/2015 | 2014005-01 | NRC | NCV | Barrier Integrity | Green | Spent Fuel Pool Cask Handling Crane 10 CFR 50.65(a)(2) Performance Not Met |  | P.2 Evaluation | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.12 | -Green: The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(2), because Exelon did not adequately demons
Region: I | Calvert Cliffs | 18986 | 06/30/2014 08/08/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Main Steam Line Drain Containment Isolation Valves not Scoped in IST |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | -Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.55a, "Codes and Standards," for Exelon's failure to meet the test requirements set forth in the American Society of Mechanical Engineers (ASME) Code f
Region: I | Calvert Cliffs | 18994 | 06/30/2014 08/08/2014 | 2014003-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate EAL Initiating Condition HA3.1 |  | H.3 Change Management | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | -Green: The inspectors identified a Green NCV of 10 CFR 50.54 (q)(2) and 10 CFR 50.47(b)(4) because Exelon did not maintain the emergency plan to adequately meet the standards in 10 CFR 50.47(b)(4). Specifically, Exelon failed to include Unit 1 and Unit 2
Region: I | Calvert Cliffs | 18979 | 03/31/2014 05/09/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | 11 and 12 AFW Pumps Inoperable due to Valves Misposition |  | H.8 Procedure Adherence | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.15 | Green: The inspectors identified a self-revealing problem consisting of NCVs of TS 3.7.3, "Auxiliary Feedwater System," and TS 5.4.1, "Procedures," because CENG Operations personnel did not adhere to procedures which resulted in a valve mispositioning eve
Region: I | Calvert Cliffs | 18980 | 03/31/2014 05/09/2014 | 2014002-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Actions for Out of Service Letdown Radiation Monitor |  | H.5 Work Management | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.15 | Green: The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.54, "Conditions of Licenses," paragraph (q)(2), because CENG did not maintain the Emergency Plan to adequately meet the standards in 50.47(b)(4). Specifical
Region: I | Calvert Cliffs | 18985 | 03/31/2014 05/09/2014 | 2014002-03 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Loss of RCS Inventory During Lowered Inventory Conditions |  | H.4 Teamwork | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.2 | Green: The inspectors identified a self-revealing NCV of Technical Specification (TS) 5.4.1, "Procedures," for the failure of Constellation Energy Nuclear Group, LLC (CENG) personnel to adequately implement procedures associated with a local leak rate tes
Region: I | Calvert Cliffs | 18973 | 12/31/2013 02/07/2014 | 2013005-01 | NRC | NCV | Initiating Events | Green | Inadequate Emergency and Abnormal Operating Procedures for the Loss of the 21 DC Bus |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | Green. The inspectors identified an NCV of Technical Specification (TS) 5.4.1, "Procedures," because Constellation Energy Nuclear Group (CENG) failed to maintain adequate guidance in Emergency Operating Procedure (EOP) 8, "Functional Recovery Procedure,"
Region: I | Calvert Cliffs | 18974 | 12/31/2013 02/07/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Pre-Conditioning of Containment Air Coolers Emergency Outlet Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.22 | Green. The inspectors identified an NCV of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XI, "Test Control," because CENG's in-service test (IST) procedures did not provide instructions to preclude preconditioning of the containment
Region: I | Calvert Cliffs | 18969 | 09/30/2013 11/04/2013 | 2013004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Post-Maintenance Test Associated with an Atmospheric Dump Valve |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.19 | Green: The inspectors identified an NCV of Technical Specifications 5.4.1, "Procedures," for the failure of Constellation Energy Nuclear Group (CENG) personnel to establish, implement, and maintain maintenance requirements associated with No. 21 atmospher
Region: I | Calvert Cliffs | 18961 | 06/30/2013 07/31/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Test Program for DFO Check Valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04Q | -Green: The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XI, "Test Control," because CENG failed to establish a test program to ensure that diesel fuel oil (DFO) transfer system header chec
Region: I | Calvert Cliffs | 18967 | 06/30/2013 07/31/2013 | 2013003-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Steam Generator Tube Rupture Emergency Operating Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | Green: The inspectors identified an NCV of Technical Specification 5.4.1.b, "Procedures," because CENG failed to maintain guidance in Emergency Operating Procedure (EOP)-6, "Steam Generator Tube Rupture (SGTR)." Specifically, EOP-6 guidance does not provi
Region: I | Calvert Cliffs | 18949 | 03/31/2013 05/02/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Design Control Measures for Diesel Fuel Oil CloudPoint |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | Green: The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Constellation failed to provide design control measures to assure appropriate specifications were translated into procedures for diesel fuel oil (DF
Region: I | Calvert Cliffs | 18960 | 03/31/2013 05/02/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Technical Specification Surveillance Testing of the Diesel Fuel Oil Transfer System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.22 | Green: The inspectors identified an NCV of Technical Specification (TS) surveillance requirement (SR) 3.8.1.7 because Constellation failed to adequately perform SR associated with the DFO transfer system. Specifically, since approximately 1996, Constellat
Region: I | Calvert Cliffs | 18943 | 12/31/2012 02/07/2013 | 2012005-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Work Package Led to Reactor Coolant System Pressure Boundary Leakage |  |  | TE?: N | 05000317 Calvert Cliffs 1 |  | 71153 | Draft. A self-revealing NCV of technical specification (TS) 3.4.13, "Reactor Coolant System (RCS) Operational LEAKAGE," was identified because Constellation failed to restore the RCS to as-designed configuration following replacement of the 11A reactor co
Region: I | Calvert Cliffs | 18929 | 09/30/2012 11/06/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | 2A Diesel Generator Ventilation Train 10 CFR 50.65 (a)(2) Performance Demonstration Not Met |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.12 | An NRC-identified NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(2), was identified because Constellation personnel did not adequately demonstrate that the 2A diesel generator ven
Region: I | Calvert Cliffs | 18930 | 09/30/2012 11/06/2012 | 2012004-02 | NRC | FIN | Mitigating Systems | Green | Corrective Actions Not Completed for Drains in the Intake Structure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.12 | An NRC-identified finding of very low safety significance was identified because Constellation staff did not follow Procedure CNG-CA-1.01-1000, "Corrective Action Program." Specifically, Constellation staff did not complete corrective actions previously p
Region: I | Calvert Cliffs | 18936 | 09/30/2012 11/06/2012 | 2012004-03 | Self - Revealed | NCV | Initiating Events | Green | Unit 1 RCS Pressure Boundary Leakage |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.15 | A self-revealing NCV of Technical Specification (TS) 3.4.13, "Reactor Coolant System (RCS) operational LEAKAGE," was identified because Constellation failed to completely isolate a fault in the RCS pressure boundary, which resulted in Constellation operat
Region: I | Calvert Cliffs | 18937 | 09/30/2012 11/06/2012 | 2012004-04 | NRC | NCV | MISC | Green | Inattentive Non-Licensed Operator | EA Case: 2012009 |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | NONE | In accordance with Inspection Procedure 92702, "Followup on Traditional Enforcement Actions Including Violations, Deviations, Confirmatory Action Letters, Confirmatory Orders, and Alternative Dispute Resolution Confirmatory Orders," the inspectors conduct
Region: I | Calvert Cliffs | 17564 | 06/30/2012 07/25/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Testing Program for ESFAS SDS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04Q | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because Constellation did not establish an operational test program for the engineered safety features actuation system (ESFAS) shutdown sequencers (SDSs). Specifical
Region: I | Calvert Cliffs | 18942 | 06/30/2012 07/25/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish and Maintain Adequate Procedures for Maintenance on Pressurizer Power-Operated Relief Valves |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.12 | A self-revealing NCV of TS 5.4.1, "Administrative Controls - Procedures," was identified for the failure to establish and maintain adequate procedures for performing maintenance on pressurizer power operated relief valves (PORVs). Specifically, the mainte
Region: I | Calvert Cliffs | 18926 | 06/21/2012 08/24/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Violation of 10 CFR 50, Appendix B, Criterion III, Design Control - Inadequate Cooling to Containment Spray Pumps |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Constellation did not assure that design control measures verified or checked the adequacy of
Region: I | Calvert Cliffs | 18924 | 03/31/2012 05/02/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Test Program for Auxiliary Feedwater Emergency Air Accumulators |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.19 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," due to Constellation's failure to establish a test program to demonstrate that the auxiliary feedwater (AFW) air-operated valves (AOVs) will operate as design
Region: I | Calvert Cliffs | 18925 | 03/31/2012 05/02/2012 | 2012002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Replace Batter Charger Circuit Board within Its Recommended Service Life |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.19 | A self-revealing NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified for the failure of Constellation to establish, implement, and maintain preventive maintenance (PM) requirements associated with the safety related No. 16 battery ch
Region: I | Calvert Cliffs | 18907 | 12/31/2011 02/02/2012 | 2011005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Did Not Adequately Prescribe and Implement Procedures Associated with Protected Equipment |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04Q | Green: A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, "lnstructions, Procedures, and Drawings," was identified, because Constellation did not prescribe and accomplish procedures appropriate to the circumstances associated with protecte
Region: I | Calvert Cliffs | 18909 | 12/31/2011 02/02/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Annual Operating Tests Are Not Comprehensive |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.11B | Green: The inspectors identified an NCV of 10 CFR Part 55.59(aX2Xii) for Constellation's failure to adrninister annual operating tests to licensed operators to accomplish a comprehensive sample of items specified by 10 CFR Part 55.45(a)(7)&(8). Specific
Region: I | Calvert Cliffs | 18908 | 12/31/2011 02/02/2012 | 2011005-03 | Self - Revealed | FIN | Initiating Events | Green | Turbine Building Siding Failure Below Design Specification |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 |  | 71153 | Green: A self-revealing finding of very low safety significance was identified because Constellation did not ensure the turbine building (TB) siding was installed in accordance with design requirements of ES-005, Civil and Structural Design Criteria. Th
Region: I | Calvert Cliffs | 18911 | 12/31/2011 02/02/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Inspection of Floor Drains Led to Clogging and EDG Failure During Hurricane |  | H.4(b) Procedural Compliance | TE?: N | 05000317 Calvert Cliffs 1 |  | 71153 | Green: The inspectors identified an NCV of TS 5.4.1, "Procedures," because Constellation did not adequately implement the procedural requirements to conduct floor drain inspections. Specifically, operators did not ensure that floor drains were free to d
Region: I | Calvert Cliffs | 18913 | 09/30/2011 11/03/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with Submerged Saltwater Pump Motor Cables |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | Green: The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," because Constellation did not promptly identify and correct a condition adverse to quality associated with submerged saltwater (SW) pump motor sa
Region: I | Calvert Cliffs | 18918 | 09/30/2011 11/03/2011 | 2011004-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Actions for Out of Service High Range Effluent Radiation Monitors |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | Green. The inspectors identified an NCV of 10 CFR Part 50.54, "Conditions of Licenses," paragraph (q), because Constellation did not maintain the Emergency Plan to adequately meet the standards in 50.47(b). Specifically, Constellation periodically remov
Region: I | Calvert Cliffs | 18919 | 09/30/2011 11/03/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Pressurizer Safety Valves Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.22 | Green: The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," because Constellation did not promptly identify and correct a condition adverse to quality associated with the Unit 2 pressurizer safety valves (
Region: I | Calvert Cliffs | 18920 | 09/30/2011 11/03/2011 | 2011004-04 | Self - Revealed | NCV | Emergency Preparedness | Green | Lack of Proficiency Evaluating Seismic Recorder Data |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71153 | Green. A self-revealing NCV of 10 CFR Part 50.54, "Conditions of Licenses," paragraph (q), was identified because Constellation did not maintain the Emergency Plan to adequately meet the standards in 50.47(b). Specifically, Constellation did not have an
Region: I | Calvert Cliffs | 18446 | 03/31/2011 01/28/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Testing of PORVs in Accordance with ASME OM Code |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | Green. The inspectors identified a very low safety significance (Green) non-cited violation (NCV) of Technical Specification (TS) 5.5.8, Inservice Testing Program, involving Constellation?s failure to perform inservice tests (ISTs) for the pressurizer p
Region: I | Calvert Cliffs | 18447 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with Submerged SR Cables |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.06 | The inspectors identified an non cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," because Constellation did not establish and take adequate measures for conditions adverse to quality associated with submerged safet
Region: I | Calvert Cliffs | 18891 | 12/31/2010 01/28/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Written Procedures During Calibration of the 1A DG SR Ventilation Temperature Controller |  | H.4(a) Human Error Prevention | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.12 | A self-revealing finding of very low safety significance was identified because Constellation did not follow written procedures during the calibration of 1TIC10541 temperature controller. Specifically, the incorrect calibration of the 1TIC10541 temperatur
Region: I | Calvert Cliffs | 18899 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Functionality Review of 0C Diesel Degraded Condition. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance because Constellation did not conduct an adequate functionality review following failure of the 0C DG (the station blackout (SBO) diesel) battery charger. Specifically, Constellation did
Region: I | Calvert Cliffs | 18898 | 12/31/2010 01/28/2011 | 2010005-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement Procedures to Calibrate and Maintain Ventilaton and Radiation Effluent Monitoring Equipment. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | NONE | The inspectors identified a finding of very low safety significance associated with a non-cited violation (NCV) of Technical Specification 5.4.1.a, "Procedures," involving Constellation's failure to implement procedures to calibrate and maintain ventilati
Region: I | Calvert Cliffs | 18439 | 09/30/2010 11/04/2010 | 2010004-01 | NRC | NCV | Emergency Preparedness | Green | Untimely Declaration of Notice of Unusual Event | EA Case: 2010188 | H.1(a) Systematic Process for Decisions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71114.05 | The inspectors identified an NCV of 10 CFR Part 50.47(b)(4) for the failure to implement the emergency classification and action level scheme in a timely manner during an actual event due to the complete loss of communications to one off-site agency. Spec
Region: I | Calvert Cliffs | 18436 | 06/30/2010 08/04/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment Associated with the 2B EDG |  | H.3(a) Work Planning | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.13 | The inspectors identified an NCV of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Constellation did not perform an adequate risk assessment, which resulted in an underestimation a
Region: I | Calvert Cliffs | 18437 | 06/30/2010 08/04/2010 | 2010003-02 | NRC | NCV | Initiating Events | Green | Inadequate Design Control Reviews of the Turbine Control System and the Nuclear Steam Supply System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.18 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Constellation did not perform adequate design reviews associated with modifications to the turbine control system and the nuclear steam supply system
Region: I | Calvert Cliffs | 18438 | 06/30/2010 08/04/2010 | 2010003-03 | Self - Revealed | FIN | Initiating Events | Green | Did Not Establish Preventive Maintenance Program for Switchyard Panels |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71153 | Green. A self-revealing finding of very low safety significance was identified because Constellation did not establish an appropriate preventive maintenance program for the 125 VDC switchyard distribution panels in accordance with MN-1, "Maintenance Pro
Region: I | Calvert Cliffs | 18427 | 04/30/2010 06/14/2010 | 2010006-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Thoroughly Evaluate and Promptly Correct Degraded Conditions Associated with Auxiliary Building Roof Leakage |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 93812 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix , Criterion XVI "Corrective Actions," was identified, because auxiliary building roof leakage into the Unit 1 and Unit 2 45 foot switchgear rooms was identified on several occasions fr
Region: I | Calvert Cliffs | 18428 | 04/30/2010 06/14/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Degraded Conditions Associated with CO-8 Relays and Implement Timely and Effective Action to Correct the Condition Adverse to Quality. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 93812 | The team identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Constellation did not thoroughly evaluate and correct a degraded condition of a CO-8 relay disc sticking or binding issues which can adversely impact the funct
Region: I | Calvert Cliffs | 18426 | 04/30/2010 06/14/2010 | 2010006-04 | NRC | FIN | Initiating Events | Green | Failure to Translate Design Calculation Setpoint of Phase Overcurrent Relay on Feeder Breakers |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 93812 | The team identified a finding for failure to translate the design calculations of phase overcurrent relays on 13 kV feeder breakers into the actual relay settings. The overcurrent relays protect the unit service transformer against faults in the primary o
Region: I | Calvert Cliffs | 18435 | 04/30/2010 06/14/2010 | 2010006-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failed to Establish Adequate Procedures for Letdown Restoration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 93812 | A self-revealing NCV of Technical Specification (TS) 5.4.1.a, "Procedures" was identified for failure to establish adequate procedures for restoration of Chemical and Volume Control System (CVCS) letdown flow. On February 18, 2010, an electrical ground fa
Region: I | Calvert Cliffs | 18418 | 03/30/2010 05/05/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain Surveillance Procedures Associated with Fire Barrier and Penetration Seal Inspections |  | H.4(b) Procedural Compliance | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.05Q | The inspectors identified a non-cited violation (NCV) of Calvert Cliffs Renewed Facility Operating License Numbers DPR-53 and DPR-54, License Condition 2.E, because Constellation did not adequately implement and maintain surveillance procedures associated
Region: I | Calvert Cliffs | 18405 | 12/31/2009 01/26/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Associated with the Flooding of a Saltwater Pump Pit |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.06 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Constellation did not correctly translate the internal flooding design basis review for the saltwater (SW) pump pit compartments into specifications,
Region: I | Calvert Cliffs | 18406 | 12/31/2009 01/26/2010 | 2009005-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide for Adequate Dose Assessment with the Containment Outage Door Open |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50.54(q), "Conditions of Licenses," because Constellation did not properly maintain the conditions of the CCNPP Emergency Plan. Specifically, Constellation did not implement timely changes to the Emergency P
Region: I | Calvert Cliffs | 18412 | 12/31/2009 01/26/2010 | 2009005-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide for Adequate Compensatory Measures with the Wide Range Noble Gas Monitor Out of Service |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50.54(q), "Conditions of Licenses," because Constellation did not properly maintain the conditions of the CCNPP Emergency Plan. Specifically, Constellation did not implement timely changes to the Emergency P
Region: I | Calvert Cliffs | 18403 | 11/20/2009 12/29/2009 | 2009007-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Corrective Actions for Bay Water Level EAL Entry Criteria |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50.54(q), for Constellation's failure to maintain the Emergency Plan to adequately meet the standards in 50.47(b). Specifically, Constellation failed to correct a condition related to not having a clear meth
Region: I | Calvert Cliffs | 18401 | 09/30/2009 11/09/2009 | 2009004-01 | NRC | URI | MISC | Green | Saltwater Pump Pit Flooding Event |  |  | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.06
Region: I | Calvert Cliffs | 18402 | 09/30/2009 11/09/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Did Not Implement Corrective Action Program Procedure Requirements |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.19 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for Unit 2 because Constellation did not adequately implement the corrective action program (CAP) requirements contained in CNG-CA-1.01-
Region: I | Calvert Cliffs | 18394 | 08/28/2009 10/08/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of Safety Related Batteries |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," in that Constellation did not assure that required testing was performed in accordance with written test
Region: I | Calvert Cliffs | 18395 | 08/28/2009 10/08/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for 125 Vdc System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Constellation did not assure that the design basis was correctly translated into specificatio
Region: I | Calvert Cliffs | 18388 | 08/28/2009 10/08/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for 4 kV Bus Undervoltage Protection |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Constellation did not verify the adequacy of design with respect to establishing the basis fo
Region: I | Calvert Cliffs | 18400 | 08/28/2009 10/08/2009 | 2009006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Potential Air Entrainment in the ECCS |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Constellation did not ensure the adequacy of the emergency core cooling system (ECCS) design
Region: I | Calvert Cliffs | 18391 | 06/30/2009 07/31/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control associated with the Safety-Related Auxiliary Feedwater Pump Room Emergency Ventilation System |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for Units 1 and 2 because Constellation did not establish an adequate test program to assure that the auxiliary feedwater (AFW) pump room emergency ventilation s
Region: I | Calvert Cliffs | 18390 | 03/31/2009 05/13/2009 | 2009002-00 | NRC | URI | MISC | Green | Auxiliary Feedwater Pump Room Emergency Ventilation Low Flow |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15
Region: I | Calvert Cliffs | 18385 | 03/31/2009 05/13/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Did Not Follow MSIV Actuator System Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.12 | A self-revealing NCV of TS 5.4.1.a, "Procedures," was identified because Constellation did not follow procedures for refilling the No. 11 main steam isolation valve (MSIV) actuator accumulator with nitrogen. On February 6, 2009, while lining up to refill
Region: I | Calvert Cliffs | 18386 | 03/31/2009 05/13/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment Associated with the No. 21 Charging Pump |  | H.3(a) Work Planning | TE?: N | 05000318 Calvert Cliffs 2 |  | 71111.13 | The inspectors identified an NCV of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Constellation did not assess and manage the increase in risk that resulted from maintenance activ
Region: I | Calvert Cliffs | 18387 | 03/31/2009 05/13/2009 | 2009002-03 | NRC | NCV | Initiating Events | Green | Did Not Comply with Technical Specification Requirements While Starting Reactor Coolant Pumps |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.2 | The inspectors identified an NCV of Technical Specifications (TS) 3.4.5, "RCS Loops - Mode 3," because Constellation did not comply with the required starting conditions for reactor coolant pumps (RCPs) during several plant startups on Unit 1. The inspect
Region: I | Calvert Cliffs | 18389 | 03/31/2009 05/13/2009 | 2009002-04 | NRC | NCV | Occupational Radiation Safety | Green | Did Not Follow Radiation Protection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000318 Calvert Cliffs 2 |  | 7112101 | The inspectors identified an NCV of T.S. 5.4.1.a, "Procedures," because Constellation did not implement radiation protection procedural requirements for obtaining airborne radioactivity samples prior to workers entering the Unit 2 steam generators. Specif
Region: I | Calvert Cliffs | 18376 | 12/30/2008 01/27/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Associated with the Auxiliary Feedwater Pump Room Temperature. |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Constellation did not provide design control measures for verifying the adequacy of a design calculation used to determine the maximum initial room te
Region: I | Calvert Cliffs | 18381 | 12/30/2008 01/27/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Actions Associated with 480 Volt Power Supply Disconnects. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.22 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because Constellation did not take timely corrective actions following the identification of degraded 480 volt power supply handswitch disconnects. Thi
Region: I | Calvert Cliffs | 18374 | 09/29/2008 11/10/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct a degraded 12 CCHX SW outlet valve positioner in a timely manner. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.12 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Constellation did not promptly identify and correct a condition adverse to quality (CAQ) related to the Unit 1 No. 12 component cooling (CC) heat e
Region: I | Calvert Cliffs | 18375 | 09/29/2008 11/10/2008 | 2008004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish and Maintain Adequate Procedures for 4 kV Circuit Breaker Maintenance |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.19 | A self-revealing, NCV of Technical Specification (TS) 5.4.1.a, "Procedures," was identified because Constellation did not adequately establish and maintain electrical maintenance procedures for 4 kV circuit breakers such that the procedures incorporated t
Region: I | Calvert Cliffs | 18369 | 06/30/2008 08/01/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Associated with the safety Related 480V MCCs |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | The inspectors identified a finding of very low safety significance associated with an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Constellation did not correctly translate the design basis maximum expected temperature for
Region: I | Calvert Cliffs | 18370 | 06/30/2008 08/01/2008 | 2008003-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Measures to Implement EALs |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71153 | The inspectors identified an NCV of 10 CFR 50.47(b)(4) and Appendix E to 10 CFR 50, Sections IV.B and IV.C because Constellation did not have a clear method to assess and determine the bay water level such that the emergency action level (EAL) classificat
Region: I | Calvert Cliffs | 18368 | 06/20/2008 07/30/2008 | 2008009-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to identify an Inoperable Pressurizer Safety Valve |  |  | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified because Constellation did not identify a degraded pressurizer safety valve. Specifically, the team found that Constellation did not recognize t
Region: I | Calvert Cliffs | 18355 | 05/23/2008 05/09/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment Associated with the 2A Emergency diesel Generator |  | H.3(a) Work Planning | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.13 | The inspectors identified an NCV of 10 CFR Part 50.65 (a)(4) because Constellation did not assess and manage the increase in risk that resulted from maintenance activities on the alternate feeder breaker for the No. 21 4kV safety bus. On December 5, 2007,
Region: I | Calvert Cliffs | 18359 | 05/23/2008 05/09/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Did Not Implement Scaffolding Procedure Requirement |  | H.4(b) Procedural Compliance | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance associated with an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Constellation did not adequately implement scaffolding control require
Region: I | Calvert Cliffs | 18360 | 05/23/2008 05/09/2008 | 2008002-04 | NRC | NCV | Initiating Events | Green | Inadequate Procedures for Draining and Venting the Reactor Coolant System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.2 | The inspectors identified an NCV of Technical Specifications (TS) 5.4.1.a, "Procedures," because Constellation did not establish and maintain adequate procedures to vent the reactor vessel head (RVH). On February 25, 2008, operators drained the Unit 1 rea
Region: I | Calvert Cliffs | 18362 | 05/23/2008 06/24/2008 | 2008006-01 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Calvert Cliffs | 18352 | 12/28/2007 02/07/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Vent Procedure for the SW Strainer Pressure Transmitters |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.19 | An NRC-identified NCV of Technical Specifications (TS) 5.4.1.a, Procedures, was identified because Constellation did not establish and maintain an adequate procedure to vent and flush the saltwater (SW) strainer pressure transmitters and flow controllers.
Region: I | Calvert Cliffs | 18351 | 12/28/2007 02/07/2008 | 2007005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Reactor Operation Above Licensed Power Limit |  | H.4(b) Procedural Compliance | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | A self-revealing NCV of very low safety significance of License Condition 2.C.(1) to Renewed Facility Operating License DPR-69, occurred when Constellation operated Unit 2 in excess of the licensed power limit of 2700 megawatt thermal (MWTH). On December
Region: I | Calvert Cliffs | 18334 | 09/27/2007 11/13/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Procedures for EDG Maintenance |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.15 | A Green, self-revealing, NCV of Technical Specifications (TS) 5.4.1.a, "Procedures," was identified because Constellation did not establish and maintain emergency diesel generator (EDG) maintenance procedures that incorporated appropriate torque values
Region: I | Calvert Cliffs | 18341 | 09/27/2007 11/13/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Lack of Acceptance Limits for Thermal Performance Testing of Component Cooling Water Heat Exchangers |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.07A | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for Units 1 and 2 because Constellation did not incorporate acceptance limits contained in the design basis calculation into the thermal performance test procedure for
Region: I | Calvert Cliffs | 18342 | 09/27/2007 11/13/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Inoperable LRNI Channel Due to Incorrect Circuit Card Installation |  | H.4(a) Human Error Prevention | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | A Green, self-revealing, NCV of TS 3.3.1, "Reactor Protection System (RPS) Instrumentation," was identified because Constellation entered Modes 1 and 2 without the TS required number of linear range nuclear instrumentation (LRNI) channels operable. On Apr
Region: I | Calvert Cliffs | 18332 | 06/28/2007 08/06/2007 | 2007003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement TS 3.6.3 Required Actions for Containment Isolation Valves |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.04S | The inspectors identified a NCV of TS 3.6.3, Containment Isolation Valves, because Constellation did not implement actions as specified in TS 3.6.3. Specifically, Constellation did not include all containment isolation valves (CIVs) within the scope of TS
Region: I | Calvert Cliffs | 18331 | 06/28/2007 08/06/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate that the MSSV Performance Was Being Effectively Controlled per 10 CFR 50.65(a)(2). |  | P.1(b) Trend Performance CAP | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.12 | The inspectors identified a NCV of 10 CFR 50.65(a)(2) because Constellation did not demonstrate that performance monitoring of the main steam safety valves (MSSVs) was being effectively controlled through the performance of appropriate preventive maintena
Region: I | Calvert Cliffs | 18330 | 06/28/2007 08/06/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | Failure to Preclude Recurrence of a Significant Condition Adverse to Quality Associated with Power Operated Relief Valves |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," occurred because Constellation did not implement adequate corrective actions for a significant condition adverse to quality associated with the slow closure of a press
Region: I | Calvert Cliffs | 18328 | 06/28/2007 08/06/2007 | 2007003-04 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedures and maintain Configuration Control during Reactor Fill | EA Case: 2007003 | H.4(b) Procedural Compliance | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | The inspectors identified a NCV of Technical Specifications (TS) 5.4.1.a, Administrative Controls, because Constellation did not maintain equipment alignment in accordance with site procedures during drain and fill of the reactor coolant system (RCS). Spe
Region: I | Calvert Cliffs | 18329 | 06/28/2007 08/06/2007 | 2007003-05 | NRC | NCV | Initiating Events | Green | Failure to Adequately Maintain the RCS Reduced Inventory Procedure | EA Case: 2007003 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71153 | The inspectors identified a NCV of TS 5.4.1.a, Administrative Controls, when Constellation did not maintain an adequate procedure to drain and fill the RCS. Specifically, OP-7 permitted operation in a reduced RCS inventory condition without requiring redu
Region: I | Calvert Cliffs | 18323 | 03/31/2007 05/07/2007 | 2007002-01 | NRC | FIN | Mitigating Systems | Green | Failure To Take timely Actions To Evaluate And Correct Station Blackout Diesel Degraded Conditions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | The inspectors identified a finding for the failure to take timely action to evaluate and correct adverse conditions associated with the station blackout (SBO) diesel generator. During the February 14, 2007, performance evaluation, the SBO diesel experien
Region: I | Calvert Cliffs | 18324 | 03/31/2007 05/07/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Failure To Adequately Implement FME Procedures And Controls |  | H.4(b) Procedural Compliance | TE?: N | 05000317 Calvert Cliffs 1 |  | 71153 | A self-revealing non-cited violation (NCV) of Technical Specification 5.4.1.a occurred because Constellation did not adequately implement foreign material exclusion (FME) procedures and controls to prevent debris from entering the spent fuel pool (SFP). T
Region: I | Calvert Cliffs | 18327 | 03/31/2007 05/07/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Recognize That One Or More Channels Of The High-Rate-Of-Change Trip function Was Inoperable |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71153 | The inspectors identified a non-cited violation (NCV) of Technical Specification Limiting Condition for Operation (LCO) of 3.3.1 and 3.0.3 because Constellation did not recognize that one or more channels of the high rate-of-change (startup rate) trip fun
Region: I | Calvert Cliffs | 18315 | 12/31/2006 02/02/2007 | 2006005-02 | NRC | NCV | Initiating Events | Green | Inadequate Tagout Review Involving a Safety Related Offsite Power Supply |  | H.3(b) Work Activity Coordination | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | A Green self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a was identified for failure to adequately implement tagging procedures. This resulted in an unexpected reactor trip of Unit 2 during preparation for a maintenance acti
Region: I | Calvert Cliffs | 18316 | 12/31/2006 02/02/2007 | 2006005-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Post-Trip Review |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000318 Calvert Cliffs 2 |  | 71153 | Green. The inspectors identified a Green finding for the failure to adequately implement post trip review procedures required by Generic Letter (GL) 83-28, "Required Actions Based on Generic Implications of Salem ATWS Events." Specifically, Constellation'
Region: I | Calvert Cliffs | 18311 | 09/30/2006 11/09/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with TS for SRW and AFW with Watertight Doors Open |  | P.2(b) Implementing Operating Experience | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.15 | The Inspectors identified a non-cited violation (NCV) for the Service Water (SRW) and Auxiliary Feedwater (AFW) systems being inoperable without completing the actions required by Technicial Specifications. Constellation did not declare AFW and SRW trains
Region: I | Calvert Cliffs | 18312 | 09/30/2006 11/09/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with TS 5.4.1 for Salt Water Strainers |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152 | The inspectors identified a NCV of TS 5.4.1.a because Constellation did not initiate a condition report (CR) to document the adverse performance of the service water (SRW) heat exchanger salt water (SW) strainers during high debris loading as required in
Region: I | Calvert Cliffs | 18305 | 06/30/2006 07/21/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish reference values or reconfirm previous values following maintenance that affected reference values of the AFW and ECCS pumps |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR 50.55a, Codes and Standards, because the licensee did not establish new reference values or reconfirm the previous reference values following maintenance that affected hydraulic or mechanical param
Region: I | Calvert Cliffs | 18301 | 03/31/2006 05/05/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Evaluation for Repetitive Functional Failures |  |  | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of 10CFR50.65 ("the Maintenance Rule") paragraph (a)(2) in that the licensee failed to demonstrate that the performance of service water turbine building isolation valves were being effectively control
Region: I | Calvert Cliffs | 18302 | 03/31/2006 05/05/2006 | 2006002-02 | NRC | NCV | Initiating Events | Green | Failure to establish adequate physical boundaries for RCP maintenance |  |  | TE?: N | 05000317 Calvert Cliffs 1 |  | 71111.2 | Green. A self-revealing non-cited violation of Technical Specification 5.4.1 occurred when requirements contained in plant procedure NO-1-112, Safety Tagging, were not adequately implemented prior to maintenance on the 12A reactor coolant pump. Specifical
Region: I | Calvert Cliffs | 18303 | 03/31/2006 05/05/2006 | 2006002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to properly control access to a high radiation area |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 7112101 | Green. A self-revealing non-cited violation (NCV) associated with the alternate access control requirements established in accordance with 10 CFR 20.1601 (c), was identified. Specifically, the licensee failed to control and properly post a high radiation
Region: I | Calvert Cliffs | 124610 | 05/07/2019 |  |  | LIV |  | Green | Licensee Identified NCV Failure to Maintain Minimum Emergency Response Organization Onsite Staffing |  |  | TE?: N | 05000317 Calvert Cliffs 1 05000318 Calvert Cliffs 2 |  | 71152
Region: I | Crystal River | 32341 | 07/31/2013 08/28/2013 | 2013003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Use Process or Engineering Controls to Control Airborne Radioactivity |  |  | TE?: N | 05000302 Crystal River 3 |  | 71124.03 | A Green self-revealing non-cited violation (NCV) of 10 CFR 20.1701 was identified for the licensee's failure to implement process or other engineering controls, to the extent practical, to control the concentration of radioactive materials in air. Specifi
Region: I | Crystal River | 32339 | 07/14/2011 08/10/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fire Loading Within Allowable Limits |  |  | TE?: N | 05000302 Crystal River 3 |  | NONE | -Green. The inspectors identified two examples of a non-cited violation of Crystal River Unit 3 Operating License Condition 2.C (9), for the failure to adequately evaluate changes to the approved Fire Protection Program. Specifically, in 1999, and 2003, t
Region: I | Crystal River | 32340 | 07/14/2011 08/10/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure OP-880B for Turbine Building Post-Fire Safe Shutdown |  | H.3(b) Work Activity Coordination | TE?: N | 05000302 Crystal River 3 |  | NONE | -Green. The inspectors identified a non-cited violation of Crystal River Unit 3 (CR3) Technical Specification 5.6.1.1.a., for inadequate guidance in procedure OP-880B, Appendix "R" Turbine Building Post-Fire Safe Shutdown Information. Specifically, the pr
Region: I | Crystal River | 32336 | 03/31/2011 04/27/2011 | 2011002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Operating Crew Failures on the 2011 Annual Requalification Operating Test |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000302 Crystal River 3 |  | 71111.11Q | A self-revealing Green finding, associated with operating crew performance on the simulator during facility-administered requalification examination was identified. Two of the eight crews evaluated failed to pass their simulator examinations. As immediate
Region: I | Crystal River | 32330 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Flood Calculations did not Reflect Plant Configuration |  |  | TE?: N | 05000302 Crystal River 3 |  | 71111.06 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion III, "Design Control," regarding the licensee's failure to ensure that the design bases of two components were correctly translated into specifications, drawings, pro
Region: I | Crystal River | 32331 | 09/30/2010 10/29/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Inoperable Fire Barrier Penetration Seals |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000302 Crystal River 3 |  | 71111.05Q | The inspectors identified an NCV, with five examples, of Crystal River Unit 3 Operating License Condition 2.C (9), fire protection program. The NCV was associated with one inoperable fire penetration seal in the ceiling of the B train decay heat and build
Region: I | Crystal River | 32332 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Submit Production Splices of Swaged Mechanical Splices for the Testing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000302 Crystal River 3 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure to establish measures to assure that testing of rebar splices
Region: I | Crystal River | 32333 | 08/27/2010 09/28/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Preconditioning of Safety-Related Air Operated Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000302 Crystal River 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, Test Control for preconditioning of a safety-related air operated valve prior to surveillance testing. The licensee entered this deficiency into their corrective action
Region: I | Crystal River | 32334 | 08/27/2010 09/28/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Requirements of Recovering from a Station Blackout into Calculations |  |  | TE?: N | 05000302 Crystal River 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.63, Loss of all alternating current power, for failure to ensure Regulatory Guide 1.155, Station Blackout commitments were implemented in calculations for restoring off-site power. The licensee entere
Region: I | Crystal River | 32335 | 08/27/2010 09/28/2010 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Service Water and Decay Cooling Expansion Tank Check Valves |  |  | TE?: N | 05000302 Crystal River 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.65(a)(1) for the licensee's failure to monitor service water and decay heat cooling expansion tank level indicator check valves. In response to this concern, the licensee closed the isolation valves a
Region: I | Crystal River | 32326 | 03/31/2010 04/27/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Compensatory Actions When a MCR to CSR Floor/Ceiling Interface Access Hatch Was Open |  |  | TE?: N | 05000302 Crystal River 3 |  | 71153 | The inspectors identified a non-cited violation of Crystal River Unit 3 Operating License Condition 2.C.(9), for failure to take compensatory actions when a main control room (MCR) and cable spreading room (CSR) floor/ceiling interface access hatch was op
Region: I | Crystal River | 32320 | 12/31/2009 01/25/2010 | 2009005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow a Plant Procedure Resulted in an Inoperable HPI System |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000302 Crystal River 3 |  | 71153 | A self-revealing Non-Cited Violation (NCV) of Improved Technical Specification (ITS) 5.6.1.1.a was identified for the failure to follow a plant procedure which resulted in a loss of a 480 volt engineered safeguards motor control center (ES MCC)-3B1. Concu
Region: I | Crystal River | 32325 | 12/31/2009 01/25/2010 | 2009005-02 | Self - Revealed | NCV | Initiating Events | Green | Manual Reactor Trip Due to Group 7 Control Rods Insertion Caused by Inadequately Protected Test Jumper (Section 4OA3.3) |  | H.4(b) Procedural Compliance | TE?: N | 05000302 Crystal River 3 |  | 71153 | A self-revealing NCV of Improved Technical Specification (ITS) 5.6.1.1.a was identified for the failure to follow the provisions of preventative maintenance procedure PM-126, Electrical Checks of CRD [Control Rod Drive] Power Train. Failure to follow PM-1
Region: I | Crystal River | 32319 | 09/30/2009 10/29/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessments When Performing Surveillance Testing |  |  | TE?: N | 05000302 Crystal River 3 |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(4) for the failure to perform adequate risk assessments associated with a number of surveillance tests. Specifically, it was determined that risk assessments were not being properly
Region: I | Crystal River | 32314 | 03/31/2009 04/30/2009 | 2009002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Have Adequate Controls in Place to Ensure the Temperature of the Emergency Diesel Room was Maintained to Support EGDG Operability |  |  | TE?: N | 05000302 Crystal River 3 |  | 71152 | A self-revealing finding was identified for failing to have adequate controls in place to ensure the temperature of the emergency diesel room was maintained to support emergency diesel generator (EGDG) operability. As a result, during cold weather conditi
Region: I | Crystal River | 32315 | 03/31/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely and Effective Corrective Actions Resulted in a Repeat Failure of a Main Feedwater Isolation Valve due to Magnesium Rotor Oxidation/Corrosion |  | P.2(b) Implementing Operating Experience | TE?: N | 05000302 Crystal River 3 |  | 71153 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, for failure to take timely and effective corrective actions to prevent a second failure of a main feedwater isolation valve (MFIV) due to corrosion of the valve a
Region: I | Crystal River | 32318 | 03/31/2009 04/30/2009 | 2009002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Peer and Peer Checking Resulted in Connecting Improper Test Equipment and a Manual Plant Trip |  | H.4(a) Human Error Prevention | TE?: N | 05000302 Crystal River 3 |  | 71153 | A self-revealing finding was identified for the failure to follow procedure HUM-NGGC-0001, Human Performance Program, which required workers to perform self and peer checks to ensure the correct action is performed on the correct component. Specifically,
Region: I | Crystal River | 31135 | 03/31/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Inoperable Fire Penetration Seal |  |  | TE?: N | 05000302 Crystal River 3 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of Crystal River Unit 3 Operating License Condition 2.C(9), Fire Protection Program. The NCV was associated with an inoperable fire penetration seal in the 3-hour fire rated ceiling of the makeup
Region: I | Crystal River | 31141 | 03/31/2008 04/30/2008 | 2008002-02 | NRC | FIN | Initiating Events | Green | Failure to Implement Adequate Equipment Protection Resulted in a Plant Transient |  | H.3(a) Work Planning | TE?: N | 05000302 Crystal River 3 |  | 71152 | A self-revealing finding was identified for failure to prevent inadvertent bumping of the condensate pump control switch during maintenance activities. As a result of bumping the control switch, a condensate pump had to be secured and reactor power was ra
Region: I | Crystal River | 31137 | 02/15/2008 03/31/2008 | 2008006-01 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustibles |  | H.4(b) Procedural Compliance | TE?: N | 05000302 Crystal River 3 |  | 7111105P | The team identified a non-cited violation of Crystal River Unit 3 Operating License Condition 2.C.(9), for the licensee's failure to properly implement fire protection program procedures for control of transient combustible materials. Specifically, transi
Region: I | Crystal River | 31138 | 02/15/2008 03/31/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Protect Cables for Valve DHV-42 |  |  | TE?: N | 05000302 Crystal River 3 |  | 7111105P | The team identified a non-cited violation of 10 CFR 50, Appendix R, Section III.G.2., for failure to protect cables from fire damage for components required for safe shutdown. Specifically, the Mecatiss MTS-3 fire wrap installed around the cables for valv
Region: I | Crystal River | 31140 | 02/15/2008 03/31/2008 | 2008006-04 | Self - Revealed | NCV | Initiating Events | Green | Reactor Coolant Pump 1B Lube Oil Collection System Leakage |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000302 Crystal River 3 |  | 7111105P | A self-revealing non-cited violation of 10 CFR 50, Appendix R, Section III.O, was identified for failure of the reactor coolant pump (RCP) oil collection system to collect and drain RCP oil leakage to a vented closed container. Specifically, the licensee
Region: I | Crystal River | 31134 | 12/31/2007 01/29/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedural Guidance Associated with Removal of Containment Debris |  | H.4(b) Procedural Compliance | TE?: N | 05000302 Crystal River 3 |  | 71111.2 | The inspectors identified a non-cited violation (NCV) of Improved Technical Specification 5.6.1.1.a, for failure to adequately implement procedures required by Regulatory Guide 1.33, Appendix A, Section 3, Procedures for Startup, Operation, and Shutdown o
Region: I | Crystal River | 31129 | 10/05/2007 10/31/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Violation of Technical Specification 5.6.1 for Failure to Implement an Adequate Procedure for Manual Starting of the Control Complex Chilled Water Chiller Units (CHHE-1A/1B) Following a LBLOCA |  |  | TE?: N | 05000302 Crystal River 3 |  | 7111121 | The inspectors identified a finding of very low safety significance involving a violation of Technical Specifications (TS) 5.6.1 for failure to implement an adequate procedure for manual starting of the Control Complex Chilled Water Chiller Units (CHHE-1A
Region: I | Crystal River | 31130 | 10/05/2007 10/31/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Violation of 10 CFR 50, Appendix B, Criterion XI for Failure to Account for Instrument Uncertainty During EFP-2 Testing |  |  | TE?: N | 05000302 Crystal River 3 |  | 7111121 | The inspectors identified a finding of very low safety significance involving a violation of 10 CFR 50, Appendix B, Criterion XI, Test Control, for failure to implement a test program which accounted for the effects of instrument uncertainty on surveillan
Region: I | Crystal River | 31128 | 06/30/2007 07/13/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance Procedures for Hydrostatic Seals Necessary to Protect Safety-Related Equipment from Internal Flooding |  |  | TE?: N | 05000302 Crystal River 3 |  | 71111.06 | The inspectors identified a non-cited violation (NCV) of Improved Technical Specification 5.6.1.1.a, for failure to adequately establish and implement procedures required by Regulatory Guide 1.33, Appendix A, Section 9, Procedures for Performing Maintenan
Region: I | Crystal River | 31125 | 03/31/2007 04/13/2007 | 2007002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Address Marine Fouling Resulted in a Plant Transient |  | P.2(b) Implementing Operating Experience | TE?: N | 05000302 Crystal River 3 |  | 71152 | A self-revealing finding was identified for the failure to address the marine fouling failure mode in the scope of the existing preventive maintenance on the intake screen wash auto start system. As a result, reactor power had to be decreased to 80 percen
Region: I | Crystal River | 31126 | 03/31/2007 04/13/2007 | 2007002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Replace a Non-refurbished ICS Module Resulted in a Reactor Trip |  | H.1(c) Communication of Decisions | TE?: N | 05000302 Crystal River 3 |  | 71153 | A self-revealing finding was identified for failure to replace a non-refurbished integrated control system (ICS) multiplier module that had been temporarily installed during the Fall 2005 refueling outage. As a result, an age-related failure of a multipli
Region: I | Crystal River | 31127 | 03/31/2007 04/13/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Repetitive Raw Water System Flush Water Strainer Baskets Degradation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000302 Crystal River 3 |  | 71153 | A self-revealing, non-cited Violation of 10 CFR 50, Appendix B, Criterion XVI was identified for failure to identify and take appropriate corrective actions for repetitive failures of the raw water pumps bearing flush water strainer baskets. As a result,
Region: I | Crystal River | 31123 | 12/31/2006 01/25/2007 | 2006005-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Conduct Adequate Surveys for Liquid Effluent Releases |  |  | TE?: N | 05000302 Crystal River 3 |  | 7112201 | The inspectors identified a non-cited violation (NCV) of 10 CFR 20.1501(a) for failure to perform accurate surveys to demonstrate compliance with Technical Specification (TS) 5.6.2.3 Offsite Dose Calculation Manual (ODCM) controls used to maintain doses t
Region: I | Crystal River | 31106 | 06/23/2006 07/20/2006 | 2006009-01 | NRC | FIN | Mitigating Systems | Green | Failure to Conduct an Extent of Condition Review after Three Motor Operated Valves Were Found with Their Pinion Gears Installed Incorrectly |  |  | TE?: N | 05000302 Crystal River 3 |  | 71152B | A Green finding was identified by the inspectors for failure to conduct an extent of condition evaluation when three motor operated valves (MOVs) which were thought to not be susceptible to incorrect pinion gear installation were found with their pinion g
Region: I | FitzPatrick | 126387 | 12/31/2019 02/05/2020 | 2019004-01 | NRC | FIN | Initiating Events | Green | Inadequate Work Instructions result in 71T-3 Reserve Station Transformer Unavailability |  | NONE | TE?: N | 05000333 FitzPatrick | Procedure Quality | 71111.18 | The inspectors identified a Green finding associated with EN-WM-105, “Planning“, Revision 6, when FitzPatrick failed to develop adequate work instructions associated with a receipt internal inspection of the 71T-3 115-kilovolt reserve station transformer
Region: I | FitzPatrick | 126423 | 12/31/2019 02/05/2020 | 2019004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Results in Loss of ‘B’ Battery Room Ventilation |  | H.1 - Resources | TE?: N | 05000333 FitzPatrick | Design Control | 71111.19 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, Design Control,” because Exelon failed to adequately translate the design associated with a modificatio
Region: I | FitzPatrick | 125568 | 08/01/2019 08/29/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Correction Factors for Lake Level in Emergency Service Water Test Procedures |  | NPP | TE?: N | 05000333 FitzPatrick | Design Control | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control.” Specifically, Exelon failed to include appropriate correction factors for lake level in procedure S
Region: I | FitzPatrick | 124988 | 06/30/2019 08/12/2019 | 2019002-01 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Exposure Greater Than 50 Percent of the Estimate |  | H.5 - Work Management | TE?: N | 05000333 FitzPatrick | Program & Process | 71124.02 | Green self-revealing finding was identified because Exelon did not adequately follow their as low as reasonably achievable (ALARA) procedure during the most recent refueling outage. Specifically, Exelon did not follow procedure RP-AA-401, “ALARA Planning
Region: I | FitzPatrick | 124984 | 05/09/2019 06/28/2019 | 2019010-01 | NRC | FIN | Mitigating Systems | Green | Finding - Failure to perform functionality determination |  | H.12 - Avoid Complacency | TE?: N | 05000333 FitzPatrick |  | 71152B | The inspectors identified a finding of very low safety significance (Green) because the licensee did not assess the effects of a degraded condition involving the Reactor Building Closed Loop Cooling (RBCLC) system as required by plant procedures.
Region: I | FitzPatrick | 124699 | 03/31/2019 05/14/2019 | 2019001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify and Correct Condition Adverse to Quality Associated with Damaged Reactor Building Siding |  | P.2 - Evaluation | TE?: N | 05000333 FitzPatrick | Configuration Control | 71111.12 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for Exelon’s failure to promptly correct a condition adverse to quality. Specifically, damaged exterior siding on the reactor b
Region: I | FitzPatrick | 24024 | 04/12/2018 04/30/2018 | 2018411-02 | NRC | NCV |  | Green | Failure to Report a Programmatic Failure in the FFD Program |  |  | TE?: N | 05000333 FitzPatrick |  | 71130.08 | ***OFFICIAL USE ONLY - SECURITY RELATED INFORMATION*** The inspectors identified a Severity Level IV non-cited violation (NCV) of 10 CFR 26.719(b)(4), for Exelon’s failure to report any degradation, or discovered vulnerability of the FFD program. Spe
Region: I | FitzPatrick | 22649 | 12/31/2017 02/14/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Battery Sizing Calculation |  | NPP | TE?: N | 05000333 FitzPatrick |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Exelon did not verify the adequacy of the Low Pressure Coolant Injection (LPCI) Motor Operated Valve (MOV) Independent Power Supply (IPS) with resp
Region: I | FitzPatrick | 22672 | 12/31/2017 02/14/2018 | 2017004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Human Error Resulting in Unplanned HPCI Isolation |  | H.12 - Avoid Complacency | TE?: N | 05000333 FitzPatrick |  | 71153 | A self-revealing NCV of very low safety significance (Green) of T.S. 5.4 “Procedures” was identified for a procedural error which resulted in the inadvertent isolation of the high pressure coolant injection (HPCI) system. Specifically, on April 4, 2017 an
Region: I | FitzPatrick | 28006 | 06/30/2017 08/07/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | Control Room Emergency Ventilation Air Suply (CREVAS) System |  | P.2 Evaluation | TE?: N | 05000333 FitzPatrick |  | 71153 | A self-revealing Green NCV of Technical Specification (TS) 3.7.3, "Control Room Emergency Ventilation Air Supply (CREVAS) System," and TS 3.7.4, "Control Room Air Conditioning (AC) System," was identified for the failure to declare one subsystem of the co
Region: I | FitzPatrick | 27999 | 12/31/2016 02/14/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure Proper Configuration Control of a PCIV During Planned Maintenance |  | H.11 Challenge the Unknown | TE?: N | 05000333 FitzPatrick |  | 71111.15 | An NRC-identified Green NCV of TS 5.4, "Procedures" was identified because Entergy staff did not implement procedure AP-12.06, "Equipment Status Control," as required. Specifically, Entergy personnel did not recognize the impact of a change associated wit
Region: I | FitzPatrick | 27998 | 09/30/2016 11/10/2016 | 2016003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Preventive Maintenance Results In Transformer Failure and Reactor Scram |  |  | TE?: N | 05000333 FitzPatrick |  | 71153 | A self-revealing Green finding (FIN) was identified for Entergy staff's failure to properly implement the requirements of EN-DC-324, "Preventive Maintenance Program," Revision 16, to ensure proper preventive maintenance (PM) was implemented for non-safety
Region: I | FitzPatrick | 27993 | 06/30/2016 08/12/2016 | 2016002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Determine Dose Rates Piror to Entering a High Radiation Area (Section 2RS1) |  | H.4 Teamwork | TE?: N | 05000333 FitzPatrick |  | 71124.01 | The inspectors identified a self-revealing, Green NCV of technical specification (TS) 5.7.1, "High Radiation Area." Specifically, on January 24 and 25, 2016, operations personnel failed to notify the Radiation Protection (RP) department and non-licensed o
Region: I | FitzPatrick | 27994 | 06/30/2016 08/12/2016 | 2016002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conduct Operations to Minimize the Introduction of Residual Radioactivity to the Site (Section 2RS8) |  | P.3 Resolution | TE?: N | 05000333 FitzPatrick |  | 71124.08 | The NRC identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 20.1406(c) due to Entergy not conducting operations to minimize the introduction of residual radioactivity into the site. For at least the past four years, Entergy allo
Region: I | FitzPatrick | 27988 | 03/31/2016 05/13/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Unintended HPCI Pump Suction Transfer during Pressure Control Mode Operation |  | H.8 Procedure Adherence | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to maintain a condition specified in an emergency operating procedure. Specifi
Region: I | FitzPatrick | 27989 | 03/31/2016 05/13/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Uncontrolled RPV Level Increase after Initiation of RHR Shutdown Cooling |  | H.11 Challenge the Unknown | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to take actions specified in the procedure for initiation of shutdown cooling. Specifically, prior to placing the 'A' loop o
Region: I | FitzPatrick | 27990 | 03/31/2016 05/13/2016 | 2016001-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Post-Maintenance Testing of the Reactor Building Ventilation System Resulted in Short-Term Inoperability of Secondary Containment |  | H.1 Resources | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a self-revealing NCV of TS 5.4, "Procedures," for FitzPatrick staff's failure to perform adequate post-maintenance testing (PMT) following maintenance on a limit switch in the reactor building ventilation system in August 2014, t
Region: I | FitzPatrick | 27986 | 12/31/2015 02/10/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Unintended Elevated Plant Risk During EDG Maintenance |  | H.5 Work Management | TE?: N | 05000333 FitzPatrick |  | 71111.13 | The inspectors identified a Green NCV of Title10 of the Code of Federal Regulations (10 CFR) 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," for failure to adequately manage the increase in risk during planne
Region: I | FitzPatrick | 27984 | 09/30/2015 11/06/2015 | 2015003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Corrective Actions Result in Control Rod Drift and Reactor Power Reduction |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.15 | A self-revealing NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified because FitzPatrick staff failed to correct a condition adverse to quality. Specifically, Entergy failed t
Region: I | FitzPatrick | 27985 | 09/30/2015 11/06/2015 | 2015003-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Instructions for Reactor Building Roof Relacement Result in Inadvertent Loss of Secondary Containment |  | H.12 Avoid Complacency | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a self-revealing violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because FitzPatrick staff failed to provide instructions appropriate to the reactor building roof replacement projec
Region: I | FitzPatrick | 27983 | 06/26/2015 08/06/2015 | 2015007-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess the Impact of SRV Leakage on Operability |  | H.14 Conservative Bias | TE?: N | 05000333 FitzPatrick |  | 71111.17T | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50 Appendix B Criterion III, Design Control, associated with Fitzpatrick's failure to adequately assess and control the acceptance criteria
Region: I | FitzPatrick | 27975 | 03/31/2015 04/28/2015 | 2015001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Incomplete Fuel Support Piece Seating Not Identified During Post-Refueling Core Verification |  | H.8 Procedure Adherence | TE?: N | 05000333 FitzPatrick |  | 71111.15 | A self-revealing, Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because the existence of a partially seated fuel support piece at reactor cell locatio
Region: I | FitzPatrick | 27976 | 03/31/2015 04/28/2015 | 2015001-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Preventive Maintenance Strategy and Test Procedure for RWR MG Resulted in Multiple Plant Transients |  | H.1 Resources | TE?: N | 05000333 FitzPatrick |  | 71152 | A self-revealing, Green non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was identified for failure to institute appropriate processes and procedures for periodic maintenance activities of the reactor water recirculation motor
Region: I | FitzPatrick | 27970 | 12/31/2014 02/06/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | TS Actions for Inoperable ECCS Not Performed Within the TS Allowed Completion Time |  | P.3 Resolution | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a Green non-cited violation (NCV) for two violations of Technical Specification (TS) 3.5.1, "ECCS [emergency core cooling systems] - Operating," associated with the non-functionality of east crescent area ventilation and cooling
Region: I | FitzPatrick | 27960 | 06/30/2014 08/08/2014 | 2014003-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Properly Ship RAM-QC |  | H.7 Documentation | TE?: N | 05000333 FitzPatrick |  | 71124.08 | Green. The inspectors identified a Green NCV of 10 CFR 71.5, "Transportation of Licensed Material," and 49 CFR 172, Subpart I, "Safety and Security Plans." Specifically, Entergy personnel shipped a radioactive quantity of category 2 Radioactive Material i
Region: I | FitzPatrick | 27954 | 03/31/2014 04/28/2014 | 2014002-01 | NRC | NCV | Initiating Events | Green | HPCI System Inoperable for Longer than Allowed by TS |  | P.5 Operating Experience | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a Green NCV of Technical Specification (TS) 3.5.1, "ECCS [emergency core cooling system] - Operating," because filling the high pressure coolant injection (HPCI) system with low quality water from the suppression pool following m
Region: I | FitzPatrick | 27946 | 09/30/2013 11/06/2013 | 2013004-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Reactor Water Recirculation Digital Flow Control Modification Post-Maintenance Test Procedure Results in Unexpected Power Increase |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71111.18 | The inspectors identified a Green self-revealing non-cited violation of Technical Specification (TS) 5.4, "Procedures," because Entergy Nuclear Northeast (Entergy) staff did not adequately preplan the implementation of a plant modification to install a di
Region: I | FitzPatrick | 27947 | 07/11/2013 08/23/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Position EDG Room Ventilation Temperature Controllers in Automatic |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non cited violation of Technical Specification (TS) 5.4, "Procedures." Specifically, following EDG maintenance, operators did not restore the 'A' and 'C' EDG ventilation sys
Region: I | FitzPatrick | 27948 | 07/11/2013 08/23/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of the FOTP NPSH |  |  | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy had not verified the adequacy of the existing design analyses for the ava
Region: I | FitzPatrick | 27934 | 06/30/2013 07/26/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Technical Specification Actions for Inoperable Control Rod Not Performed Within the Technical Specification Allowed Completion |  | H.1(c) Communication of Decisions | TE?: N | 05000333 FitzPatrick |  | 71111.15 | The inspectors identified a non-cited violation of technical specification (TS) 3.1.3, "Control Rod Operability," because Entergy operators did not take the required actions within the allowed completion time in response to indication that the scram capab
Region: I | FitzPatrick | 27935 | 06/30/2013 07/26/2013 | 2013003-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Corrective Action for Decay Heat Removal System Degradation Results in Loss of Decay Heat Removal During Refueling Outage 20 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71152 | A self-revealing finding (FIN) was identified for a loss of decay heat removal (DHR) during refueling outage 20 (R20) that was the result of inadequately remediated DHR system degradation. Specifically, prior to using the system during R20, Entergy did no
Region: I | FitzPatrick | 27917 | 12/31/2012 02/07/2013 | 2012005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Install Reserve Station Service Transformers in Accordance with Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a self-revealing, Green non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," because FitzPatrick personnel did not perform installation of replacement reserve station service transformers (RSSTs) 71T-2 a
Region: I | FitzPatrick | 27923 | 12/31/2012 02/07/2013 | 2012005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of 'A' EDG Output Breaker to Close Following Loss of Offsite Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a self-revealing, Green non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," because Entergy did not establish and implement an adequate procedure for installation of a 4160 volt alternating current (VAC
Region: I | FitzPatrick | 27916 | 09/30/2012 11/07/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action to Address Crescent Area Unit Cooler Operability |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because FitzPatrick staff did not take timely corrective action to verify that a crescent area unit cooler was operable under postul
Region: I | FitzPatrick | 27909 | 06/30/2012 08/07/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure During Removal from Service of Emergency Diesel Generator Ventilation |  | H.4(b) Procedural Compliance | TE?: N | 05000333 FitzPatrick |  | 71111.13 | The inspectors identified a self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," because Entergy personnel did not adequately implement procedures when removing the ventilation system for the 'A' emergency diesel gen
Region: I | FitzPatrick | 27910 | 06/30/2012 08/07/2012 | 2012003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Installation of Reactor Water Recirculation Motor-Generator Scoop Tube Positioners |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71152 | The inspectors identified a self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," because Entergy staff did not provide adequate procedures for installation of a plant modification to replace the reactor water recircu
Region: I | FitzPatrick | 27894 | 12/31/2011 02/07/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Mode Switch in Shutdown Scram Function Inoperable in Excess of the TS Allowed Outage Time due to Personnel Error |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000333 FitzPatrick |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 3.3.1.1, "Reactor Protection System (RPS) Instrumentation," because FitzPatrick operators did not take required action within the allowed completion time in response to
Region: I | FitzPatrick | 27901 | 12/31/2011 02/07/2012 | 2011005-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Inadequate Work Planning for 'A' Reactor Recirculation Pump Replacement. |  | H.3(b) Work Activity Coordination | TE?: N | 05000333 FitzPatrick |  | 71124.02 | The inspectors identified a self-revealing finding that involved inadequate work planning relative to the 'A' recirculation pump replacement work during refueling outage R19 that resulted in additional unplanned collective exposure (39.168 person-rem comp
Region: I | FitzPatrick | 27902 | 12/31/2011 02/07/2012 | 2011005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000333 FitzPatrick |  | 71124.02 | The inspectors identified a self-revealing NCV of TS 5.4, "Procedures," which requires that written procedures be implemented covering the activities in the applicable procedures recommended by Regulatory Guide 1.33, including procedures for RWPs and ALAR
Region: I | FitzPatrick | 27900 | 12/31/2011 02/07/2012 | 2011005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Ineffective Corrective Action for RCIC Steam Admission Valve Malfunction |  | H.3(a) Work Planning | TE?: N | 05000333 FitzPatrick |  | 71153 | The inspectors identified a self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy personnel did not promptly correct the intermittent failure of reactor core isolation cooling (RCIC) steam admission valve 13MOV-1
Region: I | FitzPatrick | 27890 | 06/30/2011 08/05/2011 | 2011003-02 | NRC | URI | Initiating Events | Green | Source Range Monitor Operability Requirements during Core Alterations |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.2 | The inspectors identified an unresolved item (URI) associated with the adequacy of the bases for a change to the definition of "core quadrant" as applied to refueling operations that was implemented by the FitzPatrick staff in 2004. During core alteration
Region: I | FitzPatrick | 27882 | 03/31/2011 05/04/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Control Room Envelope Inoperable due to Unlatched Boundary Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000333 FitzPatrick |  | 71152 | The inspectors identified a non-cited violation (NCV) of very low safety significance of 10 CFR 50, Criterion XVI, "Corrective Action," because Entergy personnel did not identify and correct a condition adverse to quality related to a control room envelop
Region: I | FitzPatrick | 27876 | 12/31/2010 02/10/2011 | 2010005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Refueling Water Level Control Resulted in Overflowing of Reactor Cavity Water in the Reactor Building |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71111.2 | A self-revealing NCV of very low safety significance of technical specification (TS) 5.4, "Procedures," was identified because Entergy procedure OP-30A, "Refueling Water Level Control," did not provide adequate guidance to operators for filling the rea
Region: I | FitzPatrick | 27881 | 12/31/2010 02/10/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Equipment Status Control for a Manually Operated Normally Locked Open Residual Heat Removal Injection Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000333 FitzPatrick |  | 71111.2 | A self-revealing NCV of very low safety significance of TS 5.4, "Procedures," was identified because Entergy personnel did not implement AP-12.06, "Equipment Status Control," as required. Specifically, Entergy personneldid not maintain status control a
Region: I | FitzPatrick | 27874 | 09/30/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Appendix R Fire Door Blocked Open Without Establishing Required Measures |  | H.4(b) Procedural Compliance | TE?: N | 05000333 FitzPatrick |  | 71111.05Q | The inspectors identified a non-cited violation (NCV) of very low safety significance of license condition 2.C(3), "Fire Protection," because Entergy personnel blocked a fire door in the open position, defeating its required three hour fire barrier functi
Region: I | FitzPatrick | 27866 | 07/02/2010 08/13/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Use Largest Load During EDG Reject Surveillance Test |  |  | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding involving a non-cited violation of James A. FitzPatrick Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.8 because Entergy did not adequately perform the largest post-accident load rejection test as require
Region: I | FitzPatrick | 27867 | 07/02/2010 08/13/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Calculations for Offsite Power Availability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Entergy did not verify the adequacy of design with respect to establishing the basis for the offsite power minimum voltage a
Region: I | FitzPatrick | 27868 | 07/02/2010 08/13/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action on RHRSW Strainer Housing Wall Degradation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding involving a non-cited violation of 10 CFR 50, Appendix 8, Criterion XVI, "Corrective Actions," for failure to identify and correct a condition adverse to quality. Specifically, Entergy did not take corrective actions to ev
Region: I | FitzPatrick | 27862 | 06/30/2010 08/04/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Fire Barrier Penetrations Not Maintained as Qualified Three Hour Fire Barriers |  | H.4(a) Human Error Prevention | TE?: N | 05000333 FitzPatrick |  | 71111.05Q | A self-revealing non-cited violation (NCV) of very low safety significance of license condition 2.C(3), "Fire Protection," was identified because Entergy personnel did not implement and maintain in effect all provisions of the approved fire protection pro
Region: I | FitzPatrick | 27856 | 12/31/2009 02/08/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Emergency Lighting Not Monitored in Accordance with 10 CFR Part 50.65 (a)(1) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71111.12 | The inspectors identified an NCV of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy staff did not demonstrate that the performance of the emergency lighting system had been effecti
Region: I | FitzPatrick | 27860 | 12/31/2009 02/08/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Standby Liquid Control Not Monitored in Accordance with 10 CFR Part 50.65 (a)(1) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71111.12 | The inspectors identified an NCV of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy staff did not demonstrate that the performance of the standby liquid control (SLC) system had be
Region: I | FitzPatrick | 27855 | 09/30/2009 10/30/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | HELB Barrier Doors Left Open and Unattended |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000333 FitzPatrick |  | 71111.04Q | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy personnel did not maintain an adequate high energy line break (HELB) barrier. Specifically, the inspectors identified that th
Region: I | FitzPatrick | 27843 | 06/30/2009 08/12/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | High Energy Line Break Door Missing Lower Support |  | H.4(a) Human Error Prevention | TE?: N | 05000333 FitzPatrick |  | 71111.04Q | The inspectors identified an NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Entergy personnel did not maintain a high energy line break (HELB) barrier. Specifically, HELB door 76 FDR-DG-272-11, locat
Region: I | FitzPatrick | 27846 | 06/30/2009 08/12/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize an Adverse HPCI Performance Trend. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71111.15 | A self-revealing NCV of very low safety significance of 10 CFR 50.55a, "Codes and Standards," was identified because Entergy personnel did not comply with the in-service testing (IST) program requirements contained within the applicable American Society o
Region: I | FitzPatrick | 27847 | 06/30/2009 08/12/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Balance Chamber Pressure for the HPCI Turbine Stop Valve Was Not Set at a Value to Ensure HPCI Operation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000333 FitzPatrick |  | 71111.22 | A self-revealing NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy personnel did not identify and correct a condition adverse to quality related to the HPCI system which caused
Region: I | FitzPatrick | 27848 | 06/30/2009 08/12/2009 | 2009003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize an Adverse EDG Rotor Insulation Performance Trend. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000333 FitzPatrick |  | 71111.22 | A self-revealing NCV of very low safety significance of 10 CFR 50, Criterion XVI, "Corrective Action," was identified because Entergy personnel did not identify and correct a condition adverse to quality related to the emergency diesel generator (EDG) sys
Region: I | FitzPatrick | 27854 | 06/30/2009 08/12/2009 | 2009003-05 | NRC | FIN | Occupational Radiation Safety | Green | Inadequate Work Planning for Strain Gauge Resulted in Unplanned Exposure) |  | H.3(a) Work Planning | TE?: N | 05000333 FitzPatrick |  | 7112102 | A self-revealing finding of very low safety significance was identified because Entergy personnel did not adequately plan and prevent unnecessary exposure consistent with Radiation Work Permit No. 08-0524 controls. Specifically, Entergy staff work plannin
Region: I | FitzPatrick | 27840 | 03/31/2009 05/07/2009 | 2009002-01 | NRC | NCV | Barrier Integrity | Green | Inoperable Control Room Envelope Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000333 FitzPatrick |  | 71111.22 | The inspectors identified an NCV of very low safety significance of 10 CFR 50, Criterion XVI, "Corrective Action," because Entergy did not identify and correct a condition adverse to quality related to a control room envelope boundary door. Specifically,
Region: I | FitzPatrick | 27831 | 12/30/2008 01/29/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Quality Standards Not Specified in Design Documents that Resulted in Unsupported HPCI Oil Tubing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71111.04Q | An NRC identified NCV of 10 CFR 50 Appendix B, Criterion III, "Design Control," was identified when Entergy did not assure that appropriate quality standards were specified and included in design documents and that deviations from such standards were cont
Region: I | FitzPatrick | 27832 | 12/30/2008 01/29/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Conduct of Relay Test Without Plant Impact Review Resulted in Loss of Emergency Bus and Shutdown Cooling |  | H.3(b) Work Activity Coordination | TE?: N | 05000333 FitzPatrick |  | 71111.2 | A self-revealing NCV of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified when Entergy did not manage the increase in risk during the conduct of relay testing associated with e
Region: I | FitzPatrick | 27826 | 09/29/2008 11/07/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Manage Risk During Maintenance Activity Resulted in Loss of Shutdown Cooling |  | H.3(b) Work Activity Coordination | TE?: N | 05000333 FitzPatrick |  | 71111.2 | A self-revealing NCV of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified when Entergy did not manage the increase in risk that resulted from removal of the 'B' reactor protect
Region: I | FitzPatrick | 27821 | 08/01/2008 09/02/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | RHR Service Water SOV Corrective Actions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000333 FitzPatrick |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not implement adequate corrective actions for the residual heat r
Region: I | FitzPatrick | 27818 | 06/30/2008 08/05/2008 | 2008003-02 | NRC | FIN | Initiating Events | Green | Surge arresters not replaced in accordance with preventive maintenance program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71111.13 | A self-revealing finding was identified when one of the 115 kV offsite power transformer 71T-3 surge arresters failed in-service. Specifically, Entergy did not adequately implement maintenance program expectations outlined in EN-DC-324, "Preventive Mainte
Region: I | FitzPatrick | 27819 | 06/30/2008 08/05/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Quality standards not specified in design documents that resulted in deficient B LPCI battery cable bend radii. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 71111.19 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy did not ensure that appropriate quality standards were specified and included in design documents and that deviations from such
Region: I | FitzPatrick | 27811 | 05/16/2008 06/16/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Guidance to Address Spurious Failures of the RCIC and LPCI Systems |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.05T | The team identified a Green non-cited violation of technical specification 5.4.1.d for failure to provide adequate procedure directions in Attachment 6 of AOP-28, "Operation During Plant Fires," Rev. 18, for operators to restore the RCIC system and secu
Region: I | FitzPatrick | 27805 | 12/31/2007 01/29/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Risk Assessment When Required by 10 CFR Part 50.65(a)(4) |  | H.4(a) Human Error Prevention | TE?: N | 05000333 FitzPatrick |  | 71111.13 | A self-revealing NCV of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified when Entergy failed to perform a risk assessment prior to commencing performance of Instrument Surveil
Region: I | FitzPatrick | 27806 | 12/31/2007 01/29/2008 | 2007005-02 | NRC | NCV | Initiating Events | Green | Failure to Implement Procedure Associated with Lake Condition Monitoring |  | H.4(b) Procedural Compliance | TE?: N | 05000333 FitzPatrick |  | 71153 | A self-revealing NCV of Technical Specification 5.4, "Procedures," was identified when operators did not implement certain steps specified in Operations Shift Standing Order 2007-020, "Lake Condition Monitoring," Revision 4, which increased the likelihood
Region: I | FitzPatrick | 27810 | 12/31/2007 01/29/2008 | 2007005-03 | NRC | FIN | Initiating Events | Green | Feedwater Low Flow Control Valve Degradation Led to Primary Containment Isolation System Group Two Isolation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000333 FitzPatrick |  | 71153 | A self-revealing finding was identified involving inadequate corrective actions when Entergy failed to correct the adverse condition of the feedwater low-flow control valve, 34FCV-137. Entergy also failed to implement corrective actions in a timely manner
Region: I | FitzPatrick | 27804 | 09/28/2007 11/02/2007 | 2007004-01 | NRC | FIN | Mitigating Systems | Green | Failure to correct negative slope of the reactor core isolation cooling system flow instrument sensing lines. |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.12 | A self-revealing finding was identified involving inadequate corrective actions when Entergy did not correct an adverse condition on the reactor core isolation cooling (RCIC) system flow instrument sensing lines. The condition allowed air bubbles to form
Region: I | FitzPatrick | 27797 | 07/20/2007 08/31/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain adequate design basis calculations for safety-related motors. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The team determined that Entergy did not maintain appropriate design basis calculations to ensure that t
Region: I | FitzPatrick | 27798 | 07/20/2007 08/31/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | EDG FOST capacity calculation did not account for vortexing. |  | P.3(a) Self-Assessment | TE?: N | 05000333 FitzPatrick |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The team determined that Entergy failed to properly identify and evaluate the potential for vortexing in
Region: I | FitzPatrick | 27795 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Maintenance on Containment Atmosphere Control Valve |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.13 | A Green, self-revealing, non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when Entergy failed to properly implement a torus exhaust v
Region: I | FitzPatrick | 27796 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a Risk Assessment When Required by 10 CFR Para 50.65(a)(4) |  | H.3(a) Work Planning | TE?: N | 05000333 FitzPatrick |  | 71111.13 | A Green, self-revealing, NCV of 10 CFR Part 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants" was identified when Entergy did not perform a risk assessment for planned maintenance activities when a tagout
Region: I | FitzPatrick | 27794 | 07/28/2006 09/11/2006 | 2006006-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Demonstrate that 'B' Train Stack High Range Effluent Radiation Monitor Sample Pump Performance was Effectively Controlled per 10 CFR 50.65(a)(2) |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000333 FitzPatrick |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50.65(a)(2), for Entergy's failure to appropriately classify the January 2006 failure of the 'B' train sample pump, 17P-4B, as a mainten
Region: I | FitzPatrick | 125250 | 08/12/2019 |  |  | LIV |  | Green | Work Management Deficiency Leads to Failure to Correct Wall Thinning on the 'B' Emergency Service Water Strainer |  |  | TE?: N | 05000333 FitzPatrick |  | 71111.15
Region: I | Ginna | 125253 | 06/28/2019 09/18/2019 | 2019010-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Testing as Required by ASME Code |  | NPP | TE?: N | 05000244 Ginna | Equipment Performance | 71111.21M | The team identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.55a, "Codes and Standards," for Exelon’s failure to perform required testing set forth in the American Society of Mechanical Engineers (ASME) Code for Operation and
Region: I | Ginna | 125254 | 06/28/2019 09/18/2019 | 2019010-02 | NRC | NOV | Mitigating Systems | Green | Failure to Ensure Electrical and Seismic Design Requirements of Motor Control Center C and D |  | NONE | TE?: N | 05000244 Ginna | Protection Against External Factors | 71111.21M | The team identified a cited violation (CV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, “Design Control,” because the licensee did not ensure that applicable regulatory requirements and the design basis were tra
Region: I | Ginna | 124711 | 03/31/2019 05/07/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Turbine Driven Auxiliary Feedwater Lubricating Oil Accumulator Degraded Air Pressure |  | H.14 - Conservative Bias | TE?: N | 05000244 Ginna | Equipment Performance | 71111.22 | The NRC identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, “Corrective Action,” and an associated violation of Technical Specification 3.7.5.C.1, when Exelon personnel did not prom
Region: I | Ginna | 25968 | 12/31/2018 01/29/2019 | 2018004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate implementation of troubleshooting plan causes a loss of bus 12A and ESF actuation |  | H.11 - Challenge the Unknown | TE?: N | 05000244 Ginna | Human Performance | 71153 | The inspectors identified a Green, self-revealed finding for Exelon’s failure to adequately implement a troubleshooting plan, in accordance with MA-AA-716-004, Attachment 1 “Troubleshooting Log”. Specifically, on October 26, 2018, Exelon staff did not fol
Region: I | Ginna | 24668 | 09/30/2018 11/02/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Procedurally Vent Flow Transmitter Results in Auxiliary Feedwater Train Inoperable |  | P.1 - Identification | TE?: N | 05000244 Ginna |  | 71111.22 | An NRC identified Green Non Cited Violation (NCV) of Technical Specification 5.4.1.a, “Procedures,” was identified for the failure of Exelon to adequately ensure entrapped air from instrument lines associated with flow transmitters FT-2002 and FT-2014
Region: I | Ginna | 24377 | 06/30/2018 08/02/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Scaling Factors in Reactor Vessel Level Monitoring System Instrumentation Uncertainty Calculation |  |  | TE?: N | 05000244 Ginna |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when Exelon failed to ensure that adequate design control measures existed to verify the adequacy of the RVLMS uncertainty calculation. Specifically, Exe
Region: I | Ginna | 24077 | 04/19/2018 05/16/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Potential Preconditioning of Turbine Driven Auxiliary Feedwater Surveillance Testing |  | NPP | TE?: N | 05000244 Ginna |  | 71152B | The NRC identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XI, "Test Control," because Exelon established unevaluated preconditioning, with a reasonable doubt of whether the
Region: I | Ginna | 24082 | 04/19/2018 05/16/2018 | 2018011-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Procedurally Verify Fuel Transfer Cart Results in Fuel Interference Event |  | H.12 - Avoid Complacency | TE?: N | 05000244 Ginna |  | 71152B | A self-revealing Green non-cited violation (NCV) of Technical Specification 5.4.1.a, "Procedures, " was identified for the failure of Exelon to operate refueling equipment in accordance with technical procedures in April and May of 2017, which resulted in
Region: I | Ginna | 22685 | 12/31/2017 02/01/2018 | 2017004-01 | NRC | FIN | Initiating Events | Green | Inadequate Component Monitoring Relating to Online Risk Management and Assessment |  | H.12 - Avoid Complacency | TE?: N | 05000244 Ginna |  | 71111.13 | The inspectors identified a finding because Exelon personnel did not follow Procedure WC-AA-101-1006, “On-Line Risk Management and Assessment,” Revision 2 to sufficiently monitor components such that the latest information was used to evaluate pla
Region: I | Ginna | 14662 | 09/30/2016 11/07/2016 | 2016003-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform Drills Required by the Site Emergency Plan. |  | H.8 Procedure Adherence | TE?: N | 05000244 Ginna |  | 71114.03 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2) for Exelon's failure to maintain an emergency plan that meets the requirements in Appendix E, "Content of Emergency Plans," to Part 5
Region: I | Ginna | 14647 | 06/30/2015 07/27/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform 1-Hour Fire Tours as Required by the Technical Requirements Manual |  | H.1 Resources | TE?: N | 05000244 Ginna |  | 71111.05Q | The inspectors identified a Green non-cited violation of Ginna Operating License Condition 2.C.(3), "Fire Protection," because Exelon Generation Company, LLC (Exelon) failed to perform 1-hour compensatory fire tours as required by Ginna's Technical Requir
Region: I | Ginna | 14648 | 06/30/2015 07/27/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Implementation Results in Inadvertent Entry into 72-Hour Technical Specification Action Statement |  | H.12 Avoid Complacency | TE?: N | 05000244 Ginna |  | 71111.12 | A self-revealing Green non-cited violation of Technical Specification (TS) 5.4.1, "Procedures," was identified for inadequate implementation of procedure M-71.4, "Removal and/or Installation of Modules within Defeated or Out-of-Service Instrument Loops."
Region: I | Ginna | 14649 | 06/30/2015 07/27/2015 | 2015002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Preferred Auxiliary Feedwater Protection from Potential Block Wall Failures |  | P.1 Identification | TE?: N | 05000244 Ginna |  | 71111.18 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," because Exelon Generation Company, LLC (Exelon) did not provide for verifying or checking the ad
Region: I | Ginna | 14640 | 03/31/2015 05/12/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Result in Failure of Bus 18 Undervoltage Solid State Switchboard Card |  |  | TE?: N | 05000244 Ginna |  | 71111.12 | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR), Appendix B, Criterion XVI, "Corrective Action," was identified for failure to establish measures to assure that a condition adverse to quality associated with the availabi
Region: I | Ginna | 14641 | 03/31/2015 05/12/2015 | 2015001-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Inadequate Protective Action Recommendation Flowchart |  | H.3 Change Management | TE?: N | 05000244 Ginna |  | 71114.04 | A self-revealing Green NCV of 10 CFR 50.54(q)(2), 10 CFR 50.47(b)(10), and 10 CFR 50, Appendix E, "Emergency Planning and Preparedness for Production and Utilization Facilities," Section IV.B.1, was identified for Exelon inadequately maintaining the effec
Region: I | Ginna | 14635 | 09/30/2014 11/03/2014 | 2014004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Packages Associated with Maintenance on the Main Generator Exciter Air Cooler Reversing Head |  | P.1 Identification | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing Green finding was identified for inadequate development and maintenance of work packages as required by Exelon Generation Company, LLC (Exelon) procedure CNG-MN-4.01-1003, "Work Order Planning," Revision 00701. Specifically, the work pack
Region: I | Ginna | 14634 | 08/22/2014 09/29/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control for Main Steam Isolation Valve (MSIV) Solenoid-Operated Valves |  |  | TE?: N | 05000244 Ginna |  | 71111.17T | The inspectors identified a finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XI, "Test Control," in that Exelon Generation Company, LLC (Exelon) did n
Region: I | Ginna | 14633 | 06/30/2014 07/24/2014 | 2014003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Implementation Results in Inadvertent Engineered Safety Feature Actuation |  | H.12 Avoid Complacency | TE?: N | 05000244 Ginna |  | 71111.2 | A self-revealing Green non-cited violation of Technical Specification 5.4.1, "Procedures," was identified for failure to perform maintenance as required by Exelon Generation Company, LLC (Exelon) procedure STP-I-9.1.16, "Undervoltage Protection - 480 Volt
Region: I | Ginna | 14624 | 03/31/2014 04/25/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Preventive Maintenance Program Procedure for a Service Water Pump Motor |  |  | TE?: N | 05000244 Ginna |  | 71111.12 | A self-revealing Green non-cited violation of Technical Specification (TS) 5.4.1, "Procedures," was identified for failure to modify an existing preventive maintenance (PM) task or schedule in accordance with Constellation Energy Nuclear Group's, LLC (CEN
Region: I | Ginna | 14625 | 03/31/2014 04/25/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Design Basis Analysis for the Emergency Diesel Generators Accounted for Limiting Cold Weather Conditions and Loading |  |  | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," because Constellation Energy Nuclear Group, LLC (CENG) did not ensure that the requirements and
Region: I | Ginna | 14630 | 03/31/2014 04/25/2014 | 2014002-03 | NRC | NCV | Emergency Preparedness | Green | Failure of Emergency Preparedness Drill Critique to Identify a Risk-Significant Planning Standard Weakness |  | H.14 Conservative Bias | TE?: N | 05000244 Ginna |  | 71114.06 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.47(b)(14) and 10 CFR 50, Appendix E, " Emergency Planning and Preparedness for Production and Utilization Facilities," Section IV.F.2.g. Speci
Region: I | Ginna | 14631 | 03/31/2014 04/25/2014 | 2014002-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adhere to Procedural Requirements for Authorizing the Application of a Tagout |  | H.12 Avoid Complacency | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing Green finding (FIN) was identified because Constellation Energy Nuclear Group, LLC (CENG) failed to authorize the application of a tagout in accordance with procedure CNG-OP-1.01-1007, "Clearance and Safety Tagging," Revision 01101. Speci
Region: I | Ginna | 14616 | 03/13/2014 04/11/2014 | 2014008-01 | NRC | FIN | Initiating Events | Green | Failure to Effectively Implement Corrective Actions Associated with Heater Drain Tank Pump Tripping Issues |  | H.8 Procedure Adherence | TE?: N | 05000244 Ginna |  | 71152B | The inspectors identified a Green finding (FIN) for Constellation Energy Nuclear Group's, LLC (CENG's) failure to effectively implement a corrective action (CA) associated with an apparent cause evaluation (ACE) that addressed both heater drain tank pumps
Region: I | Ginna | 14610 | 12/31/2013 02/14/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Programmatic Failure to Scope SSCs within the Maintenance Rule Monitoring Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.12 | The inspectors identified a non-cited violation of Title 10 of the Code of Federal Regulations 50.65(b) because CENG did not include safety-related and non-safety-related structures, systems, and components (SSCs) within the scope of the maintenance rule
Region: I | Ginna | 14611 | 12/31/2013 02/14/2014 | 2013005-03 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Modify or Establish a PM for the TDAFW DC Lube Oil Pump Switch |  |  | TE?: N | 05000244 Ginna |  | 71111.12 | A self-revealing Green finding was identified for failure to modify or establish a preventive maintenance (PM) schedule for the turbine-driven auxiliary feedwater (TDAFW) direct current (DC) lube oil pump control switch. On November 18, 2013, plant person
Region: I | Ginna | 14593 | 09/30/2013 11/12/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Scaffolding Procedure Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.13 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Constellation Energy Nuclear Group, LLC (CENG) personnel did not accomplish
Region: I | Ginna | 14594 | 09/30/2013 11/12/2013 | 2013004-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Guidance for Workers to Implement a Modification to the Main Generator Digital Protection Relays |  | H.3(b) Work Activity Coordination | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing Green finding was identified for inadequate guidance as required by Constellation Energy Nuclear Group, LLC (CENG) procedure CNG-PR-1.01-1005, "Control of Constellation Nuclear Generation Technical Procedure Format and Content," Revision
Region: I | Ginna | 14585 | 08/22/2013 10/01/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Required Voltage and Timing Criteria for Load Tap Changer Controls and Motor |  | P.2(b) Implementing Operating Experience | TE?: N | 05000244 Ginna |  | 7111121 | An NRC-identified finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," in that Constellation Energy Nuclear Group, LLC (CENG) did not e
Region: I | Ginna | 14583 | 06/30/2013 07/22/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Measures to Assure that a Misaligned Service Water Pump was Promptly Identified and Corrected |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000244 Ginna |  | 71111.15 | A self-revealing non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50 Appendix B, Criterion XVI, "Corrective Action," was identified for Constellation Energy Nuclear Group (CENG) failing to establish measures to assure that a con
Region: I | Ginna | 14577 | 03/31/2013 04/26/2013 | 2013002-01 | NRC | NCV | Initiating Events | Green | Failure to Identifiy, Account For, and Properly Evaluate Non-Fire Retardant Treated Combustibles in the Screen House |  |  | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified an non-cited violation of Ginna Operating License Condition 2.C.(3), "Fire Protection," for failure to implement and maintain in effect all fire protection features described in licensee submittals referenced in and as approved o
Region: I | Ginna | 14568 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Changes to the Relay Room Halon Suppression System Inspection and Testing Frequency |  |  | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified a Green non-cited violation of Ginna Operating License Condition 2.C.(3), "Fire Protection," for failure to adequately evaluate changes to the approved fire protection program that could adversely affect the ability to achieve an
Region: I | Ginna | 14569 | 12/31/2012 02/11/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Measures to Assure that Water in the 'B' Emergency Diesel Generator Underground Fuel Storage Tank was Promptly Identified and Corrected |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50 Appendix B, Criterion XVI, "Corrective Action," for Ginna's failure to establish measures to assure that conditions adverse to quality are p
Region: I | Ginna | 14570 | 12/31/2012 02/11/2013 | 2012005-03 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Meet a Conduct of Operations Standard Results in Loss of Spent Fuel Pool Cooling |  | H.2(d) Facilities & Equipment | TE?: N | 05000244 Ginna |  | 71111.2 | A self-revealing Green finding was identified for Ginna personnel not following Constellation procedure CNG-OP-1.01-1000, "Conduct of Operations," Revision 00700, which requires operators to understand conditions prior to starting equipment. Specifically,
Region: I | Ginna | 14576 | 12/31/2012 02/11/2013 | 2012005-04 | Self - Revealed | FIN | Initiating Events | Green | Incorrect Oil Filter Gasket Installed in the 'B' Main Feedwater Pump Canister Cover |  | H.4(a) Human Error Prevention | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing Green finding was identified for Ginna personnel not following Constellation procedure CNG-MN-4.01-GL004, "Work Package Writer's Guideline," Revision 00000, for planning a maintenance activity. Specifically, during the refueling outage, t
Region: I | Ginna | 14562 | 04/26/2012 06/08/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Validate Plant Safe Shutdown Timeline for Design Basis Tornado. |  |  | TE?: N | 05000244 Ginna |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," when it was determined that Ginna had not validated that the Safe Shutdown Analysis for a design basis tornado described in Updated Final Safety Analysis Repo
Region: I | Ginna | 14561 | 03/31/2012 04/30/2012 | 2012002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Action on Human Performance Issues Results in Two Trains of Auxiliary Feedwater Inoperable |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71111.12 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for Ginna's failure to implement adequate compensatory corrective actions associated with a series of human performance issues and valve mispositioning
Region: I | Ginna | 14554 | 12/31/2011 01/26/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Manage Risk of Reactor Protection System Channel 2 Calibrations |  | H.3(b) Work Activity Coordination | TE?: N | 05000244 Ginna |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65, "Maintenance Rule," paragraph (a)(4), when Ginna did not adequately manage an increase in risk when initiating the reactor protection system channel 2 calibration procedure which resul
Region: I | Ginna | 14555 | 12/31/2011 01/26/2012 | 2011005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Resulted in the Failure to Properly Tighten Turbine-Driven Auxiliary Feedwater System Threaded Connections |  | H.3(a) Work Planning | TE?: N | 05000244 Ginna |  | 71111.15 | A self-revealing non-cited violation of technical specification (TS) 5.4.1.a, "Procedures," was identified for Ginna's failure to properly tighten turbine-driven auxiliary feedwater (TDAFW) system threaded connections. Specifically, the performance of pro
Region: I | Ginna | 33725 | 09/30/2011 11/08/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality with the 'B' Main Steam Isolation Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for Ginna's failure to promptly identify and correct a condition adverse to quality. Specifically, Ginna did not promptly identify and
Region: I | Ginna | 33719 | 06/30/2011 07/29/2011 | 2011003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Oversight Resulting In Inadvertent Partial Safety Injection Actuation |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000244 Ginna |  | 71111.22 | A self-revealing NCV of technical specification (TS) 5.4.1.a, "Procedures," was identified when Ginna personnel did not correctly perform procedure STP-O-R-2.2, "Diesel Generator Load and Safeguard Sequence Test," Revision 00500 during the refueling outag
Region: I | Ginna | 33724 | 06/30/2011 07/29/2011 | 2011003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure for Fuel Transfer Flange Installation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000244 Ginna |  | 71111.22 | A self-revealing NCV of TS 5.4.1.a, "Procedures," was identified when Ginna personnel did not correctly establish procedure RF-401, "Fuel Transfer Blind Flange Removal and Installation," Revision 0, by not ensuring that the procedure contained sufficient
Region: I | Ginna | 33714 | 11/11/2010 12/22/2010 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Breaker Coordination for Ampetector Type LSG Trip Unit Discriminator Feature |  |  | TE?: N | 05000244 Ginna |  | 7111121 | The inspectors identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, Ginna had not verified the adequacy of their design with respect to the impact of th
Region: I | Ginna | 33715 | 11/11/2010 12/22/2010 | 2010009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Translation of NPSH Design Limits into EOPs |  |  | TE?: N | 05000244 Ginna |  | 7111121 | The inspectors identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, Ginna had not correctly translated residual heat removal (RHR) pump net positive suc
Region: I | Ginna | 33705 | 09/30/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess the Risk of Technical Support Center Inverter Maintenance |  | H.3(b) Work Activity Coordination | TE?: N | 05000244 Ginna |  | 71111.13 | The inspectors identified a very low safety significance (Green) non-cited violation (NCV) of 10 CFR 50.65, "Maintenance Rule," paragraph (a)(4), when Ginna did not perform an accurate risk assessment prior to removing the technical support center (TSC) b
Region: I | Ginna | 33712 | 09/30/2010 11/03/2010 | 2010004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Five Pumps in the Inservice Testing Alert Range |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.19 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was determined based on Ginna's failure to identify that vibration data exceeded the inservice testing (IST) acceptance criteria for five pumps. On Ju
Region: I | Ginna | 33704 | 06/11/2010 07/09/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Actions for Elevated Chlorides in the 'A' EDG Jacket Water Heat Exchanger |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71152B | The team identified an NRC-identified finding of very low safety significance associated with a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," in that measures were not established to assure that a condition a
Region: I | Ginna | 33699 | 12/31/2009 02/03/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Performance of the Diesel Air Compressor was Being Effectively Controlled Through Preventive Maintenance |  |  | TE?: N | 05000244 Ginna |  | 71111.12 | The inspectors identified an NCV of 10 CFR 50.65, "Maintenance Rule (MR)," paragraph (a)(2), when Ginna did not demonstrate that the performance of the diesel-driven service air compressor was being effectively controlled through preventive maintenance. S
Region: I | Ginna | 33700 | 12/31/2009 02/03/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Implement Containment Closeout Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000244 Ginna |  | 71111.2 | The inspectors identified an NCV of Technical Specification 5.4.1.a, "Procedures," when Ginna personnel did not correctly implement procedure A-3.1, "Containment Storage and Closeout Inspection," Revision 04200, and restrain or remove loose debris from co
Region: I | Ginna | 33703 | 12/31/2009 02/03/2010 | 2009005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Selection of Alternating Current-Powered Relays in Control Room Emergency Air Treatment System Fan Control Logic |  |  | TE?: N | 05000244 Ginna |  | 71111.22 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for Ginna's failure to select a suitable relay in the design of control room emergency air treatment system (CREATS) actuation and sequencing logic which led to
Region: I | Ginna | 33691 | 10/07/2009 11/12/2009 | 2009008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with Steam Admission Valve Leakage |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 93812 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure to establish adequate measures to correct a longstanding issue associated with steam admission valves leakage. As a re
Region: I | Ginna | 33698 | 10/07/2009 11/12/2009 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Design Control Measures Associated with the Turbine-Driven Auxiliary Feedwater Pump Governor Control Valve |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000244 Ginna |  | 93812 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to establish measures to ensure that a modification performed on the governor control valve bushing was a suitable application of materials for the
Region: I | Ginna | 33682 | 09/30/2009 11/13/2009 | 2009004-01 | NRC | FIN | Mitigating Systems | Green | Did Not Provide Adequate Compensatory Guidance to Verify Condensate Storage Tank Operability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000244 Ginna |  | 71111.2 | The inspectors identified a Green finding of very low safety significance when Ginna failed to ensure adequate procedures were developed to support implementation of compensatory measures for a degraded condiiton associated with the condensate storage tan
Region: I | Ginna | 33683 | 09/30/2009 11/13/2009 | 2009004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correctly Implement Chemical and Volume Control System Water Transfer Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified a self-revealing NCV of Technical Specification (TS) 5.4.1.a, "Procedures," when an auxiliary operator did not correctly implement procedure S-7M, "Transferring Refueling Water Storage Tank to Any Chemical and Volume Control Syst
Region: I | Ginna | 33690 | 09/30/2009 11/13/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Technical Specifications for Inservice Testing Requirements |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71111.22 | An NRC-identified NCV of TS 5.5.7, "Inservice Testing (IST) Program," was identified when Ginna failed to implement the IST program in accordance with relief request GR-2. Relief request GR-2 states that if any limiting value is exceeded, the valve is imm
Region: I | Ginna | 33674 | 06/30/2009 07/29/2009 | 2009003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Meet Technical Specification Requirements for Senior Radiation Protection Technician Qualifications |  |  | TE?: N | 05000244 Ginna |  | NONE | An NRC-identified NCV of Technical Specification 5.3.1, "Plant Staff Qualifications," was identified for failure to ensure senior radiation protection technicians (RPTs) met the minimum qualification requirements specified in American National Standards I
Region: I | Ginna | 33681 | 06/30/2009 07/29/2009 | 2009003-02 | NRC | NCV | Emergency Preparedness | Green | Operators Did Not Have Corrective Lens Kits Available to Implement Emergency Plan Requirements |  | H.2(d) Facilities & Equipment | TE?: N | 05000244 Ginna |  | 7112103 | An NRC-identified NCV of 10 CFR 50.54(q) was identified for a failure to follow and maintain in effect emergency plans which met the standards in 50.47(b). Specifically, 50.47(b)(8) states that "adequate emergency facilities and equipment to support the e
Region: I | Ginna | 33677 | 03/31/2009 05/04/2009 | 2009002-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Risk Management Results in Loss of Normal Control Room Annunciators |  | H.3(a) Work Planning | TE?: N | 05000244 Ginna |  | 71153 | A Green self-revealing finding was identified on February 5, 2009, when Ginna failed to review applicable internal operating experience and implement compensatory actions to minimize the consequences associated with replacement of the annunciator cards
Region: I | Ginna | 33672 | 12/30/2008 01/27/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Minimum Shift Manning Requirements Due to Inattentiveness |  | H.4(a) Human Error Prevention | TE?: N | 05000244 Ginna |  | NONE | An NRC-identified NCV of Technical Specification 5.4.1.a, "Procedures," was identified on November 21, 2008, when minimum shift staffing decreased below the requirements contained in procedure ND-OPS, "Operations," because a Ginna auxiliary operator (AO)
Region: I | Ginna | 33671 | 11/21/2008 12/17/2008 | 2008007-01 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  |  | TE?: N | 05000244 Ginna |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Ginna | 33667 | 09/29/2008 11/05/2008 | 2008004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Procedure Adherence Resulting in a Loss of Normal Control Room Communications |  | H.4(a) Human Error Prevention | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing NCV of Technical Specification 5.4.1.a, "Procedures," was identified on August 28, 2008, when Ginna technicians failed to adequately implement CME-38-01-BYCTSC, "Solid State Controls, 500 Amp Battery Charger Maintenance for BYCTSC" which
Region: I | Ginna | 33668 | 09/26/2008 11/06/2008 | 2008010-01 | NRC | FIN | Initiating Events | Green | Untimely Corrective Actions Associated With the 'C' Instrument Air Compressor |  | P.1(b) Trend Performance CAP | TE?: N | 05000244 Ginna |  | NONE | The inspectors identified a finding of very low safety significance for Ginna's failure to take timely corrective actions to address repetitive failures of the 'C' instrument air compressor (IAC). The 'C' IAC had a history of tripping on high blow-off pre
Region: I | Ginna | 33670 | 09/26/2008 11/06/2008 | 2008010-02 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Testing Reactor Trip Breakers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | NONE | The inspectors identified a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," forGinna's failure to establish and maintain an adequate procedure for testing the reactor trip breakers. This resulted in the inadvertent iso
Region: I | Ginna | 33656 | 06/30/2008 07/30/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | Failure to Correctly Implement Reactor Coolant Heat-up Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000244 Ginna |  | 71111.2 | The inspectors identified a self-revealing NCV of Technical Specification 5.4.1.a when control room operators closed the inlet and outlet Residual Heat Removal (RHR) system isolation valves while conducting a plant heat-up with the 'A' reactor coolant sys
Region: I | Ginna | 33665 | 06/30/2008 07/30/2008 | 2008003-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Timely ERO Augmentation of On-shift Staff |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71114.03 | The inspectors identified an NRC-identified NCV of 10 CFR 50.47(b)(2) for failure of Ginna's process for maintaining timely augmentation of on-shift staff. Ginna's nuclear emergency response plan (NERP) states that the survey team member position will be
Region: I | Ginna | 33666 | 06/30/2008 07/30/2008 | 2008003-03 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Implement Effective Occupational Exposure Control |  | H.3(b) Work Activity Coordination | TE?: N | 05000244 Ginna |  | 7112102 | The inspectors identified a self-revealing finding of very low safety significance associated with occupational exposure control. During the planned refueling outage, Ginna did not effectively manage its radioactive source term and work activities to prev
Region: I | Ginna | 33658 | 03/31/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Did Not Implement Scaffolding Procedure Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000244 Ginna |  | 71111.2 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Ginna did not adequately implement scaffolding control procedural requirements related to post-installation inspections and engineeri
Region: I | Ginna | 33659 | 03/31/2008 04/30/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Out-of-Specification Lubricating Oil Conditions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71152 | Inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when Ginna failed to promptly identify and correct a condition adverse to quality associated with out-of-specification oil samples for the 'A' residual heat removal
Region: I | Ginna | 33653 | 10/10/2007 11/01/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to correctly calibrate lead and lag timing modules for the OTDT reactor protection trip channels |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.12 | Inspectors identified a self-revealing NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," Ginna failed to correct a condition adverse to quality associated with the ability of maintenance personnel to correctly calibrate lead and lag timing
Region: I | Ginna | 33654 | 10/10/2007 11/01/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to correct 'C' SAFW room cooler head gasket leakage |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71111.15 | Inspectors identified a self-revealing NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," when service water (SW) leakage from the 'C' Standby Auxiliary Feedwater (SAFW) cooler indicated that Ginna failed to correct a condition adverse to qu
Region: I | Ginna | 33645 | 09/21/2007 11/02/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Residual Heat Removal Pump NPSH for Containment Sump Recirculation Scenarios |  |  | TE?: N | 05000244 Ginna |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that, Constellation had not provided adequate design control measures to verify the adequac
Region: I | Ginna | 33646 | 09/21/2007 11/02/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Nonconservative Differential Pressure Value Used In Motor Operated Valves 850A/B Design Analysis |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the maximum expected differential pressure established as a design input in the co
Region: I | Ginna | 33647 | 09/21/2007 11/02/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Ginna Emergency Operating Procedure not Updated After Extended Power Uprate |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000244 Ginna |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of Technical Specification 5.4.1, Procedures. Specifically, an emergency operating procedure (EOP) figure referenced in loss-of-coolant accident procedures
Region: I | Ginna | 33640 | 03/30/2007 05/15/2007 | 2007002-01 | NRC | NCV | Emergency Preparedness | Green | Ginna Communicators Not Adequately Trained To Implement EPIP 5-7 |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000244 Ginna |  | 71114.06 | The inspectors identified an NCV of 10 CFR 50.47(b)(15), radiological emergency response training, when they noted that the assigned Emergency Response Organization (ERO) communicators have not been fully trained on all communicator responsibilities as ou
Region: I | Ginna | 33641 | 03/30/2007 05/15/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | Failure of "B" MSIV due to Inadequate Design Control |  |  | TE?: N | 05000244 Ginna |  | 71153 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified because Ginna failed to control the proper design configuration of installed plant equipment. Specifically, Ginna failed to update records and procedures r
Region: I | Ginna | 33634 | 12/31/2006 01/31/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | ECCS Rendered Inoperable While in Mode 4 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71111.2 | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 3.5.3, "Emergency Core Cooling Systems" (ECCS) due to lead blankets covering the 'B' containment recirculation sump grating with the plant in the Hot Standby Mode. As a
Region: I | Ginna | 33638 | 12/31/2006 01/31/2007 | 2006005-03 | NRC | FIN | Barrier Integrity | Green | Did Not Maintain the Containment Penetration Cooling System in accordance with the UFSAR and System Drawings |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000244 Ginna |  | NONE | The inspectors identified a finding in that Ginna did not adequately maintain the containment penetration cooling system as described in the Updated Final Safety Analysis Report (UFSAR) and system drawings to ensure it would be capable of performing its i
Region: I | Ginna | 32139 | 09/30/2006 10/31/2006 | 2006004-01 | NRC | URI | Mitigating Systems | Green | Review the significance of not maintaining the Containment Penetration Cooling system in accordance with the UFSAR and system P&IDs |  |  | TE?: N | 05000244 Ginna |  | 71111.04S | The inspectors identified that Ginna did not have procedures which controlled the operation of the supply dampers for the containment penetration cooling system. Further, cooling air was not being supplied to several penetrations, and the operability of p
Region: I | Ginna | 32141 | 09/30/2006 10/31/2006 | 2006004-03 | NRC | FIN | Mitigating Systems | Green | Did not conduct a thorough operability assessment and identify that the "C" SAFW was degraded |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71111.15 | The inspectors identified that Ginna personnel did not initially adequately assess the effects of a service water leak that occurred in the room cooler for the "C" Standby Auxiliary Feedwater (SAFW) pump. Water which had accumulated in the electrical cont
Region: I | Ginna | 33631 | 08/31/2006 10/15/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Reactor Startup and Power Operation with the SAFW System Inoperable |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000244 Ginna |  | 71152B | The NRC identified a NCV for operating in an unanalyzed condition that was in violation of the Ginna Technical Specifications. Specifically, with the SAFW system inoperable, a reactor mode change was made and the plant was operated at power for approximat
Region: I | Ginna | 33632 | 08/31/2006 10/15/2006 | 2006006-02 | NRC | FIN | Initiating Events | Green | Failure to Correct an NRC-Identified Finding in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000244 Ginna |  | 71152B | The NRC identified a Finding for the failure to take prompt corrective action for a 2004 NRC-Identified Finding. Specifically, Ginna did not install an alarm in the control room for the RCS leakage detection function of the containment radioactive airborn
Region: I | Ginna | 33633 | 08/31/2006 10/15/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Use OE to Identify that the TS Basis for the AFW and SAFW Systems Was Invalid |  | P.2(b) Implementing Operating Experience | TE?: N | 05000244 Ginna |  | 71152B | The team identified a NCV of 10CFR50, Appendix B, Criterion XVI, "Corrective Action," for a failure to identify that the TS basis for the AFW and SAFW systems was incorrect. Specifically, the TS Basis for the AFW and SAFW systems stated that the recircula
Region: I | Ginna | 33627 | 06/23/2006 08/03/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Missed Fire Brigade Training |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000244 Ginna |  | 71111.05T | The team identified a NCV of license condition 2.C.3 for the failure to implement and maintan in effect all fire protection features. Specifically, Ginna failed to provide the required quarterly training to five fire brigade members in the fourth quarter
Region: I | Ginna | 32135 | 03/31/2006 05/05/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL |  |  | TE?: N | 05000244 Ginna |  | 71111.05Q | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1.d, which requires, in part, that written procedures be established, implemented, and maintained for the fire protection program. Contrary to TS 5.4.1.d, during a f
Region: I | Ginna | 32136 | 03/31/2006 05/05/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | SIMULATOR INCORRECTLY REPLICATED PLANT DESIGN |  |  | TE?: N | 05000244 Ginna |  | 71111.11Q | The inspectors identified a non-cited violation (NCV) of 10 CFR 55.46 (c)(1) which requires a plant-referenced simulator used for the administration of an operating test or to meet experience requirements must demonstrate the expected plant response to op
Region: I | Ginna | 32137 | 03/31/2006 05/05/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | MISSED FIRE BRIGADE DRILLS |  |  | TE?: N | 05000244 Ginna |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, App. R III.I.3.b which requires that drills shall be performed at regular intervals not to exceed 3 months for each shift fire brigade. Contrary to the requirement, four of five shift fir
Region: I | Hope Creek | 126322 | 12/31/2019 02/10/2020 |  | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustible Lube Oil In Accordance With Fire Protection Program Procedure |  | H.12 - Avoid Complacency | TE?: N | 05000354 Hope Creek 1 | Protection Against External Factors | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of Hope Creek Generating Station (HCGS) Technical Specification, Section 6.8, “Procedures and Programs,” because PSEG did not implement re
Region: I | Hope Creek | 126569 | 12/31/2019 02/10/2020 |  | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Evaluation of EDG Preventive Maintenance Change Request |  | P.5 - Operating Experience | TE?: N | 05000354 Hope Creek 1 | Equipment Performance | 71152 | The inspectors determined there was a self-revealing, Green Finding because PSEG did not adequately evaluate a PM change to the ‘C’ EDG JW pump seal, in accordance with MA-AA-716-210, “Preventive Maintenance Program,” Revision 10. Specifically, PSEG did n
Region: I | Hope Creek | 125985 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | FIN | Initiating Events | Green | Inadequate SRV Performance Monitoring and Analysis |  | P.5 - Operating Experience | TE?: N | 05000354 Hope Creek 1 | Human Performance | 71152 | The inspectors identified a Green finding (FIN) because PSEG did not adequately monitor and analyze safety relief valve (SRV) performance data, in accordance with ER-AA-2003, “System Performance Monitoring and Analysis,” Revision 11. Specifically, PSEG’s
Region: I | Hope Creek | 124975 | 05/21/2019 06/20/2019 | 2019012-01 | NRC | FIN | Barrier Integrity | Green | Failure to Properly Fill and Vent Flow Indicators Results in Loss of SAWA/SAWM Flow Instrumentation Accuracy |  | H.7 - Documentation | TE?: N | 05000354 Hope Creek 1 | Procedure Quality | 2515/193 | The team identified a finding of very low safety significance (Green) for the failure to ensure adequate procedures were in place to ensure that the Severe Accident Water Addition (SAWA) flow indicators, 1APFI-0100 and 1BCFI-0100, would be reliable or fun
Region: I | Hope Creek | 124803 | 03/31/2019 05/14/2019 | 2019001-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Corrective Action Program (CAP) Procedures |  | P.3 - Resolution | TE?: N | 05000354 Hope Creek 1 | Equipment Performance | 71111.12 | The inspectors identified a Green finding (FIN) because PSEG did not adequately implement, in part, procedure LS-AA-125, Corrective Action Program, requirements to disposition corrective actions associated with an inadequate reactor core isolation cooling
Region: I | Hope Creek | 124730 | 03/29/2019 05/06/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Protect Automatic Start Capability of Fire Pumps Due to Fire Damage |  | NPP | TE?: N | 05000354 Hope Creek 1 | Protection Against External Factors | 71111.05T | The inspectors identified a finding of very low safety significance (Green), involving a non-cited violation (NCV) of Hope Creek Generating Station (HCGS) Operating License Condition 2.C.(7) for failure to implement and maintain in effect all provisions o
Region: I | Hope Creek | 124737 | 03/29/2019 05/06/2019 | 2019011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance to Perform Time Critical Actions |  | P.2 - Evaluation | TE?: N | 05000354 Hope Creek 1 | Procedure Quality | 71111.05T | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of Hope Creek Generating Station (HCGS) License Condition 2.C.(7) for failure to implement and maintain in effect all provisions of the appro
Region: I | Hope Creek | 24721 | 09/30/2018 11/14/2018 | 2018003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedures for Restoration of the ‘A’ Reactor Feed Pump Turbine (RFPT) Following Maintenance |  | H.3 - Change Management | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self revealing Green finding (FIN) was identified for PSEG’s inadequate procedures for controlling the restoration of the ‘A’ RFPT trip instrumentation following maintenance. Specifically, on May 21, 2018, the ‘A’ RFPT tripped while HCGS was operating a
Region: I | Hope Creek | 24720 | 09/30/2018 11/14/2018 | 2018003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedures for Fuel Conditioning Results in Multiple Fuel Leaks |  | H.6 - Design Margins | TE?: N | 05000354 Hope Creek 1 |  | 71153 | The inspectors documented a self-revealing Green NCV of TS 6.8.1, Procedures and Programs, when PSEG did not maintain adequate procedures for fuel conditioning. Specifically, PSEG’s procedure for selecting the appropriate fuel PCI rules, NF-AB-440, BWR Fu
Region: I | Hope Creek | 25926 | 09/26/2018 01/28/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate High Pressure Coolant Injection Trip Unit Preventive Maintenance |  | P.2 - Evaluation | TE?: N | 05000354 Hope Creek 1 | Equipment Performance | 71153 | A Green self-revealing NCV of TS 6.8.1.a, “Procedures and Programs,” was identified because PSEG did not adequately establish, implement, and maintain the initial replacement frequency for the for the Rosemount trip units, which are circuit cards used in
Region: I | Hope Creek | 24060 | 06/30/2018 07/18/2018 | 2018002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Instructions for Station Service Water Pump Maintenance |  | H.1 - Resources | TE?: N | 05000354 Hope Creek 1 |  | 71111.22 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for PSEG providing inadequate written instructions for the performance of maintenance to ensure the SSW system remains capable of
Region: I | Hope Creek | 23510 | 03/31/2018 05/09/2018 | 2018001-01 | NRC | FIN | Mitigating Systems | Green | Implementing Procedures for Beyond Design Basis FLEX Mitigating Strategies Not Followed | EA Case: 12-049 | H.5 - Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71152 | A Green finding (FIN) was identified by the inspectors for multiple examples of PSEG not following the station specific procedures that implement the Salem and HCGS Final Integrated Plans for Beyond Design Basis FLEX Mitigating Strategies, EM-SA-100-1000
Region: I | Hope Creek | 22657 | 12/31/2017 02/06/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Scaffold Installed with Insufficient Separation from Safety-Related Equipment |  | H.2 - Field Presence | TE?: N | 05000354 Hope Creek 1 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” becaus
Region: I | Hope Creek | 23469 | 12/31/2017 02/06/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of Emergency Diesel Generator Speed Switch |  | P.5 - Operating Experience | TE?: N | 05000354 Hope Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, “Design Control,” because PSEG did not adequately provide for verifying or checking the adequacy of des
Region: I | Hope Creek | 21688 | 09/30/2017 11/14/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Operability Determination of Ground Fault Alarm |  | H.1 - Resources | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing finding of very low safety significance (Green) non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified when PSEG did not
Region: I | Hope Creek | 22297 | 09/30/2017 11/14/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Establishment of Maintenance Rule Goals, Monitoring, and Corrective Actions for the Reactor Protection System |  | P.2 - Evaluation | TE?: N | 05000354 Hope Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(1), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants (maintenance rule)." Specifically, PSEG
Region: I | Hope Creek | 19597 | 07/06/2017 07/07/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | Secondary Containment Integrity Not Maintained Due to Door not Properly Dogged |  | H.8 Procedure Adherence | TE?: N | 05000354 Hope Creek 1 |  | NONE | The team identified a Green, non-cited violation (NCV) of Technical Specification (TS) 3.6.5.1, for failure to maintain secondary containment integrity. Specifically, while Hope Creek station was operating in mode 1, PSEG personnel did not ensure secondar
Region: I | Hope Creek | 19592 | 03/31/2017 05/09/2017 | 2017001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Control of Defective Material Causes the 'A' EDG to Fail to Start |  | P.2 Evaluation | TE?: N | 05000354 Hope Creek 1 |  | 71152 | A self-revealing very low safety significance (Green) NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion VIII, "Identification and Control of Materials, Parts and Components," was identified because PSEG did not have ade
Region: I | Hope Creek | 19596 | 03/31/2017 05/09/2017 | 2017001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance Replacement Schedule for the HPCI Overspeed Trip Tappet Reset Spring |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing Green non-cited violation (NCV) of TS 6.8.1, "Procedures," was identified because PSEG did not establish an appropriate preventive maintenance (PM) schedule for the high pressure coolant injection (HPCI) overspeed trip system reset spring
Region: I | Hope Creek | 19591 | 02/17/2017 04/03/2017 | 2017008-01 | Self - Revealed | NCV | Barrier Integrity | Green | Improper Preventive Maintenance Deletion Results in the Inoperability of the 'A' Control Room HVAC System |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71152B | A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures and Programs," as described in Regulatory Guide (RG) 1.33, Revision 2, February 1978, was identified when PSEG did not maintain an appropriate preventive m
Region: I | Hope Creek | 19589 | 12/31/2016 02/13/2017 | 2016004-01 | Self - Revealed | NCV | Initiating Events | Green | Trip of Protected RWCU Pump during Maintenance Activity |  | H.5 Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | A self-revealing very low safety significance (Green), non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) was identified for inadequately assessing and managing risks associated with maintenance activities to prevent p
Region: I | Hope Creek | 19590 | 12/31/2016 02/13/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Implementation of a Design Change Causes Multiple 'B' Channel Instruments to be Inoperable |  | H.5 Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," and Technical Specification (TS) 3.0.4 was identified for PSEG not effectively implementing the
Region: I | Hope Creek | 19587 | 09/30/2016 11/14/2016 | 2016003-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Adherence Resulted In a Loss of Shutdown Cooling |  | H.14 Conservative Bias | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred when PSEG did not follow procedure during the transition from Cold Shutdown to refueling operations while filling up
Region: I | Hope Creek | 19588 | 09/30/2016 11/14/2016 | 2016003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Main Control Room Chiller Positioner Failure |  | H.8 Procedure Adherence | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for PSEG's inadequate corrective actions to address a condition adverse to quality (CAQ). Specifically, PSEG's corrective actions
Region: I | Hope Creek | 19568 | 06/30/2016 08/08/2016 | 2016002-01 | NRC | NCV | Public Radiation Safety | Green | Inadequate Maintenance Rule Monitoring of Multiple Systems, including the Effluent Radiation Monitoring System and the Reactor Core Isolation Cooling System |  | H.13 Consistent Process | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(2) due to an inadequate maintenance rule (MR) monitoring of the effluent radiation monitoring system (RMS) and the reactor core isolation cooling (RCIC)
Region: I | Hope Creek | 19569 | 06/30/2016 08/08/2016 | 2016002-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Scope the Filtration, Recirculation, and Ventilation System Effluent Radiation Monitor in the Maintenance Rule |  | P.3 Resolution | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(b)(2) due to inadequate MRP monitoring of effluent RMS performance. Specifically, PSEG did not include the filtration, ventilation, and recirculation system (FRVS) ventilation stack radiation monitor w
Region: I | Hope Creek | 19561 | 04/01/2016 04/25/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of Emergency Diesel Generator Takeover Switches and Remote shutdown Panel transfer/Isolation Relays |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.05T | The team identified a finding of very low safety significance, involving a non-cited violation of Hope Creek Operating License Condition 2.C.(7) for failure to implement and maintain in effect all provisions of the approved Fire Protection Program (FPP).
Region: I | Hope Creek | 19562 | 04/01/2016 04/25/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of Remote Shutdown Panel RCIC Flow Control Circuit |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.05T | The team identified a finding of very low safety significance, involving a non-cited violation of Hope Creek Technical Specification (TS) Surveillance Requirement (SR) 4.3.7.4.2, "Remote Shutdown System Instrumentation and Controls." Specifically, PSEG di
Region: I | Hope Creek | 19560 | 03/30/2016 05/10/2016 | 2016001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Correction of a Condition Adverse to Quality (CAQ) Associated with High Vibrations on the 'C' Emergency Diesel Generator |  | P.1 - Identification | TE?: N | 05000354 Hope Creek 1 |  | 71152 | A self-revealing finding of very low safety significance (Green) and associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," were identified when PSEG did not correct a condition adve
Region: I | Hope Creek | 19552 | 12/31/2015 02/02/2016 | 2015004-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures Ensuring Functionality of the MCR during the SBO |  | P.2 Evaluation | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a Green finding because PSEG did not follow procedures to ensure that an identified condition adverse to quality (CAQ) was adequately evaluated, documented, and corrected. Specifically, PSEG identified a CAQ associated with a sta
Region: I | Hope Creek | 19548 | 10/23/2015 11/25/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Acceptance Criteria for RHR and Core Spray Pump Start Times during Simulated LOCA/LOP Testing |  | H.7 Documentation | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PSEG did not establis
Region: I | Hope Creek | 19549 | 10/23/2015 11/25/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Order Instructions and Drawings Resulting in Improper Installation of a Safety-Related SW Valve |  | H.7 Documentation | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PSEG did not provide
Region: I | Hope Creek | 19547 | 09/30/2015 10/23/2015 | 2015003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Locked High Radiation Area Entry |  | H.12 Avoid Complacency | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing Green NCV of TS 6.12.2 was identified when a worker entered a posted locked high radiation area (LHRA) without proper authorization. Specifically, the worker entered the LHRA without being signed onto the proper radiation work permit (RWP
Region: I | Hope Creek | 19536 | 06/30/2015 07/28/2015 | 2015002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with Safety Relief Valve Inlet Piping |  | H.5 Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71111.08G | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified involving PSEG's failure to promptly identify and correct a condition adverse to quality. Specifically, PSEG did not identify and initiate a Corr
Region: I | Hope Creek | 19528 | 03/31/2015 04/21/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with the Reactor Core Isolation Cooling System Insulation and Oil |  | P.4 Trending | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing finding of very low safety significance (Green) and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified because PSEG did not
Region: I | Hope Creek | 19530 | 03/31/2015 04/21/2015 | 2015001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Take Timely Corrective Actions to Correct a Condition Adverse to Quality Related to a 480 VAC Masterpact Breaker Performer Plug |  | H.1 Resources | TE?: N | 05000354 Hope Creek 1 |  | 71111.19 | A self-revealing finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for PSEG's failure to take timely corrective action to correct a CAQ. Specifically, PSEG
Region: I | Hope Creek | 19531 | 02/13/2015 03/26/2015 | 2015008-01 | NRC | NCV | Initiating Events | Green | Inadequate Preventive Maintenance for Safety-Related Optical Isolators in the Residual Heat Removal System |  | P.2 Evaluation | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a Green NCV of TS 6.8.1.a, "Procedures and Programs," regarding PSEG's failure to adequately establish, implement, and justify a replacement frequency for the Residual Heat Removal (RHR) system optical isolators AT14 and AT18. Th
Region: I | Hope Creek | 19535 | 02/13/2015 03/26/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Reactor Manual Control System under 50.65(a)(1) due to Inadequate Maintenance Rule Functional Failure Evaluations |  | P.3 Resolution | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50.65(a)(1) due to inadequate maintenance rule monitoring of the Reactor Manual Control System (RMCS). Specifically, PSEG did not properly evaluate and account for 52 maintenance preventable functional failu
Region: I | Hope Creek | 19521 | 12/31/2014 02/05/2015 | 2014005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with Safety Relief Valve Discharge Piping Misalignment |  | P.1 Identification | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified when PSEG did not promptly identify and correct a condition adverse to quality. Specifically, PSEG did not initiate a notification or perform an e
Region: I | Hope Creek | 19508 | 06/30/2014 07/28/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance for Responding to an Internal Flooding Event in the HPCI and RCIC Rooms |  | H.9 Training | TE?: N | 05000354 Hope Creek 1 |  | 71111.06 | The inspectors identified a Green NCV of TS 6.8.1.a, "Procedures" because PSEG procedures HC.OP-AR.ZZ-0006 and HC.OP-AR.ZZ-0022 could potentially complicate an internal flooding event and adversely affect assumptions in Hope Creek's flood design. Specific
Region: I | Hope Creek | 19512 | 06/30/2014 07/28/2014 | 2014003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Evaluate an Identified Issue with the Moisture Separator Dump Valve Performance |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | A self-revealing finding of very low safety significance (Green) was identified for PSEG's failure to evaluate an identified deficiency in accordance with PSEG procedure LS-AA-125, Corrective Action Program." Specifically, PSEG failed to take self-recomme
Region: I | Hope Creek | 19509 | 06/30/2014 07/28/2014 | 2014003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Resulting in the Loss of a Vital 4kV Bus |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | A self-revealing Green NCV of TS 6.8.1.a, "Procedures and Programs," was identified for PSEG's failure to follow procedure MA-AA-1000, "Maintenance Standards and Practices," during the replacement of Bailey logic modules associated with the 'D' vital bus
Region: I | Hope Creek | 19513 | 06/30/2014 07/28/2014 | 2014003-04 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Implementation of Contingency Actions During Moisture Separator Emergency Level Controller Tuning |  | H.5 Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | .A self-revealing finding of very low safety significance (Green) was identified when PSEG failed to ensure that appropriate contingency actions were in place prior to the performance of 'A' moisture separator (MS) emergency level controller tuning as req
Region: I | Hope Creek | 19514 | 06/30/2014 07/28/2014 | 2014003-05 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Evaluation of a Main Control Room Chiller Design Change |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71153 | The inspectors reviewed a Green self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for PSEG's failure to effectively implement the design change process. Specifically, PSEG's design change package (DCP) 4EC-3662 failed to r
Region: I | Hope Creek | 19498 | 03/31/2014 05/13/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Preventative Maintenance for Safety-Related Circuit Cards |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," was identified regarding PSEG failing to adequately establish, implement, and justify the initial replacement frequency for the 1DD481 inv
Region: I | Hope Creek | 19499 | 03/31/2014 05/13/2014 | 2014002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Identification and Corrective Actions for a Condition Adverse to Quality related to 480 VAC Masterpact Breakers |  | P.1 Identification | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because PSEG failed to assure that a condition adverse to quality (CAQ) was promptly identified and
Region: I | Hope Creek | 19500 | 03/31/2014 05/13/2014 | 2014002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulting in the Potential Inoperability of a Safety-Related System |  | H.5 Work Management | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing Green NCV of TS 6.8.1.a, "Procedures and Programs," was identified for PSEG's failure to follow procedure HC.OP-SO.BH-0001, "Standby Liquid Control (SLC) System Operation," when restoring the SLC system after routine maintenance. Specific
Region: I | Hope Creek | 19505 | 03/31/2014 05/13/2014 | 2014002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Evaluation of 480 VAC Motor Control Center Design Change |  | H.8 Procedure Adherence | TE?: N | 05000354 Hope Creek 1 |  | 71111.18 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for PSEG's failure to adequately evaluate a modification to the design change package for replacement buckets on the Class 1E 10B232 480 VAC motor co
Region: I | Hope Creek | 19506 | 03/31/2014 05/13/2014 | 2014002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain B.5b Equipment in a State of Readiness to Support Mitigation Strategies per 10 CFR 50.54(hh)(2) |  | P.2 Evaluation | TE?: N | 05000354 Hope Creek 1 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50.54(hh)(2), "Conditions of Licenses." Specifically, PSEG failed to adequately assess the functionality of the B.5.b portable gas generator on multiple occasions and implement adequate corrective actions in
Region: I | Hope Creek | 19507 | 03/31/2014 05/13/2014 | 2014002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Use Approved Method of Post-Scram Reactor Pressure Control |  | H.13 Consistent Process | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing Green NCV of TS 6.8.1, "Procedures and Programs," was identified for PSEG's failure to use procedures during scram recovery on December 5, 2013. Specifically, PSEG failed to use an approved method of post-scram reactor pressure control, c
Region: I | Hope Creek | 19490 | 12/31/2013 02/11/2014 | 2013005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure for Configuration Control Adversely Affected Unidentified Leakage in the Drywell. |  | H.4(a) Human Error Prevention | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A Green self-revealing NCV of TS 6.8.1, "Procedures and Programs," was identified regarding PSEG's conduct of maintenance and component configuration control during system restoration from an operation with a potential for draining the reactor vessel (OPD
Region: I | Hope Creek | 19493 | 12/31/2013 02/11/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Primary Containment Closeout Procedure when Declaring the Drywell Ready for Power Operation |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for PSEG's failure to conduct
Region: I | Hope Creek | 19494 | 12/31/2013 02/11/2014 | 2013005-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Evaluation of Containment Vent Functionality |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000354 Hope Creek 1 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) for PSEG's failure to ensure evaluations addressed identified issues in accordance with PSEG procedure LS-AA-125, "Corrective Action Program." Specifically, PSEG failed to adequat
Region: I | Hope Creek | 19495 | 12/31/2013 02/11/2014 | 2013005-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify Adverse Trend Regarding Bailey Module and Auxiliary Card Failures |  | P.1(b) Trend Performance CAP | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A Green self-revealing finding was identified for PSEG's failure to identify and correct an adverse trend regarding 48 Bailey module failures across multiple systems since 2005, including six Bailey module failures in the circulating water (CW) system. As
Region: I | Hope Creek | 19488 | 09/30/2013 11/18/2013 | 2013004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Post-Maintenance Testing Procedure Prior to Returning the 'B' Filtration, Recirculation and Ventilation System (FRVS) Recirculation Fan to Service Following System Maintenance. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000354 Hope Creek 1 |  | 71111.19 | A finding of very low safety significance (Green) and associated NCV of 10 Code of Federal Regulation (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self-revealed for the licensee's failure to test the 'B' Filtration,
Region: I | Hope Creek | 19489 | 09/30/2013 11/18/2013 | 2013004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Perform Maintenance in Accordance with Station Procedurs Led to Reactor Coolant System Pressure Boundary Leakage. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A finding of very low safety-significance (Green) and associated NCV of Technical Specifications (TS) 3.4.3.2, "Reactor Coolant System (RCS) Operational Leakage," was self-revealed on June 12, 2013, when a through-wall flaw was identified in the RCS press
Region: I | Hope Creek | 19484 | 06/30/2013 07/31/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance Replacement Schedule for Tyco/Agastat General Purpose Control Relays |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing Green NCV of Technical Specifications (TS) 6.8.1, "Procedures," was identified because PSEG failed to establish an appropriate preventive maintenance (PM) schedule for Tyco/Agastat General Purpose (GP) control relays. Specifically, the ev
Region: I | Hope Creek | 19485 | 04/05/2013 05/14/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Post-Fire Safe Shutdown Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71111.05T | The team identified a Green, Non-Cited Violation (NCV) of License Condition 2.C(7) of the Hope Creek operating license, in that the procedures for shutting down the plant in response to a fire in the cable spreading room, control equipment room, or con
Region: I | Hope Creek | 19483 | 03/31/2013 05/01/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | A Technical Specification Surveillance Procedure for Remote Shutdown Panel Instrumentation was Inadequately Established and Implemented |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing NCV of very low safety significance of technical specification (TS) 6.8.1 and TS 3.3.7.4 resulted because PSEG did not properly perform the monthly channel check required by TS surveillance requirement (SR) 4.3.7.4.1 to demonstrate operab
Region: I | Hope Creek | 19481 | 02/15/2013 04/01/2013 | 2013007-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Conduct Maintenance on the CR HVAC System in Accordance with the Procedure |  | H.3(b) Work Activity Coordination | TE?: N | 05000354 Hope Creek 1 |  | 71152B | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because PSEG failed to perform maintenance on the A control room air conditioning train in accordance with the documented procedure
Region: I | Hope Creek | 19482 | 02/15/2013 04/01/2013 | 2013007-02 | NRC | NCV | Barrier Integrity | Green | Failure to Take Timely Corrective Action for an Identified Design Deficiency with the CR HVAC System |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because PSEG failed to promptly correct a design deficiency in the control room chilled water circulating low flow pump trip logic. Specifically, PSEG fail
Region: I | Hope Creek | 19480 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures to Ensure Cables Within the Scope of the Cable Monitoring Program Do Not Remain Submerged |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71111.06 | The inspectors identified a Green finding for failure to follow the PSEG procedure (ER-AA-3003) for the cable monitoring and aging management of medium and low voltage cables at PSEG nuclear plants. Specifically, Hope Creek Generating Station did not perf
Region: I | Hope Creek | 19476 | 06/30/2012 08/10/2012 | 2012003-01 | NRC | NCV | Barrier Integrity | Green | Preconditioning of the Reactor Building to Torus Vacuum Relief Valves |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | The inspectors identified a NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because PSEG conducted unacceptable preconditioning of the reactor building to torus vacuum relief valve. Specifically, PSEG's surveill
Region: I | Hope Creek | 19477 | 06/30/2012 08/10/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Average Power Range Monitor Flow Unit Summers out of Tech Spec Tolerance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71153 | The inspectors identified an NCV of very low safety significance of TSs 3.3.1 and 6.8.1 because PSEG's written procedure (HC.IC-CC.SE-0032) was not adequately established and implemented for performing the weekly channel test and calibration of the flow b
Region: I | Hope Creek | 19468 | 09/30/2011 11/10/2011 | 2011004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Corrective Actions Associated with a Known Degraded Condition of the 00-K-107 Service Air Compressor Outlet Check Valve (H0KA-0KAV-004) |  | H.3(b) Work Activity Coordination | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | A self-revealing finding was identified because the PMOC did not drive sustainable improvements in the 00-K-107 service air compressor's reliability as required by PM program procedure WC-AA-111. Specifically, PSEG did not change the PM frequency of the d
Region: I | Hope Creek | 19469 | 09/30/2011 11/10/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | HPCI Operability during SBLOCA/LOOP with the A EDG Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, PSEG did not ensure the adequacy of the high pressure coolant injection (HPCI) design under post-accident conditions. Specifically, PSEG did not evaluate t
Region: I | Hope Creek | 19459 | 01/28/2011 03/10/2011 | 2011008-01 | NRC | FIN | Initiating Events | Green | INADEQUATE CORRECTIVE ACTIONS FOR EHC TURBINE VALVE PROCEDURES |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) because PSEG did not correct turbine valve test and maintenance procedure deficiencies. Specifically, PSEG closed out notification 20413100 within their corrective action program
Region: I | Hope Creek | 19456 | 12/31/2010 02/14/2011 | 2010005-01 | NRC | FIN | Barrier Integrity | Green | RHR HEAT EXCHANGER DEFICIENT OPERABILITY EVALUATION |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a finding for a deficient operability evaluation involving leakage from the residual heat removal (RHR) system into the reactor building through a degraded gasket on the B RHR heat exchanger (HX). PSEG's operability evaluation di
Region: I | Hope Creek | 19458 | 12/31/2010 02/14/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | RCIC TURBINE BEARING HIGH OIL LEVEL |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000354 Hope Creek 1 |  | 71111.22 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions", because PSEG failed to identify and correct a condition adverse to quality. Specifically, PSEG did not identify that the reactor core isolation cooling (RCIC) t
Region: I | Hope Creek | 18886 | 09/30/2010 11/08/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW SCAFFOLD PROCEDURE |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.04Q | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PSEG did not properly implement procedural controls for scaffolds located in safety-related areas. Specifically,
Region: I | Hope Creek | 18887 | 09/30/2010 11/08/2010 | 2010004-02 | NRC | FIN | Mitigating Systems | Green | RCIC TURBINE BEARING INCORRECT OIL LEVEL INDICATION |  | H.4(a) Human Error Prevention | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance because the reactor core isolation cooling (RCIC) turbine oil level indicator operator aid was incorrect from April 29 to May 25, 2010. Specifically, PSEG did not use the operator aid pos
Region: I | Hope Creek | 18890 | 09/30/2010 11/08/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY INADEQUATE RHR PIPE VENT CONFIGURATION |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000354 Hope Creek 1 |  | 2515/177 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PSEG did not identify and correct a condition adverse to quality. Specifically, PSEG did not identify that the configuration of the residual heat remova
Region: I | Hope Creek | 18885 | 06/30/2010 08/03/2010 | 2010003-01 | Self - Revealed | FIN | Initiating Events | Green | REACTOR RECIRCULATION PUMP TRIP |  | H.3(b) Work Activity Coordination | TE?: N | 05000354 Hope Creek 1 |  | 71111.19 | A self-revealing finding of very low safety significance was identified on February 26, 2010, because the A reactor recirculation pump (RRP) tripped. The pump trip caused a reactor coolant system transient and a decrease in reactor power. The RRP tripped
Region: I | Hope Creek | 18883 | 03/31/2010 05/05/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | CONTROL ROOM CHILLER TRIP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because the B control room chiller tripped when it was started on November 18, 2009. This reduced the cooling capability of the control area chilled water s
Region: I | Hope Creek | 18884 | 03/31/2010 05/05/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | HIGH PRESSURE COOLANT INJECTION BOOSTER PUMP OUTBOARD BEARING LOW OIL LEVEL AND LEAK |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PSEG failed to identify and correct a condition adverse to quality. Specifically, PSEG did not identify that the high pressure coolant injection (HPCI)
Region: I | Hope Creek | 18873 | 10/09/2009 11/23/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | NON-CONSERVATIVE INPUT USED IN DESIGN CALCULATION FOR DC CONTROL VOLTAGE FOR 4KV SWITCHGEAR |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50 Appendix B Criterion III, Design Control, in that PSEG had not properly verified that the safety-related 'B' 4 kV switchgear had adequate DC
Region: I | Hope Creek | 18874 | 10/09/2009 11/23/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | EDG OVERHEAD CRANES NOT SEISMICALLY RESTRAINED |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50 Appendix B Criterion III, Design Control, in that PSEG design control measures had not verified the adequacy of design with respect to ensur
Region: I | Hope Creek | 18881 | 10/09/2009 11/23/2009 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR 4KV BUS DEGRADED VOLTAGE RELAY BASES |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that PSEG had not verified the adequacy of design with respect to establishing the bases for
Region: I | Hope Creek | 18870 | 09/30/2009 11/12/2009 | 2009004-01 | NRC | NCV | Barrier Integrity | Green | TRAVERSING IN-CORE PROBE CONTAINMENT ISOLATION VALVES FOUND OPEN |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71153 | The inspectors identified a non-cited violation of Technical Specification 3.6.3, "Primary Containment Isolation Valves," because PSEG did not properly secure the TIP system following a TIP system ST performed on May, 6, 2009; and the error was not identi
Region: I | Hope Creek | 18856 | 06/30/2009 08/11/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE WORK INSTRUCTIONS FOR IMPAIRING THE FLOOD PROTECTION FUNCTION OF THE SAFETY AUXILIARY COOLING SYSTEM WATER-TIGHT DOOR |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.06 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because safety auxiliary cooling system (SACS) water-tight door 4309A was blocked open without necessary compensatory measures,
Region: I | Hope Creek | 18857 | 06/30/2009 08/11/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | UNPLANNED HIGH PRESSURE COOLANT INJECTION UNAVAILABILITY DUE TO TROUBLESHOOTING |  | H.3(a) Work Planning | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing, non-cited violation of 10 CFR Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because technicians did not have adequate work instructions for troubleshooting a high pressure coolant injection (HPCI) syst
Region: I | Hope Creek | 18858 | 06/30/2009 08/11/2009 | 2009003-03 | Self - Revealed | FIN | Initiating Events | Green | AUTOMATIC REACTOR SCRAM DUE TO LEAK ON SCRAM AIR HEADER |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A finding was self-revealed because PSEG discovered an air leak at a soldered joint on the scram air header in September 2008, but did not enter the degraded condition in the corrective action program. As a result, PSEG did not evaluate the leak or take c
Region: I | Hope Creek | 18848 | 01/30/2009 03/16/2009 | 2009006-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS FOR SUSCEPTIBILITY OF AIR ACCUMULATION IN THE A CONTROL AREA CHILL WATER SYSTEM |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000354 Hope Creek 1 |  | 71152B | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criteria XVI, "Corrective Actions," was identified for PSEG's failure to implement corrective actions to address an identified condition adverse to quality which resulted in multiple trips of the 'A' Co
Region: I | Hope Creek | 18849 | 01/30/2009 03/16/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | NON-CONSERVATIVE EMERGENCY DIESEL GENERATOR TEST ACCEPTANCE CRITERIA |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for PSEG's failure to ensure that emergency diesel generator (EDG) surveillance test (ST) procedures had appropriate acceptance criteria that incorporated t
Region: I | Hope Creek | 18850 | 01/30/2009 03/16/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES CONTRIBUTES TO EMERGENCY DIESEL GENERATOR INOPERABILITY |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for PSEG's failure to adequately implement procedure requirements related to the maintenance and operation of the emergency diesel
Region: I | Hope Creek | 18841 | 09/30/2008 11/12/2008 | 2008004-01 | Self - Revealed | NCV | Initiating Events | Green | INADVERTENT FEEDWATER INJECTION THROUGH THE HIGH PRESSURE COOLANT INJECTION SYSTEM DUE TO AN INADEQUATE TEST PROCEDURE |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.19 | A self-revealing, non-cited violation of Technical Specification 6.8.1, "Procedures and Programs," was identified because, during performance of post-modification testing for the high pressure coolant injection (HPCI) feedwater injection valve, PSEG inadv
Region: I | Hope Creek | 18840 | 06/30/2008 08/01/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS FOR TRAVELING WATER SCREEN SUPPORT STRUCTURE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, for inadequate corrective actions to address previously identified corrosion of service water traveling screen seismic class 1 support structures. The actions were ins
Region: I | Hope Creek | 18834 | 03/31/2008 04/28/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | IMPROPER MANAGEMENT OF WORKING HOURS DURING REFUELING OUTAGE |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | NONE | The inspectors identified a non-cited violation of Technical Specification (TS) 6.2.2.d, "Unit Staff," because four individuals worked beyond the TS limit of 72 hours in a 7-day period without proper authorization. Additionally, PSEG did not approve the w
Region: I | Hope Creek | 18832 | 12/29/2007 02/14/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE RISK ASSESSMENT FOR MAINTENANCE ON A WATERTIGHT DOOR |  | H.3(a) Work Planning | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when PSEG disassembled a water-tight door in the reactor building without assessing the resulti
Region: I | Hope Creek | 18826 | 12/29/2007 02/14/2008 | 2007005-02 | NRC | NCV | Barrier Integrity | Green | INADEQUATE DESIGN CONTROL OF SAFETY RELIEF VALVE DISCHARGE PIPING |  | H.3(b) Work Activity Coordination | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," when a pipe support was found disconnected from safety relief valve (SRV) piping during a drywell inspection. PSEG determined that the pipe support
Region: I | Hope Creek | 18824 | 12/29/2007 02/14/2008 | 2007005-03 | Self - Revealed | FIN | Initiating Events | Green | REACTOR WATER LEVEL TRANSIENT DUE TO DIGITAL FEEDWATER CONTROL SYSTEM TROUBLESHOOTING |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71111.19 | A self-revealing finding was identified when PSEG did not provide adequate work instructions for complex troubleshooting activities associated with the digital feedwater control system (DFCS) that subsequently caused a reactor level transient during plant
Region: I | Hope Creek | 18800 | 12/29/2007 02/14/2008 | 2007005-04 | Self - Revealed | NCV | Emergency Preparedness | Green | TECHNICAL SUPPORT CENTER LOSS OF POWER WITHOUT COMPENSATORY ACTION |  | H.2(d) Facilities & Equipment | TE?: N | 05000354 Hope Creek 1 |  | 71111.2 | A self-revealing non-cited violation of 10 CFR 50.47(b)(8), "Emergency Plans," was identified when power for the Hope Creek Technical Support Center (TSC) was inadvertently removed without compensatory actions for approximately three days. PSEG's correcti
Region: I | Hope Creek | 18825 | 12/29/2007 02/14/2008 | 2007005-05 | Self - Revealed | NCV | Initiating Events | Green | INADVERTENT LOSS OF REACTOR COOLANT SYSTEM INVENTORY DUE TO LOSS OF CONFIGURATION CONTROL |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 6.8.1, "Procedures and Processes," was identified when PSEG did not include special instructions in three related work clearance documents. As a result, PSEG inadvertently drained reactor ves
Region: I | Hope Creek | 18821 | 12/29/2007 02/14/2008 | 2007005-06 | Self - Revealed | NCV | Initiating Events | Green | INADVERTENT LOSS OF REACTOR COOLANT SYSTEM INVENTORY DUE TO INADEQUATE TEST PROCEDURE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 6.8.1, "Procedures and Programs," was identified when control room operators inadvertently drained water from the reactor pressure vessel (RPV) during safety relief valve solenoid testing. PS
Region: I | Hope Creek | 18827 | 12/29/2007 02/14/2008 | 2007005-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | INADEQUATE RADIOLOGICAL SURVEY OF A HIGH RADIATION AREA |  | H.3(a) Work Planning | TE?: N | 05000354 Hope Creek 1 |  | 7112101 | A self-revealing non-cited violation of 10 CFR 20.1501, "Surveys and Monitoring - General," was identified when PSEG did not adequately perform required radiological surveys in a High Radiation Area (HRA) prior to down-posting to a Radiation Area. Three w
Region: I | Hope Creek | 18816 | 12/29/2007 02/14/2008 | 2007005-08 | Self - Revealed | FIN | Occupational Radiation Safety | Green | OCCUPATIONAL RADIATION EXPOSURE NOT AS LOW AS REASONABLY ACHIEVABLE DURING REFUELING OUTAGE |  | H.2(d) Facilities & Equipment | TE?: N | 05000354 Hope Creek 1 |  | 7112102 | A self-revealing finding was identified when PSEG did not maintain occupational radiation exposures as-low-as-reasonably-achievable (ALARA) for three different work activities during a refueling outage. Specifically, each job's total dose accumulated was
Region: I | Hope Creek | 18831 | 12/29/2007 02/14/2008 | 2007005-09 | NRC | NCV | Initiating Events | Green | FAILURE TO PROMPTLY IDENTIFY AND CORRECT INTER GRANULAR STRESS CORROSION CRACKING IN DISSIMILAR METAL WELDS IN REACTOR VESSEL NOZZLE N2A |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71111.08G | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PSEG did not promptly identify and correct an 89% through wall circumferential flaw in a dissimilar metal weld in reactor recirculation
Region: I | Hope Creek | 18812 | 09/28/2007 11/09/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | DEGRADED REACTOR CORE ISOLATION COOLING SYSTEM FLOW CONTROLLER AT THE REMOTE SHUTDOWN PANEL NOT CORRECTED |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000354 Hope Creek 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because PSEG did not identify and correct a condition adverse to quality involving a degraded reactor core isolation cooling system (RCIC) f
Region: I | Hope Creek | 18813 | 09/28/2007 11/09/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE OPERATING PROCEDURE FOR THE SERVICE WATER STRAINERS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, criterion V, "Instructions, Procedures, and Drawings," because PSEG did not have adequate procedures to operate the service water strainer baskets under conditions of high different
Region: I | Hope Creek | 18814 | 09/28/2007 11/09/2007 | 2007004-03 | Self - Revealed | NCV | Mitigating Systems | Green | FOREIGN MATERIAL RESULTS IN UNAVAILABILITY OF D SERVICE WATER TRAIN |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71111.15 | A self-revealing non-cited violation of Technical Specification 6.8.1 was identified when PSEG did not remove foreign material from the D service water bay following desilting activities that subsequently caused the D service water strainer to seize. The
Region: I | Hope Creek | 18817 | 09/28/2007 11/09/2007 | 2007006-02 | Self - Revealed | NCV | Mitigating Systems | Green | ABB 4kV HK CIRCUIT BREAKER FOR D VITAL BUS FAILED DUE TO HARDENED GREASE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000354 Hope Creek 1 |  | 71152B | A self revealing non-cited violation of 10 CFR 50, Appendix B, criterion XVI, 'Corrective Action', occurred when a safety-related 4160 volt breaker did not operate as expected on July 24, 2007, due to hardened grease in the breaker mechanism. This was the
Region: I | Hope Creek | 18818 | 09/28/2007 11/09/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | B CONTROL ROOM EMERGENCY FILTRATION FAILURE DUE TO DAMPER CONTROLLER POWER SUPPLY FAILURE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The inspectors identified, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," occurred when on June 11, 2006, the "B" Control Room Emergency Filtration (CREF) damper flow controller did not meet its Technical Specification 3
Region: I | Hope Creek | 18805 | 06/29/2007 08/10/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM A RISK ASSESSMENT WHEN REQUIRED BY 10 CFR 50.65(a)(4) |  | H.3(a) Work Planning | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50.65(a)(4) when PSEG did not assess and manage the increase in risk for corrective maintenance activities on the 'C' SSW pump following an emergent failure of a 'B' SSW ventilation supply fan
Region: I | Hope Creek | 18811 | 06/29/2007 08/10/2007 | 2007003-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW TEST PROCEDURE RESULTS IN REACTOR SCRAM |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred when technicians did not follow a procedure during undervoltage relay testing on the normal supply breaker for the 10A401 4 kV b
Region: I | Hope Creek | 18803 | 03/23/2007 05/03/2007 | 2007007-01 | NRC | NCV | MISC | Green | FITNESS-FOR-DUTY (FFD) COLLECTION PERSONNEL COLLECTING FFD SAMPLES FROM CO-WORKERS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 26, Appendix A, subpart B, 2.3 (1) when the inspectors observed PSEG's fitness-for-duty (FFD) collection technicians and security officers perform urine and breath collection on co-workers on March 21, 20
Region: I | Hope Creek | 18804 | 03/23/2007 05/03/2007 | 2007007-02 | NRC | NCV | MISC | Green | FITNESS-FOR-DUTY (FFD) COLLECTORS LEAVING FFD SPECIMENS UNATTENDED |  | H.4(b) Procedural Compliance | TE?: N | 05000354 Hope Creek 1 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 26, Appendix A, Subpart B, 2.4 (g) (20) when the inspectors observed PSEG's fitness-for-duty (FFD) collection technicians leaving split FFD urine specimens in unsealed aliquot tubes and sealed specimen co
Region: I | Hope Creek | 18795 | 12/31/2006 01/31/2007 | 2006005-01 | Self - Revealed | NCV | Mitigating Systems | Green | UNPLANNED TRIP OF THE 'B' CONTROL ROOM CHILLER AND VENTILATION TRAIN |  | H.4(a) Human Error Prevention | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when maintenance personnel lifted an energized lead (wire) that inadvertently tripped the 'B' control room chiller during m
Region: I | Hope Creek | 18797 | 12/31/2006 01/31/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | MISPOSITIONED VALVE RESULTS IN REDUCED COOLING FLOW TO THE 'C' EMERGENCY DIESEL GENERATOR |  | H.4(a) Human Error Prevention | TE?: N | 05000354 Hope Creek 1 |  | 71152 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when the safety auxiliaries cooling system (SACS) throttle valve to the 'C' emergency diesel generator (EDG) was found out
Region: I | Hope Creek | 18798 | 12/31/2006 01/31/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | HIGH TEMPERATURE CONDITION ON 'B' EMERGENCY DIESEL GENERATOR NOT FULLY IDENTIFIED IN A TIMELY MANNER |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000354 Hope Creek 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," when lube oil temperature exceeded the procedural limit of 170 degrees F on the 'B' EDG during a surveillance test on July 31, 2006. PSEG determin
Region: I | Hope Creek | 18799 | 12/08/2006 01/19/2007 | 2006015-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE STRAINER DIFFERENTIAL PRESSURE DESIGN CONTROL TO ENSURE ADEQUATE SERVICE WATER FLOW |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a non-cited violation of 10CFR50, Appendix B, Criterion III, "Design Control," for a failure to correctly translate the design basis into procedures in that measures were not established to verify the adequacy of the service water (SW)
Region: I | Hope Creek | 18801 | 12/08/2006 01/19/2007 | 2006015-02 | NRC | FIN | Mitigating Systems | Green | INADEQUATE CONTAINMENT VENT VALVE BACKUP PNEUMATIC SUPPLY |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7111121 | The team identified a finding for the failure to correctly translate the design basis of the containment ventilation backup nitrogen bottles into procedures. Specifically, the operator rounds log was revised to allow the two backup nitrogen bottles, which
Region: I | Hope Creek | 18783 | 09/30/2006 11/07/2006 | 2006004-01 | Self - Revealed | NCV | Mitigating Systems | Green | 'A' CORE SPRAY MINIMUM FLOW CHECK VALVE FAILURE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | A self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the 'A' core spray pump minimum flow check valve remained open, resulting in 56 hours of unplanned unavailability of the 'A' core spray
Region: I | Hope Creek | 18789 | 09/30/2006 11/07/2006 | 2006004-02 | Self - Revealed | FIN | Initiating Events | Green | INADVERTENT INSTRUMENT AIR COMPRESSOR TRIP |  | H.4(a) Human Error Prevention | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | A self-revealing finding was identified when an operations work control supervisor caused an inadvertent trip of the 10K107 instrument air compressor. During a tagging operation on the 00K107 air compressor, the supervisor verified that a key would fit pr
Region: I | Hope Creek | 18779 | 06/30/2006 07/21/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | CORRECTIVE ACTIONS TO PREVENT REPEAT FAILURES OF SERVICE WATER STRAINER OVERLOADS NOT IMPLEMENTED |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.13 | Inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when the 'A' service water strainer was rendered unavailable on April 18, 2006. On November 25, 2004, the 'C' service water strainer backwash arm mot
Region: I | Hope Creek | 18780 | 06/30/2006 07/21/2006 | 2006003-02 | Self - Revealed | NCV | Mitigating Systems | Green | LOSS OF SHUTDOWN REACTOR PRESSURE VESSEL LEVEL INDICATION |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.2 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when the single source of shutdown reactor water level indication was rendered inaccurate during reactor vessel reassembly
Region: I | Hope Creek | 18781 | 06/30/2006 07/21/2006 | 2006003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | DEFICIENCY IN ACCESS CONTROL TO RADIOLOGICAL AREAS |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7112101 | A self-revealing non-cited violation of 10 CFR 20.1501, "Surveys and Monitoring: General", was identified when a worker's electronic dosimeter alarmed due to dose rates in the 'A' steam jet air ejector (SJAE) room exceeding the preset alarm setpoint. Duri
Region: I | Hope Creek | 18775 | 03/31/2006 05/11/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS FOR SERVICE WATER PUMP PACKING |  |  | TE?: N | 05000354 Hope Creek 1 |  | 7111107B | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for PSEG's failure to implement corrective actions for a condition adverse to quality involving inadequate procedure guidance for service wa
Region: I | Hope Creek | 18777 | 03/31/2006 05/11/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY CONDITIONS ADVERSE TO QUALITY ON 'D' SERVICE WATER STRAINER |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when the 'D' service water strainer was rendered unavailable for 49 hours on November 6, 2005. On May 23, 2005, PSEG technicians reassembled the
Region: I | Hope Creek | 18778 | 03/31/2006 05/11/2006 | 2006002-04 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTION RESULTS IN UNAVAILABILITY OF THE 1AK400 CONTROL ROOM CHILLER |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71153 | A self-revealing, non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," was identified when the guide vane pivot arm on the 'A' control room chiller was discovered to be operating incorrectly in May 2005, rendering the chiller u
Region: I | Hope Creek | 124740 | 05/06/2019 |  |  | LIV |  | Green | Inadequate Corrective Actions to Address Previously Identified Non-Cited Violation |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.05T
Region: I | Hope Creek | 125410 | 07/30/2019 |  |  | LIV |  | Green | Licensee Identified Violation - Operation above the licenced rated thermal power |  |  | TE?: N | 05000354 Hope Creek 1 |  | 71111.15
Region: I | Indian Point | 125198 | 06/30/2019 08/13/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Scaffolding Installed in Close Proximity to Safety-Related Equipment without Adequate Engineering Evaluation |  | H.13 - Consistent Process | TE?: N | 05000286 Indian Point 3 | Protection Against External Factors | 71111.2 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee did not adequately develop engineering evaluations, in accordance with established procedures, for
Region: I | Indian Point | 124455 | 03/31/2019 05/13/2019 | 2019001-01 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately and Promptly Evaluate, Identify, and Correct Degradation of Offsite Power Feeder 13W93 |  | H.14 - Conservative Bias | TE?: N | 05000247 Indian Point 2 | Protection Against External Factors | 71111.12 | The inspectors identified a Green finding (FIN) because the licensee did not adequately and promptly evaluate, identify, and correct degraded cable conditions on the ‘C’ phase of the 13W93 offsite power feeder prior to failure, as required, by EN-MA-138,
Region: I | Indian Point | 25893 | 12/31/2018 02/07/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Transient Combustibles in the 480 Volt Electrical Switchgear Room |  | H.5 - Work Management | TE?: N | 05000286 Indian Point 3 | Human Performance | 71111.05Q | The inspectors identified a Green NCV of Unit 3 Technical Specification (TS) 5.4.1 when Entergy did not take adequate measures to control transient combustibles in accordance with established procedures and thereby did not maintain in effect all provision
Region: I | Indian Point | 25907 | 12/31/2018 02/07/2019 | 2018004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Manage Flow Accelerated Corrosion on a Reheat Steam Line Caused a Steam Leak and a Reactor Trip |  | NPP | TE?: N | 05000286 Indian Point 3 | Equipment Performance | 71153 | A self-revealed Green finding (FIN) was identified when Entergy did not adequately manage the degradation of the 36C FWH reheat steam lines, as required by EN-DC-315, “Flow Accelerated Corrosion Program.” The failure resulted in a large steam leak in the
Region: I | Indian Point | 24703 | 09/30/2018 11/08/2018 | 2018003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Guidance for Spent Fuel Movement and Storage Requirements |  | H.3 - Change Management | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Procedures,” when Entergy did not have appropriate documented instructions or written procedures for spent fuel movement and s
Region: I | Indian Point | 24704 | 09/30/2018 11/08/2018 | 2018003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Containment Fan Coolers 21 and 24 Motor Cooler Elbow Through-Wall Leaks Due to Excessive Service Water Flow Rates and Safety System Functional Failures of Containment |  |  | TE?: N | 05000247 Indian Point 2 |  | 71152 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified when Entergy did not ensure that measures were established for the selection and review for suitability of application of materials, parts, equipment
Region: I | Indian Point | 24705 | 09/30/2018 11/08/2018 | 2018003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Containment Fan Cooler 24 Through-Wall Service Water Leak Caused by Inadequate Application of Epoxy Coating Resulting in Corrosion and a Safety System Functional Failure of Containment |  | H.13 - Consistent Process | TE?: N | 05000247 Indian Point 2 |  | 71152 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified when Entergy did not ensure that activities affecting quality were prescribed by documented instructions or procedures, of a ty
Region: I | Indian Point | 24706 | 09/30/2018 11/08/2018 | 2018003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Turbine Startup Caused a Reactor Trip |  | H.13 - Consistent Process | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing Green NCV of TS 5.4.1, “Procedures,” was identified because Entergy did not provide adequate guidance in 2-SOP-26.4, “Turbine Generator Startup, Synchronization, Voltage Control, and Shutdown.” Specifically, Entergy did not provide adequa
Region: I | Indian Point | 23979 | 03/31/2018 05/10/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Adequate Test Controls for Quarterly Stroke Close Testing of the Steam Supply Valves to Turbine-Driven Auxiliary Feedwater Pump |  | H.11 - Challenge the Unknown | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” when Entergy did not assure that surveillance tests required to demonstrate that structures, systems, and components will perform satisfactorily in service
Region: I | Indian Point | 23950 | 03/31/2018 05/10/2018 | 2018001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Placing Chemical and Volume Control System Demineralizer In Service |  | P.3 - Resolution | TE?: N | 05000286 Indian Point 3 |  | 71153 | A self-revealing Green NCV of Technical Specification 5.4.1, “Procedures,” was identified because Entergy failed to provide adequate guidance in 3-SOP-CVCS-004, “Placing the CVCS Demineralizers In or Out of Service.” Specifically, Entergy did not provide
Region: I | Indian Point | 23235 | 01/10/2018 01/31/2018 | 2017010-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Diesel Fuel Oil Temperature Protection |  | H.12 - Avoid Complacency | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 2515/191 | The NRC identified a finding for the failure to assure that diesel powered Diverse and Flexible Coping Strategies (FLEX) equipment would be reliable to mitigate postulated beyond-design basis external events during very low temperature conditions. Spe
Region: I | Indian Point | 22302 | 11/03/2017 12/05/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Post-Fire Safe Shutdown Procedure |  | NPP | TE?: N | 05000286 Indian Point 3 |  | 71111.05T | An NRC-identified finding of very low safety significance (Green), involving a NCV of Indian Point Unit 3 Facility Operating License (FOL) Condition 2.H, was identified because Entergy did not implement and maintain in effect all provisions of the Fire Pr
Region: I | Indian Point | 22303 | 11/03/2017 12/05/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain B.5.b Mitigating Strategies |  | H.1 - Resources | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.05T | An NRC-identified finding of very low safety significance (Green) and NCV of 10 CFR 50.54(hh)(2), “Conditions of Licenses,” the Unit 2 FOL Condition 2.N, and the Unit 3 FOL Condition 2.AC was identified for failure to maintain strategies for addressing la
Region: I | Indian Point | 21686 | 09/30/2017 10/27/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Component Misalignments Following Scheduled Maintenance |  | H.5 - Work Management | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, “Procedures,” with two examples was identified when Entergy failed to implement procedures to ensure correct system alignment for the nuclear instrumentation permissive interlock, P6, a
Region: I | Indian Point | 28912 | 06/30/2017 08/07/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Flow Channeling Gate Closed in Accordance with the Containment Procedure |  | P.3 Resolution | TE?: N | 05000286 Indian Point 3 |  | 71111.2 | The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, "Procedures," for Entergy's failure to implement procedure OAP-007, "Containment Entry and Egress." Specifically, workers transiting the inner and outer crane wall sections of co
Region: I | Indian Point | 28910 | 03/31/2017 05/10/2017 | 2017001-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Standard Operation Procedure for the Backup Spent Fuel Pool Cooling System |  | P.2 Evaluation | TE?: N | 05000286 Indian Point 3 |  | 71111.04S | The inspectors identified an NCV of very low safety significance of TS 5.4, "Procedures," because Entergy did not adequately establish and maintain procedure 3-SOP-SFP-003, "Operation of the Backup Spent Fuel Pool Cooling (BSFPC) System." The updated fina
Region: I | Indian Point | 28911 | 03/31/2017 05/10/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Operation in Mode 1 with Pressurizer Code Safety Valves in an Inoperable Condition |  | P.2 Evaluation | TE?: N | 05000286 Indian Point 3 |  | 71153 | The inspectors identified an NCV of very low safety significance of Technical Specification (TS) 3.4.10, "Pressurizer Safety Valves," when two of three pressurizer code safety valves, RC-PCV-464 and RC-PCV-468, were reported to have failed surveillance te
Region: I | Indian Point | 28901 | 12/31/2016 02/03/2017 | 2016004-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Preventive Maintenance Classification of Starting Air Relief Valve Led to Failure |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.12 | The inspectors identified a finding of very low safety significance because Entergy did not correctly classify relief valve DA-5-2 as a high critical component. DA-5-2 is a relief valve in the emergency diesel generator (EDG) air start system; and when it
Region: I | Indian Point | 28902 | 12/31/2016 02/03/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of Leak in Service Water Pump Discharge Pipe |  | H.12 Avoid Complacency | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified an NCV of very low safety significance of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy staff did not perform an adequate operability r
Region: I | Indian Point | 28903 | 12/31/2016 02/03/2017 | 2016004-03 | NRC | FIN | Mitigating Systems | Green | Failure to Provide Indication of a Bypassed RPS Channel During Testing |  | H.14 Conservative Bias | TE?: N | 05000286 Indian Point 3 |  | 71111.18 | The inspectors identified a finding of very low safety significance when Entergy conducted testing on the Unit 3 reactor protection system (RPS) that was contrary to the guidance in IEEE standard 279-1968, a standard to which Indian Point Unit 3 was commi
Region: I | Indian Point | 28905 | 12/31/2016 02/03/2017 | 2016004-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow RPS Logic Train B Actuation Logic Test |  | H.2 Field Presence | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing NCV of Technical Specification (TS) 5.4.1(a), "Procedures," was identified because Entergy did not follow procedure 2-PT-2M3A, "Reactor Protection System Logic Train B Actuation Logic Test and Tadot," required by NRC Regulatory Guide 1.33
Region: I | Indian Point | 28883 | 10/13/2016 11/21/2016 | 2016009-01 | Self - Revealed | FIN | Initiating Events | Green | 345 kV Insulator Failure Causes Reactor Trip |  | H.12 Avoid Complacency | TE?: N | 05000286 Indian Point 3 |  | 71153 | A green self-revealing finding of ENN-EP-G-004, "Switchyard and Large Power Transformer Preventive Maintenance Guidelines," occurred in that preventive maintenance (PM) was not performed as required on the W96 345kV line insulators. Specifically, the semi
Region: I | Indian Point | 28884 | 09/30/2016 01/17/2017 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess Fire Risk Associated with Maintenance on the Unit 3 Appendix R Diesel Generator |  | P.1 Identification | TE?: N | 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) because between August 1, 2016, and August 17, 2016, Entergy did not perform an adequate risk assessment for the maintenance on the Unit 3 Appendix R
Region: I | Indian Point | 28887 | 09/30/2016 01/17/2017 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Missed Inspections on Automatic Voltage Regulator Cards Results in Emergency Diesel Generator Failure to Run |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because between 2012 and 2016, Entergy did not perform vendor specified inspections of the 23 emergency diesel generator (EDG) automatic vo
Region: I | Indian Point | 28889 | 09/30/2016 01/17/2017 | 2016003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entry into a High Radiation Area without Radiological Briefing |  | H.8 Procedure Adherence | TE?: N | 05000247 Indian Point 2 |  | 71124.01 | The inspectors identified a self-revealing NCV of TS 5.7.1e when workers entered the Unit 2 Fuel Storage Building (FSB) truck bay that was posted and controlled as a high radiation area (HRA) without receiving a briefing on the dose rates prior to enterin
Region: I | Indian Point | 28894 | 09/30/2016 01/17/2017 | 2016003-05 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Unit 2 Reactor Cavity Liner Repairs |  | H.5 Work Management | TE?: N | 05000247 Indian Point 2 |  | 71124.02 | The inspectors identified a self-revealing finding (FIN) of very low safety significance due to Entergy having unintended occupational collective exposure resulting from performance deficiencies in work planning while preparing to perform reactor cavity l
Region: I | Indian Point | 28895 | 09/30/2016 01/17/2017 | 2016003-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Two Qualified AC Sources of Offsite Power |  | H.5 Work Management | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors identified a self-revealing Green NCV for failing to comply with Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, "Electrical Power Systems, Alternating Current (AC) Sources - Operating," from February 26, 2014, to
Region: I | Indian Point | 28896 | 09/30/2016 01/17/2017 | 2016003-07 | NRC | VIO | Public Radiation Safety | Green | Inadequate Control of Floor Drains to Minimize Groundwater Contamination |  | P.3 Resolution | TE?: N | 05000247 Indian Point 2 |  | NONE | The inspectors identified an NOV of 10 CFR 20.1406(c), "Minimization of Contamination," for Entergy's failure to conduct operations to minimize the introduction of residual radioactivity into the subsurface of the site (groundwater). Specifically, Entergy
Region: I | Indian Point | 28888 | 09/20/2016 01/17/2017 | 2016003-03 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Degraded Automatic Voltage Regulator Card |  | H.14 Conservative Bias | TE?: N | 05000286 Indian Point 3 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because Entergy did not take timely corrective action to perform an inspection of the 33 EDG AVR card. As a result, the degraded solder connections on the
Region: I | Indian Point | 28876 | 06/30/2016 03/30/2017 | 2016002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Flow Channeling Gates Closed in Accordance with the Containment Procedure |  | H.12 Avoid Complacency | TE?: N | 05000247 Indian Point 2 |  | 71111.2 | The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, "Procedures," for Entergy's failure to implement procedure OAP-007, "Containment Entry and Egress." Specifically, workers transiting the inner and outer crane wall sections of co
Region: I | Indian Point | 28881 | 06/30/2016 03/30/2017 | 2016002-04 | NRC | NCV | Barrier Integrity | Green | Failure to Scope Safety-Related Main Boiler Feedwater Pump Discharge Valves into the Maintenance Rule Program |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50.65(b)(1) for Entergy's failure to include a function of a safety-related system within the scope of the maintenance rule program. Specifically, Entergy failed to include the feedwater isolation function p
Region: I | Indian Point | 28869 | 03/31/2016 05/12/2016 | 2016001-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement Risk Management Actions for the Containment Key Safety Function |  | H.7 Documentation | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) because Entergy did not effectively manage the risk associated with refueling maintenance activities. Specifically, Entergy did not demonstrate they could
Region: I | Indian Point | 28872 | 03/31/2016 05/12/2016 | 2016001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Surveillance Requirement for Main Boiler Feed Pump Trip Function |  | P.2 Evaluation | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified an NCV of TS 3.7.3, "Main Feedwater Isolation," Surveillance Requirement (SR) 3.7.3.3 on March 26, 2016, when the inspectors determined that Entergy had not conducted surveillance testing on the main boiler feed pump (MBFP) trip
Region: I | Indian Point | 28873 | 03/31/2016 05/12/2016 | 2016001-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide Adequate Procedural Guidance in Order to Prevent an Overcurrent Condition |  | H.11 Challenge the Unknown | TE?: N | 05000247 Indian Point 2 |  | 71152 | A self-revealing NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified for Entergy's failure to provide adequate guidance in procedure 2-PT-R084C, "23 Emergency Diesel Generator (EDG) Eight-Hour Load Test." Specifically, Entergy failed t
Region: I | Indian Point | 28866 | 12/18/2015 02/01/2016 | 2015012-01 | Self - Revealed | NCV | MISC | Green | Failure to Coordinate Work Activities Between Operations and Security |  | H.4 Teamwork | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71152B | (OUO-SRI) A self-revealing Green non-cited violation (NCV) of 10 CFR 73.58(b) was identified when Entergy did not manage the adverse effects on security before implementing a change in the plant configuration. Specifically, activities between the operatio
Region: I | Indian Point | 28867 | 12/18/2015 02/01/2016 | 2015012-02 | NRC | NCV | MISC | Green | Failure to Perform Testing and Maintenance on Security UPS |  | P.3 Resolution | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71152B | (OUO-SRI) The inspectors identified a Green NCV of 10 CFR 73.55(n)(1)(i) because Entergy did not implement a maintenance, testing and calibration program to ensure that security systems and equipment, including uninterruptible power supplies (UPS), remain
Region: I | Indian Point | 28859 | 09/30/2015 11/05/2015 | 2015003-01 | NRC | FIN | Mitigating Systems | Green | Blocked Drains in the 480 Volt Switchgear Room |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.06 | The inspectors identified a Green finding (FIN) because Entergy allowed the Unit 3 480 volt switchgear room floor drains to become blocked such that they could not mitigate an internal flood postulated in Action and Condition Tracking Form 95-14218. Speci
Region: I | Indian Point | 28860 | 09/30/2015 11/05/2015 | 2015003-02 | NRC | NCV | Barrier Integrity | Green | Incorrect Operability Determination Results in Failure to Comply with Technical Specification for Containment Integrity |  | H.14 Conservative Bias | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV for Unit 2 Technical Specification (TS) 3.6.1, "Containment," because between August 11 and August 14, 2015, containment out-leakage during accident conditions would have exceeded the containment leakage rate testing
Region: I | Indian Point | 28861 | 09/30/2015 11/05/2015 | 2015003-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Conduct Operations to Minimize the Introduction of Residual Radioactivity to the Site |  | P.2 Evaluation | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 20.1406(c) in that Entergy did not conduct operations to minimize the introduction of residual radioactivity into the site. Specifically, Entergy did not identif
Region: I | Indian Point | 28850 | 09/20/2015 10/05/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verif. that Prot. Device Settings Do Not Allow Connected Class 1E Loads to Become Damaged or Unavail. Under Normal & Sustained Degraded Voltage Condition During Design Basis Event |  | P.5 Operating Experience | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control." Specifically, Entergy failed to verify, in design
Region: I | Indian Point | 28854 | 09/20/2015 10/05/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verification that Adequate Voltages Would Be Available to All Class 1E Motors, MOVs, Static Loads, and MCC Control Circuits and Contractors at the Minimum DVR Dropout Setting |  | P.5 Operating Experience | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy did not verify the adequacy of their electrical design. Specifically,
Region: I | Indian Point | 28855 | 09/20/2015 10/05/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Elevated Battery Room Temperature Effects on Battery Service Life |  |  | TE?: N | 05000286 Indian Point 3 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because Entergy did not verify the adequacy of the safety-related battery test program. S
Region: I | Indian Point | 28856 | 09/20/2015 10/05/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Less Than Adequate Corrective Actions Associated with an Evaluation of the Seismic Adequacy of a 138 kV Transmission Tower Located Near the Unit 2 EDG Building |  | H.7 Documentation | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly identify and correct a condition adverse to quality. Specif
Region: I | Indian Point | 28841 | 06/30/2015 08/07/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Main Steam Safety Valve 46-3 Failure to Lift at Required Setpoint |  | P.2 Evaluation | TE?: N | 05000286 Indian Point 3 |  | 71111.22 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for Entergy's failure to take corrective actions for a condition adverse to quality involving Unit 3 Mai
Region: I | Indian Point | 28842 | 06/30/2015 08/07/2015 | 2015002-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain the Effectiveness of Emergency Plan Due to an Inadequate Basis for Emergency Action Level Thresholds |  | H.11 Challenge the Unknown | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50.54(q)(2) for Entergy's failure to maintain the effectiveness of an emergency plan that meets the requirements in Appendix E to Part 50 and the planning standards of 50.47(b). Specifically, Entergy did not
Region: I | Indian Point | 28849 | 06/24/2015 07/23/2015 | 2015010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Degraded Condition of Fire Protection System Solenoid Valve SOV-230-1 |  | H.11 Challenge the Unknown | TE?: N | 05000286 Indian Point 3 |  | 93812 | Green. The inspectors identified a Green NCV of Condition 2.H of the Indian Point Unit 3 Facility Operating License DPR-64, "Fire Protection Program," for failure to promptly identify, report, and correct a condition adverse to fire protection. Specifical
Region: I | Indian Point | 28824 | 03/31/2015 05/12/2015 | 2015001-01 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustibles in Accordance with the Approved Fire Protection Program |  | H.8 Procedure Adherence | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified an NCV of the license condition 2.K. when Entergy failed to properly control transient combustibles within the Unit 2 control room envelope in accordance with the approved fire protection program (FPP). The inspectors identified
Region: I | Indian Point | 28825 | 03/31/2015 05/12/2015 | 2015001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Degraded Fire Protection Piping Results in Piping Break |  | P.3 Resolution | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a self-revealing NCV of license condition 2.K. because Entergy did not take adequate corrective actions for degraded fire protection piping in the Unit 1 turbine building. This issue contributed to excessive leakage and failure o
Region: I | Indian Point | 28818 | 02/18/2015 03/30/2015 | 2014011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Safety Injection Make-up Capability |  | H.7 Documentation | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 92702 | The team identified a finding of very low safety significance, involving a non-cited violation of Indian Point Units 2 and 3 Facility Operating Licenses Conditions 2.K and 2.H, respectively, for failure to implement and maintain in effect all provisions o
Region: I | Indian Point | 28819 | 02/18/2015 03/30/2015 | 2014011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Barrier Analysis |  | H.6 Design Margins | TE?: N | 05000286 Indian Point 3 |  | 92702 | The team identified a finding of very low safety significance, involving a non-cited violation of Indian Point Unit 3 Facility Operating License Condition 2.H, for failure to implement and maintain in effect all provisions of the approved Fire Protection
Region: I | Indian Point | 28820 | 02/18/2015 03/30/2015 | 2014011-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Post-Fire Safe Shutdown Procedure |  | H.6 Design Margins | TE?: N | 05000286 Indian Point 3 |  | 92702 | The team identified a finding of very low safety significance, involving a non-cited violation of Indian Point Unit 3 Facility Operating License Condition 2.H, for failure to implement and maintain in effect all provisions of the approved Fire Protection
Region: I | Indian Point | 28823 | 02/18/2015 03/30/2015 | 2014011-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Post-Fire Safe Shutdown Procedure |  |  | TE?: N | 05000286 Indian Point 3 |  | 92702 | The team identified a finding of very low safety significance, involving a non-cited violation of Indian Point Unit 3 Facility Operating License Condition 2.H, for failure to implement and maintain in effect all provisions of the approved Fire Protection
Region: I | Indian Point | 28803 | 12/31/2014 02/05/2015 | 2014005-01 | NRC | FIN | Mitigating Systems | Green | Licensed Operator Requalification Remedial Exam Standard Adherence |  | H.8 Procedure Adherence | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.11B | The inspectors identified a Green finding (FIN) because Entergy did not adhere to their procedural standards for generating remedial written exams. Entergy failed to follow the guidance as stated in their procedure EN-TQ-201-03, "Systematic Approach to Tr
Region: I | Indian Point | 28801 | 09/30/2014 11/07/2014 | 2014004-01 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Refueling Activities |  | H.4 Teamwork | TE?: N | 05000247 Indian Point 2 |  | 71124.02 | A self-revealing finding (FIN) of very low safety significance (Green) was identified due to Entergy having excessive unintended occupational collective exposure. This resulted from performance deficiencies in planning and work control while performing re
Region: I | Indian Point | 28802 | 09/30/2014 11/07/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate Degraded Condition of the 22 Station Battery Capacity |  | P.2 Evaluation | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy personnel did not adequately implement procedure EN-OP-104, "Operability D
Region: I | Indian Point | 28796 | 06/20/2014 07/28/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Deficient Design Control Results in Non-Qualified Component Installed in Harsh Environment for Unit 3 BFD-FCV-406B Actuator |  | H.6 Design Margins | TE?: N | 05000286 Indian Point 3 |  | 71111.17T | The team identified a Green non-cited violation of Title 10 Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, Design Control, because Entergy did not ensure the control air pressure regulator (IA-PCV-1548) for Unit 3 auxiliary boile
Region: I | Indian Point | 28790 | 03/31/2014 05/09/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of Spalled Concrete in the Service Water Pit Structure |  | P.2 Evaluation | TE?: N | 05000286 Indian Point 3 |  | 71111.12 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Indian Point Energy Center (IPEC) staff did not evaluate spalled concrete in the Unit
Region: I | Indian Point | 28791 | 03/31/2014 05/09/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Incomplete Risk Assessment While Pressurizer Safety Valves Were Being Removed |  | H.5 Work Management | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The inspectors identified an NCV of 10 CFR Part 50.65(a)(4) when Entergy did not adequately re-assess and manage risk when planned maintenance was not completed as scheduled. Specifically, IPEC staff did not re-assess the risk when the scheduled activity
Region: I | Indian Point | 28792 | 03/31/2014 05/09/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | Spent Fuel Pool Fuel Assembly Interference Events |  | H.12 Avoid Complacency | TE?: N | 05000247 Indian Point 2 |  | 71111.2 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, when IPEC staff failed to follow fuel handling procedures which ensure that the correct spent fuel pool configuration is used in the development of the core offload plan, ensure that
Region: I | Indian Point | 28794 | 03/31/2014 05/09/2014 | 2014002-04 | NRC | NCV | Mitigating Systems | Green | Inappropriate Procedural Controls When Stopping Residual Heat Removal (RHR) Without Assurance that Reactor Coolant System (RCS) Loops Were Filled and Available for Natural Circulation Cooling |  | H.6 Design Margins | TE?: N | 05000247 Indian Point 2 |  | 71111.2 | The Inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Entergy used a test procedure that was not appropriate to the circumstances and the operating loop of RHR was stopped during the co
Region: I | Indian Point | 28795 | 03/26/2014 04/29/2014 | 2013011-02 | Licensee - Identified | NCV | MISC | Green | Operation of IP Units 2 and 3 in violation of the TS due to the RFOST and/or 22 FOST particulate limits being exceeded. | EA Case: 2013076 |  | TE?: N | 05000247 Indian Point 2 |  | NONE | From EA-13-076, letter dated April 29, 2014 This violation involves examples of operation of IP Units 2 and 3 in violation of the TS due to the RFOST and/or 22 FOST particulate limits being exceeded. As discussed below, this violation is not cited beca
Region: I | Indian Point | 28773 | 06/30/2013 07/31/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk Associated with Reactor Testing Below Normal Operating Conditions |  | H.3(a) Work Planning | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4), requirements for monitoring the effectiveness of maintenance, when Entergy did not assess and manage the risk associated with reactor protection testing
Region: I | Indian Point | 28774 | 06/30/2013 07/31/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality Affecting Pressurizer Safety Valves |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when Entergy failed to correct a condition adverse to quality associated with the Unit 3 pressurizer safety valves (PSVs). Specifically, following valve lift se
Region: I | Indian Point | 28775 | 06/30/2013 07/31/2013 | 2013003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Appropriate Procedures for Response to Safety Injection Actuation at Low Temperature |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71153 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," when Entergy did not maintain appropriate written procedures for responding to an inadvertent SI on Unit 3 when below the normal operating RCS temperature. As a result,
Region: I | Indian Point | 28772 | 03/31/2013 05/03/2013 | 2013002-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance Procedure Results in a Reactor Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.12 | A self-revealing finding of very low safety significance was identified when Entergy personnel did not use a procedure appropriate to the task for testing of a secondary plant valve, resulting in a transient that led to a manual reactor trip. On February
Region: I | Indian Point | 28771 | 02/15/2013 03/28/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement an Appropriate Procedure to Ensue That One of Two Strategies Provided Adequate Cooling Water Flow to the SGs per 50.54(hh)(2) |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71111.05T | The team identified a non-cited violation (NCV) of Unit 2 Operating License Condition 2.N, Unit 3 Operating License Condition 2.AC, and 10 CFR 50.54(hh)(2) for Entergy's failure to implement guidance for one of the two strategies intended to maintain o
Region: I | Indian Point | 28769 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Regarding Operational Controls of the Steam Generator Blowdown Valve Radiation Bypass Switch |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors identified a Green, NCV of Title 10 Code of Federal Regulations (CFR) Part 50, Criterion XVI, "Corrective Actions," because Entergy personnel did not adequately identify and correct a condition adverse to quality associated with maintenance
Region: I | Indian Point | 20787 | 11/09/2012 12/21/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Turbine Building HELB Evaluation for Effect on Safety Related Equipment |  |  | TE?: N | 05000286 Indian Point 3 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion lll, Design Control, because Entergy had not verified the adequacy of their design with respect to the potenti
Region: I | Indian Point | 26556 | 11/09/2012 12/21/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verification that Bus 6A Supply Breaker Amptector Would Not Inadvertently Trip and Lockout Bus During Degraded Grid Accident SI Load Current |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion lll, Design Control, because Entergy had not verified the adequacy of the design with respect to ensuring the Un
Region: I | Indian Point | 20788 | 11/09/2012 12/21/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Design Analyses for Recirculation Pump NPSH |  |  | TE?: N | 05000286 Indian Point 3 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR.Part 50, Appendix B, Criterion lll, Design Control, because Entergy had not verified the adequacy of the existing design analyses for interna
Region: I | Indian Point | 26557 | 11/09/2012 12/21/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Turbine Building HELB Evaluation for Effect on Safety Related Equipment |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion lll, Design Control, because Entergy had not verified the adequacy of their design with respect to the potenti
Region: I | Indian Point | 26558 | 11/09/2012 12/21/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Design Analyses for Recirculation Pump NPSH |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR.Part 50, Appendix B, Criterion lll, Design Control, because Entergy had not verified the adequacy of the existing design analyses for interna
Region: I | Indian Point | 26551 | 09/30/2012 11/08/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of Non-Conforming Safety Related Batteries |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy personnel did not adequately implement procedure EN-OP-104, "Operability Determination Process," Section 5.1, to assess
Region: I | Indian Point | 26552 | 09/30/2012 11/08/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of Safety Related Batteries |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because Entergy did not assure that all testing required to demonstrate safety related batteries will perform satisfactorily was identified and performed in
Region: I | Indian Point | 26554 | 09/30/2012 11/08/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of 22 Static Inverter with a Degraded Frequency Meter |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy staff did not adequately implement procedure EN-OP-104 "Operability Determination Process," section 5.1, to assess the o
Region: I | Indian Point | 26538 | 07/20/2012 11/28/2012 | 2012009-01 | NRC | VIO | Mitigating Systems | Green | Failure to Protect Safe Shutdown Equipment from the Effects of Fire |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71152 | The inspectors identified a finding of very low safety significance (Green), involving a cited violation of lndian Point Unit 2 Operating License Condition 2.K to implement and maintain all aspects of the approved fire protection program. Specifically, EN
Region: I | Indian Point | 26542 | 07/20/2012 11/28/2012 | 2012009-02 | NRC | NCV | Mitigating Systems | Green | Violation of Transient Combustible Control Program |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green, Non-Cited Violation of the lndian Point Nuclear Generating Unit No. 2 Amended Facility Operating License, Condition 2.K, in that ENO failed to implement and maintain in effect all provisions of the NRC-approved fire prot
Region: I | Indian Point | 20779 | 06/30/2012 08/09/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Testing 33 Station Battery (Section 1R15.1) |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because Entergy personnel did not properly document and evaluate test results to ensu
Region: I | Indian Point | 26536 | 06/30/2012 08/09/2012 | 2012003-01 | Self - Revealed | NCV | Initiating Events | Green | Foreign Materials Control Procedure Not Followed Resulting in a Degraded 21 Reactor Coolant Pump Seal Package |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Entergy personnel did not follow procedure 0-PMP-401-RCS, Reactor Coolant Pump Seal Package Inspection, to prevent foreign materia
Region: I | Indian Point | 20780 | 06/30/2012 08/09/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Battery Voltage Drop Calculation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) involving an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Entergy staff did not ensure or verify the adequacy of design with respect to the 33 battery si
Region: I | Indian Point | 26534 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Corrective Actions for Clogged Drains in the 480 Volt Switchgear Room |  | P.1(b) Trend Performance CAP | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance for Entergy staff not following Entergy Procedure EN-LI-102, Corrective Action Program. Specifically, between initial plant startup and January 17, 2012, Entergy staff did not follow Proc
Region: I | Indian Point | 20773 | 03/31/2012 04/30/2012 | 2012002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure and Instructions for Placing Pressure Regulator in Service |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | A self-revealing NCV of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified, because Entergy personnel did not ensure written maintenance instructions and an operating proced
Region: I | Indian Point | 26535 | 03/31/2012 04/30/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Abnormal Operating Procedure Not Allowed for Annuciator Alarm Deficiency |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified an NCV of Technical Specification 5.4.1.a, "Procedures", because Entergy personnel did not follow Procedure 2-AOP-ANNUN-1, Failure of Flight or Supervisory Panel Annunciators, for an intermittent control room annunciator problem.
Region: I | Indian Point | 20774 | 03/31/2012 04/30/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Failed to Update Operating Procedures and Licensing Basis Documents with Nitrogen Backup System Design and Support Function for AFW System Operability |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Entergy personnel did not ensure that the design basis for the nitrogen backup system to instrument air was correctly translated into specifications,
Region: I | Indian Point | 20778 | 03/31/2012 04/30/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with Degraded Motor Cutoff Switches on 480 Volt Breakers |  | P.2(b) Implementing Operating Experience | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified an NCV of very low safety significance, of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Actions," because Entergy personnel did not promptly identify and correct, a condition adverse to quality associated with degraded motor
Region: I | Indian Point | 20781 | 03/08/2012 04/19/2012 | 2012008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Protect Safe Shutdown Equipment from the Effects of Fire |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The inspectors identified a finding of very low safety significance (Green), involving a cited violation of Indian Point Unit 3 Operating License Condition 2.H to implement and maintain all aspects of the approved fire protection program. Specifically, EN
Region: I | Indian Point | 26530 | 12/31/2011 02/08/2012 | 2011005-01 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Actions for Repeated Control Room Fan Failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.04Q | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy personnel did not promptly correct an adverse condition related to the safety-related control room ventilation fan. Specifically, between Septem
Region: I | Indian Point | 26531 | 12/31/2011 02/08/2012 | 2011005-02 | NRC | FIN | Mitigating Systems | Green | Water Intrusion Due to Leaking Flood Penetration Seals in the 480 Volt Room During Hurricane Irene |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified a finding because Entergy procedure ENN-DC-150, Condition Monitoring of Maintenance Rule Structures, did not have appropriate quantitative or qualitative acceptance criteria for determining that important activities have been sat
Region: I | Indian Point | 26532 | 12/31/2011 02/08/2012 | 2011005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Maintenance Procedure Not Followed for Inertia Latch Cleaning on 21 Service Water Pump |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors documented a self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy personnel did not follow Entergy procedure 2-BRK-022-ELC, Westinghouse Model DB-50 Breaker Preventative Mainten
Region: I | Indian Point | 26533 | 12/02/2011 01/13/2012 | 2011007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correctly Implement an Approved Setpoint Change to Reactor Protection System Instruments |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000247 Indian Point 2 |  | 71111.17T | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Entergy did not ensure that design changes, including field changes, were subject to design control measures commensurate with those applied to th
Region: I | Indian Point | 20761 | 12/01/2011 01/13/2012 | 2011007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correctly Implement an Approved Setpoint Change to Reactor Protection System Instruments |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000286 Indian Point 3 |  | 71111.17T | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Entergy did not ensure that design changes, including field changes, were subject to design control measures commensurate with those applied to th
Region: I | Indian Point | 26525 | 09/30/2011 11/10/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Marginally Designed Fuse Results in Fuse Failure and Inoperability of the Refueling Water Storage Tank |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," because Entergy personnel did not establish measures to assure that the design basis for sizing of a fuse was adequate and correctly translated into specifica
Region: I | Indian Point | 20755 | 08/05/2011 07/11/2011 | 2011010-01 | NRC | FIN | Mitigating Systems | Green | Procedural Requirements of Engineering Change Process Not Implemented |  | H.3(b) Work Activity Coordination | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) because Entergy personnel did not adequately implement the procedural requirements of EN-DC- 115, "Engineering Change Process," during the installation of a modification to the
Region: I | Indian Point | 20758 | 08/05/2011 07/11/2011 | 2011010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Degraded EDG SW Piping |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Action," for Entergy's failure to take adequate corrective actions for a condition adverse to quality involving service water (SW) pipes to
Region: I | Indian Point | 20740 | 06/30/2011 08/08/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure and Procedural Compliance for 33 Inverter Overhaul |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not assure that the overhaul of the 33 inverter was prescribed by an appropriate procedure and that the overhaul was
Region: I | Indian Point | 26515 | 06/30/2011 08/08/2011 | 2011003-01 | NRC | NCV | Emergency Preparedness | Green | Entergy Did Not Identify and Correct a Performance Deficiency During an Emergency Preparedness Drill |  | H.1(c) Communication of Decisions | TE?: N | 05000247 Indian Point 2 |  | 71111.11Q | The inspectors identified a Green NCV of 10 CFR 50.47, "Emergency Plan," paragraph (b)(14), because Entergy staff did not properly identify an emergency response deficiency which occurred during a drill. Specifically, during the operator training scenario
Region: I | Indian Point | 26516 | 06/30/2011 08/08/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Monitoring of Maintenance Rule In-Scope Service Water Pump and Circulating Water Pump Bay Structures |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy personnel did not monitor the performance or condition of structures, systems, or components, ag
Region: I | Indian Point | 26517 | 06/30/2011 08/08/2011 | 2011003-03 | NRC | NCV | Initiating Events | Green | Inadequate Operability Evaluation for Degraded Pressurizer Modulating Heater Group Controller |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V "Instructions, Procedures, and Drawings," because Entergy personnel did not adequately implement Procedure EN-OP-104 "Operability Determination Process," to assess the operability
Region: I | Indian Point | 26521 | 06/30/2011 08/08/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Inaccurate 21 Inverter AC Output Voltmeter |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because Entergy personnel did not assure that adequate test instrumentation was available and used for 21 inverter surveillance tests. Specifically, between Apri
Region: I | Indian Point | 20754 | 05/27/2011 09/26/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Interim Compensatory Measure for Service Water Strainer Backwash Function |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a Green, Non-Cited Violation (NCV) of Indian Point Nuclear Generating Unit 3 Operating License Condition 2.H, in that Entergy did not establish an appropriate interim compensatory measure for several fire areas where 10 CFR 50 Appen
Region: I | Indian Point | 20729 | 03/31/2011 05/12/2011 | 2011002-01 | NRC | NCV | Initiating Events | Green | Entergy Personnel Did Not Evaluate and Monitor a Terminal Barrier Boric Acid Leak |  | H.4(b) Procedural Compliance | TE?: N | 05000286 Indian Point 3 |  | NONE | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion V, "lnstructions, Procedures, and Drawings," of very low safety significance (Green) because Entergy personnel did not adequately implement Boric Acid Control procedures. Specifically,
Region: I | Indian Point | 26508 | 03/31/2011 05/12/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Main Steam Configuration Control Procedure Not Adequate to Ensure Closure of MS-55D |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.04Q | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy procedure 2 COL 18.1, "Main Steam and Reheat System," was not adequate to ensure closure of main steam isolation valve (
Region: I | Indian Point | 20734 | 03/31/2011 05/12/2011 | 2011002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Lifting of 32 ABFP Steam Supply Relief Valve |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | A self-revealing NCV of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion Xl, 'Test Control,'was identified because Entergy personnel did not establish an adequate test program to assure that the 32 ABFP steam supply relief valve
Region: I | Indian Point | 26510 | 03/31/2011 05/12/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Entergy Personnel Did Not Identify a Leak on the 25 Service Water Pump Piping |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy personnel did not promptly identify and correct an adverse condition related to a service water (SW) pipe leak. Specifically, on October 29
Region: I | Indian Point | 20739 | 03/31/2011 05/12/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Application of Sealant Resulted in Drain Blockage for the Turbine-Driven Auxiliary Feedwater Pump |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a NCV of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Actions," because Entergy personnel did not identify and correct a condition adverse to quality with regard to packing leakoff
Region: I | Indian Point | 20249 | 12/31/2010 02/11/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Repeated Control Room Air Conditioner Gasket Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | 71111.12 | An NRC-identified NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because Entergy personnel did not take prompt action to correct a condition adverse to quality regarding the safety-related
Region: I | Indian Point | 26493 | 12/31/2010 02/11/2011 | 2010005-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Measures for Out-of-Service Plant Vent Process Radiation Monitor |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR 50.54, "Conditions of Licenses," paragraph (q), because Entergy staff did not implement adequate compensatory measures when the R-27 plant vent process radiation monitor, which is used for emergency action l
Region: I | Indian Point | 20250 | 12/31/2010 02/11/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program (QAP)," because Entergy personnel did not implement the qualification and experience requirements of the QAP to ensure that an individual assigned to
Region: I | Indian Point | 26494 | 12/31/2010 02/11/2011 | 2010005-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Inadequate Work Planning Control Relative to Regenerative Heat Exchanger Permanent Shielding Modification That Resulted in Additional Unplanned Collective Exposure |  | H.3(a) Work Planning | TE?: N | 05000247 Indian Point 2 |  | 71124.02 | A Green self-revealing finding was identified because Entergy personnel did not adequately plan and control work activities related to a regenerative heat exchanger permanent shielding modification in accordance with radiation work permit (RWP) 20102537,
Region: I | Indian Point | 20728 | 12/31/2010 02/11/2011 | 2010005-03 | NRC | NCV | Emergency Preparedness | Green | Failure of the Offsite Notification Procedure to Meet the Requirements of the Site Emergency Plan |  |  | TE?: N | 05000286 Indian Point 3 |  | 71153 | An NRC-identified Green NCV of 10 CFR 50.54, "Conditions of Licenses," paragraph (q), was identified because the Entergy emergency plan implementing procedure (EPIP) for notification of offsite officials did not meet the requirements of the IPEC Emergency
Region: I | Indian Point | 26495 | 12/31/2010 02/11/2011 | 2010005-03 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Inadequate Work Coordination Relative to Reactor Cavity Liner Repair That Resulted in Additional Unplanned Collective Exposure |  | H.3(b) Work Activity Coordination | TE?: N | 05000247 Indian Point 2 |  | 71124.02 | A Green self-revealing finding was identified because Entergy personnel did not adequately plan and control work activities related to reactor cavity liner repair in accordance with RWP 20102530, "2R19 Cavity Liner Repair." Specifically, outage schedule d
Region: I | Indian Point | 26496 | 12/31/2010 02/11/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion X, "Inspection," because Entergy personnel did not ensure that quality control verification inspections were consistently included and correctly specified in quality-affecting proce
Region: I | Indian Point | 26497 | 12/31/2010 02/11/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000247 Indian Point 2 |  | 71152 | he inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program (QAP)," because Entergy personnel did not implement the qualification and experience requirements of the QAP to ensure that an individual assigned to t
Region: I | Indian Point | 26501 | 12/31/2010 02/11/2011 | 2010005-06 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Main Boiler Feed Pump Speed Controller Setting |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green self-revealing finding was identified because Entergy's procedure 2 IC PC-N-P-408A, "Main Boiler Feed Pump (MBFP) Discharge Pressure Speed Control," did not provide adequate guidance to ensure proper settings for the MBFP speed controller settings
Region: I | Indian Point | 26502 | 12/31/2010 02/11/2011 | 2010005-07 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to Staff the Site TSC and OSC Within 60 Minutes of an Alert Emergency Declaration |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green self-revealing NCV of 10 CFR 50.54, "Conditions of Licenses," paragraph (q), was identified because Entergy staff did not adequately implement the requirements of the IPEC Emergency Plan. On the evening of November 7, 2010, the Unit 2 operators de
Region: I | Indian Point | 26503 | 12/31/2010 02/11/2011 | 2010005-08 | NRC | NCV | Emergency Preparedness | Green | Failure of Offsite Notification Procedure to Meet the Requirements of the Site Emergency Plan |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50.54, "Conditions of Licenses," paragraph (q), because the Entergy emergency plan implementing procedure (EPIP) for notification of offsite officials did not meet the requirements of the IPEC Emergency Plan
Region: I | Indian Point | 26507 | 12/31/2010 02/11/2011 | 2010005-09 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Meet TS Oversight Requirement |  | H.4(a) Human Error Prevention | TE?: N | 05000247 Indian Point 2 |  | NONE | A Green self-revealing NCV of Technical Specification (TS) 5.1, "Responsibility," was identified because on February 9, 2010, the control room supervisor (CRS) assigned as having the control room command function, left the control room without designating
Region: I | Indian Point | 20248 | 10/29/2010 12/13/2010 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of Service Water Strainer Room Flood Barrier |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion lll, Design Control, in that Entergy did not verify the adequacy of the flood barrier design for the service water (SW) strainer room to ensure safety-related equipment would
Region: I | Indian Point | 20241 | 09/30/2010 11/10/2010 | 2010004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Identification and Correction of a Condition Adverse to Quality to Ensure the Continued Availability of the Safety-Related No. 31 Static Inverter |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | 71111.12 | A self-revealing, non-cited violation (NCV) of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because Entergy personnel did not adequately identify and correct a condition adverse to qual
Region: I | Indian Point | 26490 | 09/30/2010 11/10/2010 | 2010004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Reactor Trip Breaker Preventative Maintenance Procedure Was Not Adequately Implemented |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 71111.19 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified because Entergy personnel did not adequately implement the preventive maintenance (PM) procedure for the B reactor trip breaker (RTB). Spec
Region: I | Indian Point | 20237 | 06/30/2010 08/12/2010 | 2010003-01 | NRC | FIN | Mitigating Systems | Green | Procedural Requirements for N-38 Component Classification for Preventative Maintenance Not Implemented |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000286 Indian Point 3 |  | 71153 | An NRC-identified finding of very low safety significance was identified because Entergy personnel did not implement procedural requirements for component classification. Specifically, Entergy staff did not classify the N-38 neutron detector as a high cri
Region: I | Indian Point | 26483 | 06/30/2010 08/12/2010 | 2010003-01 | NRC | NCV | Barrier Integrity | Green | Inoperable Control Room Ventilation System due to Damper Mispositioning |  | H.4(a) Human Error Prevention | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a Green NCV of Technical Specification (TS) 3.7.10 because Entergy personnel did not ensure proper configuration control of a damper in the control room ventilation system (CRVS), which resulted in both trains of CRVS being inope
Region: I | Indian Point | 20240 | 06/30/2010 08/12/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Neutron Detector N-38 Anomalous Behavior |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000286 Indian Point 3 |  | 71153 | An NRC-identified NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Entergy personnel did not perform an adequate operability evaluation in accordance with procedure
Region: I | Indian Point | 20236 | 04/23/2010 06/18/2010 | 2010007-01 | NRC | FIN | Initiating Events | Green | Corrective Actions That Were Developed to Address Causal Factors Associated with Reactor Trips Were Not Implemented in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | NONE | The inspectors identified a finding of very low safety significance (Green) related to the untimely completion of corrective actions that were associated with the August 10, 2009, Unit 3 automatic reactor trip due to the generator primary lockout relay tr
Region: I | Indian Point | 26487 | 04/07/2010 05/07/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Fire Scenario resulting in loss of charging pump suction |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.05T | The team identified a Green, Non-Cited Violation (NCV) of 10 CFR 50, Appendix R, III.G.3, in that Entergy failed to provide one train of reactor coolant system makeup free of fire damage for the control room, cable spread room, and cable tunnel fire zones
Region: I | Indian Point | 26488 | 04/07/2010 05/07/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Fire Scenario resulting in loss of cooling water to charging pumps |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.05T | The team identified a Green, Non-Cited Violation of 10 CFR 50, Appendix R, III.G.3, in that Entergy failed to provide one train of reactor coolant system makeup free of fire damage for the control room, cable spread room, electrical switchgear room, and c
Region: I | Indian Point | 20230 | 03/30/2010 05/13/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedures for the Steam-Driven Auxiliary Boiler Feedwater (AFW) Pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71111.19 | A self-revealing finding of very low safety significance was identified because Entergy personnel did not have adequate procedures appropriate for the circumstances for maintenance associated with the steam-driven auxiliary feedwater (AFW) pump. Specifica
Region: I | Indian Point | 26480 | 03/30/2010 05/13/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Isolation of Service Water to All Emergency Diesel Generators |  | H.3(b) Work Activity Coordination | TE?: N | 05000247 Indian Point 2 |  | 71111.2 | A self-revealing NCV of Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.2 was identified when Entergy personnel did not maintain service water (SW) cooling to the emergency diesel generators (EDGs) when the reactor was in cold sh
Region: I | Indian Point | 20235 | 03/30/2010 05/13/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Preconditioning of RWST Level Switch |  | P.2(b) Implementing Operating Experience | TE?: N | 05000286 Indian Point 3 |  | 71111.22 | An NRC-identified non-cited violation (NCV) of very low safety significance of 10 CFR 50, Appendix B, Criterion XI, "Test control," was identified because Entergy technicians conducted unacceptable preconditioning by cycling the Refueling Water Storage Ta
Region: I | Indian Point | 26481 | 03/30/2010 05/13/2010 | 2010002-03 | Self - Revealed | FIN | Initiating Events | Green | Improper Generrex Isolation Caused Reactor Trip |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing finding of very low safety significance was identified because Entergy personnel did not establish procedures that were appropriate to the task, and personnel did not adequately implement the procedures that existed for isolating the g
Region: I | Indian Point | 20220 | 12/31/2009 02/09/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Untimely Compensatory Measures for Degraded EDG Pressure Switches |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | An NRC-identified NCV of very low safety significance of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because Entergy personnel did not adequately correct a condition adverse to quality to ensure the continued operability of
Region: I | Indian Point | 26477 | 12/31/2009 02/09/2010 | 2009005-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Siren Test Failure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000247 Indian Point 2 |  | 71114.02 | A self-revealing NCV of very low safety significance of 10 CFR 50.47(b)(5) was identified because Entergy personnel did not ensure the alert and notification system (ANS) sirens remained available for notification of the populace within the plume exposure
Region: I | Indian Point | 20221 | 12/31/2009 02/09/2010 | 2009005-03 | Self - Revealed | NCV | Emergency Preparedness | Green | Siren Test Failure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000286 Indian Point 3 |  | 71114.02 | A self-revealing NCV of very low safety significance of 10 CFR 50.47(b)(5) was identified because Entergy personnel did not ensure the alert and notification system (ANS) sirens remained available for notification of the populace within the plume exposure
Region: I | Indian Point | 26478 | 12/31/2009 02/09/2010 | 2009005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Partial Loss of Control Room Indication During NI 41 Recorder Replacement |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing non-cited violation (NCV) of very low safety significance of 10 CFR 50, Appendix B Criterion V "Instructions, Procedures, and Drawings," was identified because Entergy personnel did not perform work regarding replacement of a control room
Region: I | Indian Point | 20222 | 12/31/2009 02/09/2010 | 2009005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a MCCB Service Life Nonconformance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | 71152 | An NRC-identified non-cited violation (NCV) of very low safety significance of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because Entergy personnel did not promptly identify and correct a condition adverse to quality regard
Region: I | Indian Point | 20227 | 12/31/2009 02/09/2010 | 2009005-05 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Post-Maintenance Testing and Resultant Failure of 6.9kV Breaker Auto-Transfer Following Plant Trip |  | H.3(a) Work Planning | TE?: N | 05000286 Indian Point 3 |  | 71153 | A self-revealing finding (FIN) of very low safety significance was identified because Entergy personnel did not perform adequate post-maintenance functional testing to ensure 6.9kV breakers were able to perform intended safety functions. Specifically, in
Region: I | Indian Point | 20228 | 12/31/2009 02/09/2010 | 2009005-06 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance on MBFPs Results in Unexpected Downpower and Subsequent Reactor Trip |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000286 Indian Point 3 |  | 71153 | A self-revealing finding (FIN) of very low safety significance was identified because Entergy personnel did not ensure adequate maintenance was conducted on the 31 and 32 main boiler feed pumps (MBFPs). Specifically, the inspectors determined that Entergy
Region: I | Indian Point | 26470 | 08/14/2009 07/23/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Impact on Breaker Coordination for the Westinghouse Amptector Type LSG Trip Unit Discriminator Feature |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Entergy did not verify the adequacy of design because they did not evaluate the impact of
Region: I | Indian Point | 26471 | 08/14/2009 07/23/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure That the CCW Pump Hydraulic Performance Test Procedures Had Acceptance Criteria That Incorporated the Limits from Applicable Design Documents |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Entergy did not to ensure that the component cooling water pump hydraulic performance tes
Region: I | Indian Point | 26472 | 08/14/2009 07/23/2009 | 2009007-03 | NRC | FIN | Mitigating Systems | Green | Failure to Identify Several Degraded City Water System Pipe Supports in the Utility Tunnel |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance because Entergy did not identify or evaluate material deficiencies of the city water system, as required by EN-LI-102, "Corrective Action Process." Specifically, Entergy did not identify or eva
Region: I | Indian Point | 20205 | 06/30/2009 08/12/2009 | 2009003-01 | NRC | NCV | Initiating Events | Green | Failure to assess and manage the increase in risk prior to the performance of maintenance on valve that was unisolable from the reactor coolant system. |  | H.3(a) Work Planning | TE?: N | 05000286 Indian Point 3 |  | 71153 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(4), because Entergy personnel did not adequately assess and manage increased risk associated with planned corrective maintenance. Specifically, Entergy staff did not include in their
Region: I | Indian Point | 20210 | 06/30/2009 08/12/2009 | 2009003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance Procedures on FRVs Resulted in a Manual Reactor Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71153 | A self-revealing finding of very low safety significance was identified because Entergy personnel did not have adequate procedures appropriate for maintenance associated with air-operated valves. Specifically, existing Entergy maintenance procedures did n
Region: I | Indian Point | 20202 | 06/12/2009 07/23/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Degraded Grid Protection Relay Exceeded Technical Specification Limits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | NONE | -Green. The inspectors identified an NCV of very low safety significance of 10 CFR 50, Criterion XVI, "Corrective Action," for Entergy's failure to identify and correct a condition adverse to quality related to 480-Volt bus 3A degraded grid protection. Sp
Region: I | Indian Point | 20203 | 06/12/2009 07/23/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Instrument Air 10CFR 50.65 (a)(2) Performance Demonstration Not Met |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000286 Indian Point 3 |  | NONE | Green. The inspectors identified an NCV of very low safety significance of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(2), for Entergy's failure to adequately demonstrate that the ins
Region: I | Indian Point | 26467 | 04/03/2009 08/12/2009 | 2009003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Change Package for Installation of Main Boiler Feed Pump Control System Tubing |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | The inspectors documented a self-revealing finding of very low safety significance because Entergy engineers did not provide adequate guidance in a design change package for installation of tubing in the 21 main boiler feed water pump (MBFP) control syste
Region: I | Indian Point | 20201 | 03/31/2009 05/14/2009 | 2009002-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000286 Indian Point 3 |  | 7112101 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a, "Procedures," because Entergy personnel did not generate condition reports or investigation paperwork for multiple high dose-rate alarms as required by station proce
Region: I | Indian Point | 26452 | 03/31/2009 05/14/2009 | 2009002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Identify Open Louvers in 11 Fire Pump House |  | H.4(a) Human Error Prevention | TE?: N | 05000247 Indian Point 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance because Entergy personnel did not adequately implement procedure EN-LI-102, Corrective Action Process, and promptly identify a condition adverse to quality associated with open louvers in
Region: I | Indian Point | 26453 | 03/31/2009 05/14/2009 | 2009002-02 | NRC | NCV | Initiating Events | Green | Failure to Identify Damaged Components in EDG Ventilation Motor Control Center |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified a NCV of very low safety significance related to 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because Entergy did not promptly identify and correct an adverse condition related to an electrical fault. Specifically,
Region: I | Indian Point | 26454 | 03/31/2009 05/14/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Promptly Correct Degraded 480 Volt Switchgear Room Fire Door |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified a NCV of very low safety significance related to License Condition 2.K., fire protection program, because personnel did not promptly identify and correct a degraded three-hour rated fire door latch mechanism on the west entrance
Region: I | Indian Point | 26457 | 03/31/2009 05/14/2009 | 2009002-04 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Procedure for EDG Ventilation Motor Control Center |  | P.2(b) Implementing Operating Experience | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified a NCV of very low safety significance related to TS 5.4.1, "Administrative Controls: Procedures," because Entergy did not maintain an adequate maintenance procedure for a safety-related electrical motor control center (MCC). Spec
Region: I | Indian Point | 26458 | 03/31/2009 05/14/2009 | 2009002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Include RWST Level Maintenance in Online Risk Assessment |  | H.3(a) Work Planning | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The inspectors identified a NCV of very low safety significance related to 10 CFR 50.65(a)(4), because Entergy personnel did not adequately assess the risk associated with the unavailability of the Refueling Water Storage Tank (RWST) level indication duri
Region: I | Indian Point | 26459 | 03/31/2009 05/14/2009 | 2009002-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Acceptance Criteria for Auxiliary Component Cooling Check Valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a NCV of very low safety significance related to 10 CFR 50.55a, "Codes and standards," because Entergy's procedure, 2-PT-Q031A for an auxiliary component cooling water pump, did not contain appropriate acceptance criteria for pos
Region: I | Indian Point | 26466 | 03/31/2009 05/14/2009 | 2009002-07 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 7112101 | The inspectors identified a NCV of very low safety significance related to Technical Specification 5.4.1.a, "Procedures," because Entergy personnel did not generate condition reports or investigation paperwork for multiple high dose-rate alarms as require
Region: I | Indian Point | 20200 | 12/31/2008 02/05/2009 | 2008005-01 | Self - Revealed | NCV | Mitigating Systems | Green | 34 Control Building Fan Bearing Failures Caused by Torque and Lubrication Deficiencies. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | 71111.19 | A Green, self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified, in that, Entergy failed to properly include the appropriate torque requirements and lubricant in plant instruction
Region: I | Indian Point | 20194 | 09/29/2008 11/13/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedures Results in the Inadvertent Start of Two Auxiliary Boiler Feed Pumps at Power. |  | H.4(a) Human Error Prevention | TE?: N | 05000286 Indian Point 3 |  | 71111.19 | A self-revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when maintenance technicians incorrectly attached electrical jumpers during a surveillance test and caused the inad
Region: I | Indian Point | 20195 | 09/29/2008 11/13/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Maintenance Procedures Results in Degraded EDG for 37 Days. |  | H.4(a) Human Error Prevention | TE?: N | 05000286 Indian Point 3 |  | 71153 | A self-revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when maintenance personnel improperly performed a maintenance procedure that resulted in two adjacent cylinders of
Region: I | Indian Point | 26446 | 08/15/2008 09/25/2008 | 2008012-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of Internal Recirculation Pumps |  |  | TE?: N | 05000247 Indian Point 2 |  | NONE | -Green. The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, because Entergy did not verify the adequacy of the internal recirculation pump minimum flow rates. Specifically, Entergy did not verify the ad
Region: I | Indian Point | 20190 | 08/14/2008 09/25/2008 | 2008010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of Internal Recirculation Pumps |  | P.2(b) Implementing Operating Experience | TE?: N | 05000286 Indian Point 3 |  | NONE | -Green. The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, because Entergy did not verify the adequacy of the internal recirculation pump minimum flow rates. Specifically, Entergy did not verify the ad
Region: I | Indian Point | 26447 | 08/08/2008 11/13/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Auxiliary Feedwater System Configuration Control Deficiencies |  | H.4(a) Human Error Prevention | TE?: N | 05000247 Indian Point 2 |  | 71111.04Q | The inspectors identified a Green NCV of Technical Specification 5.4.1, "Administrative Controls - Procedures," because Entergy did not implement the Auxiliary Feedwater (AFW) operating procedures required by Regulatory Guide 1.33 Appendix A. Specifically
Region: I | Indian Point | 26449 | 07/29/2008 11/13/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | On-line Leak Repairs Made Without Use of Proper Procedures |  | H.3(a) Work Planning | TE?: N | 05000247 Indian Point 2 |  | 71111.18 | The inspectors identified a non-cited violation of Technical Specification 5.4.1, "Procedures," when Entergy did not implement on-line leak repair procedures to repair a steam leak on valve MS-2A. Specifically, Entergy performed multiple leak sealant inje
Region: I | Indian Point | 26448 | 07/26/2008 11/13/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | City Water Tank Below Required Level due to Inadequate Design Change Implementation |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 5.4.1, "Procedures," because Entergy did not implement portions of an engineering change package for an alarm setpoint change following modification to the city water tank minimum
Region: I | Indian Point | 26424 | 06/30/2008 08/07/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Site Procurement Procedure for EDG Temperature Control Valve Elements |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" because Entergy personnel did not implement the requirements of procedure SAO-270, "Procurement Program," for the procurement of safety r
Region: I | Indian Point | 26425 | 06/30/2008 08/07/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Station Blackout/Appendix-R Diesel Generator Post Modification Test Deficiencies |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000247 Indian Point 2 |  | NONE | The inspectors identified a Green NCV of Technical Specification 5.4.1, "Administrative Controls - Procedures," because Entergy did not implement the requirements of EN-DC-117, "Post Modification Testing and Special Instructions," to control revisions to
Region: I | Indian Point | 26433 | 06/30/2008 08/07/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Operating Procedure for Station Blackout/Appendix-R Diesel Generator |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | NONE | The inspectors identified a Green NCV of Technical Specification 5.4.1, "Administrative Controls - Procedures," because the SBO/App-R DG operating procedure 2-SOP-27.6, "Appendix-R Diesel Generator Operation," was not adequate. Specifically, the procedure
Region: I | Indian Point | 26434 | 06/30/2008 08/07/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Seismic Design Control Associated with a Temporary Modification to Emergency Diesel Generator Service Water Return Piping |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.18 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control" because Entergy did not adequately analyze, document, or translate seismic considerations for temporary service water hoses installed on the 21 and 23 emergenc
Region: I | Indian Point | 26435 | 06/30/2008 08/07/2008 | 2008003-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Plant Start-Up Procedure Regarding MBFP Turbine Runback Arm/Defeat Switch |  | H.4(a) Human Error Prevention | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green, self-revealing non-cited violation (NCV) of Technical Specification 5.4.1, "Administrative Controls - Procedures," was identified, because Entergy did not implement the requirements of plant startup procedure 2-POP-1.3, "Plant Startup from Zero T
Region: I | Indian Point | 26438 | 06/30/2008 08/07/2008 | 2008003-06 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Camera Controls Procedure Resulting in RFI Induced MBFP Runback and Subsequent Manual Reactor Trip |  | H.4(b) Procedural Compliance | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green, self-revealing finding was identified because Entergy did not implement procedural requirements to evaluate flash photography in the vicinity of sensitive control cabinets. Specifically, Entergy did not implement procedure EN-NS-214, "Camera Cont
Region: I | Indian Point | 26439 | 06/30/2008 08/07/2008 | 2008003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Quality Records for Containment Sump Modification |  | H.3(b) Work Activity Coordination | TE?: N | 05000247 Indian Point 2 |  | NONE | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVII, "Quality Assurance Records," because Entergy did not maintain sufficient records to furnish evidence that a safety-related containment sump modification was performed in accor
Region: I | Indian Point | 20189 | 05/15/2008 06/19/2008 | 2008009-02 | NRC | NCV | Initiating Events | Green | Failure to establish and implement adequate corrective actions for procedural inadequacy |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | NONE | Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations Part 50 (10 CFR 50), Appendix B, Criterion XVI, "Corrective Action," because Entergy did not establish and implement adequate corrective actions for a condition ad
Region: I | Indian Point | 20178 | 03/31/2008 05/12/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Failure to Include AMSAC into Online Risk Assessments |  | H.3(a) Work Planning | TE?: N | 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50.65(a)(4), because Entergy did not assess and manage the increase in risk from maintenance activities prior to performing work on the U
Region: I | Indian Point | 26423 | 03/31/2008 05/12/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide an adequate procedure for installing cable termination lugs on the 21 service water pump motor cables. |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | A self-revealing, non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for failure to provide an adequate procedure for installing cable t
Region: I | Indian Point | 20179 | 03/31/2008 05/12/2008 | 2008002-02 | NRC | FIN | Mitigating Systems | Green | Inappropriate Exiting of TS 3.3.4 "Remote Shutdown." |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a Green finding, of very low safety significance, because Entergy inappropriately exited Technical Specification (TS) 3.3.4, "Remote Shutdown." Specifically, on February 25, 2008, Entergy inappropriately determined that the 32 an
Region: I | Indian Point | 20181 | 03/31/2008 05/12/2008 | 2008002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain EDG Jacket Cooling Water Pressure Switch Design Control |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.19 | A self-revealing, Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified because Entergy failed to ensure proper design control when modifying the jacket cooling water pressure switches in the Unit 3 eme
Region: I | Indian Point | 20182 | 03/31/2008 05/12/2008 | 2008002-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedures Results in Loss of Safety Bus 5A |  | H.4(a) Human Error Prevention | TE?: N | 05000286 Indian Point 3 |  | 71111.22 | A self-revealing, Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified, because maintenance technicians improperly performed a surveillance test and caused the loss of 480 volt sa
Region: I | Indian Point | 20183 | 02/08/2008 03/17/2008 | 2008007-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedure Guidance to Diagnose and Align RCP Seal Cooling |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a Green non-cited violation of technical specification 5.4.1.d for failure to provide adequate procedure directions in 3-AOP-SSD-1, "Control Room Inaccessibility Safe Shutdown Control," Rev. 6, for operators to properly determine if a
Region: I | Indian Point | 20184 | 02/08/2008 03/17/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Guidance to Isolate Steam Generator Blowdown Flow |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a Green non-cited violation of technical specification 5.4.1.d for failure to provide procedure directions in 3-AOP-SSD-1, "Control Room Inaccessibility Safe Shutdown Control," Rev. 6, that were adequate to ensure operators could isola
Region: I | Indian Point | 20185 | 02/08/2008 03/17/2008 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Directions to De-energize PORV and Letdown Valve Circuits |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a non-cited violation of technical specification 5.4.1.d for failure to provide adequate procedure directions in 3-AOP-SSD-1, "Control Room Inaccessibility Safe Shutdown Control," Rev. 6, to prevent spurious opening of the power operat
Region: I | Indian Point | 20155 | 12/31/2007 02/08/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE AN ADEQUATE EDG MAINTENANCE PROCEDURE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71111.15 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not provide an adequate procedure that assured emergency diesel generator (EDG) operability wh
Region: I | Indian Point | 26407 | 12/31/2007 02/08/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY DEGRADED FIRE BARRIER IN EDG BUILDING |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of Unit 2 license condition 2.K. because Entergy failed to identify a degraded fire barrier in the emergency diesel generator (EDG) room. Specifically, the inspectors identified a backflow preven
Region: I | Indian Point | 20156 | 12/31/2007 02/08/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY AND CORRECT DEGRADED SERVICE WATER PIPING THAT SUBSEQUENTLY LEAKED |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly identify a degraded area of Unit 3 service water piping during review of radiographs performed in ref
Region: I | Indian Point | 26408 | 12/31/2007 02/08/2008 | 2007005-02 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS TO PREVENT EXCEEDING PM FREQUENCY FOR 25 FCU |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.07A | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy failed to implement effective corrective actions for a condition adverse to quality associated with reduced flow to the containment fan
Region: I | Indian Point | 26409 | 12/31/2007 02/08/2008 | 2007005-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS FOR DEGRADED CONTAINMENT FAN COOLER UNIT SERVICE WATER FLOW |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy failed to implement corrective actions to monitor a condition adverse to quality associated with degradation of service water flow rates to
Region: I | Indian Point | 26411 | 12/31/2007 02/08/2008 | 2007005-05 | NRC | FIN | Initiating Events | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS ASSOCIATED WITH AGING CAPACITOR DEGRADATION IN A POWER SUPPLY FOR THE MAIN FEEDWATER SUCTION PRESSURE TRANSMITTER |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | A self-revealing Green finding was identified because Entergy did not implement corrective actions for an adverse condition associated with aging critical power supplies. The inspectors determined that the failure to implement corrective actions was a per
Region: I | Indian Point | 20162 | 12/18/2007 06/22/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Pressure Locking Methodology Used to Ensure Valve Operability |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not use an adequate methodology to determine if the residual heat removal pump discharge
Region: I | Indian Point | 20164 | 12/18/2007 06/22/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Calculation for TDAFW Pump Discharge Pressure Used for Surveillance Testing |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Entergy had not verified the adequacy of design for the turbine driven auxiliary feedwate
Region: I | Indian Point | 20171 | 12/18/2007 06/22/2007 | 2007006-04 | NRC | NCV | Mitigating Systems | Green | Maintenance Procedure Not Revised after Emergency Diesel Modification |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Entergy did not ensure a change to the design basis was correctly translated into mainten
Region: I | Indian Point | 20172 | 12/18/2007 06/22/2007 | 2007006-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Controls for Station Battery Sizing Calculations |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, "Design Control," in that measures had not been established to verify the proper component operating voltage requirements for battery s
Region: I | Indian Point | 20173 | 12/18/2007 06/22/2007 | 2007006-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Inputs and Testing Requirements for EDG Loading |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure that design inputs in the EDG load analysis were conservative. As a res
Region: I | Indian Point | 20174 | 12/18/2007 06/22/2007 | 2007006-07 | NRC | FIN | Mitigating Systems | Green | Inadequate Bushing Testing for the Station Auxiliary Transformer |  | H.3(a) Work Planning | TE?: N | 05000286 Indian Point 3 |  | NONE | The team identified a finding of very low safety significance involving the failure to perform a transformer bushing power factor (Doble) test within Entergy, vendor, or industry recommended frequencies. Specifically, Entergy's procedures specify the test
Region: I | Indian Point | 20161 | 10/03/2007 11/13/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MONITOR EMERGENCY LIGHTING SYSTEM IN ACCORDANCE WITH 10 CFR 50.65 (a)(1) ACTION PLAN |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000286 Indian Point 3 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy did not monitor the performance or condition of the emergency lighting system ag
Region: I | Indian Point | 26414 | 10/03/2007 11/13/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Degraded 12 Fire Main Booster Pump Cell Fire Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of License Condition 2.K., fire protection program, because Entergy failed to identify a degraded three-hour rated fire door on the east entrance of the 12 fire main booster pump room. The door
Region: I | Indian Point | 26415 | 10/03/2007 11/13/2007 | 2007004-02 | NRC | NCV | Barrier Integrity | Green | UNTIMELY CORRECTIVE ACTIONS TO REPAIR A DEGRADED SERVICE WATER FLOW INSTRUMENT |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions," in that, Entergy did not implement timely corrective actions for a degraded condition associated with the 25 Containment Fan Cooler Unit (FCU) fl
Region: I | Indian Point | 26416 | 10/03/2007 11/13/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | PROCEDURE INADEQUATE TO ENSURE OPERABILITY OF SI PUMPS DURING VENTING |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not ensure that procedures associated with operation of the safety injection (SI) system during venting we
Region: I | Indian Point | 20143 | 06/29/2007 08/03/2007 | 2007003-01 | NRC | FIN | Initiating Events | Green | FAILURE TO IDENTIFY IN THE CORRECTIVE ACTION PROCESS OR ADEQUATELY EVALUATE A DEGRADED CONDITION ASSOCIATED WITH A HIGH VOLTAGE BUSHING ON A MAIN TRANSFORMER |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000286 Indian Point 3 |  | 71153 | The inspectors identified a finding of very low safety significance (Green), in that, Entergy failed to identify in the corrective action program an adverse condition associated with the 'B' phase high voltage bushing on the 31 main transformer (MT) that
Region: I | Indian Point | 20135 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO INCLUDE THE INTAKE STRUCTURE TRASH RACKS WITHIN THE SCOPE OF THE MAINTENANCE RULE MONITORING PROGRAM |  |  | TE?: N | 05000286 Indian Point 3 |  | NONE | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(b), in that, Entergy did not include the Indian Point Unit 3 trash rack structures within the scope of the maintenance rule monitoring program. Additionally, Entergy did not demon
Region: I | Indian Point | 26398 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO INCORPORATE DESIGN BASIS INFORMATION INTO PROCEDURES TO ASSURE ADEQUATE COOLING WATER FLOW TO THE RCP THERMAL BARRIERS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not appropriately incorporate design requirements into an operating procedure used to establish adequate component
Region: I | Indian Point | 20139 | 03/31/2007 05/15/2007 | 2007002-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR RECIRCULATION SUMP INTERFERENCE REMOVAL |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 7111117A | A Green, self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified, in that, Entergy's work package failed to ensure that piping interference was correctly planned for and removed d
Region: I | Indian Point | 26399 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | FAILURE TO ESTABLISH TESTING TO ASSURE ADEQUATE COOLING WATER FLOW TO THE RCP THERMAL BARRIERS |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green, NCV of 10 CFR 50 Appendix B, Criterion XI, "Test Control," in that, Entergy did not establish appropriate testing to assure adequate component cooling water (CCW) flow to the reactor coolant pump thermal barriers. Specif
Region: I | Indian Point | 20140 | 03/31/2007 05/15/2007 | 2007002-03 | NRC | FIN | Emergency Preparedness | Green | INADEQUATE CORRECTIVE ACTIONS FOR FAILURE TO APPROPRIATELY MONITOR SERVICE WATER INTAKE BAY LEVEL |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000286 Indian Point 3 |  | 7111117A | The inspectors identified a Green finding because Entergy failed to take adequate corrective actions for an issue associated with monitoring of service water intake bay level. This deficiency could have prevented identification of entry conditions for an
Region: I | Indian Point | 26403 | 03/31/2007 05/15/2007 | 2007002-03 | NRC | FIN | Emergency Preparedness | Green | INADEQUATE CORRECTIVE ACTIONS FOR FAILURE TO APPROPRIATELY MONITOR SERVICE WATER INTAKE BAY LEVEL |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 7111117A | The inspectors identified a Green finding because Entergy failed to take adequate corrective actions for an issue associated with monitoring of service water intake bay level. This deficiency could have prevented identification of entry conditions for an
Region: I | Indian Point | 20141 | 03/31/2007 05/15/2007 | 2007002-04 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR CONDUCT OF RTD CROSS CALIBRATIONS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 71111.2 | A Green, self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified, in that, Entergy failed to ensure that appropriate procedures existed to prevent conflicting activities which led
Region: I | Indian Point | 20142 | 03/31/2007 05/15/2007 | 2007002-05 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE FOR CONTROL OF TEMPORARY MODIFICATION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000286 Indian Point 3 |  | 7111123 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy failed to generate a procedure of a type appropriate to the circumstances associated with the implement
Region: I | Indian Point | 26405 | 03/31/2007 05/15/2007 | 2007002-05 | NRC | NCV | Barrier Integrity | Green | FAILURE TO MOVE CONTAINMENT HYDROGEN ANALYZERS TO 10 CFR 50.65 (A)(1) STATUS |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000247 Indian Point 2 |  | 71152 | The inspectors identified a Green, NCV of 10 CFR 50.65(a)(2) because Entergy did not demonstrate that the performance or condition of the containment hydrogen monitoring system was being effectively controlled through the performance of appropriate preven
Region: I | Indian Point | 21609 | 02/16/2007 02/05/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL ASSOCIATED WITH VORTEXING AND NET POSITIVE SUCTION HEAD CALCULATIONS |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not ensure adequate suction submergence for the three safety injection (SI) pumps by not
Region: I | Indian Point | 21610 | 02/16/2007 02/05/2008 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DIFFERENTIAL PRESSURE VALUE USED FOR MOV 746 AND MOV 747 TONENSURE VALVE CAPABILITY |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not accurately incorporate design parameters into valve thrust calculations for motor op
Region: I | Indian Point | 26383 | 02/16/2007 02/05/2008 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR ENVIRONMENTAL EFFECTS TO ENSURE THE AVAILABILITY OF THE TURBINE DRIVEN AUXILIARY FEEDWATER PUMP OPERATION |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not establish adequate design control measures to ensure the availability of the
Region: I | Indian Point | 26384 | 02/16/2007 02/05/2008 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY MONITOR GAS TURBINE SYSTEM PERFORMANCE AS REQUIRED BY THE MAINTENANCE RULE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50.65(a)(1), the Maintenance Rule, in that, Entergy failed to monitor the gas turbine (GT) system in a manner that provided reasonable assuranc
Region: I | Indian Point | 26391 | 02/16/2007 02/05/2008 | 2007007-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO CORRECT DEGRADED GAS TURBINE 1 RELIABILITY |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving Entergy procedure, EN-LI-102, "Corrective Action Process," in that, Entergy failed to take corrective actions to address degraded GT-1 reliability. This resulted in a two and one half
Region: I | Indian Point | 26392 | 02/16/2007 02/05/2008 | 2007007-07 | NRC | NCV | Mitigating Systems | Green | INADEQUATE STATION BATTERY CAPACITY TESTING FOR DEGRADATION MONITORING |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Technical Specification 3.8.6.6, in that, Entergy did not perform station battery capacity testing in accordance with IEEE Standard 450-1995 (related
Region: I | Indian Point | 26393 | 02/16/2007 02/05/2008 | 2007007-08 | NRC | NCV | Mitigating Systems | Green | INEFFECTIVE CORRECTIVE ACTION FOR HIGH INTER-TIER BATTERY RESISTANCES |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Entergy did not take effective corrective actions for a condition adverse to quality conce
Region: I | Indian Point | 26394 | 02/16/2007 02/05/2008 | 2007007-09 | NRC | NCV | Mitigating Systems | Green | UNTIMELY CORRECTIVE ACTIONS FOR DECREASE IN BATTERY MARGIN |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Entergy did not promptly identify and correct a condition adverse to quality, with respect
Region: I | Indian Point | 20128 | 12/31/2006 02/01/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS FOR DEGRADED NUCLEAR INSTRUMENTATION SYSTEM PERFORMANCE |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000286 Indian Point 3 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy failed to take timely corrective actions for a condition adverse to quality associated with age-related degradation of the
Region: I | Indian Point | 21604 | 12/31/2006 02/01/2007 | 2006005-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS TO CORRECT A DEGRADED CONDITION WHICH IMPACTED GAS TURBINE #1 RELIABILITY AND AVAILABILITY |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The inspectors identified a Green finding, in that, Entergy's corrective actions were inadequate to resolve a deficiency associated with the gas turbine 1 (GT-1) starting diesel. This deficiency was identified following a failure of GT-1 to start on Febru
Region: I | Indian Point | 21606 | 12/31/2006 02/01/2007 | 2006005-04 | NRC | NCV | Initiating Events | Green | INADEQUATE RISK ASSESSMENT FOR 21 MBFP STEAM INLET VALVE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50.65(a)(4), because Entergy did not adequately assess and manage the risk of on-line maintenance activities while operating with a degr
Region: I | Indian Point | 21607 | 12/31/2006 02/01/2007 | 2006005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO SURVEY AND PROVIDE ACCESS TO AN UNPOSTED HIGH RADIATION AREA |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000247 Indian Point 2 |  | 7112101 | A Green, self-revealing NCV of 10 CFR 20.1501 with respect to 10 CFR 20.1902(b) was identified, in that, Entergy failed to survey radiological condition changes after a plant manipulation that was likely to cause a change in radiological conditions, and t
Region: I | Indian Point | 21608 | 12/31/2006 02/01/2007 | 2006005-06 | Self - Revealed | FIN | Occupational Radiation Safety | Green | UNIT 2 CONTAINMENT SUMP STRAINER MODIFICATION COLLECTIVE EXPOSURE OVERRUNS DUE TO INADEQUATE MOD PREPARATION |  | H.3(a) Work Planning | TE?: N | 05000247 Indian Point 2 |  | 7112102 | A self-revealing finding was identified that involved inadequate modification planning and construction preparations relative to a Unit 2 containment sump strainer modification that resulted in significant unplanned collective exposure (93.7 person-rem co
Region: I | Indian Point | 20133 | 12/05/2006 12/21/2006 | 2006006-01 | NRC | FIN | MISC | Green | FAILURE TO ENTER SAFETY CULTURE ASSESSMENT RESULTS INTO CORRECTIVE ACTION PROGRAM |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000286 Indian Point 3 |  | NONE | The NRC inspectors identified a finding when Entergy failed to initiate condition reports in accordance with EN-LI-102, "Corrective Action Process," for the adverse conditions identified in the 2006 Safety Culture Assessment. Consequently, the adverse con
Region: I | Indian Point | 21594 | 12/05/2006 12/21/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY A DEGRADED CONDITION OF AN AUXILIARY FEED WATER CHECK VALVE IN THE CORRECTIVE ACTION PROGRAM |  |  | TE?: N | 05000247 Indian Point 2 |  | 71152B | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Entergy failed to identify a condition adverse to quality associated with improper internal clearances on BFD-68, an auxiliary fee
Region: I | Indian Point | 21595 | 12/05/2006 12/21/2006 | 2006006-02 | NRC | FIN | MISC | Green | FAILURE TO ENTER SAFETY CULTURE ASSESSMENT RESULTS INTO CORRECTIVE ACTION PROGRAM |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000247 Indian Point 2 |  | 71152B | The NRC inspectors identified a finding when Entergy failed to initiate condition reports in accordance with EN-LI-102, "Corrective Action Process," for the adverse conditions identified in the 2006 Safety Culture Assessment. Consequently, the adverse con
Region: I | Indian Point | 21602 | 12/05/2006 12/21/2006 | 2006006-03 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE EVALUATION OF LEAKING 22 STEAM GENERATOR LOW FLOW BYPASS VALVE FCV-427L |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000247 Indian Point 2 |  | 71152B | A self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified, in that, Entergy failed to adequately evaluate leakage into the 22 steam generator. During the Indian Point Unit 2 reactor trip on August 2
Region: I | Indian Point | 21590 | 09/30/2006 11/13/2006 | 2006004-03 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE OPERATING PROCEDURES FOR LOSS OF BOTH HEATER DRAIN TANK PUMPS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green self-revealing finding was identified because Entergy failed to develop adequate procedures for governing the response to a loss of both heater drain tank pumps and to an approaching rod insertion limit (RIL) alarm condition. Specifically, the pro
Region: I | Indian Point | 21591 | 09/30/2006 11/13/2006 | 2006004-04 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE PROCEDURE FOR CALIBRATING THE STEAM DUMP LOSS OF LOAD CONTROLLER |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green self-revealing finding was identified because Entergy failed to develop an accurate procedure for calibration of the steam dump loss of load controller. This resulted in the steam dumps failing to operate properly during a plant transient, complic
Region: I | Indian Point | 20124 | 06/30/2006 08/11/2006 | 2006003-01 | NRC | NCV | Initiating Events | Green | Failure to Perform an Adequate Risk Assessment when required by 10 CFR 50.65(a)(4) for the Nuclear Power Range Channel N42 Axial Offset Calibration. |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified a non-cited violation of Title 10 of the Code of Federal Regulations (CFR), Part 50.65(a)(4) for failure to perform a risk assessment of emergent maintenance conducted on nuclear power range channel N42 on April 6, 2006. In respo
Region: I | Indian Point | 21574 | 06/30/2006 08/11/2006 | 2006003-01 | NRC | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR PLACING RHR PUMP SUCTION PRESSURE GAUGES IN SERVICE |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.04Q | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy's procedures failed to ensure that the 22 residua
Region: I | Indian Point | 21575 | 06/30/2006 08/11/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY DEGRADED RESIDUAL HEAT REMOVAL PUMP CELL FIRE DOOR |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The inspectors identified a Green NCV of license condition 2.K. because Entergy failed to identify a condition adverse to fire protection related to a degraded fire door between the 21 and 22 RHR pump cells. A similar condition with the same door had been
Region: I | Indian Point | 21571 | 06/30/2006 08/11/2006 | 2006003-03 | Self - Revealed | FIN | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS FOR DEGRADATION OF SERVICE WATER PIPING |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | A Green self-revealing finding was identified because Entergy failed to take adequate corrective actions for a degraded service water pipe in the primary auxiliary building. Degradation of this pipe was identified in 2003, but was not adequately evaluated
Region: I | Indian Point | 21576 | 06/30/2006 08/11/2006 | 2006003-04 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PLANT PROCEDURES FOR IMPLEMENTATION OF COMPENSATORY MEASURES |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because plant procedures were not followed during the installation of compensatory measures to restore operability of the RHR pumps
Region: I | Indian Point | 21580 | 06/30/2006 08/11/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | INADEQUATE POST-WORK TEST ON 21 EMERGENCY DIESEL GENERATOR |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because Entergy's post-maintenance test on the 21 emergency diesel generator (EDG) following a governor replacement in November 2004 was not adequate to ens
Region: I | Indian Point | 21581 | 06/30/2006 08/11/2006 | 2006003-06 | NRC | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR VENTING THE REACTOR VESSEL HEAD WHILE SHUTDOWN |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.2 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because plant procedures for reactor coolant system venting following depressurization were inadequate. This resulted in the format
Region: I | Indian Point | 21582 | 06/30/2006 08/11/2006 | 2006003-07 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ASSESS THE RISK OF MAINTENANCE ACTIVITIES ON VALVE SI-869A |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR Part 50.65(a)(4) because Entergy did not assess the risk associated with maintenance on the discharge containment isolation valve from the 21 containment spray pump, SI-869A. This maintenance resulted in the
Region: I | Indian Point | 21583 | 06/30/2006 08/11/2006 | 2006003-08 | NRC | NCV | Mitigating Systems | Green | INADEQUATE SURVEILLANCE TEST PROCEDURE FOR EMERGENCY DIESEL GENERATORS |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because plant surveillance procedure 2-PT-R84B, "22 EDG 8 Hour Load Run," was not adequate to ensure testing at the appropriate pow
Region: I | Indian Point | 21587 | 06/30/2006 08/11/2006 | 2006003-09 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO IMPLEMENT PROCEDURAL REQUIREMENTS ASSOCIATED WITH CORE SUPPORT BARREL REPLACEMENT |  |  | TE?: N | 05000247 Indian Point 2 |  | 7112101 | A Green self-revealing NCV of Technical Specification 5.4.1 was identified because Entergy failed to follow procedural requirements during the core support barrel installation activity. As a result, dose rates were significantly higher than expected durin
Region: I | Indian Point | 21572 | 06/30/2006 08/11/2006 | 2006003-10 | NRC | NCV | Occupational Radiation Safety | Green | INADEQUATE SURVEY DURING CORE BARREL REPLACEMENT CAUSED UNINTENDED EXPOSURE |  |  | TE?: N | 05000247 Indian Point 2 |  | 7112101 | A Green self-revealing NCV of 10 CFR Part 20.1501, "General," was identified because Entergy failed to take adequate radiation surveys during the installation of the core support barrel. As a result, Entergy did not recognize that actual radiological cond
Region: I | Indian Point | 21573 | 06/30/2006 08/11/2006 | 2006003-11 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE PROCEDURE FOR PLACING STANDBY MAIN LUBE OIL COOLER IN SERVICE |  |  | TE?: N | 05000247 Indian Point 2 |  | 71153 | A Green self-revealing finding was identified because Entergy's procedure for placing the standby main lube oil cooler in service was inadequate. A deficiency in the procedure resulted in a loss of main feedwater, an automatic start of the motor-driven au
Region: I | Indian Point | 21568 | 03/01/2006 05/10/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EFFECTIVELY CONTROL THE PERFORMANCE OF THE ROD POSITION INDICATION SYSTEM |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.12 | The NRC identified a Green NCV of 10 CFR 50.65(a)(2) because Entergy failed to effectively control the performance of the rod position indication system through the use of appropriate preventative maintenance. This resulted in the failure of seven rod bot
Region: I | Indian Point | 21570 | 03/01/2006 05/10/2006 | 2006002-04 | Self - Revealed | NCV | Initiating Events | Green | SCAFFOLDING CONTROL ISSUE RESULTS IN REACTOR TRIP |  |  | TE?: N | 05000247 Indian Point 2 |  | 7111114 | The NRC identified a Green self-revealing NCV of 10 CFR 50.65(a)(4) because Entergy did not adequately assess the risk associated with scaffold construction activities in the cable spreading room. Entergy procedure IP-SMM-WM-100, "Work Management Process,
Region: I | Indian Point | 21569 | 02/22/2006 05/10/2006 | 2006002-03 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS FOR UTILITY TUNNEL DEGRADATION |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.13 | The NRC identified a Green self-revealing NCV of license condition 2.K. because Entergy did not take adequate corrective actions for degraded fire protection piping in the utility tunnel. This issue contributed to failure of a 10 inch high-pressure fire p
Region: I | Indian Point | 21563 | 01/29/2006 05/10/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | DEGRADED RESIDUAL HEAT REMOVAL PUMP FIRE DOOR |  |  | TE?: N | 05000247 Indian Point 2 |  | 71111.05Q | The NRC identified a Green NCV of license condition 2.K. because Entergy failed to identify a degraded three-hour rated fire door between the 21 and 22 residual heat removal pump cells. The door, which provides a barrier to fire and hot gases between the
Region: I | Indian Point | 20118 | 01/18/2006 05/10/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE RISK ASSESSMENT WHEN REQUIRED BY 10 CFR 50.65(a) (4) FOR THE 33 EDG DURING EMERGENT CONDITIONS |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(4), when Entergy failed to re-perform a risk assessment on the 33 emergency diesel generator during a High Wind Warning issued by the National Weather Service on January 18, 2006, wh
Region: I | Indian Point | 20117 | 01/10/2006 05/10/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE RISK ASSESSMENT WHEN REQUIRED BY 10 CFR 50.65(a)(4) FOR APPENDIX R EDG |  |  | TE?: N | 05000286 Indian Point 3 |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(4), when Entergy failed to perform a risk assessment for the appendix 'R' emergency diesel generator when it was removed from service for planned maintenance on January 10, 2006. Ent
Region: I | Indian Point | 125984 | 11/05/2019 |  |  | LIV |  | Green | Network Bypass between EP-Only and business LANs |  |  | TE?: N | 05000247 Indian Point 2 05000286 Indian Point 3 |  | 71130.10P
Region: I | Limerick | 126247 | 12/31/2019 02/12/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency Diesel Generator Lube Oil Pressure Sensing Line Shear Due to Inadequate Corrective Actions |  | H.14 - Conservative Bias | TE?: N | 05000353 Limerick 2 | Equipment Performance | 71153 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, with a corresponding violation of LGS Unit 2 technical specification (TS) 3.8.1.1, was identified when Exelon failed to correct a degraded lube oil system instrumenta
Region: I | Limerick | 125967 | 09/30/2019 11/12/2019 | 2019003-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of Power to Offgas Components Led to Manual Reactor Trip Due to Inadequate Response Procedure |  | P.3 - Resolution | TE?: N | 05000353 Limerick 2 | Procedure Quality | 71153 | A self-revealing Green non-cited violation of LGS unit 2 technical specification 6.8.1.a was identified when a response procedure used to stabilize the plant did not fully address a loss of power which impacted the unit 2 offgas system. This led to degrad
Region: I | Limerick | 125161 | 06/30/2019 08/06/2019 | 2019002-01 | Self - Revealed | FIN | Initiating Events | Green | Waterbox Manway was not Closed Causing Internal Flooding |  | H.12 - Avoid Complacency | TE?: N | 05000353 Limerick 2 | Protection Against External Factors | 71111.06 | A self-revealing Green finding was identified due to internal flooding on May 5, 2019. Specifically, a work order instruction to reinstall a manway on the Unit 2 main condenser waterbox was not performed which caused flooding in the condenser area and con
Region: I | Limerick | 124838 | 06/30/2019 08/06/2019 | 2019002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Tagging Error Leads to Inoperability of the ‘B’ CREFAS system |  | H.12 - Avoid Complacency | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 | Human Performance | 71152 | A self-revealed Green NCV of Limerick Generating Station Technical Specifications 6.8, "Procedures and Programs," was identified on February 21, 2018, when Exelon failed to properly implement procedure OP-MA-109-101, “Clearance and Tagging,” step 7.1.4, t
Region: I | Limerick | 124428 | 02/15/2019 03/14/2019 | 2019011-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Functionality Assessment of the Diesel Driven Fire Pump |  | P.2 - Evaluation | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 | Protection Against External Factors | 71111.05T | The inspectors identified a Green finding associated with Exelon procedure, OP-AA-108-115, “Operability Determinations,” because operators did not perform adequate functionality assessments of the Diesel Driven Fire Pump (DDFP) when excess cooling water s
Region: I | Limerick | 25904 | 12/31/2018 02/13/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain the Design Control of the ‘D23’ Emergency Diesel Generator |  | H.11 - Challenge the Unknown | TE?: N | 05000353 Limerick 2 |  | 71152 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion III was identified when Exelon replaced the ‘D23’ emergency diesel generator (EDG) lube oil heater temperature switch with a new style switch on December 6, 2018. The new style switch subseque
Region: I | Limerick | 25876 | 11/02/2018 12/13/2018 | 2018011-01 | Self - Revealed | NCV | Mitigating Systems | Green | High Pressure Coolant Injection Pump Mechanical Seal Leak |  | H.7 - Documentation | TE?: N | 05000352 Limerick 1 |  | 71152B | A self-revealing Green NCV of Limerick TS LCO 3.0.4 was identified because Exelon staff failed to adequately implement work instructions for HPCI system maintenance. This resulted in a violation of TS LCO 3.0.4 due to HCPI being inoperable during a mode c
Region: I | Limerick | 24671 | 09/30/2018 11/13/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk Associated with Fuel Oil Storage Tank Maintenance |  | H.8 - Procedure Adherence | TE?: N | 05000352 Limerick 1 |  | 71111.13 | An NRC identified Green NCV of 10 CFR 50.65(a)(4) was identified when Exelon failed to assess and manage risk associated with fuel oil storage tank maintenance by not properly evaluating and establishing compensatory actions for maintaining availability o
Region: I | Limerick | 24672 | 09/30/2018 11/13/2018 | 2018003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correct Adverse Environmental Conditions Impacting Low Pressure Coolant Injection Outboard Isolation Valve |  | H.13 - Consistent Process | TE?: N | 05000352 Limerick 1 |  | 71153 | A self-revealed Green NCV of 10 CFR 50, Appendix B, Criterion XVI, was identified when Exelon failed to correct adverse environmental conditions affecting the Unit 1 low pressure coolant injection (LPCI) outboard isolation valve actuator that resulted in
Region: I | Limerick | 24033 | 06/30/2018 08/09/2018 | 2018002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Conduct Adequate Radiation Surveys and Evaluate Potential Radiological Hazards |  | H.11 - Challenge the Unknown | TE?: N | 05000352 Limerick 1 |  | 71124.01 | A self-revealing Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 20.1501, “Surveys and Monitoring: General,” was identified when Exelon failed to perform adequate loose surface contamination s
Region: I | Limerick | 24049 | 03/31/2018 05/11/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Emergency Diesel Generator Lube Oil Pipe Nipple Fitting |  | P.1 - Identification | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealed Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” and LGS Unit 2 technical specification (TS) 3.8.1.1 was identified when Exelon failed to correct a degraded lube oil pipe nipple fitting on the ‘
Region: I | Limerick | 24050 | 03/31/2018 05/11/2018 | 2018001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency Diesel Generator Combustion Air Overheating |  | P.3 - Resolution | TE?: N | 05000352 Limerick 1 |  | 71153 | A self-revealed Green NCV of LGS Unit 1 TS 6.8.1 and TS 3.8.1.1 was identified when Exelon failed to properly maintain an operating procedure to maintain a fail-safe design feature for the EDGs which led to the ‘D12’ EDG combustion air overheating and cau
Region: I | Limerick | 23148 | 12/31/2017 02/01/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unplanned HPCI Inoperability Due to Isolating All Suction Sources During Post-Maintenance Testing |  | H.5 - Work Management | TE?: N | 05000353 Limerick 2 |  | 71153 | The inspectors identified a self-revealing Green NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for Exelon’s failure to adequately establish post-maintenance testing instructions for a re
Region: I | Limerick | 22668 | 11/20/2017 12/18/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Document Technical Basis for Service Temperature Changes for Limitorque Motor Operated Valve Limit Switches |  | H.6 - Design Margins | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.21N | The inspection team identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," because Exelon’s design control measures did not provide for verifying or checking the adeq
Region: I | Limerick | 21672 | 09/30/2017 11/02/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Operational Condition Mode Change from Startup to Run was Made with RCIC Inoperable |  | H.7 - Documentation | TE?: N | 05000353 Limerick 2 |  | 71111.04S | The inspectors identified a Green NCV of Unit 2 technical specification (TS) 3.0.4, when Exelon changed the operating condition of Unit 2 from mode 2 (startup) to mode 1 (run) with reactor core isolation cooling (RCIC) inoperable for surveillance testing.
Region: I | Limerick | 36348 | 06/30/2017 07/31/2017 | 2017002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Design Control of the Drywell Unit Cooler Condensate Flow Rate Monitoring System |  | H.14 Conservative Bias | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing Green NCV of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," occurred when Exelon failed to verify or check the adequacy of design of a new Unit 2 drywell unit cooler condensate flow rate monitor
Region: I | Limerick | 36346 | 03/31/2017 05/11/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Staging of Equipment and Routing of Temporary Power Cables |  | H.9 Training | TE?: N | 05000353 Limerick 2 |  | 71111.04Q | The inspectors identified a Green NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for Exelon's failure to establish instructions appropriate to the circumstances to properly stage equipmen
Region: I | Limerick | 36347 | 03/31/2017 05/11/2017 | 2017001-02 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement Human Performance Tools Results in Draining of Emergency Diesel Generator Jacket Water System |  | H.12 Avoid Complacency | TE?: N | 05000352 Limerick 1 |  | 71111.04S | The inspectors identified a Green self-revealing finding for the failure of Exelon personnel to follow procedures related to human performance tools which resulted in the inadvertent opening of a valve on the 'D13' emergency diesel generator (EDG). Specif
Region: I | Limerick | 36341 | 12/31/2016 02/08/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Effective Preventive Maintenance Under 50.65 (a)(2) for the Instrument Airsystem |  | H.8 Procedure Adherence | TE?: N | 05000352 Limerick 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 Code of Federal Regulations (CFR) 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Exelon did not demonstrate that the performance of the Unit 1 instrument a
Region: I | Limerick | 36342 | 12/31/2016 02/08/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Control Structure Chiller Unit Trip Caused by Failure to Implement Procedures |  | H.12 Avoid Complacency | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152 | A self-revealing Green NCV of LGS Units 1 and 2 technical specification 6.8.1 was identified when Exelon did not properly implement a surveillance procedure. Specifically, operators secured cooling water to the operating 'A' control structure chilled wate
Region: I | Limerick | 36340 | 09/30/2016 11/03/2016 | 2016003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Control of Plant Processing Computer Modification |  | H.11 Challenge the Unknown | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing finding of very low safety significance (Green) was identified when Exelon did not implement their engineering design control procedures during the plant processing computer (PPC) modification. Specifically, procedure CC-AA-103-1003, "Own
Region: I | Limerick | 36323 | 03/31/2016 05/12/2016 | 2016001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Reactor Enclosure Recirculation System Design Change Was Not Evaluated |  |  | TE?: N | 05000352 Limerick 1 |  | 71111.12 | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50 (10 CFR 50), Appendix B, Criterion III, "Design Control," was identified because Exelon did not properly maintain the design of the LGS Unit 1 reactor enclosure rec
Region: I | Limerick | 36328 | 03/31/2016 05/12/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Seismic Qualification of Safety Related Battery Not Maintained |  | H.12 Avoid Complacency | TE?: N | 05000352 Limerick 1 |  | 71111.18 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," and technical specification 3.8.2, "D.C. Sources," because Exelon failed to ensure the design control measures for field changes impacting the seismic suppo
Region: I | Limerick | 36329 | 03/31/2016 05/12/2016 | 2016001-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Staging and Housekeeping Walkdowns During Pre-Outage Preparations |  | H.9 Training | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.2 | The inspectors identified a Green NCV of technical specification 6.8.1 for Exelon's failure to properly control, store, and stage material in accordance with station procedures within Class I buildings during refueling outage preparation. Specifically, Ex
Region: I | Limerick | 36335 | 03/31/2016 05/12/2016 | 2016001-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entry Into A High Radiation Area Without Radiological Briefing and Complying With The RWP |  | H.8 Procedure Adherence | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71124.01 | A self-revealing Green NCV of LGS Unit 1 technical specification 6.12.1 was identified involving improper entry of two workers into the Unit 1 reactor drywell on March 22, 2016. Specifically, the workers entered the drywell, an area controlled as a Lock
Region: I | Limerick | 36336 | 03/31/2016 05/12/2016 | 2016001-05 | Self - Revealed | NCV | Initiating Events | Green | Main Turbine Digital Electrohydraulic Control System Modification Failed to Revise the Plant Startup Procedure |  | H.3 Change Management | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing Green NCV of LGS Unit 2 technical specification 6.8.1 was identified because Exelon failed to maintain a plant startup procedure. Specifically, the implementing procedure for normal plant startup from hot shutdown or cold shutdown to rate
Region: I | Limerick | 36337 | 03/31/2016 05/12/2016 | 2016001-06 | NRC | NCV | Public Radiation Safety | Green | Failure to Implement Procedures for Control of Potentially Contaminated Clean Systems |  | P.3 Resolution | TE?: N | 05000353 Limerick 2 |  | 71153 | The inspectors identified a Green NCV of technical specification 6.8.1 because Exelon failed to implement procedure CY-AA-170-210, "Potentially Contaminated System Control Program," for the evaluation and control of potentially cross-contaminated systems.
Region: I | Limerick | 36322 | 12/31/2015 02/03/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Seismic Qualification of Safety Related Block Wall Not Maintained |  | H.8 Procedure Adherence | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, because Exelon did not properly store circuit breakers and ground trucks in accordance with established design. Specifically, Exelon personnel stored circuit br
Region: I | Limerick | 36321 | 09/30/2015 11/03/2015 | 2015003-01 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Procedure for RWCU Backwashing Operations |  | H.12 Avoid Complacency | TE?: N | 05000353 Limerick 2 |  | 71124.01 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," occurred because Exelon failed to establish, implement, and maintain an adequate procedure for the control of radioactivity and limiting personnel exposure duri
Region: I | Limerick | 36315 | 09/30/2015 11/03/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance of the HPCI System Motor Control Center |  |  | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," was identified because Exelon failed to adequately implement a preventive maintenance (PM) task for the 2DB-1-14 High Pressure Coolant Injection (HPCI) Direct C
Region: I | Limerick | 36316 | 07/30/2015 09/08/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of EDG Voltage to Start Safety Related Motors |  | P.1 Identification | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of the 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Exelon did not verify and assure in design basis calculations, that adequate vo
Region: I | Limerick | 36317 | 07/30/2015 09/08/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequate Voltage Available for DC Equipment |  | H.7 Documentation | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that Exelon's design control measures did not verify the adequacy of the design regardin
Region: I | Limerick | 35386 | 06/30/2015 08/04/2015 | 2015002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Design Requirements Not Met for Installed Instrument Gas Tubing Fitting |  |  | TE?: N | 05000352 Limerick 1 |  | 71153 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified because Exelon failed to control the proper design configuration of installed plant equipment in Unit 1. Specifically, a fitting used in the safety-relate
Region: I | Limerick | 36303 | 03/31/2015 05/14/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Fire Safe Shutdown Diesel Generator Maintenance Program Did Not Account for Cold Temperatures due to Inadequate Specification for Fuel Oil Cloud Point |  | H.1 Resources | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.15 | The inspectors identified an NCV of LGS Units 1 and 2 operating license condition 2.C(3), Fire Protection, because Exelon did not implement and maintain in effect all provisions of the NRC approved fire protection program. Specifically, Exelon did not imp
Region: I | Limerick | 36304 | 03/31/2015 05/14/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Startup Procedure Considered High Pressure Coolant Injection Operable With High Reactor Water Level Trip Actuated |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.2 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR), Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Exelon prescribed a procedure affecting quality with instructions which were not appropria
Region: I | Limerick | 36298 | 12/31/2014 02/02/2015 | 2014005-01 | NRC | NCV | Initiating Events | Green | Unplanned Manual Power Reduction to 90% on Unit 1. |  | H.2 Field Presence | TE?: N | 05000353 Limerick 2 |  | NONE | A self-revealing, Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1.b, "Administrative Controls," was identified for LGS' failure to properly implement station procedure MA-AA-716-100, "Maintenance Alterations Process," during trouble-
Region: I | Limerick | 36297 | 09/30/2014 10/30/2014 | 2014004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71114.05 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (CFR) 50.54(q)(2), 10 CFR 50.47(b)(10), and 10 CFR Part 50, Appendix E, Section IV.4, for not maintaining the effectiveness of the LGS, Units 1 and 2, emergency plan as a
Region: I | Limerick | 36296 | 06/30/2014 08/11/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions Following Repeat Test Failures of a High Pressure Coolant Injection System Level Instrument |  | P.2 Evaluation | TE?: N | 05000353 Limerick 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to adequately evaluate and correct repeat calibration test failures in April 2012 and in February 2014 on the Unit 2 high pressure coolant
Region: I | Limerick | 36290 | 03/24/2014 05/07/2014 | 2014002-01 | NRC | FIN | Public Radiation Safety | Green | Failure to Evaluate ODCM Change in Accordance with Technical Specification 6.14 |  | H.6 Design Margins | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | NONE | The NRC identified an NCV of T/S 6.14, Offsite Dose Calculation Manual (ODCM), for failure to evaluate and provide sufficient information to support a change to the ODCM. Specifically, LGS revised the ODCM to allow the RHRSW monitors to be non-functional
Region: I | Limerick | 36031 | 12/31/2013 02/06/2014 | 2013005-01 | NRC | FIN | Barrier Integrity | Green | Failure to Properly Plan Work for Failed Airlock Door Magnetic Switch |  | H.3 Change Management | TE?: N | 05000353 Limerick 2 |  | 71153 | The inspectors identified a self-revealing finding (FIN) of very low safety significance (Green) was identified for Exelon's failure to appropriately prioritize work activities associated with a degraded Unit 2 magnetic switch for a secondary containment
Region: I | Limerick | 36019 | 09/30/2013 11/14/2013 | 2013004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate and Untimely Corrective Actions Associated With the Unit 1 Instrument Air System |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000352 Limerick 1 |  | 71111.04S | A self-revealing finding of very low safety significance was identified for Exelon's failure to take adequate and timely corrective actions to address the inadvertent depressurization of the Unit 1 Instrument Air (IA) headers. This led to a repeat depress
Region: I | Limerick | 36024 | 09/30/2013 11/14/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Technical Specification Surveillance Requirements on the Unit 2 Primary Containment Instrument Gas System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000353 Limerick 2 |  | 71111.13 | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," for Exelon's failure to implement surveillance test procedures specified for the Primary Containment Instrument Gas (PCIG) system as required by Regu
Region: I | Limerick | 36025 | 09/30/2013 11/14/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality associated with Defective Material Being Reinstalled into a Safety - Related System |  | P.3 Resolution | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with Exelon staff's failure to correct a condition adverse to quality (CAQ) associated with defe
Region: I | Limerick | 36013 | 06/30/2013 08/06/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with Emergency Diesel Generator D24 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000353 Limerick 2 |  | 71111.15 | The inspectors identified a Green non-cited violation (NCV) of 10 Code of Federal Regulation (CFR) 50, Appendix B, Criterion XVI, "Corrective Action", because Exelon personnel did not identify and correct a condition adverse to quality associated with eme
Region: I | Limerick | 36014 | 06/30/2013 08/06/2013 | 2013003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Adhere to Radiation Protection Procedures for Evacaution of the Unit 2 Upper Drywell in Preparation for Irradiated Component Moves |  | H.3(b) Work Activity Coordination | TE?: N | 05000353 Limerick 2 |  | 71124.01 | The inspectors identified a self-revealing finding of very low safety significance associated with failure to comply with Technical Specification (TS) 6.8 procedures. Specifically, the inspectors identified that the licensee failed to implement radiation
Region: I | Limerick | 36018 | 06/30/2013 08/06/2013 | 2013003-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Partial Procedure Change Process |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing Green finding of Technical Specification 6.8.1, "Administrative Controls-Procedures," was identified because Exelon personnel did not implement procedure use and adherence requirements when operators changed the scope of work for surveill
Region: I | Limerick | 36009 | 05/24/2013 07/01/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Brigade Transportation |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.05T | The NRC identified a Green, Non-Cited Violation (NCV) of License Condition 2.C.(3) of the Limerick Generating Station operating license, in that Exelon did not provide adequate procedural guidance for transporting the fire brigade and equipment to the
Region: I | Limerick | 36010 | 05/24/2013 07/01/2013 | 2013007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Establish Preventive Maintenance for Safe Shutdown Transfer/Isolation Switches |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.05T | The NRC identified a Green finding for the failure to establish a preventive maintenance strategy for fire safe shutdown transfer/isolation switches in accordance with the Exelon procedure ER-AA-200, Preventive Maintenance Program. As a result, Exelon
Region: I | Limerick | 36008 | 03/31/2013 05/13/2013 | 2013002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Assess Battery Charger Operability in a Timely Manner |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a Finding (FIN) of very low safety significance (Green) for the failure to adequately assess the operability of multiple safeguard battery chargers in a timely manner after an issue report (IR) was generated for battery charger t
Region: I | Limerick | 35989 | 12/31/2012 02/05/2013 | 2012005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Administer an NRC Annual Operating Test Simulator Scenario Re-examination That Met Procedural Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.11B | The inspectors identified a Green finding of of Exelon procedure TQ-AA-150, "Operator Training Programs," and TQ-AA-155, "Conduct of Simulator Training and Evaluation," based on a determination that the minimum number of scenarios required for simulator r
Region: I | Limerick | 35981 | 12/31/2012 02/05/2013 | 2012005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Revise EDG Tank Cleaning Work Instructions |  | H.4(b) Procedural Compliance | TE?: N | 05000353 Limerick 2 |  | 71111.19 | A self-revealing Green NCV of Technical Specification 6.8.1, "Administrative Controls-Procedures," was identified because Exelon did not implement procedure use and adherence requirements when workers changed the scope of work on EDG fuel oil day tanks an
Region: I | Limerick | 35990 | 12/18/2012 01/15/2013 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Voltage to Safety-Related Equipment with Offsite Power Available |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a non-cited violation of Title 10 of the Code of Federat Regutations (10 CFR) Part 50, Appendix B, Criterion lll, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy
Region: I | Limerick | 35999 | 12/18/2012 01/15/2013 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | 480V Motor Control Circuit Breaker Overcurrent Protection |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Limerick Generating Station License Condition 2.C.(3), "Fire Protection," which states Exelon Generation Company shall implement and maintain in ef
Region: I | Limerick | 35979 | 11/09/2012 12/18/2012 | 2012010-01 | NRC | FIN | Initiating Events | Green | Failure to Take Timely Corrective Actions to Address the 144D Load Center ODM contingency actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 |  | 71152B | Green. The inspectors identified a finding of very low safety significance (Green) for Exelon's failure to complete an evaluation of the off-normal bus alignment prior to the summer period. Consequently, on July 18, 2012, LGS experienced a fault of the 12
Region: I | Limerick | 35966 | 09/30/2012 11/01/2012 | 2012004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish and Perform Adequate Preventive Maintenance on 480VAC Load Center Power Transformers |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71153 | A self-revealing NCV of Limerick Technical Specification (TS) 6.8, "Procedures and Programs," was identified for failure to establish and perform adequate preventive maintenance (PM) activities to routinely inspect the 480 volt-alternating current (VAC)
Region: I | Limerick | 35973 | 09/30/2012 11/01/2012 | 2012004-02 | NRC | VIO | Mitigating Systems | Green | Failure to Immediately Reduce Reactor Power per the Alarm Response Card Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a cited violation of very low safety significance (Green) of TS 6.8, "Procedures and Programs," because Limerick operators did not adequately follow an alarm response procedure when responding to a MCR alarm on July 11, 2012.
Region: I | Limerick | 35974 | 09/30/2012 11/01/2012 | 2012004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Testing Following Circuit Breaker Replacement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000353 Limerick 2 |  | 71153 | A self-revealing NCV of TS 6.8, "Procedures and Programs," was identified because Exelon did not maintain adequate maintenance procedures associated with work performed on the Unit 2 'B' residual heat removal (RHR) pump motor circuit breaker. Specifica
Region: I | Limerick | 35975 | 09/30/2012 11/01/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Failure to enter Technical Specifications in a Timely Manner |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a NCV of very low safety significance (Green) of TS 3.3.1.1, "Reactor Protection System (RPS) Instrumentation," because Limerick operators did not enter the required TS action in a timely manner in response to an RPS instrument
Region: I | Limerick | 35964 | 06/30/2012 08/02/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Timely Corrective Actions to Replace Age Degraded Relays |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71153 | The inspectors identified a Green NCV of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon failed to conduct timely corrective actions to preclude repetition of a condition adverse to quality invo
Region: I | Limerick | 35960 | 12/31/2011 01/20/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for a Previous NRC Finding for Programmatic Deficiencies in the Preventive Maintenance Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to implement adequate corrective actions for a previous NRC identified finding. The previous finding involved a failure to perform adequat
Region: I | Limerick | 35956 | 11/04/2011 12/19/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Alternate AC Source Capability to Recover from Station Blackout |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.17T | The team identified a non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current (AC) Power," because Exelon did not demonstrate that the alternate AC (AAC) source could provide acceptable capability to withstand a station blackout (SBO) within
Region: I | Limerick | 35957 | 09/30/2011 11/04/2011 | 2011004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Adequate Restoration Instructions for Turbine Control Valve Online Maintenance |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000353 Limerick 2 |  | 71153 | A Green, self-revealing finding was identified because Exelon did not provide adequate instructions for restoration of the Limerick Unit 2 number three turbine control valve (CV #3) following maintenance. During a fill and vent activity of the electro-hyd
Region: I | Limerick | 35959 | 09/30/2011 11/04/2011 | 2011004-03 | NRC | NCV | Initiating Events | Green | Test Equipment Interference Resulting in Reactor Scram |  |  | TE?: N | 05000352 Limerick 1 |  | NONE | A Green, self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," occurred when Exelon did not adequately assess the potential impacts of test equipment on turbine trip circuitry. This resulted in an automatic reactor scram of Unit
Region: I | Limerick | 35954 | 08/19/2011 09/12/2011 | 2011503-01 | NRC | NCVIV | Emergency Preparedness | Green | (Traditional Enforcement) Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval | EA Case: 2011128 |  | TE?: Y SL-IV-NCVIV | 05000352 Limerick 1 05000353 Limerick 2 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: I | Limerick | 35955 | 08/19/2011 09/12/2011 | 2011503-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | NONE | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: I | Limerick | 35952 | 06/30/2011 08/04/2011 | 2011003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Position Recirculation Isolation Valves in Accordance with Clearance |  | H.4(a) Human Error Prevention | TE?: N | 05000353 Limerick 2 |  | 71111.2 | A Green, self-revealing NCV of Technical Specification (TS) 6.8.1, "Procedures and Programs," was identified for failure to position the Unit 2 recirculation loop isolation valves in accordance with the clearance instruction. As a result, the decay heat r
Region: I | Limerick | 35953 | 06/30/2011 08/04/2011 | 2011003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify Adverse Trend regarding Out of Calibration Instrumentatio |  | P.1(b) Trend Performance CAP | TE?: N | 05000353 Limerick 2 |  | 71152 | A Green self-revealing finding was identified for Exelon's failure to identify and correct an adverse trend regarding out of calibration temperature switches in the Unit 1 and Unit 2 stator cooling water (SCW) systems. Specifically, between 1990 and 2011
Region: I | Limerick | 35947 | 03/31/2011 04/27/2011 | 2011002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Address Repeat TS Response Time Test Failures (Section 4OA2.2) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action Program," because Exelon did not adequately evaluate and correct a condition adverse to quality regarding repeat failures of a Technical Specification (
Region: I | Limerick | 35945 | 11/19/2010 12/23/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Three of Four RHR Unit Coolers Unreliable due to Various Planned and Unplanned Conditions (Silting). |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152B | The inspectors identified a violation of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Action," in that Exelon failed to correct a condition adverse to quality for a safetyrelated support system that was essential to successful mitigating system opera
Region: I | Limerick | 35938 | 09/30/2010 11/09/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Compensatory Action for Inoperable Fire Door |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.05Q | The inspectors identified a Green NCV of Limerick Generating Station operating License Condition 2.C.3, in that Exelon failed to take compensatory actions for an inoperable fire door. Specifically, on two occasions a required fire door was found in a cond
Region: I | Limerick | 35939 | 09/30/2010 11/09/2010 | 2010004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify Incorrectly Adjusted Control Power Relay Resulting in Unit 1 Manual Scram |  |  | TE?: N | 05000352 Limerick 1 |  | 71111.12 | A self-revealing Green finding was identified for the failure to identify that the latching mechanism on a bus 114A/124A control power auxiliary relay (27X) was incorrectly adjusted during prior post-maintenance testing activities. Specifically, proper po
Region: I | Limerick | 35940 | 09/30/2010 11/09/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate PM on EDGs |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152 | The inspectors identified a Green NCV of Limerick Unit 2 Technical Specification (TS) 6.8.1, "Procedures and Programs," in that Exelon did not provide an adequate procedure for preventive maintenance (PM) of the Limerick Emergency Diesel Generator (EDG) l
Region: I | Limerick | 35934 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Cooling Water Flow to Residual Heat Removal Room Unit Cooler |  | H.4(a) Human Error Prevention | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.07A | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for improperly positioning the Emergency Service Water (ESW) throttle valve to the Unit 1 'A' Residual Heat Removal (RHR) room unit cooler during an ESW flo
Region: I | Limerick | 35935 | 12/31/2009 01/28/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Degraded Instrument Line in Emergency Service Water System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.12 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for Exelon's failure to identify a condition adverse to quality associated with the 'A' ESW pump discharge pressure instrument line.
Region: I | Limerick | 35926 | 10/30/2009 12/11/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Battery Capacity to Recover from Station Blackout |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current (AC) Power," because Exelon's coping analysis did not determine whether the battery capability and capacity was
Region: I | Limerick | 35924 | 09/30/2009 11/03/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Test 480 Volt Motor Control Unit Circuit Breakers |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to establish a test program for all safety-related 480 volt motor control unit (MCU) circuit breakers to assure that necessary testing was perfo
Region: I | Limerick | 35925 | 09/30/2009 11/03/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct 480V Breaker Thermography |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failing to correct a condition adverse to quality associated with the performance of thermography on safety-related breakers. Specifically, althou
Region: I | Limerick | 35916 | 06/17/2009 08/10/2009 | 2009003-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Assess Erratic Time Delay Relay Operation on Unit 2 HPCI Operability |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000353 Limerick 2 |  | 71111.15 | The inspectors identified a Green finding associated with the failure to adequately assess erratic time delay relay operation on Unit 2 High Pressure Coolant Injection (HPCI) system operability in a timely manner commensurate with the potential safety sig
Region: I | Limerick | 35914 | 03/31/2009 05/07/2009 | 2009002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Design Control for Reactor Building Temperatures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to translate minimum room temperatures assumed in an isolation actuation instrumentation setpoint calculation into Unit 1 and 2 procedures suc
Region: I | Limerick | 35907 | 12/31/2008 01/30/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Test following Containment Isolation System Relay Replacement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000353 Limerick 2 |  | 71111.19 | The inspectors identified a NCV of Technical Specification 6.8.1, "Administrative Controls-Procedures", because Exelon did not maintain adequate maintenance procedures associated with work performed on the Unit 2 Nuclear Steam Supply Shutoff System (NSSSS
Region: I | Limerick | 35906 | 09/30/2008 11/14/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Secondary Containment Control Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000353 Limerick 2 |  | 71111.06 | The inspectors identified a NCV of Technical Specification (TS) 6.8.1, "Administrative Controls - Procedures," because Exelon did not maintain adequate procedures in that Emergency Operating Procedure T-103, "Secondary Containment Control," contained an i
Region: I | Limerick | 35904 | 09/12/2008 10/22/2008 | 2008009-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Bleeder Trip Valve Testing |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000352 Limerick 1 |  | 71152B | The inspectors identified a finding of very low safety significance for Exelon's failure to complete the testing described in the Updated Final Safety Analysis Report (UFSAR) for one of the third stage feedwater heater bleeder trip valves. Exelon entered
Region: I | Limerick | 35909 | 08/19/2008 10/03/2008 | 2008006-01 | NRC | NCV | MISC | Green | Failure to translate preventative maintenance practices described in design calculations used to upgrade the LGS 125 ton Reactor Building Bridge Crane into the approved crane inspection procedures. |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | NONE | A Green non-cited violation (NCV) of 10CFR Part 50, Appendix B, Criterion III, "Design Control" was identified. The NCV was related to the licensee's failure to translate preventative maintenance practices described in design calculations used to upgrade
Region: I | Limerick | 35903 | 06/30/2008 08/13/2008 | 2008003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Adverse Condition Associated with Motor Operated Valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulation, Part 20 (10CFR50), Appendix B, Criterion XVI, Corrective Action, for not correcting a condition adverse to quality associated with safety-related motor operated valve motor co
Region: I | Limerick | 35897 | 03/22/2008 04/28/2008 | 2008002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Correct Main Turbine Bypass Valve Adverse Condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000352 Limerick 1 |  | 71111.15 | The inspectors identified a Green finding for failure to identify corrective actions for an adverse condition associated with unsatisfactory performance of a Unit 1 main turbine bypass valve following an automatic scram event on March 22, 2008. As a resul
Region: I | Limerick | 35902 | 03/09/2008 04/28/2008 | 2008002-03 | NRC | NCV | Initiating Events | Green | Failure to Promptly Implement Actions for a Low SST Level |  | H.4(b) Procedural Compliance | TE?: N | 05000352 Limerick 1 |  | 71111.2 | Inspectors identified a Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1 for failure to promptly implement actions to recover the Unit 1 skimmer surge tank (SST) level during the 1R12 Unit 1 refueling outage. Prompt action by the oper
Region: I | Limerick | 35896 | 02/01/2008 04/28/2008 | 2008002-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance Procedure for the 2A Main Transformer |  |  | TE?: N | 05000353 Limerick 2 |  | 71111.12 | A self-revealing finding was identified for an inadequate maintenance procedure regarding electrical connections associated with the Unit 2A Main Transformer bushings. The procedure was not clear as to the appropriate method to prepare the surface for an
Region: I | Limerick | 35895 | 11/09/2007 12/17/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Required Voltage for Load Tap Changer Motor |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee did not ensure the automatic load tap changer (LTC) controls and motor for the 101 and 201 safeguards, 10 station auxilia
Region: I | Limerick | 35894 | 08/09/2007 08/27/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire safe Shutdown Procedure for Securing HPCI |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.05T | The team identified a finding of very low safety significance (Green) involving a non-cited violation of the Limerick Generating Station operating license, in that the procedure for shutting down the plant in response to a fire in the cable spreading ro
Region: I | Limerick | 35892 | 04/24/2007 07/25/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate HPCI/RCIC Flow Controller Tuning Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000353 Limerick 2 |  | 71111.15 | The inspectors identified a Green, self-revealing, non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion V, "Instructions Procedures and Drawings," due to an inadequate maintenance procedure for flow controller settings for the High Pressure Coolant
Region: I | Limerick | 35893 | 03/10/2007 05/15/2007 | 2007002-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Clearance Results in Opening of the Scram Discharge Vent Drain Valves |  | H.3(b) Work Activity Coordination | TE?: N | 05000353 Limerick 2 |  | 71111.2 | The inspectors identified a green, self-revealing, non-cited violation of Technical Specification 6.8, "Procedures and Programs," due to an inadequate safety tagging clearance which resulted in inadvertently opening the scram discharge volume vent and dra
Region: I | Limerick | 35891 | 12/31/2006 02/01/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Failure to perform timely corrective actions for a revision to an Offsite Electrical Power Voltage Calculation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71153 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion XVI, "Corrective Actions," because a condition adverse to quality related to a non-conservative offsite electrical voltage calculation was identified by Exelon i
Region: I | Limerick | 35886 | 06/27/2006 07/24/2006 | 2006003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Annual Operating Test Administered at Limerick |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71111.11B | The inspectors identified a Green non-cited violation (NCV) of 10CFR55.59 (a)(2)(ii) for an inadequate annual operating test that was administered at Limerick. Exelon procedures and commitments made by the licensee in 1991 require questions on job perform
Region: I | Limerick | 35887 | 06/23/2006 07/28/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon's actions to correct a Residual Heat Removal (RHR) system procedure deficiency, i |  |  | TE?: N | 05000352 Limerick 1 05000353 Limerick 2 |  | 71152B | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to implement effective corrective actions to correct a residual heat removal (RHR) system procedure deficiency. Specifically, a procedu
Region: I | Limerick | 35885 | 03/12/2006 05/02/2006 | 2006002-01 | Self - Revealed | NCV | Initiating Events | Green | Unit 2 Core Alterations Without Audible Source Range Monitor Alarms |  |  | TE?: N | 05000353 Limerick 2 |  | 7111114 | A self-revealing NCV was identified for the licensee's failure to comply with Technical Specification (TS) 3.9.2, "Instrumentation." Plant operations staff inappropriately started core alterations after the loss of all Unit 2 source range monitor audible
Region: I | Limerick | 124666 | 05/13/2019 |  |  | LIV |  | Green | Inoperable Fire-Rated Assembly |  |  | TE?: N | 05000352 Limerick 1 |  | 71152
Region: I | Millstone | 126066 | 12/31/2019 02/10/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | EDG Usable Fuel Calculations Failed to Consider Appropriate EDG Frequency Variations |  | NPP | TE?: N | 05000336 Millstone 2 | Design Control | 71111.12 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate the applicable design basis for the Unit 2 emergenc
Region: I | Millstone | 125651 | 09/30/2019 11/06/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to establish a preventive maintenance schedule for the Unit 3 emergency diesel generator governor drive components |  | NPP | TE?: N | 05000423 Millstone 3 | Procedure Quality | 71111.15 | A finding of very low safety significance (Green) and associated non-cited violation (NCV) of Millstone Power Station Unit 3 technical specification 6.8.1.a, Procedures and Programs, was self-revealed on July 9, 2019 when the 'A' emergency diesel generato
Region: I | Millstone | 125533 | 08/08/2019 09/18/2019 | 2019010-01 | NRC | NCV | Initiating Events | Green | Failure to control transient combustible lube oil in accordance with fire protection program procedure |  | H.12 - Avoid Complacency | TE?: N | 05000423 Millstone 3 | Protection Against External Factors | 71111.05T | The team identified a finding of very low safety significance (Green) and an associated NCV of Millstone Unit 3 License Condition 2.H, Fire Protection, for the licensee’s failure to implement and maintain in effect all provisions of the approved Fire Prot
Region: I | Millstone | 125577 | 08/08/2019 09/18/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Unit 2 Alternative Shutdown Procedure for Fire in East 480 Volt Load Center Room |  | NPP | TE?: N | 05000336 Millstone 2 | Protection Against External Factors | 71111.05T | The team identified a finding of very low safety significance (Green) and an associated NCV of Millstone Unit 2 Operating License Condition 2.C.(3) for failure to implement and maintain in effect all provisions of the approved Fire Protection Program. Spe
Region: I | Millstone | 125179 | 06/30/2019 08/12/2019 | 2019002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate post maintenance testing resulted in engineered safety features building emergency ventilation failure to start |  | H.4 - Teamwork | TE?: N | 05000423 Millstone 3 | Configuration Control | 71111.19 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” was self-revealed on June 13, 2019 when 3HVQ*ACUS2B, the Unit 3 'B' train engineered safety features (ESF) building air co
Region: I | Millstone | 125110 | 06/30/2019 08/12/2019 | 2019002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Degraded jacket water piping for emergency diesel generator not promptly corrected |  | H.5 - Work Management | TE?: N | 05000423 Millstone 3 | Equipment Performance | 71152 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was self-revealed when Dominion did not promptly correct deficient welds on the Unit 3 'A' emergency diesel generato
Region: I | Millstone | 124387 | 03/31/2019 05/14/2019 | 2019001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate maintenance procedures led to both control room emergency ventilation trains declared inoperable and unable to perform their safety function |  | P.6 - Self-Assessment | TE?: N | 05000336 Millstone 2 | Configuration Control | 71153 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified when inadequate maintenance procedures for control room boundary doors and ventilation equipment resulted in both control room em
Region: I | Millstone | 24631 | 09/30/2018 11/02/2018 | 2018003-01 | NRC | UNKN | Mitigating Systems | Green | Failure to Assure that Safety Related Service Piping Conformed to the Procurement Documents |  | NPP | TE?: N | 05000336 Millstone 2 |  | 71111.15 | The inspectors identified a Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion VII, “Control of Purchased Material, Equipment, and Services,” when the licensee failed to identify that a replacement service water pipe spool (JGD-1-25
Region: I | Millstone | 24342 | 06/13/2018 07/13/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Over-Duty Breakers on Safety-Related Buses on Unit 2 |  | P.2 - Evaluation | TE?: N | 05000336 Millstone 2 |  | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control.” Specifically, Dominion incorrectly concluded that the 480V safety-related breakers conformed with t
Region: I | Millstone | 24343 | 06/13/2018 07/13/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Over-Duty Breakers on Safety-Related Bus 34C on Unit 3 |  | P.1 - Identification | TE?: N | 05000423 Millstone 3 |  | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control.” Specifically, Dominion did not adequately evaluate the results of the Unit 3 short circuit calc
Region: I | Millstone | 24344 | 06/13/2018 07/13/2018 | 2018010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Part 21 Power Supply Defects |  | P.5 - Operating Experience | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings.” Specifically, Dominion did not accomplish repairs to safety-related power sup
Region: I | Millstone | 24345 | 06/13/2018 07/13/2018 | 2018010-04 | NRC | NCV | Mitigating Systems | Green | Flood Seals Not Installed in Unit 2 ‘A’ EDG and Auxiliary Building Penetrations |  | P.3 - Resolution | TE?: N | 05000336 Millstone 2 |  | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XIV, “Corrective Actions.” Dominion identified a condition adverse to quality but did not correct the condition. Specific
Region: I | Millstone | 24346 | 06/13/2018 07/13/2018 | 2018010-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of ECCS Valve Interlocks |  | NPP | TE?: N | 05000423 Millstone 3 |  | 71111.21M | The team identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control." Specifically, Dominion did not ensure that all testing required to demonstrate that ECCS valve interlock ci
Region: I | Millstone | 22644 | 12/31/2017 02/01/2018 | 2017004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain RCS Pressure during Solid Plant Cooldown |  | H.5 - Work Management | TE?: N | 05000423 Millstone 3 |  | 71111.2 | A self-revealed NCV of very low safety significance (Green) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified wherein, on October 13, 2017, Dominion faile
Region: I | Millstone | 21681 | 09/30/2017 10/27/2017 | 2017003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Results in Inadvertent Lowering of Spent Fuel Pool Level |  | H.12 - Avoid Complacency | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71152 | A self-revealing NCV of very low safety significance (Green) of Technical Specification (TS) 6.8, “Procedures,” was identified because Dominion did not adequately establish Operating Procedure (OP) 2305, “Spent Fuel Pool Cooling and Purification Syste
Region: I | Millstone | 25426 | 08/31/2017 09/13/2017 |  | NRC | NCV | Mitigating Systems | Green | Failure to Replace Auxiliary Feedwater Solenoid Valves within the Required Frequency |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.21N | The inspection team identified a Green non-cited violation of Technical Specification 6.8.1.a, "Procedures," because Dominion did not implement procedures as required by Regulatory Guide 1.33, Revision 2, Appendix A.9, "Procedures for Performing Maintenan
Region: I | Millstone | 23471 | 03/31/2017 05/11/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain CST Temperature in Accordance with Procedure Requirements |  | P.3 - Resolution | TE?: N | 05000336 Millstone 2 |  | 71111.01 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement Operating Procedure (OP) 2319B, "Condensate S
Region: I | Millstone | 23470 | 03/31/2017 05/11/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Change of 'C' Charging Pump Testing Requirements Contrary to ASME OM |  | H.3 - Change Management | TE?: N | 05000423 Millstone 3 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50.55a(f) because Dominion did not perform all required inservice testing (IST) of the Unit 3 'C' charging pump, 3CHS*P3C, in accordance with the American Society of Mechanical Engineers (ASME) Operation and
Region: I | Millstone | 25412 | 12/31/2016 02/01/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Routine Failure to Perform Engineering Evaluation of Long Term Scaffolding |  | P.3 Resolution | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.05Q | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement procedure MA-AA-105, "Scaffolding," Revision
Region: I | Millstone | 25413 | 12/31/2016 02/01/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.2 Field Presence | TE?: N | 05000336 Millstone 2 |  | 71111.11B | The inspectors identified an NCV of 10 CFR 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure that the integrity of an operating test administered to licensed operators was maintained. During the annual operating exam,
Region: I | Millstone | 25414 | 12/31/2016 02/01/2017 | 2016004-03 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action for Vital Inverters |  | H.5 Work Management | TE?: N | 05000423 Millstone 3 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to take timely corrective actions to replace degraded diodes in Unit 3 vital inverters INV-1 and INV-2 upon receipt of information t
Region: I | Millstone | 25401 | 09/30/2016 11/04/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Review Standing Orders |  | H.2 Field Presence | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.11Q | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1.a, for Dominion's failure to implement procedures as required by Regulatory Guide 1.33, Revision 2, Appendix A.1, "Administrative Procedures", during the performance of watch turn
Region: I | Millstone | 25403 | 09/30/2016 11/04/2016 | 2016003-02 | NRC | NCV | Initiating Events | Green | Failure to Scope Safety Related Acoustic Valve Monitoring System into the Maintenance Rule |  | H.8 Procedure Adherence | TE?: N | 05000423 Millstone 3 |  | 71111.12 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(b)(1), for Dominion's failure to include the safety-related Unit 2 Pressurizer Safety Valve, Acoustic Valve Monitoring System (AVMS) SSC within the scope o
Region: I | Millstone | 25409 | 08/11/2016 09/14/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Unaaproved OMA in Lieu of Meeting III.G.2 Fire Protection Requirements for Fire Area R-14, Lower 4kV Swithchgear Room and Cable Vault |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.05T | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Millstone Power Station, Unit 2, Renewed Facility Operating License Condition 2.C.(3) to implement and maintain in effect all provisions of the approv
Region: I | Millstone | 25394 | 07/22/2016 09/02/2016 | 2016009-01 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Correct Inadequate Procedural Direction for Responding to a LOCA with Failure of an RSS Heat Exchanger Tube |  | H.14 Conservative Bias | TE?: N | 05000423 Millstone 3 |  | 71152B | The inspectors identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to promptly correct a condition adverse to quality. Specifically, Dominion did not tak
Region: I | Millstone | 25393 | 07/22/2016 09/02/2016 | 2016009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions for Chronic Leakage at Residual Heat Removal Heat Exchanger Bottom Head Flanges |  | H.5 Work Management | TE?: N | 05000423 Millstone 3 |  | 71152B | The inspectors identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to correct conditions adverse to quality. Specifically, since 1985 Dominion has not co
Region: I | Millstone | 25399 | 07/22/2016 09/02/2016 | 2016009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Take Corrective Action to Preclude Repetition of the Condition that Caused Premature Failure of a Battery Cell |  | H.11 Challenge the Unknown | TE?: N | 05000336 Millstone 2 |  | 71152B | The inspectors identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action," for Dominion's failure to take corrective actions to preclude repetition of a significant condition adverse to
Region: I | Millstone | 25390 | 06/30/2016 07/25/2016 | 2016002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Secondary Containment Inoperability Due to Inadequate Procedures |  | H.6 Design Margins | TE?: N | 05000423 Millstone 3 |  | 71111.15 | The inspectors identified a self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Dominion did not develop a Unit 3 Supplementary Leak Collection and Release System (SLCRS) damper preventative ma
Region: I | Millstone | 23754 | 03/31/2016 05/04/2016 | 2016001-01 | NRC | VIO | Mitigating Systems | Green | Repetitive Failures to Correct Unit 3 Turbine Driven Auxiliary Feedwater Pump Performance Issues | EA Case: 2016090 | H.6 - Design Margins | TE?: N | 05000423 Millstone 3 |  | 71111.15 | The inspectors identified a Green NOV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's repetitive failure to take effective corrective actions for significant conditions adverse to
Region: I | Millstone | 25389 | 03/31/2016 05/04/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Failure of Feedwater Isolation Valve to Close Due to Electrical Jumper Being Installed |  | H.5 Work Management | TE?: N | 05000423 Millstone 3 |  | 71111.19 | The inspectors identified a self-revealing Green NCV of TS 3.3.2 for Dominion's failure to meet the operability requirements for the 'C' feedwater isolation valve (FWIV) testing and valve limit testing work associated with Design Change MP3-09-01030, an e
Region: I | Millstone | 23745 | 12/31/2015 02/04/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Charging Packing Lubrication Pump Inadequate Operating Procedure Acceptance Criteria |  | H.7 Documentation | TE?: N | 05000336 Millstone 2 |  | 71111.15 | The inspectors identified a Green, Non-Cited Violation (NCV) of 10 CFR 50 Appendix B Criterion V, Instructions, Procedures, and Drawings associated with Dominion's failure to include in the Unit 2 charging pump operating procedure appropriate acceptance c
Region: I | Millstone | 23746 | 12/31/2015 02/04/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Turbine Driven Auxiliary Feedwater Pump Corrective Actions to Prevent Reccurence |  | H.13 Consistent Process | TE?: N | 05000336 Millstone 2 |  | 71153 | The inspectors identified a green NCV of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, for Dominion's failure to take corrective action to prevent recurrence for a significant condition adverse to quality according to the definition in PI-AA-200
Region: I | Millstone | 23749 | 11/30/2015 01/05/2016 | 2015012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedural Guidance During a Loss of RCS Inventory |  | H.8 Procedure Adherence | TE?: N | 05000336 Millstone 2 |  | 93812 | The NRC identified a Green NCV of Millstone Power Station Unit No. 2 Technical Specifications (TS) 6.8.1, "Procedures" involving Dominion's failure to implement procedural steps when prompted by plant conditions to mitigate the event. Specifically, when p
Region: I | Millstone | 23750 | 11/30/2015 01/05/2016 | 2015012-02 | NRC | NCV | Mitigating Systems | Green | Failure of the STA to Support the Crew During a Plant Cooldown |  | H.4 Teamwork | TE?: N | 05000336 Millstone 2 |  | 93812 | The NRC identified a Green NCV of Millstone Power Station Unit No. 2 TS 6.8.1, "Procedures" involving the shift technical advisor's (STA's) failure to follow position-specific procedural guidance, to support all phases of plant operation. Specifically, th
Region: I | Millstone | 23751 | 11/30/2015 01/05/2016 | 2015012-03 | NRC | NCV | Initiating Events | Green | Procedure Failed to Direct Adequate Venting of SDC System |  | H.1 Resources | TE?: N | 05000336 Millstone 2 |  | 93812 | A self-revealing Green NCV of Millstone Power Station Unit No. 2 TS 6.8.1, "Procedures," was identified because the procedure used by Dominion to place the SDC system in service did not verify that the SDC suction line to the LPSI pumps was filled and ven
Region: I | Millstone | 23738 | 09/30/2015 11/10/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Change of Pump Reference Values Contrary to ASME OM |  | P.2 Evaluation | TE?: N | 05000423 Millstone 3 |  | 71111.22 | The inspectors identified a Green NCV of Millstone Unit 3 Technical Specification (TS) Surveillance Requirement 4.0.5 because Dominion did not implement the Inservice Testing (IST) Program in accordance with the American Society of Mechanical Engineers (A
Region: I | Millstone | 23744 | 09/30/2015 11/10/2015 | 2015003-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Direction to Mitigate a LOCA and Failure of an RSS Heat Exchanger Tube |  | P.2 Evaluation | TE?: N | 05000423 Millstone 3 |  | 71153 | The inspectors identified a Green NCV of Millstone Unit 3 TS 6.8.1, as specified by Regulatory Guide (RG) 1.33, associated with Dominion's failure to implement adequate procedures to address a hypothetical large break loss of coolant accident (LBLOCA) ins
Region: I | Millstone | 23730 | 05/01/2015 06/12/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Reactor Building Closed Cooling Water System Pump Oil Leakage Results in Technical Specification Inoperability |  | H.14 Conservative Bias | TE?: N | 05000336 Millstone 2 |  | 7111121 | The team identified a non-cited violation (NCV) of Millstone Power Station Unit 2, Technical Specification (TS) 3.7.3.1 the reactor building component cooling water (RBCCW) system Limiting Condition of Operation (LCO) in that Dominion failed to maintain
Region: I | Millstone | 23731 | 05/01/2015 06/12/2015 | 2015007-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Provide 10 CFR 50.59 Evaluation for Interim Action Associated with Implementation of Operability Determination Procedure |  |  | TE?: Y SL-IV-NCVIV | 05000336 Millstone 2 |  | 7111121 | The team identified a Severity Level IV, non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.59, "Changes, Tests, and Experiments," in that Dominion failed to perform a written evaluation to provide the bases for determi
Region: I | Millstone | 23736 | 05/01/2015 06/12/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Circuit Breaker Interrupting Capability |  |  | TE?: N | 05000336 Millstone 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," in that Dominion did not correctly
Region: I | Millstone | 23723 | 03/31/2015 05/08/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Charging and Primary Closed Cooling Water Area Heater Transformers Equipment Environmental Qualification Non-Conformance |  | H.8 Procedure Adherence | TE?: N | 05000423 Millstone 3 |  | 71111.15 | The inspectors identified a Green, Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI associated with Dominion's failure to promptly identify conditions adverse to quality associated with the Millstone Power Station Unit 3 CHS (Charging System) &
Region: I | Millstone | 23724 | 03/31/2015 05/08/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Replace Defective Fuses in the "A" EDG Resulting in Generator Failure |  | P.5 Operating Experience | TE?: N | 05000336 Millstone 2 |  | 71111.19 | The inspectors identified a Green, Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI associated with Dominion's failure to prevent recurrence of a significant condition adverse to quality, installation of defective fuses in the Unit 2 EDGs from
Region: I | Millstone | 23696 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Review Additional Failures Against the SLCRS (a)(1) Monitoring Plan |  | P.3 Resolution | TE?: N | 05000423 Millstone 3 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65 (a)(1) for the failure to determine if the goals or corrective actions for the (a)(1) monitoring plan for the SLCRS system should be adjusted following an additional failure of the auxiliary building v
Region: I | Millstone | 23697 | 12/31/2014 02/10/2015 | 2014005-02 | NRC | NCV | Initiating Events | Green | Failure to Manage Risk of RSST Testing |  | H.3 Change Management | TE?: N | 05000423 Millstone 3 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65 (a)(4) for the failure to properly assess and manage the risk of work in the switchyard during the Unit 3 refueling outage. The inspectors determined that Dominion incorrectly assumed the risk mitigati
Region: I | Millstone | 23698 | 12/31/2014 02/10/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Multiple 'A' HVK Start and Runtime Failures |  | H.14 Conservative Bias | TE?: N | 05000423 Millstone 3 |  | 71111.15 | Green: The inspectors identified a Green, NCV of 10 CFR 50, Appendix B, Criterion XVI associated with Dominion's failure to promptly identify or correct conditions adverse to quality associated with the equipment reliability of the Millstone Power Station
Region: I | Millstone | 23703 | 12/31/2014 02/10/2015 | 2014005-04 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Refueling Outage 2R22 Activities |  | H.5 Work Management | TE?: N | 05000336 Millstone 2 |  | 71124.02 | A self-revealing finding (FIN) of very low safety significance (Green) was identified due to the accrual of excessive unintended occupational collective radiation exposure during Millstone refueling outage 2R22. This resulted from performance deficiencies
Region: I | Millstone | 23704 | 12/31/2014 02/10/2015 | 2014005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Standing Order Restrictions into the EOPs and AOPs for the Unit 3 TDAFW Pump Flow Control Valves |  | P.3 Resolution | TE?: N | 05000423 Millstone 3 |  | 71152 | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1, "Procedures," for the failure to accurately maintain the EOPs and Abnormal Operating Procedures (AOPs) by not including operating restrictions that had been promulgated as a temp
Region: I | Millstone | 23714 | 12/09/2014 01/15/2015 | 2014013-01 | NRC | NCV | Mitigating Systems | Green | Failure to Resolve Anomalous Data During Complex Troubleshooting of the Turbine Driven Auxiliary Feedwater Pump Controls |  | H.4 Teamwork | TE?: N | 05000423 Millstone 3 |  | 93812 | The Team identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to follow procedure MA-AA-103, Conduct of Troubleshooting, Revision 11 foll
Region: I | Millstone | 23720 | 12/09/2014 01/15/2015 | 2014013-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Adverse Conditions related to the Turbine Driven Auxiliary Feedwater Pump Governor to Control Valve Linkage |  | H.14 Conservative Bias | TE?: N | 05000423 Millstone 3 |  | 93812 | The Team identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions" associated with the failure to identify and correct adverse conditions related to the TDAFW pump governor to control valve linkage which potentially could h
Region: I | Millstone | 23712 | 08/01/2014 08/28/2014 | 2014011-02 | NRC | FIN | Initiating Events | Green | Inadequate Implementation of Dominion's Design Change Process |  | H.8 Procedure Adherence | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 93812 | The NRC identified a finding of very low safety significance (Green), in that Dominion did not ensure correct implementation of their design change process procedure when establishing licensing basis requirements for removal of the SPS. Specifically, Domi
Region: I | Millstone | 23713 | 08/01/2014 08/28/2014 | 2014011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Implement Emergency Operating Procedures |  | H.8 Procedure Adherence | TE?: N | 05000423 Millstone 3 |  | 93812 | The NRC identified a Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1 "Procedures," because the Millstone Unit 3 control room personnel did not implement Emergency Operating Procedures (EOP) in a timely manner and in accordance with E
Region: I | Millstone | 23688 | 07/21/2014 08/28/2014 | 2014008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Maintenance Instructions for the Turbine Driven Auxiliary Feedwater Pump Governor Control Valve Linkage |  | H.7 Documentation | TE?: N | 05000423 Millstone 3 |  | 93812 | The inspectors identified a self-revealing Green NCV of TS 6.8.1, "Procedures and Programs," when Dominion did not maintain an adequate maintenance procedure to ensure reliable performance of the TDAFW system. Specifically, TDAFW properly started follow
Region: I | Millstone | 23680 | 06/30/2014 08/12/2014 | 2014003-02 | NRC | NCV | Emergency Preparedness | Green | .NCV 05000336/2014003-03 and 05000423/2014003-03, Failure to Adequately Maintain EALs |  | P.1 Identification | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71152 | Green. The inspectors identified a Green NCV associated with emergency preparedness planning standard 10 CFR 50.47(b)(4) and the requirements of Sections IV.B and IV.C of Appendix E to 10 CFR Part 50. Specifically, Dominion did not maintain the Millstone
Region: I | Millstone | 23687 | 05/10/2014 08/12/2014 | 2014003-03 | NRC | NCV | Initiating Events | Green | NCV 05000336/2014003-01, Failure to Maintain Adequate Procedure for RCS Drain/Fill |  | H.12 Avoid Complacency | TE?: N | 05000336 Millstone 2 |  | 71111.2 | Green. The inspectors identified a Green NCV of TS 6.8.1, Procedures, for Dominion's failure to maintain an adequate procedure for reactor filling and draining that incorporates guidance contained in NRC Generic Letter 88-17. Specifically, OP2301E, draini
Region: I | Millstone | 23679 | 04/20/2014 08/12/2014 | 2014003-01 | NRC | NCV | Occupational Radiation Safety | Green | NCV 05000336/2014003-02, Failure to Utilize Respiratory Protection as Specified in Work Control Documents |  | H.14 Conservative Bias | TE?: N | 05000336 Millstone 2 |  | 71124.03 | Green. The inspectors identified a self-revealing Green NCV of Technical Specification (TS) 6.81, Regulatory Guide 1.33, Appendix 'A', Radiation Work Permits (RWP) and as low as reasonably achievable (ALARA) procedures, for Dominion's failure to utilize r
Region: I | Millstone | 23672 | 02/23/2014 05/07/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2014002-01, Failure to Evaluate Test Results Outside of Acceptance Criteria for 'A' Service Water Pump |  | H.6 Design Margins | TE?: N | 05000423 Millstone 3 |  | 71111.15 | -Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XI, "Test Control," because Dominion did not properly evaluate test results outside of the acceptance criteria for the Unit 3 '
Region: I | Millstone | 23664 | 12/31/2013 02/10/2014 | 2013005-01 | NRC | FIN | Mitigating Systems | Green | FIN 05000423/2013005-01), Inadequate Operability Determination for the TDAFW Pump following an Overspeed Trip |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000423 Millstone 3 |  | 71111.15 | Green. The inspectors identified a Green Finding (FIN) for the failure to follow Dominion Procedure OP-AA-102, "Operability Determinations," and establish adequate compensatory measures to restore reliability to the Unit 3 Turbine Driven Auxiliary Feedwat
Region: I | Millstone | 23665 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2013005-02, Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000336 Millstone 2 |  | NONE | -Green. The inspectors identified an NCV of Millstone Unit 2 Operating License Condition 2.C. (3) for failure to implement and maintain all aspects of the approved Fire Protection Program (FPP). Specifically, Dominion had not adequately implemented an alt
Region: I | Millstone | 23660 | 10/04/2013 11/08/2013 | 2013004-01 | NRC | VIO | Barrier Integrity | Green | (VIO 05000423/2013004-01, Inadequate Corrective Actions to Restore Degraded Unit 3 Main Feedwater Isolation Valves |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000423 Millstone 3 |  | 71111.15 | Green. The inspectors identified a cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's continued failure to take timely and effective corrective actions for conditions adverse to quality involving the degradation o
Region: I | Millstone | 23663 | 10/04/2013 11/08/2013 | 2013004-02 | NRC | FIN | Mitigating Systems | Green | FIN 05000423/2013004-02, Inadequate Operability Determination for the Turbine Drive Auxiliary Feedwater (TDAFW) Pump |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000423 Millstone 3 |  | 71111.15 | Green. The inspectors identified a finding (FIN) for Dominion's failure to complete an adequate and timely operability determination as required by OP-AA-102, "Operability Determination," to assess governor control oscillations following completion of mai
Region: I | Millstone | 23653 | 08/08/2013 09/16/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2013005-01, Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.05T | Green. The team identified a finding of very low safety significance involving a non-cited violation of Millstone Unit 2 Operating License Condition 2.C. (3) for failure to implement and maintain all aspects of the approved Fire Protection Program (FPP).
Region: I | Millstone | 23658 | 08/08/2013 09/16/2013 | 2013010-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2013010-02, Spurious Operation of Pressurizer Spray Valves Not Analyzed |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.05T | -Green. The team identified a finding of very low safety significance involving a non cited violation of Millstone Unit 2 Operating License Condition 2.C. (3) for failure to implement and maintain all aspects of the approved Fire Protection Program. Speci
Region: I | Millstone | 23659 | 08/08/2013 09/16/2013 | 2013010-03 | NRC | NCV | Mitigating Systems | Green | NCV 05000336, 423/2013010-03, Failure to Maintain Cold Shutdown Material On-Site |  |  | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.05T | -Green. The team identified a finding of very low safety significance, involving a non-cited violation of Millstone Unit 2 Operating License Condition 2.C. (3) and Unit 3 Operating License Condition 2.H for the failure to implement and maintain all aspect
Region: I | Millstone | 23639 | 06/30/2013 08/06/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2013003-01, Failure to Implement Annunciator Response Procedure for a Loss of Ventilation during a Battery Charge |  | H.4(b) Procedural Compliance | TE?: N | 05000423 Millstone 3 |  | 71111.13 | -Green. The inspectors identified a NCV of Technical Specification (TS) 6.8.1, "Procedures and Programs," for failing to implement Annunciator Response Procedure (ARP) OP 3353VP1B1-4 (BATT ROOM 1, 3, 5, EXHAUST FAN FLOW LOW) and stop the equalizing batter
Region: I | Millstone | 23644 | 06/30/2013 08/06/2013 | 2013003-02 | Self - Revealed | NCV | Initiating Events | Green | NCV 05000423/2013003-02, Failure to Establish Measures for the Identification and Control of Design Interfaces and for Coordinating among participating design organizations |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000423 Millstone 3 |  | 71111.2 | -Green. The inspectors noted a self-revealing Green NCV of 10 CFR 50, Criterion III, "Design Control," when Dominion's did not adequately implement established measures for the identification and control of design interfaces and for coordinating among par
Region: I | Millstone | 23645 | 06/30/2013 08/06/2013 | 2013003-03 | NRC | NCV | Emergency Preparedness | Green | NCV 05000423/2013003-03, Failure to make a 10 CFR 50.72(b)(3)(v) report for a major loss of emergency assessment capability for the stack radiation monitor |  |  | TE?: N | 05000423 Millstone 3 |  | 71153 | -Severity Level IV. The inspectors identified a Severity Level IV NCV of 10 CFR 50.72(b)(3)(xiii) for the failure to make the required initial notification to the NRC within eight hours of a major loss of monitoring capability. On April 16, Dominion decla
Region: I | Millstone | 23638 | 03/31/2013 04/11/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2013002-01: Inadequate Post Maintenance Testing Following PORV Maintenance |  | H.3(b) Work Activity Coordination | TE?: N | 05000336 Millstone 2 |  | 71152 | Green. The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion XI, "Test Control," for Dominion's failure to perform an adequate post maintenance test (PMT) on 2-RC-404, the Unit 2 'B' power operated relief valve (PORV). Specifically, a s
Region: I | Millstone | 23646 | 02/15/2013 03/28/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2013007-01, Failure to Verify 480VAC MCC Starters Had Adequate Control Voltage to Operate Under All Design Conditions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000423 Millstone 3 |  | 71111.17T | Green. The team identified a finding of very low safety significance involving a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," in that Dominion did not verify that
Region: I | Millstone | 23628 | 12/31/2012 01/16/2013 | 2012005-01 | NRC | NCV | Barrier Integrity | Green | NCV 05000423/2012005-02, Failure to Establish Proper Test Controls for the Wide Range Logarithmic Post Accident Neutron Flux Monitors |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000423 Millstone 3 |  | 71153 | Green. The inspectors identified an NCV of 10 CFR 50, Appendix B, Criteria XI, Test Control, associated with the Barrier Integrity cornerstone. Specifically, Dominion did not ensure that the wide range logarithmic post accident neutron monitor system was
Region: I | Millstone | 23635 | 10/29/2012 01/16/2013 | 2012005-02 | NRC | NCV | Emergency Preparedness | Green | NCV 05000336/2012005-01 and 05000423/2012005-01, Failure to Adequately Implement Flooding EALs |  | H.2(d) Facilities & Equipment | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.01 | Green. The inspectors identified an NCV associated with emergency preparedness (EP) planning standard 10 CFR 50.47(b)(4), and the requirements of Sections IV.B and IV.C of Appendix E to 10 CFR Part 50. Specifically, Dominion did not maintain in effect the
Region: I | Millstone | 23626 | 09/30/2012 11/02/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | NCV 05000336/2012004-02, Corrective Action to Prevent Recurrence Ineffective to Preclude Repetition of a Significant Condition Adverse to Quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the corrective action to prevent recurrence of a significant condition adverse to quality did not preclude repetition of the event. Sp
Region: I | Millstone | 23627 | 09/30/2012 11/02/2012 | 2012004-02 | NRC | NCV | Barrier Integrity | Green | NCV 05000423/2012002-01, Inadequate Post Maintenance Test Directions following Design Change to 3HVC*FN1B |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000423 Millstone 3 |  | 71111.19 | Green. The inspectors identified an NCV of 10 CFR 50 Appendix 'B' Criteria V "Instructions, Procedures, and Drawings" of very low safety significance (Green) for Dominion's failure to adequately specify post maintenance test (PMT) requirements for the con
Region: I | Millstone | 23651 | 08/21/2012 11/16/2012 | 2012503-01 | NRC | NCV | Emergency Preparedness | Green | NCV 05000336/2012503-001 and 05000423/2012503-001, Failure to Adequately Implement Fuel Clad Barrier EALs |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71114.01 | The NRC identified a non-cited violation (NCV) associated with emergency preparedness planning standard 10 CFR 50.47(b)(4), and the requirements of Sections IV.B and IV.C of Appendix E to 10 CFR Part 50. Specifically, Dominion did not maintain in effect t
Region: I | Millstone | 23614 | 08/03/2012 08/31/2012 | 2012010-01 | NRC | NCV | Barrier Integrity | Green | NCV 05000423/2012010-01 Failure to Take Timely Corrective Actions to Restore Degraded Unit 3 Main Feedwater Isolation Valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000423 Millstone 3 |  | 71152B | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criteria XVI, "Corrective Action," for Dominion's failure to take timely corrective actions for conditions adverse to quality involving the degradation of the closing capability of fou
Region: I | Millstone | 23618 | 08/03/2012 08/31/2012 | 2012010-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2012010-02 Failure to Take Prompt and Effective Corrective Actions to Address TDAFW Pump Trip Latch Mechanism Degradation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000423 Millstone 3 |  | 71152B | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criteria XVI, "Corrective Action," for Dominion's failure to take prompt and effective corrective actions for conditions adverse to quality involving degradation of the Unit 3 turbine
Region: I | Millstone | 23619 | 08/03/2012 08/31/2012 | 2012010-03 | NRC | FIN | MISC | Green | FIN 05000336&423/2012010-03 Failure to Perform Effectiveness Reviews for Formal Self-Assessments |  | H.4(b) Procedural Compliance | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71152B | Green. The inspectors identified a finding (FIN) of very low safety significance (Green) for Dominion's failure to perform procedurally required effectiveness reviews for numerous formal self-assessments. Consequently, Dominion missed opportunities to ide
Region: I | Millstone | 23612 | 06/30/2012 07/23/2012 | 2012003-01 | NRC | FIN | Mitigating Systems | Green | FIN 05000423/2012003-01, Inadequate Operability Determination for 3FWS*CTV41 Feedwater Isolation Valve Hydraulic Actuators. |  |  | TE?: N | 05000423 Millstone 3 |  | 71111.15 | Green. An NRC identified finding (FIN) of very low safety significance (Green) was identified for Dominion's failure to adequately assess the operability of the Unit 3 Feedwater isolation valves, 3FWS*CTV41A, B, C and D in accordance with OP-AA-102-1001,
Region: I | Millstone | 23613 | 05/11/2012 06/20/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2012007-01, Inadequate Assumptions used in Emergency Motor Control Center Control Circuit Voltage Drop Calculation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 7111121 | -Green: The team identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, because Dominion had not verified the adequacy of their design with respect to the
Region: I | Millstone | 23610 | 09/30/2011 11/10/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | NCV 05000336/2011004-01, Failure to Electrically Isolate a Dissimilar Metal Flanged Joint Leads to Forced Shutdown Due to Service Water Leak |  | H.4(a) Human Error Prevention | TE?: N | 05000336 Millstone 2 |  | 71111.2 | Green. A self-revealing NCV of 10 CFR 50, Appendix B Criterion V, "Instructions, Procedures, and Drawings," was identified for Dominion's failure to properly electrically isolate service water (SW) flanged joints of dissimilar metals. This caused a more r
Region: I | Millstone | 23596 | 06/30/2011 08/03/2011 | 2011003-01 | Self - Revealed | FIN | Initiating Events | Green | (FIN 05000336/2011003-04 Failure to Follow Procedure for Starting a Second SGFP Results in Reactor Trip) |  | H.4(b) Procedural Compliance | TE?: N | 05000336 Millstone 2 |  | 71153 | -Green. A self-revealing Green finding (FIN) was identified for Dominion's failure to follow procedure OP 2204, "Load Changes" when starting the second steam generator feedwater pump (SGFP). Specifically, the operating crew did not maintain SGFP suction p
Region: I | Millstone | 23601 | 06/30/2011 08/03/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | (NCV 05000423/2011003-01, Failure to Take Timely Corrective Actions for Dealloying of Aluminum Bronze Service Water Valves). |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000423 Millstone 3 |  | 71111.15 | -Green. The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action in that Dominion did not take timely corrective action to address repetitive failures of aluminum-bronze (Al-Br) service water valves that were install
Region: I | Millstone | 23602 | 06/30/2011 08/03/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | (NCV 0500336/2011003-02 Untimely Corrective Action for Safety Related Inverters Leads to Repetitive Out of Calibration Results) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71111.22 | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action in that Dominion did not take timely corrective action to address repetitive out of calibration conditions associated with safety related inverters. Sp
Region: I | Millstone | 23603 | 06/30/2011 08/03/2011 | 2011003-04 | Self - Revealed | NCV | Barrier Integrity | Green | (NCV 0500336/2011003-03 Inadequate Corrective Action Results in Loss of Enclosure Building's Safety Function.) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" was identified in that Dominion did not take adequate corrective action to address the cause of main steam safety valve (MSSV) exhaust pipe bushings not seating which
Region: I | Millstone | 23609 | 04/29/2011 05/27/2011 | 2011008-02 | Self - Revealed | FIN | Initiating Events | Green | FIN 05000336/2011008-02, Improper Operation of Turbine Control Valves During Testing. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000336 Millstone 2 |  | 93812 | Green: The team identified a self-revealing finding of very low safety significance (Green) for improper operation of the turbine controls during turbine control valve testing. Specifically, the inspectors identified that control room operators failed to
Region: I | Millstone | 23589 | 03/31/2011 05/09/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | NCV 05000423/2011002-01, Failure to Prevent Safety Related Cables from Being Submerged |  | P.2(b) Implementing Operating Experience | TE?: N | 05000423 Millstone 3 |  | 71111.06 | Green. A self-revealing Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for Dominion's failure to maintain safety related cables in an environment for which they were designed. Specifically, 4
Region: I | Millstone | 23594 | 03/31/2011 05/09/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | NCV 05000423/2011002-02, Improper Restoration of Air Conditioning Equipment Following Maintenance Results in Inoperability of 'B' Train of Recirculation Spray System |  | H.4(b) Procedural Compliance | TE?: N | 05000423 Millstone 3 |  | 71111.19 | Green. A self-revealing Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for Dominion's failure to properly restore 3HVQ*ACUS2B, Containment Recirculation Pumps and Cooler
Region: I | Millstone | 23582 | 12/31/2010 02/07/2011 | 2010005-01 | Self - Revealed | FIN | Initiating Events | Green | (FIN 05000336/2010005-01, Failure to Provide an Adequate Procedure for Backwashing Condenser Water Boxes Results in Reactor Trip). |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing finding of very low significance was identified for Dominion's failure to provide an adequate procedure for backwashing the Unit 2 condenser water boxes in accordance with procedure MP-05-MMM, "Manuals, Procedures, Guidelines, Hand
Region: I | Millstone | 23583 | 12/31/2010 02/07/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | (NCV 05000423/2010005-01, Failure to Take Adequate Corrective Actions for a Broken JW Banjo Bolt on the 3B EDG). |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000423 Millstone 3 |  | 71152 | Green. The inspectors identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Dominion did not take adequate corrective action following the identification
Region: I | Millstone | 23565 | 09/30/2010 11/03/2010 | 2010004-01 | Self - Revealed | FIN | Initiating Events | Green | FIN 05000336/2010004-01, Failure to Implement Timely Corrective Action for a Degraded FRV Results in Manual Reactor Trip |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing finding (FIN) of very low safety significance was identified for Dominion's failure to implement timely corrective action for a degraded #2 feedwater regulating valve (FRV) in accordance with procedure PI-AA-200, "Corrective Action
Region: I | Millstone | 23569 | 09/30/2010 11/03/2010 | 2010004-02 | NRC | NCV | Initiating Events | Green | NCV 055000336/2010004-01, Failure to Promptly Identify and Correct the Source of a Unit 2 RCS Pressure Boundary Leak). |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71152 | Green. The inspector identified a Green, NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for Dominion's failure to promptly identify and correct the source of a reactor coolant system (RCS) pressure boundary leak from July 3, 2009, thro
Region: I | Millstone | 23584 | 09/22/2010 11/05/2010 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2010008+01; 05000423/2010008+01, Failure to Properly Control Fire Fighting Strategies. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71111.05T | Green. The team identified a non-cited violation of Millstone Unit 2 Operating License Condition 2.C.(3), and Unit 3 Operating License Condition 2.H, for the failure to implement all provisions of the approved Fire Protection Programs. Specifically, Do
Region: I | Millstone | 23587 | 09/22/2010 11/05/2010 | 2010008-02 | NRC | VIO | Mitigating Systems | Green | VIO 05000336/2010008-02, Failure to Protect Safe Shutdown Equipment From the Effects of Fire . |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.05T | Green. The team identified a cited violation of 10 CFR Part 50, Appendix R, Section III.G.2 for the failure to protect required post-fire safe shutdown components and cabling to ensure one of the redundant trains of equipment remains free from fire dam
Region: I | Millstone | 23588 | 09/22/2010 11/04/2010 | 2010011-01 | Self - Revealed | VIO | Mitigating Systems | Green | Failure to develop a mitigation strategy for depressurization of the Unit 3 steam generators and use a portable pump for injection make-up. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000423 Millstone 3 |  | 71111.05T | This finding, affecting the Mitigating Systems Cornerstone, is related to developing a strategy to maintain core cooling and mitigate fuel damage, under the circumstances associated with loss of large areas of the plant due to explosions or fire; in respo
Region: I | Millstone | 23556 | 06/30/2010 08/05/2010 | 2010003-01 | NRC | FIN | Initiating Events | Green | FIN 05000336/2010003-02, Failure to Properly Plan Work Activities for "D" Circulating Water Bay Outage Results in Manual Reactor Trip. |  | H.3(a) Work Planning | TE?: N | 05000336 Millstone 2 |  | 71153 | -Green. A self-revealing finding (FIN) of very low safety significance was identified for Dominion's failure to properly plan the work associated with the "D" circulating water (CW) bay outage in accordance with procedure WM-AA-3000, "Managing Complex Wor
Region: I | Millstone | 23557 | 06/30/2010 08/05/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2010003-01, Failure to Properly Evaluate a Degraded Governor Results in "A" EDG Inoperability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000336 Millstone 2 |  | 71152 | -Green. A self revealing non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action" was identified for Dominion's failure to properly evaluate a condition adverse to quality involving the Unit 2 "A" Emergency Diesel Generator (E
Region: I | Millstone | 23562 | 06/30/2010 08/05/2010 | 2010003-03 | NRC | FIN | Initiating Events | Green | FIN 05000423/2010003-03, Reactor Trip Caused by Loss of Positive Control of Steam Generator Level |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000423 Millstone 3 |  | 71111.2 | -Green. A self-revealing finding (FIN) of very low safety significance was identified for Dominion's failure to implement effective corrective actions for known degraded conditions associated with the steam generator (SG) water level control system. Speci
Region: I | Millstone | 23563 | 06/30/2010 08/05/2010 | 2010003-04 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2010003-02 Charging Pump Overheating and Cavitation during RCS Loop Vacuum Fill |  | H.3(b) Work Activity Coordination | TE?: N | 05000423 Millstone 3 |  | 71111.2 | -Green. A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings", was identified for Dominion's failure to have an adequate procedure for starting the charging pumps. Specifically, OP 3304A, "Charging and Letdow
Region: I | Millstone | 23143 | 12/31/2009 02/03/2010 | 2009005-03 | NRC | NCV | Initiating Events | Green | NCV 05000336/2009-03 RCS Drain Down Loss of Configuration Control |  | H.4(b) Procedural Compliance | TE?: N | 05000336 Millstone 2 |  | 71111.2 | Green. A self revealing NCV (Green) finding of Technical Specification 6.8.1(a) was identified for the failure to adequately implement procedures during partial draining of the reactor coolant system (RCS) in preparation for defueling the core. On October
Region: I | Millstone | 23141 | 11/15/2009 02/03/2010 | 2009005-01 | NRC | NCV | Barrier Integrity | Green | NCV 05000336/2009005-01, TS Surveillance Channel Calibration of ICCMS Not Performed |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.15 | Green. A NRC identified NCV of very low safety significance (Green) was identified for Dominion's failure to perform a channel calibration of the Unit 2 Inadequate Core Cooling Monitoring System (ICCMS) every 18 months as required by technical specificati
Region: I | Millstone | 23555 | 11/15/2009 02/03/2010 | 2009005-04 | NRC | FIN | Mitigating Systems | Green | FIN 05000336/2009005-04 Inadequate and Untimely Corrective Actions Causes Loss of Annunciators and Declaration of a NOUE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing (Green) finding was identified for Dominion's failure to provide effective corrective actions for known degraded conditions on the VR-11 and VR 21 120 volt AC non-vital instrument power supplies. Specifically, VR-11 and VR-21 were
Region: I | Millstone | 23142 | 10/06/2009 02/03/2010 | 2009005-02 | NRC | FIN | Initiating Events | Green | FIN 05000336/2009005-02 Implementation of Design Change results in Rapid Shutdown of Reactor |  | H.3(a) Work Planning | TE?: N | 05000336 Millstone 2 |  | 71111.2 | Green. A self-revealing (Green) finding was identified for Dominion's failure to take adequate precautions and/or adequately schedule maintenance on Unit 2's motor operated disconnect switch (MOD) for their main transformer. Specifically, on October 6, 20
Region: I | Millstone | 23137 | 09/30/2009 11/05/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | (NCV 05000336/2009004-02 Inadequate Procedures Caused a Leak from the Charging Header into the Auxiliary Building Drain System) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 |  | 71111.2 | Green. A violation of 10 CFR 50, Appendix B, Criteria V dispositioned as an NCV was identified for Dominion's failure to provide adequate operating procedures that were appropriate for the circumstances to operate the Unit 2 charging pumps during reactor
Region: I | Millstone | 23138 | 09/30/2009 11/05/2009 | 2009004-02 | NRC | FIN | Initiating Events | Green | (FIN 05000336/2009004-01 Inadequate and Untimely Corrective Actions Causes Reactor Trip) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | Green. A self-revealing finding of very low safety significance (Green) was identified for Dominion's failure to provide timely and effective corrective actions for known degraded conditions on the Unit 2 VR-11 and VR 21 120 volt AC non-vital instrument p
Region: I | Millstone | 23140 | 09/30/2009 11/05/2009 | 2009004-03 | NRC | URI | MISC | Green | URI 05000336/2009004-03. |  |  | TE?: N | 05000336 Millstone 2 |  | 71152 | Introduction: During a recent Problem Identification and Resolution Inspection, the inspectors identified a potential violation of 10 CFR 50.55(a)(2)(c)(1) involving Dominion's conformance with the specifications of ASME Code Section XI and Section III re
Region: I | Millstone | 23127 | 04/20/2009 07/27/2009 | 2009003-01 | NRC | NCV | Occupational Radiation Safety | Green | NCV 05000336/2009003-01, Failure to Survey a Contaminated Component |  | H.4(b) Procedural Compliance | TE?: N | 05000336 Millstone 2 |  | 7112101 | Green. An NRC-identified finding of very low safety significance (Green) was identified for Dominion's failure to effectively survey, label, and control contaminated tools and equipment. Specifically, Dominion failed to perform adequate surveys to identif
Region: I | Millstone | 23125 | 03/31/2009 05/14/2009 | 2009002-01 | NRC | FIN | Initiating Events | Green | FIN 05000423/2009002-01, Failure to Control Steam Generator Water Levels Results in Automatic Reactor Trip |  | H.3(b) Work Activity Coordination | TE?: N | 05000423 Millstone 3 |  | 71153 | Green. A self-revealing finding of very low safety significance (Green) was identified for Dominion's failure to control Unit 3 Steam Generator (SG) levels while operating at power. Specifically, Dominion's failure to control SG levels resulted in a react
Region: I | Millstone | 23128 | 03/06/2009 03/31/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Performance Testing of Safety Related Batteries |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," in that, Unit 2 and Unit 3 written test procedures for battery performance testing were not adequate an
Region: I | Millstone | 23129 | 03/06/2009 03/31/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Degraded Battery Cell |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Dominion did not take did not take corrective actions for a degraded cell in a Unit 2 sa
Region: I | Millstone | 23130 | 03/06/2009 03/31/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Safety Related Inverter Out-of-Calibration Results |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Dominion did not take corrective actions for repeated out-of-calibration test results as
Region: I | Millstone | 23136 | 03/06/2009 03/31/2009 | 2009006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Potential Air Entrapment in Recirculation Spray System Heat Exchangers |  |  | TE?: N | 05000423 Millstone 3 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Dominion did not ensure the adequacy of the recirculation spray system heat exchanger design
Region: I | Millstone | 23119 | 12/05/2008 01/14/2009 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2008008-01, Failure to Ensure Equipment Necessary For Fire Safe Shutdown Available. |  | H.4(b) Procedural Compliance | TE?: N | 05000336 Millstone 2 |  | 71111.05T | The team identified that Dominion failed to administratively control and ensure the availability of all necessary fire safe shutdown equipment to perform manual actions in the 4kV upper switchgear room. This finding was determined to be of very low safety
Region: I | Millstone | 23120 | 12/05/2008 01/14/2009 | 2008008-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000336/2008008-02, Failure to Ensure Timely Manual Action Consistent with the Post-Fire Safe Shutdown Analysis. |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.05T | The team identified that Dominion failed to ensure that a post-fire manual action to restore auxiliary feedwater (AFW) flow to a steam generator (SG) would be performed within 30 minutes of a plant trip consistent with the Millstone Unit 2 fire safe shutd
Region: I | Millstone | 23126 | 10/20/2008 03/23/2009 | 2008010-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000423/2008010-01, RHR pumps inoperable in the event of a LLOCA, due to a suction air void |  |  | TE?: N | 05000423 Millstone 3 |  | 93812 | -Green. The team identified a noncited violation (NCV) of Technical Specification (TS) 3.5.2.d which requires an operable residual heat removal (RHR) pump for each train of the emergency core cooling system (ECCS). The team found that Dominion did not mai
Region: I | Millstone | 23113 | 09/30/2008 11/10/2008 | 2008004-01 | Self - Revealed | FIN | Initiating Events | Green | (FIN 05000336/2008004-01, Installation of Incorrect Internal Trim Package in Valve 2-HD-103A Results in Reactor Trip) |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71153 | A self-revealing finding of very low safety significance (Green) was identified for Dominion's failure to ensure the proper internal trim package (cage) was installed in valve 2-HD-103A, the 1A feedwater heater level control valve as required by Millstone
Region: I | Millstone | 23118 | 09/30/2008 11/10/2008 | 2008004-02 | Self - Revealed | NCV | Initiating Events | Green | (NCV 05000336/2008004-02 Failure to Correct Safety Valve Lifting Following Uncomplicated Reactor Trips). |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified for failure to take effective corrective actions to prevent a Millstone Unit 2 (MP2) steam generator safety valve from lifting following u
Region: I | Millstone | 23112 | 08/29/2008 10/03/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Millstone | 23103 | 06/30/2008 08/12/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Fire Protection Deficiency Resulting in Potential Loss of All Charging Pumps |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000423 Millstone 3 |  | NONE | The inspectors identified a Green, NCV of the Millstone Unit 3 operating license condition 2.H, "Fire Protection," in that Dominion failed to correct a fire protection program deficiency and assure that one train of charging would remain free of fire dama
Region: I | Millstone | 23104 | 06/30/2008 08/12/2008 | 2008003-02 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Instructions Causes Reactor Coolant System Unidentified Leakage in Excess of Technical Specification Limits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 71153 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" for Dominion's failure to provide adequate maintenance instructions in the authorized work order (AWO) for replacin
Region: I | Millstone | 23099 | 03/31/2008 05/09/2008 | 2008002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate a Unit 2 Charging System Non conforming Condition against the Current Licensing Bases |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 71111.15 | The inspectors identified a finding for Dominion's failure to evaluate a non-conforming plant condition against the current licensing basis (CLB) as required by Dominion procedure OP-AA-102-1101, Revision 0, "Development of Technical Basis to Support Oper
Region: I | Millstone | 23100 | 03/31/2008 05/09/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Unacceptable Unit 2 Charging Pump Surveillance Test Data |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.22 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for Dominion's failure to adequately evaluate surveillance test results to ensure test acceptance criteria had been met on June 20, 2007. Specifi
Region: I | Millstone | 23101 | 03/31/2008 05/09/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Service Water Bypass Flow Path following a Failed IST |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000336 Millstone 2 |  | 71111.22 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to identify a condition adverse to quality after the "B" service water (SW) pump failed a Technical Specification in
Region: I | Millstone | 23105 | 02/29/2008 04/08/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to take adequate corrective actions for a condition affecting control room operability and temperature limits post-trip |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000336 Millstone 2 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to take adequate corrective actions for a condition adverse to quality involving the potential for Unit 2 control ro
Region: I | Millstone | 23110 | 02/29/2008 04/08/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to take adequate corrective actions for a Unit 2 charging system common mode failure vulnerability |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to take adequate corrective actions for a condition adverse to quality involving a longstanding degraded condition i
Region: I | Millstone | 23111 | 02/29/2008 04/08/2008 | 2008006-03 | NRC | NCV | Barrier Integrity | Green | Failure to take adequate corrective actions for a condition adverse to quality involving a non-conservative IST procedure |  |  | TE?: N | 05000336 Millstone 2 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure, in January 2005, to take adequate corrective actions for a condition adverse to quality involving a non conservativ
Region: I | Millstone | 23095 | 11/14/2007 02/07/2008 | 2007005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure ESF Building Protection from Missiles Generated by a Design Based Tornado |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.01 | Green. The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Dominion's failure to identify that the engineered safety featured (ESF) building was not adequately protected against the
Region: I | Millstone | 23096 | 11/14/2007 02/07/2008 | 2007005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Complete Specified Requirements (10CFR55.53(f)) Prior to Allowing the Operator to Resume Control Room Watch Standing Activities |  |  | TE?: N | 05000423 Millstone 3 |  | 71111.11B | Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 55.53(e) for the licensee's failure to complete the requirements of 10 CFR 55.53(f) prior to an inactive licensed operator resuming control room watchstanding duties. Specifically, bec
Region: I | Millstone | 23097 | 11/14/2007 02/07/2008 | 2007005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Core Thermal Power at or below 3411 MWTH |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000423 Millstone 3 |  | NONE | Green. A Green self-revealing non-cited violation (NCV) of Dominion Nuclear Connecticut (DNC), Inc.'s Unit 3 License, Number NPF-49, Section 2.C.(1) was identified for Dominion's failure to maintain reactor core thermal power less than or equal to 3411 me
Region: I | Millstone | 23090 | 10/05/2007 11/16/2007 | 2007007-02 | NRC | NCV | Initiating Events | Green | Auxiliary Building Fire Safe Shutdown Procedure Lacked RCP Seal Thermal Shock Precautions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000423 Millstone 3 |  | 71111.05T | The team identified a Green NCV of the Millstone Unit 3 Technical Specification 6.8.1.g, in that the procedure for shutting down the plant in response to an auxiliary building fire scenario did not provide precautions to operators to prevent thermal shock
Region: I | Millstone | 23092 | 10/05/2007 11/16/2007 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Auxiliary Shutdown Panel Reactor Head Vent Valves Not Isolated from Effects of a Control Room Fire |  |  | TE?: N | 05000423 Millstone 3 |  | 71111.05T | The team identified a Green NCV of Millstone Unit 3 operating license condition 2.H, "Fire Protection," in that Dominion did not ensure for a control room fire that the control circuits for the reactor head vent valves would not be damaged by fire when co
Region: I | Millstone | 23093 | 10/05/2007 11/16/2007 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Emergency Light Unit High Failure Rate |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000423 Millstone 3 |  | 71111.05T | The team identified a Green NCV of the Millstone Unit 3 operating license condition 2.H, "Fire Protection," in that Dominion failed to correct an adverse trend in emergency lighting unit (ELU) performance. Dominion entered this issue into the corrective a
Region: I | Millstone | 23088 | 09/30/2007 11/01/2007 | 2007004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform Fill and Vent of TPCCW Heat Exchanger Resulted in Loss of Two TPCCW Pumps |  | H.4(b) Procedural Compliance | TE?: N | 05000423 Millstone 3 |  | 71111.19 | A self-revealing finding was identified for Dominion's failure to implement procedure OP 3330B, "Turbine Plant Component Cooling Water" during restoration of the "B" turbine plant component cooling water (TPCCW) heat exchanger on August 28, 2007. Specific
Region: I | Millstone | 23087 | 06/30/2007 08/10/2007 | 2007003-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Evaluations on Boric Acid Leaks |  | H.4(b) Procedural Compliance | TE?: N | 05000423 Millstone 3 |  | 71111.08P | The inspectors identified that Dominion did not follow Boric Acid Corrosion Control program procedures. Specifically, plant personnel failed to adequately perform boric acid leak evaluations as required by Dominion procedure DNAP-1004, "Boric Acid Corrosi
Region: I | Millstone | 23079 | 06/30/2007 08/10/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Procedure for the Unit 2 'C' Charging Pump Results in Pump Failure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000336 Millstone 2 |  | 71111.12 | A self-revealing finding was identified when Dominion did not ensure an adequate work procedure was available for maintenance performed on the Unit 2 'C' charging pump on May 5, 2007, resulting in a failure of the pump on June 11, 2007. Specifically, the
Region: I | Millstone | 23086 | 06/30/2007 08/10/2007 | 2007003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Surveillance Test Data |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.19 | The inspectors identified that Dominion did not adequately evaluate surveillance test results to ensure test acceptance criteria had been met on May 10, 2007. Specifically, the inspectors identified that the 'C' charging pump pulsation dampener surveillan
Region: I | Millstone | 23078 | 06/30/2007 08/10/2007 | 2007003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Safety-Related Surveillance Procedure Resulted in 'A' Safety Injection Accumulator Inoperability |  | H.4(a) Human Error Prevention | TE?: N | 05000423 Millstone 3 |  | 71111.22 | A self-revealing finding was identified when Dominion incorrectly performed a safety-related surveillance procedure. Specifically, Operations mistakenly performed a biennial surveillance test that verified remote vent valve position by opening a nitrogen
Region: I | Millstone | 23069 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT SURVEILLANCE PROCEDURES RESULTED IN A TEMPORARY LOSS OF CONTAINMENT COOLING AND HIGH PRESSURIZER LEVEL TSAS ENTRY |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000423 Millstone 3 |  | 71111.22 | A Green self-revealing NCV of Technical Specification (TS) 6.8.1, AProcedures,@ was identified because Dominion did not adequately implement procedures while performing a surveillance to test containment isolation slave relays. This resulted in three cont
Region: I | Millstone | 23077 | 03/31/2007 05/15/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT A DEGRADED CONDITION OF THE 480V MCCS PER CRITERION XVI OF APPENDIX B TO 10 CFR PART 50 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71111.2 | A Green NRC-identified NCV of 10 CFR 50, Appendix B, Criterion XVI, ACorrective Action,@ was identified for failure to promptly correct a degraded condition associated with the air conditioning (A/C) for the B61 480 volt alternating current (VAC) motor co
Region: I | Millstone | 23061 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | FIN | Mitigating Systems | Green | INADEQUATE CONTROL OF OUTSIDE MAINTENANCE ACTIVITIES THAT RESULTED IN UNEXPECTED FLOODING OF BOTH EDG ROOMS |  | H.3(b) Work Activity Coordination | TE?: N | 05000336 Millstone 2 |  | 71111.06 | The inspectors identified a Green finding because Dominion did not adequately control outside maintenance activities that degraded the Unit 2 storm drainage system and blocked a credited surface area runoff flow path protecting the emergency diesel genera
Region: I | Millstone | 23062 | 12/31/2006 01/30/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT SURVEILLANCE PROCEDURES RESULTED IN A TEMPORARY LOSS OF SPENT FUEL POOL COOLING |  | H.4(a) Human Error Prevention | TE?: N | 05000336 Millstone 2 |  | 71111.2 | A Green self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures", was identified because Operations did not adequately implement procedures while performing a surveillance to manually cycle the "C" reactor building comp
Region: I | Millstone | 23065 | 12/31/2006 01/30/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY SCAFFOLDING RENDERED THE #1 STEAM GENERATOR MAIN STEAM ISOLATION VALVE COULD RENDER THE MAIN STEAM ISOLATION VALVLE INOPERABLE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.22 | A Green self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Dominion did not identify that scaffolding had been constructed in a manner that would interfere with the Unit 2 #1 steam generator (SG) main s
Region: I | Millstone | 23048 | 09/30/2006 11/07/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS TO PREVENT REPEAT VITAL AC 480V SWITCHGEAR COOLING DAMPER FAILURES |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000336 Millstone 2 |  | 71111.04Q | A Green self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Dominion did not take effective corrective action to prevent the east 480 volt vital AC switchgear cooling damper (2-HV-2
Region: I | Millstone | 23050 | 09/30/2006 11/07/2006 | 2006004-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IDENTIFY AN ADVERSE CONDITION AFFECTING CONTROL ROOM EMERGENCY VENTILATION PERFORMANCE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000336 Millstone 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct a condition adverse to quality affecting the "B" control room emergency ventilation (CREV) train's ability to
Region: I | Millstone | 23051 | 09/30/2006 11/07/2006 | 2006004-04 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO ACCOUNT FOR ALL SHIPPED RADIOACTIVE MATERIAL ON THE UNIFORM MANIFEST |  | H.4(b) Procedural Compliance | TE?: N | 05000423 Millstone 3 |  | 7112202 | A self-revealing NCV of 10 CFR 20, Appendix G, "Requirements for Transfers of Low-Level Radioactive Waste Intended for Disposal at Licensed Land Disposal Facilities and Manifest," was identified for failure to list on a shipping manifest all radioactive m
Region: I | Millstone | 23060 | 09/30/2006 11/07/2006 | 2006004-05 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION REQUIRED ACTIONS FOR INOPERABLE CONTAINMENT HIGH RANGE RADIATION MONITORS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000423 Millstone 3 |  | 71152 | A Green NCV was identified regarding the site engineering organization's failure to evaluate, in a timely manner, the effects that thermally induced currents (TIC) have on the operability of the Unit 3 containment high range radiation monitors(HRRM) (RMS*
Region: I | Millstone | 23040 | 06/30/2006 07/28/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | DID NOT EVALUATE AND CORRECT A SIGNIFICANT CONDITION ADVERSE TO QUALITY ASSOCIATED WITH GRAVITY FEED BORATION LINES |  |  | TE?: N | 05000423 Millstone 3 |  | 71111.04Q | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to fully evaluate and correct a significant condition adverse to quality which led to a repeat occurrence of air introduction in the gravit
Region: I | Millstone | 23042 | 06/30/2006 07/28/2006 | 2006003-02 | NRC | FIN | Mitigating Systems | Green | DID NOT IDENTIFY OR EVALUATE AIR VOIDS LOCATED IN AUXILIARY FEEDWATER SYSTEM |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.15 | The inspectors identified a finding when Dominion did not recognize that a portion of the auxiliary feedwater (AFW) discharge header contained air voids after they determined that AFW flow instrumentation was behaving erratically as a result of air in the
Region: I | Millstone | 23041 | 06/30/2006 07/28/2006 | 2006003-03 | NRC | NCV | Initiating Events | Green | DID NOT ADEQUATELY EVALUATE A REACTOR PROTECTION SYSTEM SET POINT MODIFICATION |  |  | TE?: N | 05000423 Millstone 3 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for an inadequate design change review for a steam generator low-low water level setpoint modification. Specifically, Dominion did not fully consider the impa
Region: I | Millstone | 23016 | 03/31/2006 05/05/2006 | 2006002-01 | NRC | NCV | Initiating Events | Green | MISPOSITIONING OF BORIC ACID VALVES RESULTING IN UNINTENDED POSITIVE REACTIVITY ADDITION |  |  | TE?: N | 05000423 Millstone 3 |  | 7111114 | A Green self-revealing non-cited violation of Technical Specification 6.8.1, "Procedures", was identified for adequate implementation of procedures which resulted in an unintended positive reactivity addition. On February 17, 2006, Operations personnel mi
Region: I | Millstone | 23023 | 03/31/2006 05/05/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH TS DURING WRNI SURVEILLANCES |  |  | TE?: N | 05000336 Millstone 2 |  | NONE | The inspectors identified a Green NCV for the failure to comply with TS 3.3.1.1, "Reactor Protection Instrumentation," during routine monthly surveillance testing of the Wide Range Nuclear Instrument (WRNIs). During a review of control room logs from Janu
Region: I | Millstone | 23024 | 03/03/2006 04/17/2006 | 2006006-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM EVALUATIONS ON BORIC ACID LEAKS |  |  | TE?: N | 05000336 Millstone 2 05000423 Millstone 3 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" for Dominion's failure to follow Boric Acid Corrosion Control Program (BACCP) procedures. Specifically, plant perso
Region: I | Millstone | 23025 | 03/03/2006 04/17/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO INCLUDE ACCEPTANCE CRITERIA IN MAINTENANCE PROCEDURES |  |  | TE?: N | 05000423 Millstone 3 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Criterion V, "Instructions, Procedures, and Drawings" for failing to include appropriate acceptance criteria associated with the measurement of the Unit 3 TDAFW pump governor control valve stuffing box i
Region: I | Millstone | 23035 | 03/03/2006 04/17/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE SUITABILITY OF APPLICATIONS EVALUATION FOR DAMPENER MODIFICATION |  |  | TE?: N | 05000336 Millstone 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control" associated with the Unit 2 charging system pump discharge dampener modification. Specifically, the licensee's review of the design modification failed to adequ
Region: I | Millstone | 23036 | 03/03/2006 04/17/2006 | 2006006-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE AND CORRECT CONDITION ADVERSE TO QUALITY ASSOCIATED WITH TDAFW PUMP |  |  | TE?: N | 05000423 Millstone 3 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to take effective corrective action to prevent a repeat failure of the Unit 3 turbine-driven auxiliary feedwater (TDAFW) pump. Specificall
Region: I | Millstone | 23037 | 03/03/2006 04/17/2006 | 2006006-05 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IMPLEMENT EFFECTIVE CORRECTIVE ACTIONS ASSOCIATED WITH REPETITIVE LLRT FAILURES |  |  | TE?: N | 05000423 Millstone 3 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action", for failure to take adequate corrective actions to prevent repetitive local leak rate test failures associated with the Unit 3 reactor plant chilled water
Region: I | Millstone | 125138 | 08/12/2019 |  |  | LIV |  | Green | Failure to properly assess and manage the increased risk associated with a service water pump swap. |  |  | TE?: N | 05000336 Millstone 2 |  | 71111.13
Region: I | Millstone | 125566 | 09/19/2019 |  |  | LIV |  | Green | Licensee identified violation of cyber security program |  |  | TE?: N | 05000336 Millstone 2 |  | 71152
Region: I | Nine Mile Point | 126200 | 12/31/2019 02/05/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulted in Unplanned Reactor Core Isolation Cooling System Isolation and Unavailability |  | H.12 - Avoid Complacency | TE?: N | 05000410 Nine Mile Point 2 | Human Performance | 71152 | A self-revealed Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures and Drawings,” was identified at Unit 2 when Exelon maintenance personn
Region: I | Nine Mile Point | 125693 | 09/30/2019 11/06/2019 | 2019003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Obtain Station ALARA Committee Approval for a Dose Estimate Change Which Resulted in Collective Dose Greater Than 5 Person-Rem and Exceeding the Estimate by More Than 50 Percent |  | H.4 - Teamwork | TE?: N | 05000220 Nine Mile Point 1 | Program & Process | 71124.02 | The inspectors identified a finding and Green NCV of Technical Specification 6.4.1, "Administrative Controls, Procedures" for Exelon's failure to follow its procedure to maintain doses As Low As Reasonably Achievable (ALARA) during the most recent Unit 1
Region: I | Nine Mile Point | 125653 | 08/30/2019 10/07/2019 | 2019010-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to promptly identify and correct deficient grease used as a lubricant for safety-related motor-operated valves. |  | P.2 - Evaluation | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 | Configuration Control | 71152B | A self-revealed Green Finding and associated NCV of 10 Code of Federal Regulation (CFR) 50, Appendix B, Criterion XVI, “Corrective Action,” was identified when Exelon failed to promptly identify and correct deficient material. Specifically, from October 2
Region: I | Nine Mile Point | 125077 | 06/30/2019 08/12/2019 | 2019002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Address and Disposition Turbine Stop Valve 13 Issues Resulted in Reactor Scram |  | NPP | TE?: N | 05000220 Nine Mile Point 1 | Procedure Quality | 71153 | A self-revealed Green finding (FIN) of PI-AA-125, “Corrective Action Program Procedure,” was identified when Exelon failed to address and disposition issues for the main steam system turbine stop valve (TSV) 13. Specifically, after issues were identified
Region: I | Nine Mile Point | 124460 | 03/31/2019 05/08/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Acceptance Criteria for Unit 2 High Pressure Core Spray Diesel Generator Hot Restart Surveillance |  | H.3 - Change Management | TE?: N | 05000410 Nine Mile Point 2 | Human Performance | 71111.15 | The NRC identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” when Exelon failed to provide adequate acceptance criteria in procedure N2-OSP-EGS-M@002, “Diesel G
Region: I | Nine Mile Point | 124714 | 03/31/2019 05/08/2019 | 2019001-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Instructions Result in a Reactor Scram |  | H.11 - Challenge the Unknown | TE?: N | 05000410 Nine Mile Point 2 | Procedure Quality | 71152 | A self-revealed Green finding was identified when Exelon failed to adequately develop work order steps, in accordance with MA-CE-716-010-1000, “Maximo Work Order Planning Manual,” Revision 3, to perform Unit 2 main generator relay testing. Specifically, E
Region: I | Nine Mile Point | 124605 | 03/31/2019 05/08/2019 | 2019001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 High Pressure Core Spray Diesel Generator Failure |  | NONE | TE?: N | 05000410 Nine Mile Point 2 | Human Performance | 71152 | The inspectors documented a self-revealed Green finding and associated non-cited violation of Unit 2 Technical Specification 5.4.1 “Procedures,” when Exelon failed to implement procedure N2-MSP-EGS-R002, "Diesel Generator Inspection Division III," Revisio
Region: I | Nine Mile Point | 25917 | 12/31/2018 02/13/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Risk Mitigation Actions Result in Loss of Decay Heat Removal and Offsite Power |  | H.5 - Work Management | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | A self-revealed Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4), “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” was identified when Exelon
Region: I | Nine Mile Point | 24652 | 09/30/2018 11/09/2018 | 2018003-01 | NRC | UNKN | Mitigating Systems | Green | Failure to Ensure that Thermal Power is Less Than or Equal to the Licensed Power Limit |  | H.1 - Resources | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | The inspectors identified a Green finding and associated non-cited violation (NCV) of the Nine Mile Point Nuclear Station Unit 2 Operating License (NPF-69), Condition 2.C(1), “Maximum Power Level,” when Exelon failed to ensure that thermal power is less t
Region: I | Nine Mile Point | 24107 | 06/30/2018 08/08/2018 | 2018002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure Proper Control of the Standby Gas Treatment System Damper Valve, 2GTS*V2000B, Within Procedures, Materials, and Design Control Measures |  | P.1 - Identification | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71111.19 | The inspectors identified a Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, when Exelon failed to ensure proper control of the SGTS damper valve 2GTS*V2000B within procedures, materials, and design control me
Region: I | Nine Mile Point | 24336 | 06/30/2018 08/08/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Causes Water Hammer Condition Resulting in Isolation and Inoperability of the 12 Train of the Emergency Water Condenser |  | H.1 - Resources | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, when Exelon did not provide appropriate quantitative or qualitative criteria and guidance to operators in proce
Region: I | Nine Mile Point | 23194 | 12/31/2017 02/13/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Main Control Room Annunciators 10 CFR 50.65(a)(2) demonstration not met. |  | H.13 - Consistent Process | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.12 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65 (a)(2), because Exelon did not adequately demonstrate that the performance of the main control room (MCR) annunciators was effectively controlled through p
Region: I | Nine Mile Point | 23173 | 12/31/2017 02/13/2018 | 2017004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Fill and Vent Procedure for Control Room Chiller Results in Unplanned LCO Entry |  | P.2 - Evaluation | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for Exelon’s failure to ensure that activities affecting quality were prescribed in a manner appropriate to the circumstances for t
Region: I | Nine Mile Point | 23171 | 12/31/2017 02/13/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination for Internal Flood Barrier |  | H.5 - Work Management | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” when Exelon failed to perform an adequate operability determination in accordance with OP-AA-108-115, “Operability Determinations,”
Region: I | Nine Mile Point | 23172 | 12/31/2017 02/13/2018 | 2017004-04 | Self - Revealed | FIN | Initiating Events | Green | Ineffective Correction Action Results in Failure of Instrument Air System |  | NPP | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a self-revealing Green finding (FIN) of CNG-CA-1.01-1000, “Corrective Action Program,” Revision 01100, because Constellation Energy Nuclear Group (CENG) failed to implement corrective actions at NMPNS Unit 2 to remove and replace
Region: I | Nine Mile Point | 32936 | 06/30/2017 08/04/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition results in Unplanned Yellow Risk Condition |  | H.4 Teamwork | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when Exelon did not assess and manage the increase in risk for online maintenance activities. Specifically
Region: I | Nine Mile Point | 32928 | 03/31/2017 05/12/2017 | 2017001-01 | NRC | NCV | Barrier Integrity | Green | Deficient Design Control of Outboard MSIV Pilot Valve Instrument Air Supply |  | H.7 Documentation | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.15 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," for Exelon's failure to correctly translate the design basis into the NMPNS Unit 1 instrument air system to
Region: I | Nine Mile Point | 23475 | 03/31/2017 05/12/2017 | 2017001-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Identify and Correct a Non-Conforming Condition in Safety-Related UPSs |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71152 | The inspectors documented a self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to identify and correct a non-conformance (an inadequate capacitor) in safety-related uninterruptable power supplies (
Region: I | Nine Mile Point | 32910 | 06/30/2016 08/08/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Ineffective Corrective Action Results in Water Intrusion to Battery Switchgear Room |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.01 | The inspectors identified a Green finding (FIN) of PI-AA-125, "Corrective Action Program," Revision 3, when Exelon failed to implement adequate corrective actions in March 2003, to prevent water intrusion into the Unit 2 normal switchgear building area at
Region: I | Nine Mile Point | 32915 | 06/30/2016 08/08/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Wide Range Level Indication Impacts Operability of HPCS and RCIC |  | P.1 Identification | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | The inspectors identified a Green NCV of Unit 2 Technical Specification (TS) 3.5.1, "Emergency Core Cooling (ECCS) Systems-Operating," and TS 3.5.3, "Reactor Core Isolation Cooling (RCIC) System," for failure to ensure all necessary attendant instrumentat
Region: I | Nine Mile Point | 32916 | 06/30/2016 08/08/2016 | 2016002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Understand Radiological Conditions Results in Unintended Exposure (Section 2RS1) |  | H.4 Teamwork | TE?: N | 05000410 Nine Mile Point 2 |  | NONE | A self-revealing NCV of TS 5.4.1 "Procedures" was identified when a worker performed a radiological work activity without notifying radiation protection personnel and, as a result, did not comply with procedure RP-AA-1008, "Unescorted Access to and Conduc
Region: I | Nine Mile Point | 32896 | 03/31/2016 05/12/2016 | 2016001-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure Leads to Failure to Manage Elevated Risk during Preventive Maintenance |  | H.8 Procedure Adherence | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | The inspectors identified a Green non-cited (NCV) of Title 10 of the Code of Federal Regulation (10 CFR) 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for Exelon's failure to take risk management acti
Region: I | Nine Mile Point | 32904 | 03/31/2016 05/12/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | 50.65(a)(4) Risk Evaluation Not Properly Performed Prior to Residual Heat Removal Heat Exchanger Testing |  | H.5 Work Management | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when Exelon did not assess and manage the in
Region: I | Nine Mile Point | 32905 | 03/31/2016 05/12/2016 | 2016001-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Tagout Results in Reactor Building Closed-Loop Cooling Drain Down Event |  | H.8 Procedure Adherence | TE?: N | 05000220 Nine Mile Point 1 |  | 71152 | A self-revealing Green non-cited violation of Technical Specification (TS) 6.4.1, "Procedures," was identified when a Unit 1 Exelon operator did not maintain proper configuration control of a plant system during a system tagout for planned maintenance. Sp
Region: I | Nine Mile Point | 32893 | 09/30/2015 11/09/2015 | 2015003-01 | Self - Revealed | FIN | Initiating Events | Green | Use of Incorrect Grounding Cart Results in Loss of Electrical Bus |  | H.11 Challenge the Unknown | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | The inspectors identified a self-revealing Green finding (FIN) for Exelon Generation Company, LLC (Exelon) personnel's failure to stop when met with unexpected conditions as required by procedure HU-AA-101, "Human Performance Tools and Verification Practi
Region: I | Nine Mile Point | 32887 | 08/28/2015 10/15/2015 | 2015009-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with Secondary Containment Leakage |  | P.2 Evaluation | TE?: N | 05000410 Nine Mile Point 2 |  | 71152B | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Actions," because between 2007 and 2015, Exelon staff did not promptly identify and correct a deficien
Region: I | Nine Mile Point | 32892 | 08/28/2015 10/15/2015 | 2015009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Rule Monitoring of Unit 1 600 VAC Breaker Super System |  | P.2 Evaluation | TE?: N | 05000220 Nine Mile Point 1 |  | 71152B | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," under section (a)(1) and (a)(2) for failing to pro
Region: I | Nine Mile Point | 32886 | 06/30/2015 08/05/2015 | 2015002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Notify Changes to Work Scope |  | H.11 Challenge the Unknown | TE?: N | 05000220 Nine Mile Point 1 |  | 71124.01 | The inspectors identified a self-revealing non-cited violation of Unit 1 Technical Specification (TS) 6.4, "Procedures," for failure to follow the planned scaffold erection work scope that resulted in two personnel receiving unplanned internal exposures.
Region: I | Nine Mile Point | 32881 | 03/31/2015 05/06/2015 | 2015001-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Declare Notice of Unusual Event Following Sodium Bisulfite Spill in Unit 1 Screenhouse |  | H.11 Challenge the Unknown | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | The inspectors documented a Green NRC-identified NCV of 10 CFR 50.54(q)(2) when Exelon failed to declare a Notice of Unusual Event Emergency Action Level (EAL) (HU3.1) when entry conditions were met. Specifically, on February 4, 2015, between 9:55 a.m. an
Region: I | Nine Mile Point | 32882 | 03/31/2015 05/06/2015 | 2015001-02 | NRC | FIN | Initiating Events | Green | Failure to Perform an Adequate Review of Planned Work Activities Results in a Manual Reactor Scram |  | H.12 Avoid Complacency | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | The inspectors documented a self-revealing Green finding (FIN) for Exelon's failure to properly review a work package associated with the replacement of a reactor vessel level recorder as required by MA-AA-716-234, "FIN Team Process," Revision 8. Specific
Region: I | Nine Mile Point | 32876 | 12/31/2014 02/05/2015 | 2014005-03 | NRC | NCV | Barrier Integrity | Green | Missed Surveillance Test of Alternate Decay Heat Removal Secondary Conainment Isolation Valves |  | H.12 Avoid Complacency | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.12 | [DRAFT] The ADH removal system is a non-safety-related system used to remove decay heat from the spent fuel pool (SFP) and the reactor core during shutdown conditions. It consists of two loops-a primary loop that circulates hot water from the SFP to a hea
Region: I | Nine Mile Point | 32862 | 10/10/2014 11/20/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Deficient Design Control of Unit 1 Electrical Calculations to Evaluate Minimum Voltages to Class 1E Accident Initiated Motors and MOVs during a Design Basis Event |  | P.5 Operating Experience | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The inspectors identified a Green non-cite violation of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for failure to verify and assure in Unit 1 design basis calculations that adequate voltages would be
Region: I | Nine Mile Point | 32863 | 10/10/2014 11/20/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Deficient Design Control of Unit 1 Electrical Protection Design to Ensure Survivability of Safety-Related Loads during a LOCA Coincident with Sustained Degraded Voltage |  | P.5 Operating Experience | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The inspectors identified a Green non-cited violation of Title 10 of The Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for failure to verify the adequacy of Unit 1 electrical design during a design basis loss-of-coolant
Region: I | Nine Mile Point | 32864 | 10/10/2014 11/20/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Deficient Design Control of Protective Device Sizing for Unit 1 Core Spray Injection Motor-Operated Valves |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The inspectors identified a Green non-cited violation of Title 10 of The Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," because Exelon Generation Company, LLC (Exelon) did not verify the design adequacy of Unit 1 electri
Region: I | Nine Mile Point | 32858 | 09/30/2014 11/04/2014 | 2014004-01 | NRC | FIN | Barrier Integrity | Green | Loss of Secondary Containment due to Loss of Auxiliary Boiler System |  | H.1 Resources | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | The inspectors identified a Green finding (FIN) of CNG-PR-1.01-1005, "Control of Technical Procedure Format and Content," Revision 00500, because Exelon Generation Company, LLC (Exelon) provided Unit 2 operators with an inadequate auxiliary boiler system
Region: I | Nine Mile Point | 32841 | 06/30/2014 08/07/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Testing of Reactor Core Isolation Cooling during 165 psig Reactor Pressure Test for Surveillance Requirement 3.5.3.4 |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion XI, "Test Control," due to Exelon Generation (Exelon) staff's procedures for meeting the Unit 2 Technical Specification (TS
Region: I | Nine Mile Point | 32853 | 06/30/2014 08/07/2014 | 2014003-02 | NRC | NCV | Initiating Events | Green | Failure to Correct a Significant Condition Adverse to Quality in a Timely Manner |  | P.3 Resolution | TE?: N | 05000220 Nine Mile Point 1 |  | 71152 | The inspectors identified a non-cited violation of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to ensure that corrective actions to preclude repetition for a significant condition advers
Region: I | Nine Mile Point | 32854 | 06/30/2014 08/07/2014 | 2014003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Spent Fuel Cooling Pump due to Inadequate Procedures |  | H.11 Challenge the Unknown | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing non-cited violation of Technical Specification 5.4.1, "Procedures," was identified at Unit 2 for Exelon Generation's (Exelon's) failure to provide procedures to override valve 2SFC*AOV154, filters inlet isolation valve, prior to loss of o
Region: I | Nine Mile Point | 32857 | 06/30/2014 08/07/2014 | 2014003-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify Single-Point Vulnerabilities Results in a Manual Reactor Scram |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing Green Finding (FIN) was identified at Unit 2 against procedure CNG-AM-1.01-2000, "Scoping and Identification of Critical Components," Revision 00200. Specifically, Exelon Generation (Exelon) staff performed an inadequate AP-913 evaluation
Region: I | Nine Mile Point | 32831 | 03/31/2014 04/28/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Measures Employed During Control Room HVAC Modification |  | H.5 Work Management | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.18 | The inspectors identified a Green non-cited violoation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," because Constellation Energy Nuclear Group, LLC (CENG) did not implement adequate design contro
Region: I | Nine Mile Point | 32840 | 03/31/2014 04/28/2014 | 2014002-02 | NRC | NCV | Initiating Events | Green | Invalid Low Reactor Water Level results in Unit 2 Automatic Reactor Scram |  | H.14 Conservative Bias | TE?: N | 05000410 Nine Mile Point 2 05000410 Nine Mile Point 2 |  | 71153 | The inspectors documented a self-revealing Green non-cited violation of Technical Specification (TS) 5.4, "Procedures," for Constellation Energy Nuclear Goup's, LLC (CENG's) failure to ensure proper communication of a change in work scope prior to impleme
Region: I | Nine Mile Point | 32829 | 12/31/2013 02/10/2014 | 2013005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Surveillance Test for Unit 1 Smoke Removal Dampers |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.12 | The inspectors identified a Green NCV of Unit 1 license condition DPR-63, Section 2.D(7), "Fire Protection," because CENG staff did not perform visual inspections of fire dampers associated with Unit 1 between 2002 and 2013 in accordance with the Fire Pro
Region: I | Nine Mile Point | 32830 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Procedural Requirements for Evaluating Control Room Deficiencies as Operator Workarounds |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a Green finding (FIN) for CENG staff's failure to properly classify operator workarounds, operator burdens, or control room deficiencies in accordance with CNG-OP-1.01-2010, "Operator Workaround/Challenge Control," Revision 0. Sp
Region: I | Nine Mile Point | 32816 | 12/01/2013 12/10/2013 | 2013010-01 | Self - Revealed | NCV | Initiating Events | Green | Improper Bus Restoration Results in a Loss of Shutdown Cooling |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000220 Nine Mile Point 1 |  | NONE | The inspectors documented a violation of Unit 1 Technical Specification (TS) 6.4.1, "Procedures," because Constellation Energy Nuclear Group (CENG) failed to properly restore from a loss of a vital direct current (DC) bus in accordance with station off
Region: I | Nine Mile Point | 32817 | 12/01/2013 12/10/2013 | 2013010-02 | NRC | FIN | Initiating Events | Green | Configuration Control error results in loss of a vital DC Bus |  | H.4(a) Human Error Prevention | TE?: N | 05000220 Nine Mile Point 1 |  | NONE | The inspectors documented a self-revealing Green finding of CENG's Conduct of Maintenance procedure, CNG-MN-1.01-1000, because CENG personnel failed to verify they were on the proper equipment prior to commencing maintenance activities. Additionally, R
Region: I | Nine Mile Point | 32827 | 08/23/2013 10/01/2013 | 2013007-01 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct a Condition Adverse To Quality Associated With HPCS Medium Voltage Power Supply Cables |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000410 Nine Mile Point 2 |  | 71152B | The inspectors identified an NCV of 10 CFR 50, Appendix B Criterion XVI, "Corrective Actions," because between November 5, 2012, and July 22, 2013, NMPNS did not promptly identify and correct a failed automatic de-watering system for the buried high pr
Region: I | Nine Mile Point | 32811 | 06/30/2013 08/13/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Containment Isolation System Surveillance Procedure Resulting in Isolation of the Reactor Coolant Isolation Cooling Isolation |  | H.4(a) Human Error Prevention | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing non-cited violation of Technical Specification 5.4.1, "Procedures," was identified at Unit 2 when a Constellation Energy Nuclear Group (CENG) instrumentation and control (I&C) technician did not properly implement procedure N2-ISP-LDS-Q01
Region: I | Nine Mile Point | 32814 | 06/30/2013 08/13/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Implementation for Battery Cell Replacement |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a non-cited violation at Unit 2 of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Constellation Energy Nuclear Group (CENG) did not assure
Region: I | Nine Mile Point | 32815 | 06/30/2013 08/13/2013 | 2013003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Battery Sizing Calculation |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a non-cited violation at Unit 2 of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," because Constellation Energy Nuclear Group (CENG) did not verify the adequacy of the de
Region: I | Nine Mile Point | 32807 | 06/30/2013 08/13/2013 | 2013003-04 | NRC | NCV | Initiating Events | Green | Improper Bus Restoration Results in a Loss of Shutdown Cooling | EA Case: 2013186 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A self-revealing apparent violation of Technical Specification 6.4.1, "Procedures," was identified at Unit 1 because Constellation Energy Nuclear Group (CENG) failed to properly recover from a loss of a vital direct current (DC) bus in accordance with sta
Region: I | Nine Mile Point | 32810 | 06/30/2013 08/13/2013 | 2013003-05 | Self - Revealed | NCV | Barrier Integrity | Green | Containment Leakage Exceeds Technical Specification 3.3.3 Limits |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A self-revealing non-cited violation of Technical Specification (TS) 3.3.3, "Leakage Rate," was identified for Constellation Energy Nuclear Group's (CENG) failure from December 3 to December 13, 2012, to maintain containment leakage less than 1.5 percent
Region: I | Nine Mile Point | 32796 | 03/31/2013 05/09/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Rule Monitoring of the Leak Detection System Performance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.12 | The inspectors identified an non-cited violation of Title 10 of the Code of Federal Regulations 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," under section (a)(1) of the rule for failing to properly monitor
Region: I | Nine Mile Point | 32801 | 03/31/2013 05/09/2013 | 2013002-02 | Self - Revealed | FIN | Initiating Events | Green | Test Conditions Not Properly Established |  | H.4(a) Human Error Prevention | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.22 | A self-revealing finding (FIN) was identified for the failure of CENG, maintenance personnel to ensure appropriate conditions were established during a surveillance test to confirm the lockup valves for flow control valve (FCV)-29-137 were properly functi
Region: I | Nine Mile Point | 32803 | 03/31/2013 05/09/2013 | 2013002-04 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedure Change Review Results in Reactor Scram |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A self-revealing finding (FIN) was identified for CENG's failure to perform a cross-disciplinary engineering review in 2003, as required by station procedures, of the amplidyne excitation system operation setting. On September 20, 2012, Unit 1 experienced
Region: I | Nine Mile Point | 32806 | 03/31/2013 05/09/2013 | 2013002-05 | NRC | NCVIV | Initiating Events | Green | Failure to Perform a 50.59 Evaluation for a Procedure Change |  |  | TE?: Y SL-IV-NCVIV | 05000220 Nine Mile Point 1 |  | 71153 | The inspectors identified a Severity Level IV non-cited violation (NCV) and associated Green finding (FIN) of Title 10 of the Code of Federal Regulations (10 CFR) 50.59, "Changes, Tests and Experiments," because Unit 1 failed to perform a written 50.59 ev
Region: I | Nine Mile Point | 32791 | 12/31/2012 02/11/2013 | 2012005-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Develop Adequate Inspection Requirements for Main Transformer Modification Results in Reactor Scram |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.04Q | A self-revealing Green finding (FIN) was identified for Nine Mile Point Nuclear Station, LLC. (NMPNS's) failure to develop adequate inspection requirements for the Unit 1 main transformer replacement. As a result, improper configuration of the main tran
Region: I | Nine Mile Point | 32794 | 12/31/2012 02/11/2013 | 2012005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Post Maintenance Test Results in Subsequent Failure of 11 CREVS Fan |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.19 | A self-revealing Green NCV of TS 6.4.1 occurred because NMPNS failed to develop an adequate post maintenance test (PMT) to determine operability of the 11 control room emergency ventilation system. Specifically, troubleshooting on December 2 failed to i
Region: I | Nine Mile Point | 32927 | 12/31/2012 02/11/2013 | 2012005-04 | NRC | URI | Barrier Integrity | Green | Assessment of Containment Leakage Due to Containment Isolation Valve Failure |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71153
Region: I | Nine Mile Point | 32782 | 09/30/2012 11/09/2012 | 2012004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Implementation of Operational Decision Making Issues Monitoring Plan for EPR Results in ReactorScram |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.12 | A self-revealing Green finding (FIN) was identified for NMPNS' failure to adequately implement the monitoring activities specified in the operation decision making issues (ODMI) plan for the Unit 1 electronic pressure regulator (EPR) in accordance with
Region: I | Nine Mile Point | 32783 | 09/30/2012 11/09/2012 | 2012004-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Evaluation and Implementation of Design Modifications to the Turbine Gland Seal Supply System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.18 | A self-revealing Green finding (FIN) was identified for NMPNS' failure to properly evaluate and implement plant design changes on the Unit 2 turbine gland seal steam supply system. Specifically, incorrect implementation of ECP-11-000977, "Turbine Gland
Region: I | Nine Mile Point | 32784 | 09/30/2012 11/09/2012 | 2012004-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Installation Instructions for Control Rod Blade Storage Rack |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.18 | A self-revealing Green finding (FIN) was identified for NMPNS' failure to provide adequate instructions for the installation of a control rod blade storage rack in the Unit 1 spent fuel pool. Specifically, certain critical steps were missing from the in
Region: I | Nine Mile Point | 32789 | 09/30/2012 11/09/2012 | 2012004-04 | Self - Revealed | FIN | Public Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Refueling Activities |  | H.3(a) Work Planning | TE?: N | 05000410 Nine Mile Point 2 |  | NONE | A self-revealing Green finding (FIN) was identified due to NMPNS having unplanned, unintended occupational collective dose resulting from deficiencies in As Low As Reasonably Achievable (ALARA) planning and work control while performing refueling activ
Region: I | Nine Mile Point | 32776 | 06/30/2012 08/03/2012 | 2012003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Spent Fuel Pool Cooling due to Inadequate Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | A self-revealing NCV of TS 5.4.1, "Procedures," was identified for NMPNS' failure to provide an adequate procedure for spent fuel pool (SFP) cooling system restoration. Specifically, procedure N2-PM-082, "RPV Floodup/Draindown," Revision 00600, did not co
Region: I | Nine Mile Point | 32777 | 06/30/2012 08/03/2012 | 2012003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Corrective Action for Instrument Fill and Vent Activities |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.19 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for NMPNS' failure to effectively implement corrective actions. Specifically, NMPNS's corrective actions from a differential fill and vent evolution whi
Region: I | Nine Mile Point | 32778 | 06/30/2012 08/03/2012 | 2012003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Special Operating Procedure for Loss of Spent Fuel Pool Cooling |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified for NMPNS' failure to provide an adequate special operating procedure for loss of SFP cooling. On May 25, 2012, following a loss of SFP cooling, the inadequate procedural guidance delaye
Region: I | Nine Mile Point | 32774 | 03/31/2012 05/04/2012 | 2012002-01 | Self - Revealed | FIN | Initiating Events | Green | Did Not Correctly Implement Procedure During Power Supply Transfer |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.13 | A Green self-revealing finding was identified for the failure of Nine Mile Point Nuclear Station (NMPNS) to properly implement procedure N1-OP-30, "4.16 kV, 600V and 480V House Service," Revision 02800 when shifting the power supply for power board (PB) 1
Region: I | Nine Mile Point | 32775 | 03/31/2012 05/04/2012 | 2012002-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Torque Applied to Shutdown Cooling Isolation Valve Closure Bolts |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A Green self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified due to NMPNS' failure to adequately implement Standard Design Specification SDS-006, "Bolt-Torque Requirements for Unit 1 and U
Region: I | Nine Mile Point | 32767 | 12/31/2011 01/27/2012 | 2011005-01 | NRC | FIN | Barrier Integrity | Green | Troubleshooting Approach Not Consistent With Technical Specification Bases |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | The inspectors identified a Green finding for the failure of NMPNS to follow the technical specifications (TS) bases associated with limiting condition for operation (LCO) 3.0.2. Specifically on October 24, 2011, on three separate occasions, NMPNS entered
Region: I | Nine Mile Point | 32771 | 12/31/2011 01/27/2012 | 2011005-02 | NRC | FIN | Initiating Events | Green | Failure to Meet Fleet Standards for Preventive Maintenance Templates |  | H.4(b) Procedural Compliance | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71152 | The inspectors identified a Green finding for the failure of NMPNS to meet the fleet standard for establishing and implementing preventive maintenance (PM) templates. Specifically, in 2009, NMPNS failed to implement PM templates for critical non-safety re
Region: I | Nine Mile Point | 32772 | 12/31/2011 01/27/2012 | 2011005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Valve Packing Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A Green self-revealing NCV of technical specification (TS) 5.4.1, "Procedures," was identified for NMPNS' failure to properly implement S-MMP-GEN-201, "Site Valve Packing Procedure," Revision 00600 when maintenance personnel repacked recirculation pump di
Region: I | Nine Mile Point | 32773 | 12/09/2011 01/23/2012 | 2011011-01 | NRC | NCV | Mitigating Systems | Green | Vital Bus Degraded Voltage Time Delay Not Maintained Within LOCA Analysis Assumptions |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71152 | The inspector identified a finding of very low safety significance (Green) irwotving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion lll "Design Control," in that station personnel did not implement appropriate measures to ensure design
Region: I | Nine Mile Point | 32764 | 09/30/2011 11/10/2011 | 2011004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Actions to Prevent Vibration Induced Failure on a Socket Weld for a Vent Line on the 'A' FWP Minimum Flow Line |  | P.2(b) Implementing Operating Experience | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A Green self revealing finding was identified for inadequate implementation of corrective actions regarding vibration induced failures of socket welds. This finding resulted in an August 11, 2011, Nine Mile Unit 2 scram due to a failed socket weld on the
Region: I | Nine Mile Point | 32763 | 06/30/2011 07/29/2011 | 2011003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedural Guidance for Main Turbine and Generator Maintenance Activities |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A Green self revealing finding for inadequate procedural guidance was identified. The inadequate procedural guidance resulted in a May 2, 2011 Nine Mile Unit 1 scram due to a turbine trip. NMPNS determined that the turbine tripped when the main turbine ma
Region: I | Nine Mile Point | 31730 | 03/31/2011 05/11/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Identification and Corrective Actions for Emergency Diesel Generator Temperature Control Valve Degradation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing finding of very low safety significance associated with a non-cited violation (NCV) of 10 CFR Part 50, Criterion XVI, "Corrective Action," was identified following a monthly surveillance test (ST) on January 18, 2011, when Unit 2 operator
Region: I | Nine Mile Point | 32757 | 03/31/2011 05/11/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions to Correct Motor Control Center Spring Clip Engagement Issues |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000220 Nine Mile Point 1 |  | 71152 | The inspectors identified a finding of very low safety significance associated with a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for Nine Mile Point Nuclear Station's (NMPNS) failure to take adequate corre
Region: I | Nine Mile Point | 31723 | 12/31/2010 01/19/2011 | 2010005-01 | Self - Revealed | NCV | Initiating Events | Green | Reactor Scram due to Inadequate Post-Maintenance Testing |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71153 | A self-revealing finding of very low safety significance associated with a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "lnstructions, Procedures, and Drawings," was identified when previously unidentified inadequate electrical
Region: I | Nine Mile Point | 31721 | 09/30/2010 11/02/2010 | 2010004-01 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During RHR System Modification |  | H.3(b) Work Activity Coordination | TE?: N | 05000410 Nine Mile Point 2 |  | 71124.02 | A self-revealing finding of very low safety significance was identified due to Nine Mile Point Nuclear Station (NMPNS) having unplanned, unintended occupational collective dose resulting from deficiencies in "as low as is reasonably achievable" (ALARA)
Region: I | Nine Mile Point | 31722 | 09/30/2010 11/02/2010 | 2010004-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Refueling Floor Activities |  | H.3(a) Work Planning | TE?: N | 05000410 Nine Mile Point 2 |  | 71124.02 | A self-revealing finding of very low safety significance was identified due to Nine Mile Point Nuclear Station (NMPNS) having unplanned, unintended occupational collective dose resulting from deficiencies in "as low as is reasonably achievable" (ALARA)
Region: I | Nine Mile Point | 31720 | 06/30/2010 08/03/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Excessive Reactor Pressure Vessel Drain Down due to Inadequate Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.2 | A self-revealing finding of very low safety significance associated with a non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was identified when Nine Mile Point Nuclear Station (NMPNS) Unit 2 operators used an inadequate procedu
Region: I | Nine Mile Point | 31717 | 03/30/2010 05/06/2010 | 2010002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Maintenance Procedure Results in Loss of Loads for Non-Vital UPS |  | H.3(b) Work Activity Coordination | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | A self-revealing finding of very low safety significance was identified for inadequate coordination during concurrent execution of a maintenance procedure and an operating procedure, which resulted in a loss of power to the loads supplied by Unit 2 uninte
Region: I | Nine Mile Point | 31718 | 03/30/2010 05/06/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Performance Testing of Division 1 Battery |  | H.4(b) Procedural Compliance | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.18 | An NRC-identified finding of very low safety significance associated with a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified, in that Unit 2 Division 1 vital battery, 2BYS*BAT2A (the 2A battery), perfor
Region: I | Nine Mile Point | 31719 | 03/30/2010 05/06/2010 | 2010002-03 | NRC | NCV | Initiating Events | Green | Reactor Scram due to Inadequate Procedure for RHR Detector Restoration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing finding of very low safety significance associated with a non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was identified when technicians used an inadequate procedure for filling and venting a Unit 2 residual
Region: I | Nine Mile Point | 31708 | 12/31/2009 01/29/2010 | 2009005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Two APRMs Inoperable Contrary to Procedure Requirement |  | H.4(b) Procedural Compliance | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.13 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.4, "Procedures," was identified when Unit 1 operators removed average power range monitor (APRM) 18 from service for maintenance while APRM 14 was inoperable due to a detector ma
Region: I | Nine Mile Point | 31709 | 12/31/2009 01/29/2010 | 2009005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement the Operator Workaround Program During 2009 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71152 | An NRC-identified finding was identified on November 19, 2009, when inspectors determined the NMPNS Operator Workaround program had not been implemented at Unit 1 and Unit 2 in accordance with Nuclear Administration Instruction NAI-REL-02, "Control of Ope
Region: I | Nine Mile Point | 31704 | 10/23/2009 12/04/2009 | 2009010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Scope the SPDS Function of the Plant Process Computer Into the Maintenance Rule |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50.65 b(2) for failure to properly scope the Safety Parameter Display System (SPDS) function of the Unit 1 Plant Process Computer into the Maintenance Rule. As a result, a required Structure, System, and Com
Region: I | Nine Mile Point | 31705 | 10/23/2009 12/04/2009 | 2009010-02 | NRC | NCV | Mitigating Systems | Green | Deficient Control of Plant Staff Overtime |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000220 Nine Mile Point 1 |  | 71152B | The inspectors identified a Green NCV of Unit 1 TS 6.2.2.d, "Unit Staff," for not properly implementing and maintaining procedures for controlling plant staff work hours of personnel performing safety-related activities. Constellation management authorize
Region: I | Nine Mile Point | 31695 | 10/16/2009 11/24/2009 | 2009009-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify procedural inadequacies and non-compliances that contributed to the November 4, 2008 SW pumps foreign material intrusion events. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000410 Nine Mile Point 2 |  | 95001 | The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving two examples of conditions adverse to quality not properly identified and corrected. For the first example, Constellation failed to ident
Region: I | Nine Mile Point | 31694 | 09/30/2009 11/02/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Unqualified HPCS Pump Power Cables Used in Submerged Conditions |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | An NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified, in that Nine Mile Point Nuclear Station (NMPNS) failed to maintain the Unit 2 high pressure core spray (HPCS) pump power cables in
Region: I | Nine Mile Point | 31689 | 06/30/2009 07/27/2009 | 2009003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Startup Procedure for Second Stage Reheaters Leads to Turbine Trip |  | H.4(b) Procedural Compliance | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.2 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.4, "Procedures," was identified when operators did not follow the operating procedure when placing the Unit 1 second stage main steam reheaters in service during plant power asce
Region: I | Nine Mile Point | 31693 | 06/19/2009 08/03/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Brigade Training Program Procedure | EA Case: 2009191 | H.4(b) Procedural Compliance | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71111.05T | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Unit 1 Technical Specifications, section 6.4.1 and Unit 2 Technical Specifications, section 5.4.1., for NMPNS's failure to correctly implement the fir
Region: I | Nine Mile Point | 31683 | 03/31/2009 05/07/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Instructions Result in Residual Heat Removal System Voiding |  | P.2(b) Implementing Operating Experience | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when inadequate instructions for maintenance that had previously been performed on the Unit 2 residual heat rem
Region: I | Nine Mile Point | 31687 | 03/31/2009 05/07/2009 | 2009002-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Main Steam Isolation Valve Troubleshooting |  | P.2(b) Implementing Operating Experience | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.22 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when use of an inadequate maintenance procedure resulted in unanticipated partial closure of Unit 1 main steam
Region: I | Nine Mile Point | 31688 | 03/31/2009 05/07/2009 | 2009002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Perform Standby Liquid Control System Surveillance |  | H.4(a) Human Error Prevention | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was identified on January 30, 2009, when operators did not align the Unit 2 Division 2 Standby Liquid Control (SLC) system in accordance with the surveillance pr
Region: I | Nine Mile Point | 31681 | 12/30/2008 01/26/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | Untimely Corrective Action for Degraded Service Water Pumps |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | An NRC-identified Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified on November 8, 2008 in that Nine Mile Point Nuclear Station (NMPNS) did not take prompt action to verify that service water (SW)
Region: I | Nine Mile Point | 31674 | 10/31/2008 12/15/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Unit 1 600V MCC Control Circuit Voltage Drop Calculations |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that Constellation had used non-conservative inputs in voltage drop calculations with respe
Region: I | Nine Mile Point | 31676 | 10/31/2008 12/15/2008 | 2008008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Regarding Adequacy of Safety Bus Allowable Degraded Voltage Relay Reset Setpoint and Impact on Offsite Power Supply |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000410 Nine Mile Point 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that Constellation did not verify the adequacy of design with respect to ensuring the availab
Region: I | Nine Mile Point | 31680 | 10/20/2008 04/23/2008 | 2008301-01 | NRC | FIN | Mitigating Systems | Green | Inappropriate EOP Guidance |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | NONE | A Green finding was identified by the NRC because senior reactor operators were trained to interpret and execute the Primary Containment Control Emergency Operating Procedure (EOP-PC) step PCP-10 in accordance with guidance of the Transient Mitigation Gui
Region: I | Nine Mile Point | 31673 | 09/29/2008 11/05/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Risk Assessment for RCIC Unavailability |  | H.3(a) Work Planning | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.13 | An NRC-identified non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified for inaccurate risk assessments completed for August 5 and 6, 2008. Specifically, the unavailable reactor core isolation cooling (RCIC) system was not properly incorporated i
Region: I | Nine Mile Point | 31672 | 09/29/2008 11/05/2008 | 2008004-02 | NRC | FIN | Initiating Events | Green | Inadequate Maintenance Practices Result in a Plant Transient |  | H.3(a) Work Planning | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing finding was identified on July 14, 2008, when inadequate maintenance practices, during replacement and troubleshooting of a Unit 2 radioactive waste sump pump, caused an electrical transient that resulted in the loss of numerous plant com
Region: I | Nine Mile Point | 31668 | 07/31/2008 09/11/2008 | 2008007-01 | NRC | FIN | Initiating Events | Green | Failure to perform a technical evaluation or restore a nonconformance to the original design requirement |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71152 | A self revealing Green finding was identified because Constellation failed to either perform a technical evaluation or restore a nonconforming condition to the original design requirement which resulted in a failure of the Unit 2 instrument air piping on
Region: I | Nine Mile Point | 31660 | 06/30/2008 07/29/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Meet TS Oversight Requirement |  | H.4(a) Human Error Prevention | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.13 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.1, "Responsibility," was identified on April 26, 2008, when the Unit 1 shift manager (SM) left the control room without designating another senior reactor operator (SRO) qualifie
Region: I | Nine Mile Point | 31661 | 06/30/2008 07/29/2008 | 2008003-02 | NRC | FIN | Initiating Events | Green | Untimely Corrective Action for IA System Corrosion Resulted in Reactor Feedwater Valve Malfunction |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.2 | A self-revealing finding was identified on April 18, 2008, when NMPNS failed to take appropriate corrective actions to address corrosion products in the instrument air (IA) system in a timely manner, which led to an accumulation of water in the Unit 2 IA
Region: I | Nine Mile Point | 31665 | 06/30/2008 07/29/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Evaluate the Effect of Accelerated Aging of J-10 Relays |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing non-cited violation (NCV) of 10 CRF 50, Appendix B, Criterion XVI, "Corrective Action," was identified on March 22, 2008, when the Unit 2 Division I emergency diesel generator (EDG) service water (SW) return isolation valve failed to full
Region: I | Nine Mile Point | 31666 | 06/30/2008 07/29/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Control Operations Staff Overtime |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71152 | An NRC-identified non-cited violation (NCV) of Unit 1 Technical Specification (TS) 6.2.2 and Unit 2 TS 5.2.2, "Unit Staff," was identified for not properly implementing and maintaining procedures for controlling plant staff work hours of personnel perform
Region: I | Nine Mile Point | 31667 | 06/30/2008 07/29/2008 | 2008003-05 | NRC | NCV | Mitigating Systems | Green | Repetitive Improper Authorization and Evaluation of Overtime Deviations |  | P.1(b) Trend Performance CAP | TE?: N | 05000220 Nine Mile Point 1 05000410 Nine Mile Point 2 |  | 71152 | A non-cited violation (NCV) of Unit 1 Technical Specification (TS) 6.2.2 and Unit 2 TS 5.2.2, "Unit Staff," was identified by the inspectors for a recurring trend of operations personnel being required to stand 24 hour shifts in order to ensure adequate s
Region: I | Nine Mile Point | 31659 | 03/31/2008 05/06/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Perform Procedure Caused Inadvertent Isolation of RCIC Steam Supply |  | H.4(a) Human Error Prevention | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing, non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was identified on January 14, 2008, when technicians improperly performed a surveillance procedure which resulted in isolation of the Unit 2 RCIC system. Specif
Region: I | Nine Mile Point | 31654 | 12/29/2007 02/08/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate RCIC Room Temperature Channel Checks |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | An NRC-identified NCV of Unit 2 TS 3.3.6.1, "Primary Containment Isolation Instrumentation," occurred when NMPNS failed to perform Technical Specification (TS) required channel checks of the reactor core isolation cooling (RCIC) room area temperature inst
Region: I | Nine Mile Point | 31658 | 12/29/2007 02/08/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Loss of Shutdown Cooling due to Inadequate Maintenance Planning |  | H.3(b) Work Activity Coordination | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.2 | A self-revealing NCV of Unit 2 TS 5.4, "Procedures," occurred when NMPNS failed to adequately implement procedure GAP-PSH-01, "Work Control," while Unit 2 was in the refueling mode. Specifically, an unanticipated loss of shut down cooling (SDC) occurred b
Region: I | Nine Mile Point | 31651 | 09/28/2007 11/07/2007 | 2007004-01 | NRC | NCV | Initiating Events | Green | Inadequate CCP system venting procedure resulted in loss of main CCP pumps |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing Green NCV of Unit 2 Technical Specification (TS) 5.4, "Procedures," occurred when an inadequate procedure was used to vent the reactor building closed loop cooling water (CCP) system which resulted in tripping both CCP pumps on low suctio
Region: I | Nine Mile Point | 31652 | 09/28/2007 11/07/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Installation of a Design Change Resulted in Inadvertent Discharge of the CO2 Suppression System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing Green NCV of Unit 2 TS 5.4, "Procedures," occurred when an inadequate procedure was used for installation of a fire protection modification. Specifically, the installation procedure enabled plant technicians to establish an electrical cir
Region: I | Nine Mile Point | 31649 | 06/29/2007 06/27/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure To Take Action Per Operating Experience Results In Two Inoperable IRM Channels During Reactor Startup |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.2 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," occurred when NMPNS failed to identify and correct a condition adverse to quality, associated with two of the four Unit 1 intermediate range monitor (IRM) instrument
Region: I | Nine Mile Point | 31650 | 06/29/2007 06/27/2007 | 2007003-02 | NRC | NCV | Barrier Integrity | Green | Procedural Noncompliance Resulted In Failure to Establish Primary Containment Prior to Reactor Startup. |  | H.4(b) Procedural Compliance | TE?: N | 05000220 Nine Mile Point 1 |  | 71111.2 | A self-revealing Green NCV of Unit 1 TS 6.4, "Procedures," occurred on April 2, 2007, when operators failed to resolve a position discrepancy identified with respect to the emergency cooling system (EC) vent line isolation valves prior to reactor startup
Region: I | Nine Mile Point | 31648 | 03/31/2007 04/30/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Caused Inadvertent Isolation of RCIC Steam Supply |  | H.4(a) Human Error Prevention | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.22 | A self-revealing, non-cited violation (NCV) of technical specification (TS) 5.4, "Procedures," was identified on January 11, 2007, when the Unit 2 reactor core isolation cooling (RCIC) system automatically isolated as a result of an improperly performed s
Region: I | Nine Mile Point | 31645 | 01/18/2007 02/13/2007 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Integrity of Unit 2 Examinations and Tests |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000410 Nine Mile Point 2 |  | NONE | A Green NRC-identified non-cited violation (NCV) of 10CFR55.49 was identified, concerning an apparent compromise of the 2006 annual operating requalification examinations at Unit 2. NRC inspectors identified practices that collectively had the impact of c
Region: I | Nine Mile Point | 31646 | 01/18/2007 02/13/2007 | 2006011-03 | NRC | FIN | Mitigating Systems | Green | Unit 1 Crew Failure Rate on the Dynamic Simulator Portion of the Annual Operating Examinations |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | NONE | A finding of very low safety significance (Green) was identified at Unit 1. The finding was associated with crew performance on the simulator during the 2006 facility-administered requalification examinations. Of the six crews evaluated, two failed to pas
Region: I | Nine Mile Point | 31647 | 01/18/2007 02/13/2007 | 2006011-04 | NRC | FIN | Mitigating Systems | Green | Unit 2 Crew Failure Rate on the Dynamic Simulator Portion of the Annual Operating Examinations |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | NONE | A finding of very low safety significance (Green) was identified at Unit 2. The finding was associated with crew performance on the simulator during the 2006 facility-administered requalification examinations. Of the six crews evaluated, two failed to pas
Region: I | Nine Mile Point | 31641 | 10/20/2006 12/01/2006 | 2006008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Unit 1 EDG Raw Water Cooling System |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The team identified a green, non-cited violation of 10CFR50, Appendix B, Design Control, in that measures had not been established to verify or check the adequacy of the Unit 1 Emergency Diesel Generator (EDG) cooling water design. Specifically, the EDG c
Region: I | Nine Mile Point | 31642 | 10/20/2006 12/01/2006 | 2006008-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Assumptions in Safety Related Battery Sizing Calculation |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 7111121 | The team identified a green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for Constellation's failure to ensure that adequate design control measures existed to verify the adequacy of the design capacity for the Unit 1 Batt
Region: I | Nine Mile Point | 31638 | 06/30/2006 08/07/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | RCIC Alignment During Maintenance Not Consistent With Design Bases. |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71111.15 | An NRC-identified NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified on February 8, 2006, when the reactor core isolation cooling (RCIC) system was operated in an unanalyzed configuration that degraded plant safety. Specifically
Region: I | Nine Mile Point | 31639 | 06/30/2006 08/07/2006 | 2006003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate use of human performance tools during maintenance results in an equipment failure that causes a reactor scram. |  |  | TE?: N | 05000410 Nine Mile Point 2 |  | 71153 | A self-revealing finding of very low safety significance occurred on March 9, 2006, when Nine Mile Point Unit 2 automatically scrammed due to a main turbine trip caused by low condenser vacuum. The loss of condenser vacuum occurred when the normal turbine
Region: I | Nine Mile Point | 125670 | 10/07/2019 |  |  | LIV |  | Green | Failure to lock an inoperable Primary Containment Vacuum Breaker resulted in a condition prohibited by Technical Specifications |  |  | TE?: N | 05000220 Nine Mile Point 1 |  | 71152B
Region: I | Oyster Creek | 21652 | 09/30/2017 10/17/2017 | 2017003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Augmented Offgas System Procedure Resulted in a Manual Scram |  | H.12 - Avoid Complacency | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing NCV of Technical Specification 6.8.1, “Procedures and Programs,” was identified because Exelon did not adequately establish and maintain the augmented offgas (AOG) system operation procedure as required by NRC Regulatory Guide 1.33, “Qual
Region: I | Oyster Creek | 35084 | 06/30/2017 08/03/2017 | 2017002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Operability Determination of No. 2 EDG degraded fuel oil filter |  | P.2 - Evaluation | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a finding associated with Exelon procedure OP-AA-108-115, "Operability Determinations," because Exelon did not adequately assess the No. 2 emergency diesel generator operability with a degraded fuel oil filter. Specifically, Exel
Region: I | Oyster Creek | 35074 | 06/30/2016 08/02/2016 | 2016002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Maintenance Procedure associated with Reactor Recirculation Pump Seal |  |  | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing NCV of Technical Specification 6.8.1, "Procedures and Programs," was identified because Exelon did not adequately establish and maintain the reactor recirculation pump (RRP) reassembly maintenance procedures as required by NRC Regulatory
Region: I | Oyster Creek | 35060 | 03/31/2016 05/12/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Slower than Normal Scram Time of a Control Rod Drive |  | P.1 Identification | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not promptly identify and correct a condition adverse to quality. Specifically, Exelon did not identify the scram time test result for contro
Region: I | Oyster Creek | 35067 | 03/31/2016 05/12/2016 | 2016001-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Use Respiratory Protection as Required in RWP/ALARA Plan for Drywell Head Reassembly |  | H.8 Procedure Adherence | TE?: N | 05000219 Oyster Creek |  | 71124.01 | A self-revealing Green NCV of Technical Specification 6.8.1, "Procedures and Programs" was identified for Exelon's failure to use respiratory protection, as required in the radiation work permit (RWP)/as low as reasonably achievable (ALARA) plan 14-406 fo
Region: I | Oyster Creek | 35058 | 12/31/2015 01/28/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Preconditioning of the Standby Liquid Control Relief Valves |  | P.2 Evaluation | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified an NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XI, "Test Control," because Exelon conducted unacceptable preconditioning of the standby liquid control (SLC) relief valves prior to American Society of Mec
Region: I | Oyster Creek | 35059 | 12/31/2015 01/28/2016 | 2015004-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Problem Identification and Resolution Leading to Degradation of EPR Causing a Reactor Scram |  |  | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding was identified because Exelon did not adequately identify and correct conditions, per LS-AA-120, "Issue Identification and Screening Process," that led to degradation of the electric pressure regulator (EPR) wiring, which resulted
Region: I | Oyster Creek | 34486 | 09/30/2015 11/02/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Temperature Input in the Electromatic Relief Valve Voltage Drop Calculation |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified an NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion III, "Design Control," in that Exelon's measures for verifying the adequacy of design of the electromatic relief valve (EMRV) voltage drop calculation were
Region: I | Oyster Creek | 34458 | 06/30/2015 08/12/2015 | 2015002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Assessment of Degraded 4k Emergency Switchgear Roll-Up Door Floor Gasket |  | P.2 Evaluation | TE?: N | 05000219 Oyster Creek |  | 71111.06 | The inspectors identified a finding associated with Exelon procedure, OP-AA-108-115, "Operability Determinations," because Exelon did not adequately assess a degraded floor gasket for the 'D' emergency 4 kilovolt (kV) switchgear roll-up door. Specifically
Region: I | Oyster Creek | 34459 | 06/30/2015 08/12/2015 | 2015002-02 | Self - Revealed | FIN | Mitigating Systems | Green | Failure Rates Exceed Twenty Percent for Annual Requalification Exam |  | H.9 Training | TE?: N | 05000219 Oyster Creek |  | 71111.11B | A self-revealing finding was identified associated with inadequate licensed operator performance during licensed operator requalification exams in accordance with TQ-AA-150, "Operator Training Program." Specifically, two of seven crews failed the simulato
Region: I | Oyster Creek | 34460 | 06/30/2015 08/12/2015 | 2015002-03 | Self - Revealed | NCV | Initiating Events | Green | Reactor Water Cleanup Procedure Not Followed Resulting in a Level Transient |  | H.11 Challenge the Unknown | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing NCV of Technical Specification 6.8.1(a), "Procedures and Programs," was identified because Exelon did not follow procedure 303, "Reactor Cleanup Demineralizer System," during the system restoration on March 26, 2015. Specifically, during
Region: I | Oyster Creek | 34461 | 06/30/2015 08/12/2015 | 2015002-04 | Self - Revealed | FIN | Initiating Events | Green | Reset of the Automatic Voltage Regulator Controller Led to an Automatic Reactor Scram |  | H.11 Challenge the Unknown | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding was identified because Exelon did not properly screen work in accordance with MA-AA-716-010, "Maintenance Planning." Specifically, on September 12, 2014, Exelon did not screen the automatic voltage regulator's (AVR) human machine
Region: I | Oyster Creek | 34457 | 04/24/2015 05/27/2015 | 2015008-02 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Actions to Restore Design Conformance of Two SDV Vent & Drain Valves Pressure Regulator Valves |  | H.13 Consistent Process | TE?: N | 05000219 Oyster Creek |  | 71111.17T | Green. The NRC identified an NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly correct a condition adverse to quality. Specifically, corrective actions to restore des
Region: I | Oyster Creek | 34446 | 03/31/2015 05/14/2015 | 2015001-01 | NRC | NCV | Barrier Integrity | Green | Post Maintenance Test Results Were Not Evaluated to Assure that Technical Specifications Requirements Were Satisfied. |  | H.8 Procedure Adherence | TE?: N | 05000219 Oyster Creek |  | 71111.19 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," when Exelon did not document and adequately evaluate test results to assure that test requirements had been satisfied. Specifically, Exelon did not perform the p
Region: I | Oyster Creek | 34448 | 03/31/2015 05/14/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Testing for Emergency Service Water Pump Breaker |  | H.5 Work Management | TE?: N | 05000219 Oyster Creek |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" for Exelon's failure to develop an adequate post maintenance test to determine operability of the 'A' emergency service water pump breaker. Sp
Region: I | Oyster Creek | 34445 | 12/31/2014 02/11/2015 | 2014005-01 | NRC | NCV | Initiating Events | Green | Reactor Head Cooling Spray Piping Flange Misalignment |  | P.2 Evaluation | TE?: N | 05000219 Oyster Creek |  | 71111.08G | The inspectors identified a Green Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not promptly correct a condition adverse to quality associated with reactor head cooling (RHC) spray line 2-i
Region: I | Oyster Creek | 34443 | 12/31/2014 02/11/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Plant Shutdown Procedure Was Inadequate For Soft Shutdown |  | H.7 Documentation | TE?: N | 05000219 Oyster Creek |  | 71153 | The inspectors identified a Non-Cited Violation (NCV) of very low safety significance (Green) of TS 6.8.1, Procedures and Programs, because Exelon did not adequately establish and maintain the plant shutdown procedure. Specifically, the procedure was not
Region: I | Oyster Creek | 34444 | 12/31/2014 02/11/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | Procedures Not Implemented During Plant Shutdown |  | H.8 Procedure Adherence | TE?: N | 05000219 Oyster Creek |  | 71153 | The inspectors identified an NCV of very low safety significance (Green) of TS 6.8.1, Procedures and Programs, because Oyster Creek Operators did not adequately implement procedures when performing a plant shutdown. Specifically, the operators failed to e
Region: I | Oyster Creek | 34442 | 12/12/2014 01/20/2015 | 2014010-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Evaluate a Temporary Configuration Change |  | P.5 Operating Experience | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding (FIN) of very low safety significance was identified for Exelon's failure to implement the temporary configuration change program when a temporary repair was performed on condenser bellows expansion joint Y-1-26. The temporary rep
Region: I | Oyster Creek | 34440 | 09/30/2014 11/13/2014 | 2014004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000219 Oyster Creek |  | 71114.05 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2), 10 CFR 50.47(b)(10), and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the Oyster Creek emergency plan as a resu
Region: I | Oyster Creek | 34434 | 06/30/2014 08/06/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct High Oil Level in D Emergency Service Water Pump Upper Motor Bearing |  | P.1 Identification | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The NRC inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not promptly identify and correct a condition adverse to quality. Specifically, Exelon did not identify and correct a high oil level
Region: I | Oyster Creek | 34429 | 03/31/2014 05/15/2014 | 2014002-01 | NRC | NCV | Initiating Events | Green | Untimely Performance of a 50.65 a(4) Risk Evaluation during a Maximum Emergency Generation Action |  | H.11 Challenge the Unknown | TE?: N | 05000219 Oyster Creek |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR Part 50.65(a)(4), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," because Exelon did not reassess and manage risk after the grid operator declared a ma
Region: I | Oyster Creek | 34432 | 03/31/2014 05/15/2014 | 2014002-02 | Self - Revealed | NCV | Initiating Events | Green | Corrective Action to Prevent Recurrence Ineffective to Preclude Repetition of a Significant Condition Adverse to Quality |  |  | TE?: N | 05000219 Oyster Creek |  | 71152 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the corrective action to prevent recurrence of a significant condition adverse to quality did not preclude repetition of the
Region: I | Oyster Creek | 34427 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Physical Change To Security Feature Causes Flood Control Feature To Be Ineffective |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.01 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Exelon did not ensure applicable regulatory requirements and design basis for the emergency diesel generators were correctly translat
Region: I | Oyster Creek | 34418 | 06/30/2013 08/07/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Degraded Emergency Diesel Generator Bypass Sight Glass not identified in the Corrective Action Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 71111.15 | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not promptly identify a condition adverse to quality. Specifically, from December 10, 2012 to April 4, 2013, Exelon did not ident
Region: I | Oyster Creek | 34426 | 06/30/2013 08/07/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Alarm Response Procedures did not implement Technical Specification Requirements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green NCV of technical specification 6.8.1a for improperly implementing technical specifications requirements into alarm response procedures for the 125 VDC (volts - direct current) system. The inspectors determined that the im
Region: I | Oyster Creek | 34416 | 03/31/2013 04/29/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Emergency service water non-conformance not entered identified as a condition adverse to quality and not entered into corrective action program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," when Exelon did not promptly identify or correct a condition adverse to quality. The inspectors determined that failing to identify and enter a condit
Region: I | Oyster Creek | 34412 | 12/31/2012 01/31/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Inspection and Torquing of Bolted Connection Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Exelon did not properly implement procedural controls to ensure adequate thread engagement for standby li
Region: I | Oyster Creek | 34413 | 12/31/2012 01/31/2013 | 2012005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Application of Strippable Coating to the Refueling Cavity Liner and the Failure to Configure a Valve in the Leakage Collection System Resulting in Increased Potential for Corrosion |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000219 Oyster Creek |  | 71111.08G | Green. A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Exelon procedures and work orders were not effective in preventing refueling cavity leakage from overflowing onto the exter
Region: I | Oyster Creek | 34410 | 08/31/2012 09/28/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate the impact of Increased Emergency Diesel Generators Loading on the Volume of Available Fuel Oil |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for Exelon's failure to promptly identify and correct a condition adverse to quality. Specifically, Exelon did not promptly identify and correct the impac
Region: I | Oyster Creek | 34408 | 06/30/2012 07/31/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Entry into a non-conservative technical specification with both isolation condensers inoperable during power operation |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification 3.8, "Isolation Condenser", specification D, when Exelon did not enter the correct technical specification and take the required actions when both isolation condensers were made inoperable i
Region: I | Oyster Creek | 34409 | 06/30/2012 07/31/2012 | 2012003-02 | NRC | FIN | Mitigating Systems | Green | APRM 7 Finding |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green finding when Exelon did not perform an adequate operability determination of Average Power Range Monitor (APRM) 7 prior to restoring it to operation on March 24, 2012, after it was declared inoperable on February 2, 2012.
Region: I | Oyster Creek | 34395 | 03/31/2012 05/02/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | Abnormal operating procedure conflicts with technical specification requirement |  |  | TE?: N | 05000219 Oyster Creek |  | NONE | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1a, "Procedures and Programs," for improperly implementing technical specifications requirements into abnormal operation procedures for the reactor recirculation system. The insp
Region: I | Oyster Creek | 34396 | 03/31/2012 05/02/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Risk management actions not implemented to manage increased online risk during a surveillance test |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000219 Oyster Creek |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," when Exelon did not implement risk management actions to manage the risk associated with the performance
Region: I | Oyster Creek | 34401 | 03/31/2012 05/02/2012 | 2012002-03 | NRC | NCV | Barrier Integrity | Green | Reactivity management procedures not maintained in accordance with industry standards |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000219 Oyster Creek |  | 71152 | The inspectors identified a Green NCV of TS 6.8.1a for not maintaining operating procedures in accordance with NRC and industry standards which required prudent, conservative lowering of reactor power prior to performing evolutions which had the potenti
Region: I | Oyster Creek | 34388 | 12/31/2011 02/08/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish New Reference Values in Accordance with ASME Code |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50.55a, Codes and Standards, because Exelon did not complete an adequate analysis when establishing a new reference value for the A containment spray pump in accordance with the American Society of Mech
Region: I | Oyster Creek | 34394 | 08/15/2011 09/12/2011 | 2011503-01 | NRC | NCV | Emergency Preparedness | Green | Traditional Enforcement Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000219 Oyster Creek |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level lV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the l
Region: I | Oyster Creek | 34389 | 08/15/2011 09/12/2011 | 2011503-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000219 Oyster Creek |  | 71114.04 | In response to the NCV and finding, Exelon entered the issue into their corrective action program as IR 01184333 and subsequently implemented Revision 3 of the Oyster Creek Emergency Plan, which restored the EAL HU6 Basis to the Revision 10 (of the pre-Ex
Region: I | Oyster Creek | 34385 | 06/30/2011 07/25/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform acceptance inspection of contractor work results in damage to safety related instrument cable |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.12 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion X, "Inspection," when Exelon did not conduct a post maintenance inspection of work accomplished by a contractor on main steam isolation valve (MSIV), V-1-10, which resulted in heat d
Region: I | Oyster Creek | 34376 | 04/01/2011 05/05/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Control Cables for the Reactor Coolant Inventory Makeup Source Not Protected From Fire Damage |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.05T | The team identified an NCV of 10 CFR 50, Appendix R, lll.G.2, in that Exelon failed to maintain the credited reactor coolant inventory makeup system free of fire damage in the event of a fire in the 'B' 480 volt (V) switchgear room. Specifically, Exelon
Region: I | Oyster Creek | 34365 | 04/01/2011 05/04/2011 | 2011009-01 | NRC | NCV | Barrier Integrity | Green | B.5.b. Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.05T | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Oyster Creek | 34377 | 03/31/2011 05/13/2011 | 2011002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Make an Accurate lmmediate Operability Determination |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) when Exelon did not make an accurate immediate operability determination in accordance with OP-M-108-115 "Operability Determinations" following discovery of a through wall leak
Region: I | Oyster Creek | 34378 | 03/31/2011 05/13/2011 | 2011002-02 | NRC | NCV | Initiating Events | Green | Failure to Establish Proper Baseline Data for Service Water Pumps in Accordance with ASME Code |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.22 | The inspectors identified a Green NCV of 10CFR 50.55a, Codes and Standards, because Exelon did not properly establish baseline reference values for the service water pumps as required by the American Society of Mechanical Engineers (ASME) Operation and
Region: I | Oyster Creek | 34381 | 03/31/2011 05/13/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedures for Responding to the Loss of Control Room Annunciator |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71153 | The inspectors identified a Green NCV of technical specification 6.8.1.a for Exelon's failure to have written procedures for activities listed in Regulatory Guide 1.33 , which includes procedures for abnormal, off-normal, or alarm conditions and procedu
Region: I | Oyster Creek | 34348 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Snubber Maintenance History Not Taken Into Account When Conducting Service Life Reviews |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.12 | The inspectors identified a Green non-cited violation of technical specification 4.5.M.1.f, "Snubber Service Life Monitoring", while inspecting 4 snubber testing failures that occurred during 1R23. Specifically, Exelon's snubber testing program, contained
Region: I | Oyster Creek | 34349 | 12/31/2010 02/08/2011 | 2010005-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Conduct Representative Sampling of Stack Effluents |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71153 | A Green, self-revealing NCV of Technical Specification 6.8.4 occurred for Exelon's failure to maintain continuous, representative monitoring and sampling of plant stack gaseous effluents, as required by the Offsite Dose Calculation Manual, due to degradat
Region: I | Oyster Creek | 34354 | 12/31/2010 02/08/2011 | 2010005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Procedures Resulting in Reactor Scram |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71153 | A Green, self-revealing NCV of Technical Specification 6.8.1.a occurred when Exelon did not adequately implement plant startup procedures which resulted in an automatic reactor scram. Immediate corrective actions included just in time training with all re
Region: I | Oyster Creek | 34356 | 08/27/2010 10/07/2010 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | Scaffold Installation Procedure Not Properly Implemented |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, because Exelon did not properly implement scaffolding control pro
Region: I | Oyster Creek | 34357 | 08/27/2010 10/07/2010 | 2010008-02 | NRC | NCV | Mitigating Systems | Green | EDG Low Voltage Control Cable Submergence |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green) involving an NCVof 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, Exelon did not maintain safety-related emergency diesel generator (EDG) instrumentation and low
Region: I | Oyster Creek | 34362 | 08/27/2010 10/07/2010 | 2010008-03 | NRC | NCV | Mitigating Systems | Green | 1A2 and 1B2 480 V Load Center Transformer Cooling Fan Testing |  |  | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green) involving an NCVof 10 CFR 50, Appendix B, Criterion XI, Test Control, because Exelon had not established a test program for safety-related load center transformer cooling fans to con
Region: I | Oyster Creek | 34363 | 08/27/2010 10/07/2010 | 2010008-04 | NRC | NCV | Mitigating Systems | Green | Core Spray System I Pump Room Degraded Ball Float Drain Valve |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green) involving an NCVof 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, because Exelon did not identify and correct a condition adverse to quality. Specifically, Exelon did not i
Region: I | Oyster Creek | 34337 | 07/02/2010 08/09/2010 | 2010003-01 | NRC | FIN | Mitigating Systems | Green | Preconditioning of Isolation Condenser Valves Prior to ASME In-service Test |  | H.3(b) Work Activity Coordination | TE?: N | 05000219 Oyster Creek |  | 71111.19 | Green: The inspectors identified a Green finding when Exelon cycled valves for maintenance prior to performing scheduled quarterly in-service testing (IST) which resulted in unacceptable preconditioning of valves within the isolation condenser system on A
Region: I | Oyster Creek | 34338 | 07/02/2010 08/09/2010 | 2010003-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide Adequate Compensatory Actions for the RAGEMS Being Out Of Service |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000219 Oyster Creek |  | 71152 | Green: The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.54(q), "Conditions of Licenses," because Exelon did not properly maintain the conditions of the Oyster Creek Emergency Plan. Specifically, Exelon did not implement timely comp
Region: I | Oyster Creek | 34341 | 07/02/2010 08/09/2010 | 2010003-03 | NRC | NCV | Emergency Preparedness | Green | Failure To Notify the NRC within the time requirements of 10 CFR 50.72 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000219 Oyster Creek |  | 71153 | Green: The NRC identified a Severity Level IV non-cited violation (NCV) of 10 CFR 50.72 when Exelon did not make the required initial notification within 8 hours of the occurrence of the condition. Specifically, on the morning of April 7th, a maintenance
Region: I | Oyster Creek | 34342 | 07/02/2010 08/09/2010 | 2010003-04 | NRC | NCV | Mitigating Systems | Green | Core Spray ASME Code Compliance Issues |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000219 Oyster Creek |  | 71111.15 | Green: The inspectors identified a SL IV, Green non-cited violation of 10CFR50.55(a) when Exelon did properly implement the ASME code requirements for the core spray system check valves. Specifically, Exelon did not properly implement the ASME Check Valve
Region: I | Oyster Creek | 34343 | 07/02/2010 08/04/2010 | 2010007-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions Associated With the Reactor Building to Torus Vacuum Breaker Trip Valve Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71152B | Green. The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for Exelon's failure to promptly identify and correct a condition adverse to
Region: I | Oyster Creek | 34347 | 07/02/2010 08/04/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Preventive Maintenance Procedure Leading to Incomplete Fire Diesel Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71152B | Green. The inspectors identified a Green non-cited violation of Technical Specification 6.8.1 for Exelon's failure to follow MA-MA-716-009, "Preventive Maintenance Work Order Process." Specifically, Exelon closed work order R2120325 without completing t
Region: I | Oyster Creek | 34332 | 04/02/2010 04/30/2010 | 2010002-01 | NRC | NCV | Barrier Integrity | Green | Adjustments to Maintenance Rule System Performance Criteria not made after Biannual Evaluation |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000219 Oyster Creek |  | 71111.12 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(3), requirements for monitoring the effectiveness of maintenance at nuclear power plants (maintenance rule), because Exelon did not make adjustments to established performan
Region: I | Oyster Creek | 34335 | 04/02/2010 04/30/2010 | 2010002-02 | NRC | NCV | Barrier Integrity | Green | Failure To Declare The Rod Worth Minimizer Inoperable At The Time Operability Criteria Was Not Met And Enter The Correct Technical Specification Action Statement |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000219 Oyster Creek |  | 71111.15 | An NRC identified NCV of Technical Specification (TS) 6.8.1, Procedures and Programs, was identified when Exelon did not declare the rod worth minimizer (RWM) inoperable prior to completing the withdrawal of the twelfth rod during a reactor startup on
Region: I | Oyster Creek | 34331 | 12/31/2009 01/26/2010 | 2009005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Action for the 'B' Spent Fuel Pool Cooling Pump |  | H.3(b) Work Activity Coordination | TE?: N | 05000219 Oyster Creek |  | 71152 | A self-revealing non-cited violation (NCV) was identified of 10CFR50 Appendix B, Criterion XVI, "Corrective Action" was identified when Exelon did not take timely corrective action to address an identified degrading trend in the performance on the B spent
Region: I | Oyster Creek | 34329 | 09/30/2009 10/28/2009 | 2009004-01 | Self - Revealed | NCV | Initiating Events | Green | Unexpected power drop when transferring mode of control of recirculation pump |  | H.4(a) Human Error Prevention | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing NCV of Oyster Creek Technical Specification 6.8.1, "Procedures and Programs," occurred when Exelon did not properly implement procedures to transfer the "D" reactor recirculation pump from local manual to remote manual control which resul
Region: I | Oyster Creek | 34325 | 08/13/2009 09/26/2009 | 2009009-02 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct a Degraded Condition Leading to #1 EDG Inability to Perform Its Safety Function |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000219 Oyster Creek |  | 93812 | The NRC identified a finding of very low safety significance (Green) that involved a non-cited violation (NCV) of 10 CFR50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not identify and correct a degraded condition which resulted in
Region: I | Oyster Creek | 34326 | 08/13/2009 09/26/2009 | 2009009-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Control Foreign Material in the Shell Side of the 'B' Isolation Condenser |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000219 Oyster Creek |  | 93812 | The NRC identified a self-revealing finding of very low safety significance (Green) that involved an NCV of Oyster Creek Technical Specification 6.8.1, "Procedures and Programs," because Exelon did not adequately implement a safety- related maintenance ac
Region: I | Oyster Creek | 34301 | 06/30/2009 07/30/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Medium Voltage Cables Maintained Submerged for Extended Period of Time |  | P.2(b) Implementing Operating Experience | TE?: N | 05000219 Oyster Creek |  | 71111.06 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon has not implemented effective actions to minimize water accumulation and submergence of medium voltage cables contained in the turbine building cl
Region: I | Oyster Creek | 34304 | 06/30/2009 07/30/2009 | 2009003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Evaluation Results In Instrument Air Transient |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self revealing finding occurred when Exelon did not adequately evaluate the impact of water which had entered the service air system in December 2008 which resulted in an accumulation of failed desiccant and corrosion products in the 'C&D' instrument ai
Region: I | Oyster Creek | 34305 | 06/30/2009 07/30/2009 | 2009003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Solder Joint Causes Safety Related Station Battery Charger Failure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self revealing NCV of Oyster Creek Technical Specifications 6.8.1, "Procedures and Programs," occurred when Exelon did not properly implement maintenance instructions and perform adequate soldering on the 'C2' battery charger. This resulted in a wire co
Region: I | Oyster Creek | 34306 | 06/30/2009 07/30/2009 | 2009003-04 | NRC | NCV | Barrier Integrity | Green | Non-Conservative Acceptance Criteria Specified In SBGTS Surveillance Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.19 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," because Exelon did not ensure that the surveillance test procedure utilized for the standby gas treatment system (SBGTS) included appropriate a
Region: I | Oyster Creek | 34312 | 06/30/2009 07/30/2009 | 2009003-05 | Self - Revealed | NCV | Barrier Integrity | Green | Adverse Trend on #1 SBGTS Not Identified |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 71111.22 | A self revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," occurred when Exelon did not identify a degraded condition on the #1SBGTS HEPA filter in March 2009. This resulted in the HEPA filter exceeding the technical specification
Region: I | Oyster Creek | 34313 | 06/30/2009 07/30/2009 | 2009003-06 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Secondary Containment Integrity During Maintenance on Reactor Building Roof |  | H.4(a) Human Error Prevention | TE?: N | 05000219 Oyster Creek |  | 71152 | A self revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" occurred when Exelon personnel did not properly implement a procedure for the control of secondary containment integrity during maintenance activities whe
Region: I | Oyster Creek | 34314 | 06/30/2009 07/30/2009 | 2009003-07 | Self - Revealed | FIN | Initiating Events | Green | Ineffective Use of Operating Experience on Main Power Transformer Cooling System |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000219 Oyster Creek |  | 71153 | A self revealing finding occurred when Exelon did not adequately evaluate operating experience (OE) regarding transformer cooling issues. Specifically, Exelon did not identify and correct a single point vulnerability (SPV) on the main transformers cooling
Region: I | Oyster Creek | 34299 | 05/15/2009 06/26/2009 | 2009007-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Design Control for RBCCW Containment Isolation Valve Modification |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71111.17T | Green. The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Exelon did not ensure the adequacy of a reactor building closed cooling water system co
Region: I | Oyster Creek | 34288 | 03/31/2009 05/05/2009 | 2009002-01 | NRC | NCV | Emergency Preparedness | Green | Failure of the Oyster Creek RAGEMS to Meet the Requirements of the Emergency Plan |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000219 Oyster Creek |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10CFR50.54(q), "Conditions of Licenses," because Exelon did not properly maintain the conditions of the Oyster Creek Emergency Plan. Specifically, Exelon did not implement timely corrective or compe
Region: I | Oyster Creek | 33622 | 12/31/2008 01/28/2009 | 2008005-01 | Self - Revealed | NCV | Initiating Events | Green | Conduct of Maintenance Procedure Not Properly Implemented |  | H.4(a) Human Error Prevention | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred when Exelon did not perform an adequate self-check and did not properly use test equipment during 480 VAC breaker maintena
Region: I | Oyster Creek | 33625 | 12/31/2008 01/28/2009 | 2008005-02 | NRC | NCV | Barrier Integrity | Green | Core Alterations Performed Without the Required Configuration of Source Range Nuclear Monitors |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.2 | The inspectors identified an NCV of Technical Specification 3.9.D "Refueling", when Exelon performed core alterations without the required configuration of operable source range monitors (SRM). Specifically, Exelon installed two fuel assemblies in a react
Region: I | Oyster Creek | 33619 | 09/30/2008 10/29/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Scaffold Installation Procedure Not Properly Implemented |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71111.15 | Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because AmerGen did not properly implement scaffolding control procedural requirements on August 11, 2008. Specif
Region: I | Oyster Creek | 33609 | 06/30/2008 07/31/2008 | 2008003-01 | Self - Revealed | FIN | Initiating Events | Green | Improper Valve Reassembly Results in Instrument Air Transient |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000219 Oyster Creek |  | NONE | A self-revealing finding was identified when AmerGen improperly reassembled the inlet valve actuator on the 'C & D' instrument air dryers which damaged its o-ring and subsequently resulted in an instrument air transient on March 24, 2008. This finding was
Region: I | Oyster Creek | 33610 | 06/30/2008 07/31/2008 | 2008003-02 | Self - Revealed | FIN | Initiating Events | Green | Instrument Air Transient Due to Insufficient Preventive Maintenance on Service Air Compressors |  |  | TE?: N | 05000219 Oyster Creek |  | NONE | A self revealing finding occurred when the suction air filters to the '1-1' and '1-2' service air compressors became clogged with debris which affected the availability and reliability of the compressors on April 25, 2008. In 2001, AmerGen implemented a m
Region: I | Oyster Creek | 33611 | 06/30/2008 07/31/2008 | 2008003-03 | NRC | FIN | Mitigating Systems | Green | Potential Preconditioning of Core Spray Valves Prior to ASME In-service Test |  | H.3(b) Work Activity Coordination | TE?: N | 05000219 Oyster Creek |  | 71111.22 | The inspectors identified that AmerGen had scheduled surveillance tests in a sequence that would have resulted in unacceptable preconditioning of valves within the core spray system on May 19, 2008. This finding was determined not to be a violation of NRC
Region: I | Oyster Creek | 33612 | 06/30/2008 07/31/2008 | 2008003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Diesel Driven Fire Pump Unavailable Due to Improper Testing |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000219 Oyster Creek |  | 71152 | A self revealing finding occurred when AmerGen did not properly implement a functional test procedure for the '1-1' diesel driven fire pump on November 7, 2007. Specifically, operations personnel did not accurately measure the speed of the pump while perf
Region: I | Oyster Creek | 33613 | 06/27/2008 07/28/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Review the Impact of Site Staffing Changes to the Fire Protection Program |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.05T | The team identified that in July 2002, AmerGen failed to review a change to personnel resources that would increase the time necessary to complete an NRC approved hot shutdown repair after a fire in the A 480V switchgear room. Specifically, AmerGen elimin
Region: I | Oyster Creek | 33608 | 03/31/2008 04/28/2008 | 2008002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Risk Assessment Identified Prior to Commencement of Maintenance |  | H.3(a) Work Planning | TE?: N | 05000219 Oyster Creek |  | 71111.13 | The inspectors identified that AmerGen performed an inadequate risk assessment for a planned, but not yet commenced, maintenance activity on the Bank 6 startup transformer in February 2008; which resulted in an under-estimation of the risk associated with
Region: I | Oyster Creek | 33597 | 12/31/2007 01/25/2008 | 2007005-01 | Self - Revealed | FIN | Mitigating Systems | Green | Degraded Fuel Oil in the 1-1 Fire Diesel Fuel Oil Storage Tank Not Identified |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self revealing finding occurred when AmerGen did not identify a degraded fuel oil condition on the '1-1' diesel driven fire pump in September 2007. This resulted in the pump being unable to maintain adequate discharge pressure on October 1, 2007 during
Region: I | Oyster Creek | 33598 | 12/31/2007 01/25/2008 | 2007005-02 | Self - Revealed | FIN | Initiating Events | Green | Service Water Pump Motor Failure Due to Inadequate Refurbishment Process |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self revealing finding occurred when the '1-1' service water pump motor failed on August 15, 2007 due to an inadequate motor refurbishment by a vendor. AmerGen previously noted a problem with the motor refurbishment process used by the vendor in July 20
Region: I | Oyster Creek | 33599 | 12/31/2007 01/25/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Operations Personnel Did Not Appropriately Implement Reactor Startup Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71152 | The inspectors identified that AmerGen did not properly implement procedures during a reactor startup on July 20, 2007. Specifically, operations personnel withdrew source range monitors (SRM) from the core without first ensuring adequate overlap with the
Region: I | Oyster Creek | 33607 | 12/31/2007 01/25/2008 | 2007005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Evaluation of IRM Channels Prior to Reactor Startup |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding occurred when AmerGen operated in a condition prohibited by technical specifications on July 20, 2007. Specifically, AmerGen did not identify that intermediate range monitor (IRM)-16 was inoperable and ensure that the required num
Region: I | Oyster Creek | 33592 | 09/28/2007 10/29/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Degraded Condition on the Remote Shutdown Panel Not Properly Identified. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified that AmerGen did not properly identify that the remote shutdown panel (RSP) was not capable of performing its design function when the 'B' isolation condenser (IC) makeup valve control power indicating status light was not illumi
Region: I | Oyster Creek | 33593 | 09/28/2007 10/29/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Improper Repair of a Fire Rated Penetration Seal |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000219 Oyster Creek |  | 71111.19 | The inspectors identified that AmerGen did not properly implement fire protection plan requirements on June 22, 2007. Specifically, AmerGen did not repair fire penetration 762 in accordance with procedures and resulted in an unqualified configuration of s
Region: I | Oyster Creek | 33594 | 09/28/2007 10/29/2007 | 2007004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Implementation During Response to a Reactor Feedpump Trip and Reactor Scram |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding was identified when AmerGen personnel did not properly implement procedural guidance during a response to a reactor feedwater pump (RFP) trip and a reactor scram on July 17, 2007. Specifically, the operating crew did not properly
Region: I | Oyster Creek | 33587 | 09/27/2007 11/01/2007 | 2007502-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Require State PAR Notifications Within 15 Minutes of Emergency Declaration. |  |  | TE?: N | 05000219 Oyster Creek |  | 71114.01 | A NRC-identified non-cited violation (NCV) of 10 CFR 50.47(b)(5) and 10 CFR Part 50, Appendix E, Section IV.D.3, was identified for failure of the licensee's state and local notifications procedures to require that the notifications of protective action r
Region: I | Oyster Creek | 33583 | 06/29/2007 07/26/2007 | 2007003-01 | NRC | NCV | Public Radiation Safety | Green | Inadequate Identification of Unacceptable Quality Assurance Test Results for Effluent Monitoring |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 7112201 | The inspectors identified that quality assurance test results for effluent monitoring of Sr-89 and Sr-90 in the first quarter of 2006 did not meet test acceptance criteria and AmerGen had not evaluated the condition as of April 27, 2007. This finding was
Region: I | Oyster Creek | 33584 | 05/25/2007 07/06/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria In Emergency Diesel Generator Battery Service Test Procedures |  |  | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," in that, AmerGen did not incorporate the requirements and acceptance limits contained in applicab
Region: I | Oyster Creek | 33585 | 05/25/2007 07/06/2007 | 2007006-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Containment Hardened Vent Valve Accumulator Test Criteria |  |  | TE?: N | 05000219 Oyster Creek |  | 7111121 | The team identified a finding of very low safety significance (Green), in that, the licensee did not correctly translate the design of the containment hardened vent valve accumulators into test procedures. Specifically, the acceptance criteria for allowab
Region: I | Oyster Creek | 33581 | 03/31/2007 05/08/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Improper Identification of an Inoperable Fire Barrier Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000219 Oyster Creek |  | 71111.05Q | The inspectors identified that AmerGen did not properly implement fire protection plan requirements on January 11 and January 16, 2007. Specifically, AmerGen did not identify that a fire barrier door for the safety-related 'B' 480 volt room was obstructed
Region: I | Oyster Creek | 33582 | 03/31/2007 05/08/2007 | 2007002-02 | Self - Revealed | NCV | Initiating Events | Green | 'D' EMRV Adverse Trend Not Properly Identified |  | P.1(b) Trend Performance CAP | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding was identified when AmerGen did not properly identify an adverse trend on the 'D' electromatic relief valve (EMRV) pressure switch between May 2006 and December 2006, which resulted in an opening of the 'D' EMRV below its actuatio
Region: I | Oyster Creek | 33572 | 12/31/2006 01/19/2007 | 2006005-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Operability Determination Associated With Elevated Isolation Condenser Shell Temperatures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000219 Oyster Creek |  | 71111.15 | The inspectors identified that AmerGen did not perform an adequate operability determination to assure the 'A' isolation condenser (IC) could meet its design bases requirements with elevated shell temperatures on October 6, 2006. This finding was determin
Region: I | Oyster Creek | 33573 | 12/31/2006 01/19/2007 | 2006005-02 | Self - Revealed | NCV | Initiating Events | Green | Clearance Activity Performed Out of Sequence And Causes Trip of 'A' Shutdown Cooling Pump |  | H.4(b) Procedural Compliance | TE?: N | 05000219 Oyster Creek |  | 71111.2 | A self-revealing finding was identified regarding inadequate procedure adherence when work activities on the 480 V '1A2' switchgear during 1R21 refueling outage resulted in a trip of a reactor building closed cooling water (RBCCW) and shutdown cooling (SD
Region: I | Oyster Creek | 33574 | 12/31/2006 01/19/2007 | 2006005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Implementation Results in Loss of Power to the 'B' 125V DC Distribution Center |  | H.4(a) Human Error Prevention | TE?: N | 05000219 Oyster Creek |  | 71153 | A self revealing finding was identified regarding inadequate procedure implementation when the 'B' 125 VDC battery main breaker was inadvertently operated and resulted in a loss of power to the 'B' DC distribution center on October 10, 2006. This finding
Region: I | Oyster Creek | 33566 | 09/30/2006 10/24/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Fire Protection Plan Requirements Not Implemented |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000219 Oyster Creek |  | 71111.05Q | The inspectors identified that AmerGen did not implement fire protection plan requirements on August 17, 2006. Specifically, AmerGen did not identify that a low pressure condition existed on the 4160 Volt carbon dioxide (CO2) suppression system which resu
Region: I | Oyster Creek | 33567 | 09/30/2006 10/24/2006 | 2006004-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Planning Results in #1 Air Compressor Trip |  | H.3(b) Work Activity Coordination | TE?: N | 05000219 Oyster Creek |  | 7111112B | A self-revealing finding was identified when AmerGen did not implement adequate work planning to ensure the availability and reliability of the #1 air compressor. This resulted in a trip of the air compressor on September 7, 2006. This finding was determi
Region: I | Oyster Creek | 33568 | 09/30/2006 10/24/2006 | 2006004-03 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Foreign Material Control Results in #1 Emergency Diesel Generator Unavailability |  | H.4(a) Human Error Prevention | TE?: N | 05000219 Oyster Creek |  | 71111.22 | A self-revealing finding was identified regarding inadequate foreign material control during performance of a maintenance activity on the #1 emergency diesel generator (EDG) on July 10, 2006. During performance of vibration data collection, a vibration pr
Region: I | Oyster Creek | 33569 | 09/30/2006 10/24/2006 | 2006004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Actions for the 'A' ESW pump breaker |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000219 Oyster Creek |  | 71111.22 | A self-revealing finding was identified when AmerGen did not take timely corrective actions for a degraded condition on the 'A' emergency service water (ESW) pump. Specifically, a corrective action identified in February 2006 was not completed in a timely
Region: I | Oyster Creek | 33559 | 06/30/2006 07/13/2006 | 2006003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Actions for the Standby Gas Treatment System |  |  | TE?: N | 05000219 Oyster Creek |  | 7111112B | A self-revealing finding occurred when AmerGen did not take timely corrective actions for a non-conforming condition on the standby gas treatment (SBGT) system between March 2005 and May 2006. Specifically, sand and debris were identified in the SBGT syst
Region: I | Oyster Creek | 33562 | 06/30/2006 07/13/2006 | 2006003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Scaffold Disassembly Results in Core Spray Booster Pump Unavailability |  |  | TE?: N | 05000219 Oyster Creek |  | 7111112B | A self-revealing finding was identified regarding an inadequate disassembly of scaffold which resulted in the unavailability of the 'B' core spray booster pump on June 27, 2006. During disassembly of a scaffold, a scaffold coupler fell and damaged the 'B'
Region: I | Oyster Creek | 33563 | 06/30/2006 07/13/2006 | 2006003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedures Results in a Hydrogen Detonation in Augmented Offgas System |  |  | TE?: N | 05000219 Oyster Creek |  | 71153 | A self-revealing finding was identified regarding inadequate procedure adherence when operators did not properly implement an alarm response procedure which contributed to a hydrogen detonation and the isolation of the offgas and augmented offgas (AOG) an
Region: I | Oyster Creek | 33556 | 04/24/2006 05/19/2006 | 2006006-01 | NRC | NCV | Initiating Events | Green | Failure to Identify That a Main Steam Isolation Valve Did Not Close Within TS Surveillance Acceptance Criteria |  |  | TE?: N | 05000219 Oyster Creek |  | 71152B | The inspectors identified a Green NCV of 10CFR50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify that the "A" outboard main steam isolation valve (MSIV) did not stroke closed within the allowable time specified in the surveill
Region: I | Oyster Creek | 33557 | 04/24/2006 05/19/2006 | 2006006-02 | NRC | FIN | Public Radiation Safety | Green | Failure to Take Timely Corrective Actions to Ensure the Availability and Reliability of the Augmented Off-Gas System |  |  | TE?: N | 05000219 Oyster Creek |  | 71152B | The inspectors identified a Green Finding for the failure to take timely actions to correct known deficiencies associated with the augmented off-gas (AOG) system, which impacted the system's reliability and availability since October 2003. In 2003, Oyster
Region: I | Oyster Creek | 33544 | 03/31/2006 05/08/2006 | 2006002-02 | Self - Revealed | FIN | Initiating Events | Green | Untimely Corrective Actions Causes Unplanned Power Reduction Due to 'A' Feedwater Packing Leakage |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self-revealing finding was identified regarding untimely corrective actions when packing on the 'A' feedwater regulating valve failed on February 10, 2006, and resulted in an upset of plant stability. This finding was determined not to be a violation of
Region: I | Oyster Creek | 33552 | 03/31/2006 05/08/2006 | 2006002-03 | Self - Revealed | NCV | Mitigating Systems | Green | 'D' ESW Pump Start Failure |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.12 | A self-revealing finding was identified regarding inadequate procedure quality when the 'D' emergency service water (ESW) pump did not start on December 19, 2005. A preventive maintenance procedure was not adequate to identify a degraded condition associa
Region: I | Oyster Creek | 33553 | 03/31/2006 05/08/2006 | 2006002-04 | Self - Revealed | NCV | Public Radiation Safety | Green | Unauthorized Unmonitored Effluent Discharge to the Environment |  |  | TE?: N | 05000219 Oyster Creek |  | 71111.2 | A self-revealing finding was identified regarding inadequate procedure adherence when work activities on the main condenser during a forced maintenance outage resulted in an unauthorized, unmonitored effluent discharge to the environment between January 3
Region: I | Oyster Creek | 33554 | 03/31/2006 05/08/2006 | 2006002-05 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Administrative Control of High Radiation Area Keys |  |  | TE?: N | 05000219 Oyster Creek |  | 7112101 | The inspectors identified that AmerGen did not properly implement administrative controls for locked high radiation area (HRA) access keys maintained under the control of operations personnel. This finding was determined to be a non-cited violation of tec
Region: I | Peach Bottom | 125711 | 09/30/2019 10/22/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | E-1 Emergency Diesel Generator Failure Due to a Cable Fault |  | P.3 - Resolution | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 | Equipment Performance | 71152 | The inspectors identified a self-revealing, Green non-cited violation (NCV) associated with 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, “Corrective Action,” because Exelon did not identify and correct a condition adverse to qu
Region: I | Peach Bottom | 124835 | 03/31/2019 05/09/2019 | 2019001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Identify and Correct Vibration Induced Fretting Through Wall Wear of the High Pressure Coolant Injection (HPCI) Differential Pressure Sensing Line |  | P.5 - Operating Experience | TE?: N | 05000278 Peach Bottom 3 | Equipment Performance | 71152 | The inspectors identified a self-revealing finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for PB's failure to establish measures to assure that a condition adverse to q
Region: I | Peach Bottom | 124668 | 03/31/2019 05/09/2019 | 2019001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure of a Main Steam Isolation Valve to Fully Close |  | NPP | TE?: N | 05000278 Peach Bottom 3 | RCS Equipment and Barrier Performance | 71153 | The inspectors identified a self-revealing non-cited violation (NCV) of 10 CFR Part 50 Appendix B, Criterion XVI, "Corrective Action," because Exelon did not correct a condition adverse to quality on the Main Steam Isolation Valves (MSIV). Specifically, E
Region: I | Peach Bottom | 25953 | 02/08/2019 03/05/2019 | 2018012-01 | NRC | FIN | Barrier Integrity | Green | Spent Fuel Pool Instrument Level Indicator Failure to Evaluate and Track Functionality |  | P.2 - Evaluation | TE?: N | 05000278 Peach Bottom 3 |  | 2515/191 | The team identified a finding (FIN) of very low safety significance (Green) associated with implementation of CC-PB-118, “Peach Bottom Implementation of Diverse and Flexible Coping Strategies (FLEX) and Spent Fuel Pool Instrumentation (SFPI) Program,” whe
Region: I | Peach Bottom | 124383 | 02/01/2019 03/14/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Drywell Local Temperature Exceeds Analyzed Environmental Qualification (EQ) Value, Shortening Qualified Life for Several EQ Components |  | H.7 - Documentation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 | Design Control | 71111.21N | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50.49(j) and 10 CFR Part 50.49(d), Environmental Qualification (EQ) of Electric Equipment Important to Safety for Nuclear Power Plants, because E
Region: I | Peach Bottom | 25971 | 12/31/2018 02/13/2019 | 2018004-01 | NRC | FIN | Initiating Events | Green | Installation of Condensate Pump Cables Not in Accordance with Standard |  | H.2 - Field Presence | TE?: N | 05000278 Peach Bottom 3 |  | 71153 | The inspectors identified a self-revealing Green finding because Exelon did not conduct cable replacement in accordance with E-1317, Wire and Cable Notes and Details Power, Control, Instrument Cables, for the Unit 3 condensate pump transformers. Specifica
Region: I | Peach Bottom | 24390 | 09/30/2018 11/13/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | High Pressure Coolant Injection System Exhaust Pressure Switches Exceeded Documented Qualified Life |  | P.2 - Evaluation | TE?: N | 05000277 Peach Bottom 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” because Exelon did not establish measures to ensure that environmental qualification requirements for qualified components were correctly translated into
Region: I | Peach Bottom | 24074 | 06/30/2018 08/13/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Promptly Correct a Condition Adverse to Quality Concerning Battery Charger 2B-003-1 |  | P.1 - Identification | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.19 | The NRC identified a Green non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, “Corrective Action,” because Exelon did not identify and promptly correct a condition adverse to quality (CAQ) commensurate wi
Region: I | Peach Bottom | 24000 | 04/20/2018 05/09/2018 | 2018010-01 | NRC | FIN | Mitigating Systems | Green | Failure to Identify Time-Critical Action |  | P.2 - Evaluation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.05T | The inspectors identified a green finding because Exelon did not identify, validate, and incorporate a time-critical action reference in calculation PF-0016-025, "Fire Area 025 - Fire Safe Shutdown Analysis," in accordance with Sections 4.2 and 4.3 of OP-
Region: I | Peach Bottom | 24001 | 04/20/2018 05/09/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Develop and Maintain Mitigating Strategy |  | NPP | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.05T | The inspectors identified a Green non-cited violation of 10 CFR 50.54(hh)(2), "Conditions of Licenses," and Peach Bottom Unit 2 and Unit 3 Renewed Facility Operating License Condition 2.C.(11), "Mitigating Strategy License Condition," because Exelon did n
Region: I | Peach Bottom | 23520 | 03/31/2018 05/02/2018 | 2018001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Actions to Address Primary Containment Isolation Valve Condition Adverse to Quality |  | H.6 - Design Margins | TE?: N | 05000278 Peach Bottom 3 |  | 71111.12 | A Green self-revealing non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Exelon did not implement prompt corrective actions to address a condition adverse to qualit
Region: I | Peach Bottom | 21634 | 09/30/2017 11/02/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Instructions Not Followed for Replacement of HPSW Ventilation Switch Block |  | NPP | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.15 | A self-revealing NCV of Technical Specification (TS) 5.4.1, “Procedures,” of very low safety significance (Green) was identified for Exelon not implementing procedural instructions for the replacement of the HS-3-40H-3AV060 switch block associated wi
Region: I | Peach Bottom | 14360 | 03/31/2017 05/11/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Address '2C' Core Spray Motor Elevated Vibrations |  | P.3 Resolution | TE?: N | 05000277 Peach Bottom 2 |  | 71152B | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, because Exelon did not implement corrective actions in a timely manner to correct a condition adverse to quality on the '2C' core spray motor. Speci
Region: I | Peach Bottom | 23487 | 03/31/2017 05/11/2017 | 2017008-02 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Actions to Address Elevated Primary Containment Isolation Valve Leakage |  | P.3 - Resolution | TE?: N | 05000278 Peach Bottom 3 |  | 71152B | The inspectors identified a self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, because Exelon did not promptly implement corrective actions to address a condition adverse to quality on two containment isolation v
Region: I | Peach Bottom | 14359 | 12/31/2016 02/09/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Remove Foreign Material in CAD System Piping |  |  | TE?: N | 05000277 Peach Bottom 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion XVI, "Corrective Action," because Exelon did not adequately identify and correct a condition adverse to qua
Region: I | Peach Bottom | 14354 | 09/30/2016 11/03/2016 | 2016003-01 | NRC | FIN | Initiating Events | Green | Reactor Feed Pump Controller Power Supply Shelf Life Not Maintained. |  |  | TE?: N | 05000277 Peach Bottom 2 |  | 71153 | A self-revealing finding of very low safety significance (Green) was identified for Exelon's failure to maintain the Unit 2 'C' reactor feed pump (RFP) Woodward controller secondary power supply in accordance with PES-S-002, Exelon Shelf Life Program. Spe
Region: I | Peach Bottom | 14347 | 06/30/2016 08/08/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Improperly Stored Material in Reactor Building |  | H.8 Procedure Adherence | TE?: N | 05000277 Peach Bottom 2 |  | 71111.13 | Green. The NRC identified a very low safety significance (Green) NCV of Technical Specification (TS) 5.4.1 for Exelon's failure to adequately implement procedure requirements governing the storage of material in a safety-related structure. Specifically,
Region: I | Peach Bottom | 14348 | 06/30/2016 08/08/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Address Condition Adverse to the Fire Protection Program Alternative Shutdown Capability |  | H.1 Resources | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152 | Green. The inspectors identified an NCV of very low safety significance (Green) of PB Unit 2 and Unit 3 Facility Operating License condition 2.C.(4) for failure to implement and maintain in effect all provisions of the approved fire protection program. Ex
Region: I | Peach Bottom | 14353 | 06/30/2016 08/08/2016 | 2016002-03 | Self - Revealed | FIN | Initiating Events | Green | Human Performance Event Results in Emergent Downpower |  | H.2 Field Presence | TE?: N | 05000277 Peach Bottom 2 |  | 71153 | Green. A self-revealing finding of very low safety significance (Green) was identified for the failure of Exelon operators to use human performance error reduction tools during equipment manipulation in accordance with HU-AA-101, "Human Performance Tools
Region: I | Peach Bottom | 14346 | 12/31/2015 02/12/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Design Basis of EDG Lubrication System |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.22 | The inspectors identified a non-cited violation (NCV) of very low safety significance of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for not ensuring that the adequacy of PBAPS' emergency diesel generator (ED
Region: I | Peach Bottom | 14341 | 09/30/2015 11/09/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Incomplete Testing of Components from the Remote Shutdown Panels |  | H.12 Avoid Complacency | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1.a after Exelon did not establish and implement procedures to adequately test the Unit 2 and Unit 3 remote shutdown panels (RSPs). Specifically, Exelon's surveillance procedure did
Region: I | Peach Bottom | 14340 | 04/24/2015 06/04/2015 | 2015008-01 | NRC | FIN | Initiating Events | Green | Failure to Initiate IRs for Out-of-Calibration Single Point Vulnerabilitys. |  | P.1 Identification | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) because PBAPS did not initiate issue reports (IR) to identify out-of-tolerance conditions for a number of single point vulnerability (SPV) instruments. An SPV instrument is any in
Region: I | Peach Bottom | 14339 | 03/31/2015 05/13/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Flood Detection Level Switches into Maintenance Rule |  | H.3 Change Management | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of very low safety significance (Green) of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Exelon did not include certain flood indica
Region: I | Peach Bottom | 14336 | 09/30/2014 11/07/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Corrective Actions Not Timely for EOC of Appendix R Broken Wires |  | P.2 Evaluation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of the PBAPS Units 2 and 3 operating licenses, Section 2.C.4, "Fire Protection," because Exelon did not have the ability to implement all provisions of their approved Fire Protection Program as d
Region: I | Peach Bottom | 14337 | 09/30/2014 11/07/2014 | 2014004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Scaffold Obstructs 'A' RHR Discharge Check Valve |  | H.5 Work Management | TE?: N | 05000277 Peach Bottom 2 |  | 71111.22 | A self-revealing finding was identified involving an NCV of very low safety significance (Green) for Technical Specification (TS) 5.4.1 "Procedures," because Exelon did not correctly implement procedure MA-MA-796-024-1001, Revision 8, "Scaffold Criteria f
Region: I | Peach Bottom | 14338 | 09/30/2014 11/07/2014 | 2014004-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71114.05 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2), 10 CFR 50.47(b)(10), and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the PBAPS, Units 2 and 3, Emergency
Region: I | Peach Bottom | 14328 | 04/04/2014 05/19/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Deficient E2 EDG Loading Calculation Design |  | P.2 Evaluation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a Green non-cited violation of Title 10 Code of Federal Regulations 50, Appendix B, Criterion III, Design Control, for failure to verify and ensure that the emergency diesel generators (EDGs) were capable of performing their design s
Region: I | Peach Bottom | 14329 | 04/04/2014 05/19/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Voltage Assumption Used to Verify MOV Capability |  | P.2 Evaluation | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a Green non-cited violation of Title 10 Code of Federal Regulations 50, Appendix B, Criterion III, Design Control. Specifically, Exelon did not correctly verify the capability of alternating current motor-operated valves (MOVs) at a
Region: I | Peach Bottom | 14320 | 09/30/2013 11/15/2013 | 2013004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate EP Procedure Change Management Controls to Ensure Adquate EAL Classification and Assessment Capability for Effluent Parameters |  | H.3(b) Work Activity Coordination | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.22 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulation (CFR) 50.54(q)(2) associated with 50.47(b)(4) because PBAPS failed to control emergency planning (EP) procedure changes in a manner that would ensure
Region: I | Peach Bottom | 14321 | 09/30/2013 11/15/2013 | 2013004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure of Conspicuously Post and Lost/Guard a HRA on the Unit 3 Turbine Deck Scaffold. |  | H.3(a) Work Planning | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | NONE | The inspectors identified a NCV of very low safety significance of Technical Specification (TS) 5.7.2 because Exelon did not control the access point to a Locked High Radiation Area (LHRA). The performance deficiency (PD) was related to not controlling ac
Region: I | Peach Bottom | 14304 | 03/31/2013 05/09/2013 | 2013002-01 | NRC | FIN | Barrier Integrity | Green | Inadequate Operability Determination in Response to Power Load Unbalance Device Failure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000277 Peach Bottom 2 |  | 71111.13 | The inspectors identified a Green finding for PBAPS's failure to follow the operability determination (OD) process described in Procedure OP-AA-108-115, "Operability Determinations." Specifically, on February 24, 2013, between 6:15 a.m. and 10:30 a.m., an
Region: I | Peach Bottom | 14299 | 09/30/2012 11/14/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preplanning and Performance of Maintenance/Modifications Resulted in Unavailability of RHR 'B' Loop. |  | H.3(a) Work Planning | TE?: N | 05000277 Peach Bottom 2 |  | 71111.13 | The inspectors identified a Green, self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures." The inspectors determined that PBAPS did not properly preplan and perform maintenance/modifications to the Unit 2 low press
Region: I | Peach Bottom | 14288 | 06/30/2012 08/14/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control to Demonstrate RCIC System Design Basis Start-up Response Time | EA Case: 2012094 | H.4(b) Procedural Compliance | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.22 | The inspectors identified a NCV of very low safety significance of Title 10 Code of Federal Regulation (CFR) 50, Appendix B, Criterion XI, "Test Control," because Exelon conducted unacceptable pre-conditioning of the reactor core isolation cooling (RCIC
Region: I | Peach Bottom | 14279 | 03/31/2012 05/07/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action to Address Emergency Diesel Generator Control Power Circuit Chronic Internal Faults | EA Case: 2011224 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.19 | The inspectors determined that PBAPS did not establish measures to promptly identify and correct a condition adverse to the quality related to the emergency diesel generator (EDG) control power circuit. The performance deficiency (PD) constituted a Green,
Region: I | Peach Bottom | 14280 | 03/31/2012 05/07/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action to Address Residual Heat Removal Heat Exchanger Graphite Gasket Leaks | EA Case: 2011224 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 |  | 71111.19 | The inspectors determined that PBAPS did not promptly identify and correct residual heat removal (RHR) heat exchanger (HX) graphoil gasket leaks. The PD constituted a Green, self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Acti
Region: I | Peach Bottom | 14281 | 03/31/2012 05/07/2012 | 2012002-03 | NRC | NCV | Initiating Events | Green | Untimely Corrective Actions Resulted in Spent Fuel Pool Boraflex Degradation Exceeding Design Limits | EA Case: 2011224 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152 | The inspectors identified a PD that was determined to be a finding of very low safety significance (Green) involving a NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure by PBAPS to take timely corrective action to corr
Region: I | Peach Bottom | 14275 | 12/31/2011 02/10/2012 | 2011005-01 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Action to Correct MOV Degraded Stem Lubrication |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.12 | The inspectors determined that PBAPS's failure to promptly correct a condition adverse to quality associated with a safety-related MOV constituted a Green, self-revealing NCV of 10 CFR, Appendix B, Criterion XVI, "Corrective Action." Specifically, correct
Region: I | Peach Bottom | 14289 | 12/31/2011 02/10/2012 | 2012003-02 | NRC | FIN | Public Radiation Safety | Green | Failure to Establish, Implement, and Maintain Adequate QA for Effluent and Environmental Monitoring |  | H.4(b) Procedural Compliance | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71124.06 | The inspectors identified a Green finding associated with the failure to establish, implement, and maintain adequate quality assurance (QA) program elements in the area Enclosure 4 of effluent and environmental monitoring as required by Peach Bottom, Un
Region: I | Peach Bottom | 14274 | 08/12/2011 09/16/2011 | 2011010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with Safety Relief Valve Lift Setpoint Drift. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) involving a NCV of 10 CFR 50, Appendix B, Criterion XVl, "Corrective Action," because Exelon staff did not implement timely corrective action associated with safety relief valve
Region: I | Peach Bottom | 14257 | 03/31/2011 05/06/2011 | 2011002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Fuel Handling Procedures Were Inadequate to Prevent Fuel fro mContacting an Obstruction |  | H.4(a) Human Error Prevention | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | NONE | A Green self-revealing NCV of Technical Specification (TS) 5.4.1 "Procedures" was identified, because PBAPS's procedures for refueling equipment operation and core alterations were inadequate to prevent a fuel bundle from contacting a core spray inspectio
Region: I | Peach Bottom | 14258 | 03/11/2011 04/25/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Capability of the EDG Fuel Oil Transfer Pumps to Fulfill Their Safety Functions Under all Conditions |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion lll, "Design Control," in that, Exelon did not ensure the ability to transfer fuel oil between underground fuel oil storage t
Region: I | Peach Bottom | 14266 | 03/11/2011 04/25/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Temporary Battery Cart Seismic Configuration Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion lll, "Design Control," in that Exelon did not verify the adequacy of the seismic design for temporary battery cells that had
Region: I | Peach Bottom | 14256 | 12/31/2010 02/03/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Main Steam Isolation Valve Test Control |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion Xl, "Test Control." The inspectors determined that PBAPS's test control of ST-O-07G-470-3, "Main Steam lsolation Valve (MSIV) Closure Timing," Revision 15, was inadequate to demo
Region: I | Peach Bottom | 14255 | 09/30/2010 11/10/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Voltage was Available to Safety-Related Equipment |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | NONE | The inspectors identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Exelon did not assure that applicable regulatory requirements and the design basis were correctly transl
Region: I | Peach Bottom | 14252 | 03/31/2010 05/12/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Action to Address Multiple Slow Control Rods with Adverse Scram Pilot Solenoid Valve Diaphragms |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 |  | 71111.12 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," occurred when PBAPS failed to identify and correct a condition adverse to the quality. Specifically, an issue related to control rod drive scram solenoid pilot valve
Region: I | Peach Bottom | 14249 | 12/31/2009 02/08/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Continuously Submerged Cables Design Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.06 | The inspectors identified an NCV of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," because PBAPS has not maintained safety-related power cables (including low voltage cables) in an environment for which they were designed and tested. Specif
Region: I | Peach Bottom | 14247 | 12/31/2009 02/08/2010 | 2009005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures and Implement the Exelon Nuclear Cable Condition Monitoring Program For Non Safety Related Control And Power Cables Within The Scope Of The Maintenance Rule. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.06 | The inspectors identified a finding for the failure to follow the Exelon fleet procedure for cable monitoring (ER-AA-3003) of non-safety-related cables within the scope of the 10 CFR 50.65 (the Maintenance Rule). Specifically, PBAPS had reported to the NR
Region: I | Peach Bottom | 14248 | 12/31/2009 02/08/2010 | 2009005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Verification Practices while Handling Fuel and Fuel Components |  | H.4(a) Human Error Prevention | TE?: N | 05000277 Peach Bottom 2 |  | 71152 | A Green self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when PBAPS inadequately implemented human performance tools and verification practices for fuel handling and fuel component handling
Region: I | Peach Bottom | 14237 | 09/30/2009 11/12/2009 | 2009004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Adherence Results in the Loss of Safety Function of Systems Supplied by the SGIG System |  | H.4(a) Human Error Prevention | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71153 | A self-revealing Green NCV was identified for failure to comply with Technical Specification (TS) 5.4.1, "Procedures," which required that procedures be established, implemented, and maintained for the safety grade instrument gas (SGIG) system. Specifical
Region: I | Peach Bottom | 14234 | 09/30/2009 10/28/2009 | 2009010-01 | NRC | NCV | Barrier Integrity | Green | PBAPS Failed to Maintain the Capability to Ensure at Least 500 gpm SFP External Make-up flow Was Achievable Within Two Hours. |  | H.2(d) Facilities & Equipment | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Peach Bottom | 14233 | 08/07/2009 09/21/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate CAs for Grease Applied to DC Contactors |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152B | The inspectors identified a non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for failure to identify and correct a condition adverse to quality. Specifically, in March 2009, Exelon did not take adequate corrective act
Region: I | Peach Bottom | 14231 | 06/30/2009 08/10/2009 | 2009003-01 | Self - Revealed | NCV | Mitigating Systems | Green | MOV Program Procedures Were Inadequate with Regard to periodicity of preventive Maintenance Activities for Stem Lubrication. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified. Specifically, Exelon's Motor Operated Valve (MOV) Program procedures lacked specific instructions to prescribe an acceptable frequency fo
Region: I | Peach Bottom | 14232 | 05/23/2009 08/10/2009 | 2009003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedure Adherence Results in Trip of 3 'A' Recirc Pump and Plant Transient |  | H.4(b) Procedural Compliance | TE?: N | 05000278 Peach Bottom 3 |  | 71153 | A self-revealing finding was identified when PBAPS personnel incorrectly performed a maintenance procedure for tuning the reactor recirculation pump (RRP) motor generator (MG) set voltage regulator. Specifically, maintenance personnel adjusted a potentiom
Region: I | Peach Bottom | 14226 | 03/31/2009 05/12/2009 | 2009002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Work Instructions Result in Inadvertent ESF Actuation |  | H.3(a) Work Planning | TE?: N | 05000278 Peach Bottom 3 |  | 71111.13 | A self-revealing NCV of 10 CFR 50 Appendix B, Criteria V, "Instructions, Procedures and Drawings" was identified when inadequate work instructions resulted in a momentary shorting of a terminal lead during maintenance, which caused an inadvertent Unit 3,
Region: I | Peach Bottom | 14227 | 03/31/2009 05/12/2009 | 2009002-02 | Self - Revealed | NCV | Initiating Events | Green | Inoperable 'A' Wide-Range Neutron Monitoring (WRNM) Results in a Condition Prohibited by Technical Specifications |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000278 Peach Bottom 3 |  | 71111.15 | A self-revealing, Green NCV of Unit 3 TS 3.0.4 was identified by the inspectors on January 26, 2009, when a half-scram occurred on Unit 3, shortly after Unit 3 entered Mode 2 for plant startup. Specifically, the 'A' Wide-Range Neutron Monitoring (WRNM) wa
Region: I | Peach Bottom | 14222 | 12/30/2008 01/29/2009 | 2008005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Incorrect Performance of Procedure Step Resulted in Inoperability of a DC Bus for Longer than the TS Allowed Outage Time |  | H.3(b) Work Activity Coordination | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71153 | A self-revealing (Green) NCV of Technical Specification (TS) 5.4.1 was identified when operators inadequately implemented an abnormal operating (AO) procedure on two occasions. Specifically, an event where the Unit 2 Division II direct current (DC) electr
Region: I | Peach Bottom | 14217 | 09/29/2008 11/14/2008 | 2008004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate EOC Review Results in Delay in Discovery of ESW Leaks |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.15 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures and Drawings," was identified for a failure to follow procedure, WC-PB-2000, "Outage Control Center (OCC) Emergent Issue Response," that resulted in an inadequate ex
Region: I | Peach Bottom | 14218 | 09/29/2008 11/14/2008 | 2008004-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Comply with 10 CFR 20 Appendix G |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7112202 | The inspectors identified a NCV of 10 CFR 20, Appendix G, Section III.C. 5. Specifically, the licensee did not conduct a Quality Assurance Program sufficient to assure conformance with 10 CFR 61.55, in that, the program was not adequate to identify incorr
Region: I | Peach Bottom | 14214 | 06/30/2008 08/13/2008 | 2008003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Foreign Material Discovered in Fire Valve |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.12 | Green. A self-revealing NCV of PBAPS's Unit 2 License Condition 2.C (4), "Fire Protection Program," was identified when maintenance personnel discovered foreign material inside a supply valve to an automatic 13KV switchgear sprinkler system installed beca
Region: I | Peach Bottom | 14204 | 05/21/2008 05/21/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Battery Connection Resistance Testing |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of Technical Specification (TS) 3.8.4.5, in that Exelon did not verify certain battery connection resistances were within the TS limit. Specifically, Exelon did
Region: I | Peach Bottom | 14208 | 05/16/2008 06/25/2008 | 2008006-01 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Peach Bottom | 14209 | 05/16/2008 06/25/2008 | 2008006-02 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Peach Bottom | 14213 | 05/16/2008 06/25/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | B..5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: I | Peach Bottom | 14207 | 04/30/2008 06/05/2008 | 2008502-01 | NRC | NCV | Emergency Preparedness | Green | Failure of the Peach Bottom Dose Assessment Program to Meet the Requirements of 10 CFR 50.47(b)(9) |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71114.01 | A NRC-identified non-cited violation (NCV) of 10 CFR 50.47(b)(9) and 10 CFR Part 50, Appendix E, Section IV.B, was identified for failure of the licensee's dose assessment program to provide for the means for continually assessing the impact of the releas
Region: I | Peach Bottom | 14205 | 04/11/2008 05/21/2008 | 2008007-02 | NRC | FIN | Mitigating Systems | Green | Non-conservative Inputs Used in Design Calculations for Offsite Power Operability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a finding of very low safety significance, in that Exelon failed to use appropriate inputs in design calculations as required by Exelon Procedure CC-AA-102 - Design Input and Configuration Change Impact Screening. The requirements of t
Region: I | Peach Bottom | 14202 | 03/31/2008 04/28/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Document Fire Brigade Deficiencies |  | P.3(a) Self-Assessment | TE?: N | 05000277 Peach Bottom 2 |  | 71111.05A | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1, which requires that written procedures be implemented covering the Fire Protection Program. The Fire Drill Performance procedure was inadequately implemented beca
Region: I | Peach Bottom | 14200 | 12/31/2007 02/14/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include Reactor Building Drain System Into the Scope of the Maintenance Rule Program |  | P.2(b) Implementing Operating Experience | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.12 | A Green non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified for PBAPS's failure to include the reactor building equipment and floor drain plugs in the scope of t
Region: I | Peach Bottom | 14191 | 06/30/2007 07/31/2007 | 2007003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Implementation of Work Order Instructions Caused the Installation of an Incorrect Size Breaker and Resulted in a Fire in the '4T4' 480 Volt Load Center |  | H.4(b) Procedural Compliance | TE?: N | 05000278 Peach Bottom 3 |  | 71153 | A self-revealing finding was identified for inadequate implementation of work order (WO) instructions to verify the correct breaker frame size during the overhaul of a compatible spare breaker for installation into the '4T4' 480 volt load center. This con
Region: I | Peach Bottom | 14192 | 06/30/2007 07/31/2007 | 2007003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Missed Procedure Step Resulted in Unplanned Overloading of the E-3 EDG |  | H.4(b) Procedural Compliance | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71153 | A self-revealing NCV of Technical Specification (TS) 5.4.1, was identified when operators inadequately implemented a surveillance procedure by missing a procedure step. The missed step placed the E-3 emergency diesel generator (EDG) in the isochronous mod
Region: I | Peach Bottom | 14198 | 06/30/2007 07/31/2007 | 2007003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Procedural Compliance Issues Result in Damage to the Diesel Driven Fire Pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71153 | A self-revealing NCV of TS 5.4.1, was identified when operators manipulated a diesel-driven fire pump (DDFP) cooling water valve outside of procedure guidance. The improper manipulation led to misalignment of the DDFP cooling water that subsequently damag
Region: I | Peach Bottom | 14186 | 05/18/2007 06/27/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a 2006 NRC-Identified NCV in a Timely Manner - Quarterly Surveillance Test with Non-Conservative Acceptance Criteria for the HPCI Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71152B | The NRC identified a Green NCV of 10CFR50, Appendix B, Criterion XVI, "Corrective Actions," related to the failure to correct the March 2006 deficiency identified in NCV 05000277,278/2006009-01, related to less than adequate acceptance criteria in a quart
Region: I | Peach Bottom | 14187 | 05/18/2007 06/27/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a 2005 NRC-Identified NCV in a Timely Manner - Failure to Follow a Site Procedure Resulted in a Delayed Operability Determination |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000277 Peach Bottom 2 |  | 71152B | The NRC identified a Green NCV of 10CFR50, Appendix B, Criterion XVI, "Corrective Action," for failure to correct a condition adverse to quality for approximately 22 months, associated with Class 1, 2, and 3 pressure boundary leakage. Specifically, NCV 05
Region: I | Peach Bottom | 14174 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Non-Technical Specifications Position Incorrectly Credited for Active License Maintenance |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.11B | The inspectors identified a NCV of 10 CFR 55.53(e), "Conditions of Licenses," for incorrectly credited individuals with actively performing the functions of a senior operator (SO) while that individual was staffing a position that was not specified in PBA
Region: I | Peach Bottom | 14175 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Public Radiation Safety | Green | Exelon Did Not Establish and Implement Adequate Procedures for Quality Assurance of Effluent Monitoring as Required by Technical Specification 5.4.1. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7112201 | The inspectors identified a NCV of TS 5.4.1.C for inadequately establishing and maintaining procedures for effluent monitoring. Specifically, the quality assurance (QA) required procedures for effluent monitoring were inadequate to detect non-representati
Region: I | Peach Bottom | 14176 | 03/31/2007 05/15/2007 | 2007002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Develop and Implement HPCI Surveillance Testing in a Manner Consistent with Vendor Specified Test Instructions |  |  | TE?: N | 05000277 Peach Bottom 2 |  | 71153 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for inadequate surveillance procedure development that changed the use of a common high pressure coolant injection (HPCI)\\reactor co
Region: I | Peach Bottom | 14172 | 12/31/2006 02/05/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determinations Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000277 Peach Bottom 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for a failure to follow administrative procedures for conducting operability evaluations of nonconforming equipment which resul
Region: I | Peach Bottom | 14171 | 09/30/2006 11/03/2006 | 2006004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Procedures by Performing Equipment Manipulations Without Instructions |  | H.4(b) Procedural Compliance | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71153 | A self-revealing non-cited violation of Technical Specification (TS) 5.4.1.a, "Procedures," occurred when, during a pre-job walk down, a senior reactor operator (SRO) inappropriately operated an instrument valve without a procedure. This inappropriate val
Region: I | Peach Bottom | 14169 | 06/30/2006 07/26/2006 | 2006003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Annual Operating Test Administered at Limerick |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.11Q | The inspectors identified a finding of very low safety significance (Green) non-cited violation (NCV) of 10 CFR 55.59(a)(2)(ii) for an inadequate annual operating test that was administered at Limerick for Peach Bottom and Limerick Senior Reactor Operator
Region: I | Peach Bottom | 14167 | 06/30/2006 07/26/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Foreign Material Exclusion Controls for the HPCI Turbine Exhaust Drain Inboard Isolation Valve. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000278 Peach Bottom 3 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when PBAPS personnel inadequately accomplished foreign material exclusion (FME) recovery procedures for the Unit 3 high pressure coolant
Region: I | Peach Bottom | 14168 | 06/30/2006 07/26/2006 | 2006003-03 | NRC | NCV | Emergency Preparedness | Green | Exelon Did Not Maintain Respiratory Protective Equipment in Accordance with Manufacture's Guidance and Regulatory Requirements. |  |  | TE?: N | 05000277 Peach Bottom 2 |  | 7112103 | The inspectors identified a Green NCV of 10 CFR 50.47(b)(10) was identified for failure to maintain protective measures for emergency workers. On April 20, 2006, the NRC identified a ready-for-use self-contained breathing apparatus (SCBA), in the main con
Region: I | Peach Bottom | 14166 | 04/21/2006 06/01/2006 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Pumps Test Acceptance Criteria |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, Test Control. The team determined that the licensee had failed to ensure that the high pressure coolant injection (HPCI)
Region: I | Peach Bottom | 14165 | 03/31/2006 05/03/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Post-Maintenance Testing of the E-2 EDG Air Coolant Auxiliary Pump |  |  | TE?: N | 05000278 Peach Bottom 3 |  | 71111.19 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for not adequately testing the E-2 emergency diesel generator (EDG) air coolant auxiliary pump following shaft packing replacement. Th
Region: I | Peach Bottom | 124385 | 03/14/2019 |  |  | LIV |  | Green | Failure to Replace 27 Environmenatal Qualification (EQ) Components or Demonstrate Additional Qualificatoin Prior to the End of Designated Qualified Life |  |  | TE?: N | 05000277 Peach Bottom 2 05000278 Peach Bottom 3 |  | 71111.21N
Region: I | Peach Bottom | 14366 | 08/03/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Corrective Action not Implemented Correctly for Replacement of Reactor Core Isolation Coolilng (RCIC) Reverse Control Relay (RCR) Contacts |  | H.8 Procedure Adherence | TE?: N | 05000278 Peach Bottom 3 |  | 71111.15 | A self-revealing non-cited violation (NCV) of 10 Code of Federal Regulation (CFR) Part 50, Appendix B, Criterion XVI, Corrective Actions, of very low safety significance (Green) was identified for Exelon not correcting a condition adverse to quality conce
Region: I | Pilgrim | 25920 | 12/31/2018 02/13/2019 | 2018004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Implement Work Order for Feedwater Regulating Valve ‘A’ |  | P.3 - Resolution | TE?: N | 05000293 Pilgrim 1 | Equipment Performance | 71111.19 | A Green self-revealing finding was identified for the inadequate implementation of a work order on feedwater regulating valve ‘A,’ as required by EN-WM-102, “Work Implementation and Closeout.” Specifically, Entergy did not install the encoder and stepper
Region: I | Pilgrim | 24632 | 09/30/2018 11/13/2018 | 2018003-06 | NRC | NCV | Barrier Integrity | Green | Failure to Identify a Condition Adverse to Quality Associated with Elevated Standby Gas Treatment System Accumulator Leakage |  | H.9 - Training | TE?: N | 05000293 Pilgrim 1 |  | 71111.19 | The inspectors identified a Green non-cited violation of Technical Specifications 3.7.B.1.c because Entergy exceeded the TS allowed outage time for the standby gas treatment system when the station did not identify an adverse condition associated with ele
Region: I | Pilgrim | 24078 | 06/30/2018 08/14/2018 | 2018002-03 | NRC | NCV | Initiating Events | Green | Failure to Properly Implement the Fatigue Management Program – Work Hour Controls for Covered Workers |  | P.3 - Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 26.205(d). During the period December 2017 to April 2018, Entergy did not properly control the work hours of several workers who performed work covered under 10 CFR 26.4(a). Specifically, on eleven occasions
Region: I | Pilgrim | 24079 | 06/30/2018 08/14/2018 | 2018002-04 | Self - Revealed | FIN | Barrier Integrity | Green | Loss of Secondary Containment Integrity due to Simultaneously Opened Airlock Doors |  | H.9 - Training | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealed Green finding was identified when Entergy did not ensure implementation of Procedure 1.3.135, “Control of Doors,” which requires station personnel to ensure closing and latching of doors. This resulted in the loss of secondary containment
Region: I | Pilgrim | 22637 | 11/13/2017 12/21/2017 | 2017009-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Address Previously Identified Non-Cited Violation |  | P.2 - Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71152B | An NRC-identified Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified because Entergy staff did not promptly identify and correct a condition adverse to quality associat
Region: I | Pilgrim | 22640 | 11/13/2017 12/21/2017 | 2017009-02 | NRC | FIN | Mitigating Systems | Green | Failure to Correct Programmatic Issues with Implementation of the Operability Determination Process |  | H.13 - Consistent Process | TE?: N | 05000293 Pilgrim 1 |  | 71152B | An NRC-identified Green finding without an associated regulatory violation (FIN) against Entergy procedure EN-LI-102, “Corrective Action Program,” was identified because Entergy staff did not ensure that corrective actions were developed to adequately add
Region: I | Pilgrim | 22638 | 11/13/2017 12/21/2017 | 2017009-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for SSW Pump Issues Result in Multiple Pump Failures |  | P.3 - Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71152B | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI with two examples was identified because Entergy did not identify and correct a condition adverse to quality associated with the salt service water (SSW) pumps. Specifically, correcti
Region: I | Pilgrim | 22639 | 11/13/2017 12/21/2017 | 2017009-04 | NRC | NCV | Mitigating Systems | Green | Loss of Control Power to EDG not Corrected in Accordance with CAP |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71152B | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI was identified because Entergy did not identify and correct a condition adverse to quality associated with a previous failure of the 125 volt direct current (VDC) control power to th
Region: I | Pilgrim | 21657 | 09/30/2017 11/14/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Loss of Control Room Air Conditioning |  | H.6 - Design Margins | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | An NRC-identified Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified when Entergy did not establish an adequate abnormal operating procedure (AOP
Region: I | Pilgrim | 21658 | 09/30/2017 11/14/2017 | 2017003-02 | Self - Revealed | NCV | Barrier Integrity | Green | HPCI Turbine Exhaust Check Valve Failures Exceed Primary Containment Leakage Limit |  | P.3 - Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71152 | A self-revealed Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” and TS 3.7.A.2, “Containment Systems – Primary Containment,” was identified when Entergy did not appropriately establish procedures for mainten
Region: I | Pilgrim | 21659 | 09/30/2017 11/14/2017 | 2017003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance Replacement Schedule for the SRVs Solenoid Valve |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71153 | An NRC-identified Green NCV of Technical Specification (TS) 5.4.1.a, “Procedures,” was identified because Entergy did not establish an appropriate preventive maintenance (PM) schedule for replacement of non-metallic parts internal to the ‘A’ safety relief
Region: I | Pilgrim | 21633 | 09/30/2017 11/14/2017 | 2017003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Improper Environmental Qualification of Replacement Differential Pressure Indication Switches |  | P.2 - Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71153 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified in that Entergy did not correct a condition adverse to quality when they replaced differential pressure indication switch (DPIS)-2352, DPIS-1244,
Region: I | Pilgrim | 23490 | 09/30/2017 11/14/2017 | 2017003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Verify, Justify, and Document Activation Energy for Main Steam Isolation Valve Position Indicator Switch Assembly Components |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71153 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified in that Entergy did not assure that the applicable design bases were correctly translated into specifications, drawings, procedures, and instruction
Region: I | Pilgrim | 21660 | 09/30/2017 11/14/2017 | 2017003-06 | Self - Revealed | NCV | Barrier Integrity | Green | MSIVs Fail Local Leak Rate Test and Exceed La |  | P.2 - Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealed Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” and TS 4.7.A.2.a.3.2 and TS 4.7.A.2.a.3.4, “Primary Containment- Primary Containment Integrity,” was identified because Entergy did not implement a vendor recommende
Region: I | Pilgrim | 21661 | 09/30/2017 11/14/2017 | 2017003-07 | Self - Revealed | NCV | Mitigating Systems | Green | Core Spray Voiding Due to Inadequate Instructions |  | H.12 - Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealed Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures and Drawings,” and TS 3.5.A, “Core Spray and Low Pressure Coolant Injection Systems,” was identified when Entergy did not appropriately establish procedures fo
Region: I | Pilgrim | 21628 | 08/17/2017 09/28/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate the Correct Design Limit for the Condensate Storage Tank Water Temperature |  | NPP | TE?: N | 05000293 Pilgrim 1 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, “Design Control,” in that Entergy did not transl
Region: I | Pilgrim | 21629 | 08/17/2017 09/28/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verification of Emergency Diesel Generator Under-Frequency Alarm Setpoint |  | H.12 - Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green) involving an NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” in that Entergy did not adequately verify that the emergency diesel generator (EDG) under-frequen
Region: I | Pilgrim | 18470 | 06/30/2017 08/14/2017 | 2017002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedure Requirements for the Control of a Flood Protection Barrier |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71111.2 | An NRC-identified Green finding was identified because Entergy personnel did not follow Procedure 1.3.135, "Control of Doors," to adequately control a condenser bay flood protection door. Specifically, on May 22, 2017, Entergy personnel failed to control
Region: I | Pilgrim | 18029 | 06/30/2017 08/14/2017 | 2017002-03 | NRC | NCV | Initiating Events | Green | Inaccurate Suppression Pool Water Level Instrument not Identified during Post-Event Prompt Investigation |  | P.1 Identification | TE?: N | 05000293 Pilgrim 1 |  | 71153 | An NRC-identified Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy staff did not identify and correct a condition adverse to quality related to suppre
Region: I | Pilgrim | 23489 | 06/30/2017 08/14/2017 | 2017002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Improper System Restoration Results in Suppression Pool Inoperability |  | H.8 - Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green NCV of TS 5.4.1.a, "Procedures," was identified on March 31, 2017, when operators did not follow procedures and caused an inadvertent increase in the suppression pool water level. The inspectors determined that the operators did not
Region: I | Pilgrim | 18469 | 06/30/2017 08/14/2017 | 2017002-05 | Self - Revealed | NCV | Barrier Integrity | Green | Damper Failure Causes Loss of Secondary Containment |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," and TS 3.7.C.2, "Containment Systems - Secondary Containment," was identified because Entergy did not establish an appropriate interval to ove
Region: I | Pilgrim | 18463 | 06/30/2017 08/14/2017 | 2017002-06 | NRC | NCV | Barrier Integrity | Green | Secondary Containment Testing not Performed per Technical Specifications |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71153 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," and TS 4.7.C, "Containment Systems - Secondary Containment," was identified when Entergy performed a surveillance test requiring a refueling outage while online. Spec
Region: I | Pilgrim | 18022 | 03/31/2017 05/15/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures for Controlled Shutdown |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71111.19 | The inspectors identified a Green NCV of TS 5.4.1 "Procedures," when Entergy did not follow the site procedures for limiting condition for operation (LCO) entries, Technical Specification (TS) usage, and procedure adherence. Specifically, on March 1, 20
Region: I | Pilgrim | 18027 | 03/31/2017 05/15/2017 | 2017001-03 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Actions Associated with Boraflex Degradation in the Spent Fuel Pool |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," when Entergy did not take timely corrective action to correct a condition adverse to quality. Specifically, when BADGER testing results revealed gaps
Region: I | Pilgrim | 18458 | 03/21/2017 05/10/2017 | 2016011-08 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of Maintenance Rule Scoped Components |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of 10 CFR 50.65(a)(2), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants." Specifically, Entergy did not demonstrate that the performance of 18 maintenance rule scoped
Region: I | Pilgrim | 18450 | 03/12/2017 05/10/2017 | 2016011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify All Root Causes of a Significant Condition Adverse to Quality |  | H.12 Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not adequately determine all root causes associated with a significant
Region: I | Pilgrim | 18455 | 03/12/2017 05/10/2017 | 2016011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Corrective Actions to Preclude Repetition of a Significant Condition Adverse to Quality |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not implement CAPRs for a significant condition adverse to quality identified in root cause evaluation CR-PNP-2016-0
Region: I | Pilgrim | 18451 | 03/12/2017 05/10/2017 | 2016011-03 | NRC | FIN | Initiating Events | Green | Failure to Issue Appropriate Corrective Actions to Preclude Repetition for the Causes of the September 2016 Scram |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green finding because Entergy did not issue appropriate CAPRs in accordance with Entergy procedure EN-LI-102, "Corrective Action Process," Revision 28. Specifically, Entergy did not issue adequate CAPRs associated with Root Cause
Region: I | Pilgrim | 18456 | 03/12/2017 05/10/2017 | 2016011-04 | NRC | NCV | Mitigating Systems | Green | Programmatic Issue with Implementation of the Operability Determination Process |  | H.4 Teamwork | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, the NRC team identified a programmatic issue because in some cases, Entergy did not enter the operabili
Region: I | Pilgrim | 18457 | 03/12/2017 05/10/2017 | 2016011-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Corrective Actions to Address Scope of Procedure Quality Issues |  | H.1 Resources | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy implemented inadequate corrective actions to address the procedure quality issues identified in CR-PNP-2016 02058. Speci
Region: I | Pilgrim | 18033 | 03/12/2017 05/10/2017 | 2016011-06 | NRC | NCV | Mitigating Systems | Green | Design Change Not Appropriately Reviewed by Entergy |  |  | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a preliminary greater than Green finding and apparent violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with Entergy's failure to ensure that design changes were subject to design control measures
Region: I | Pilgrim | 18461 | 03/12/2017 05/10/2017 | 2016011-09 | NRC | NCV | Barrier Integrity | Green | Ineffective Corrective Actions to Address Conditions Adverse to Quality Regarding Components in Contact with or Close Proximity to the Drywell Liner |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with Entergy's failure to correct a condition adverse to quality affecting safety-related equipment. Specifically, during a p
Region: I | Pilgrim | 18459 | 03/12/2017 05/10/2017 | 2016011-10 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality for the Residual Heat Removal System |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not take timely corrective action for a previously identified condition adverse to quality. Specifically, Entergy fa
Region: I | Pilgrim | 18460 | 03/12/2017 05/10/2017 | 2016011-11 | NRC | FIN | Mitigating Systems | Green | Failure to Adequaely Develop and Implement Targeted Performance Improvement Plans |  | H.3 Change Management | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The NRC team identified a Green finding because Entergy did not adequately develop and implement a CAPR of a root cause related to a Category 'A' CR, as required by Entergy Procedure EN-LI-102, "Corrective Action Program." Specifically, Entergy did not ad
Region: I | Pilgrim | 17982 | 12/31/2016 02/14/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Perform an Operability Evaluation for a Recirculation Flow Converter |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not perform a prompt operability determination and adequately eva
Region: I | Pilgrim | 17992 | 12/31/2016 02/14/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Ineffective Corrective Actions to Correct High Pressure Coolant Injection System Vibrations |  | H.6 Design Margins | TE?: N | 05000293 Pilgrim 1 |  | 71152 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified in that Entergy did not identify and correct a condition adverse to quality related to high pressure coolant injection (HPCI) pump degraded perfor
Region: I | Pilgrim | 17993 | 12/31/2016 02/14/2017 | 2016004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Assess and Manage Risk Associated with Shutdown Transformer Protective Relay Testing |  | H.12 Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for Entergy's failure to properly assess and manage the increase in risk due to performing protective rela
Region: I | Pilgrim | 18000 | 12/31/2016 02/14/2017 | 2016004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correct a Condition Adverse to Quality Associated with Main Steam Isolation Valve |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified in that Entergy did not promptly correct a condition adverse to quality associated with the operability of a MSIV. Specifically, Entergy did not t
Region: I | Pilgrim | 18001 | 12/31/2016 02/14/2017 | 2016004-05 | Self - Revealed | FIN | Initiating Events | Green | Feedwater Regulating Valve Failure Results in Reactor Scram |  | H.5 Work Management | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green finding was identified for the inadequate implementation of a work order on the 'A' feedwater regulating valve (FRV) encoder as required by EN-WM-102. Specifically, Entergy did not install a wire assembly on the 'A' FRV encoder as r
Region: I | Pilgrim | 17970 | 09/30/2016 11/14/2016 | 2016003-01 | NRC | NCV | Public Radiation Safety | Green | Process Radiation Monitor Subsystems 10 CFR 50.65(a)(2) Not Met |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | Inspectors identified a Green NCV of 10 CFR 50.65 (a)(2), because Entergy did not adequately demonstrate that the performance of the process radiation monitors (PRMs) was effectively controlled through performance of appropriate preventive maintenance. Sp
Region: I | Pilgrim | 17971 | 09/30/2016 11/14/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Assessment on EDG 'B' |  | P.5 Operating Experience | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," in that Entergy did not perform an adequate operability evaluation in accordance with
Region: I | Pilgrim | 17969 | 09/30/2016 11/14/2016 | 2016003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Implement Agastat Control Relays Preventive Maintenance Procedure in Accordance with TS 5.4.1 |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, "Procedures," because Entergy did not implement procedures recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Entergy did not implement preventive maint
Region: I | Pilgrim | 17981 | 09/30/2016 11/14/2016 | 2016003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Evaluate the Effect of Degraded Normally Energized Agastat Relays on PCIVs Operability |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not perform an immediate operability determination and adequately evaluate the operability of primary containment
Region: I | Pilgrim | 17968 | 06/30/2016 08/10/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Inadequate Review of Vendor Documents Results in Shear Pin Failure |  | H.12 Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A Green self-revealing finding was identified for the inadequate design verification of the travelling screens system in accordance with EN-DC-149, "Acceptance of Vendor Documents." Specifically, Entergy replaced travelling screens 'C' and 'D' during the
Region: I | Pilgrim | 17962 | 06/29/2016 07/06/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degraded SSW Pump Discharge Piping Supports that Called into Question the Operability of Both SSW Loops) |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71111.17T | Green. The team identified a violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly identify and correct a condition adverse to quality. Specifically, Entergy
Region: I | Pilgrim | 17963 | 06/29/2016 07/06/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Translate SSW Support Design Drawings into the Installation Work Orders to Ensure SSW Discharge Piping was Adequately Supported) |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.17T | Green. The team documented a self-revealing violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," as Entergy failed to verify the adequacy of the design to assure that applicable regulatory requirements and the design basis were correctly t
Region: I | Pilgrim | 17967 | 04/08/2016 05/20/2016 | 2016009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with the Salt Service Water System) |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 95003 | Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not ensure that an identified condition adverse to quality related to maintenance
Region: I | Pilgrim | 17961 | 01/15/2016 02/29/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Core Spray System Leakage |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 95003 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly correct a condition adverse to quality for the core spray system. Specifically, though Entergy identified in March 2015 th
Region: I | Pilgrim | 17943 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Implementation of Corrective Action following Winter Storm Juno |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because Entergy did not adequately implement corrective actions for an identified condition adverse to quality. Specifically, Entergy did not implement al
Region: I | Pilgrim | 17944 | 12/31/2015 02/11/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Procedure Changes in accordance with TS 5.4.1a |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71152 | The inspectors identified an NCV of TS 5.4.1, "Procedures," because Entergy was not adequately maintaining procedures listed in Regulatory Guide (RG) 1.33, Revision 2, Appendix A, February 1978. Specifically, the inspectors identified several examples whe
Region: I | Pilgrim | 17945 | 12/31/2015 02/11/2016 | 2015004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify the Cause of a Significant Condition Adverse to Quality |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," when Entergy did not determine the cause of a significant condition adverse to quality (SCAQ). Specifically, a causal evaluation was not performed for a f
Region: I | Pilgrim | 17946 | 12/31/2015 02/11/2016 | 2015004-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Design Control of MSIV Nitrogen Supply Line Support leads to Scram |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," was identified because Entergy did not use the correct work planning and design controls to repair the support for the nitr
Region: I | Pilgrim | 17942 | 11/19/2015 12/21/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Reactor Recirculation System Motor Operated Valves for the Post-fire Cold Shutdown Function | EA Case: 2015008 | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71111.05T | The team identified a finding of very low safety significance involving a non-cited violation of Pilgrim Operating License Condition 3.F for failure to implement and maintain all aspects of the approved Fire Protection Program. Specifically, Entergy's pos
Region: I | Pilgrim | 17913 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Main Control Room Annunciators 10 CFR 50.65(a)(2) Not Met |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | Green. Inspectors identified a Green NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, paragraph (a)(2), because Entergy did not adequately demonstrate that the main control room annunciators (a)(2
Region: I | Pilgrim | 17914 | 09/30/2015 11/12/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate EDG Common Cause Determinations Result in TS Violation |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | Green. The inspectors identified a Green Non-Cited Violation (NCV) of TS 3.5.F, "Minimum Low Pressure Cooling and Diesel Generator Availability," for failure to adequately perform technical specification (TS) surveillance requirement (SR) 4.5.F.1 to deter
Region: I | Pilgrim | 17918 | 09/30/2015 11/12/2015 | 2015003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Assessment of the Shutdown Transformer |  | H.12 Avoid Complacency | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, "Instructions, Procedures, and Drawings," when Entergy failed to adequately assess the operability of the shutdown transformer as required by EN-OP-104, "Operability Evaluation Process
Region: I | Pilgrim | 17920 | 09/30/2015 11/12/2015 | 2015003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Comply with RWP Instructions to Contact RP Prior to Dogbone Gasket Removal |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | NONE | The inspector identified a self-revealing Green NCV of Technical Specification 5.4.1, Regulatory Guide 1.33, Appendix "A" Procedures. Procedure EN RP 100 Radiation Worker Expectations, Section 5.4 Radiological Work Permit (RWP), requires radiation workers
Region: I | Pilgrim | 17927 | 08/20/2015 10/01/2015 | 2015010-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedures for Placing Main Turbine in Service |  | H.6 Design Margins | TE?: N | 05000293 Pilgrim 1 |  | NONE | The inspectors identified a self-revealing Green non-cited violation of Technical Specification 5.4.1, "Procedures," because Entergy did not provide adequate procedures in that appropriate operator actions to recover systems and components important to sa
Region: I | Pilgrim | 17929 | 08/20/2015 10/01/2015 | 2015010-02 | NRC | VIO | Emergency Preparedness | Green | NOV for Untimely Actions to Restore Station Meteorological Towers |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The inspectors identified a Green cited violation 10 CFR 50.54(q)(2) because Entergy did not ensure that the Pilgrim Emergency Plan met the planning standards in 10 CFR 50.47(b). Specifically, in December 2011, Entergy cancelled preventative maintenance o
Region: I | Pilgrim | 17928 | 08/20/2015 10/01/2015 | 2015010-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate Guidance and Invalid Compensatory Measures for Out-of-Service EAL Instrumentation |  | P.1 Identification | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50.54(q)(2) because Entergy did not follow and maintain an emergency plan that meets the requirements of planning standards 10 CFR 50.47(b) and Appendix E. Specifically, the Emergency Plan Im
Region: I | Pilgrim | 17934 | 08/20/2015 10/01/2015 | 2015010-04 | NRC | VIO | MISC | Green | NOV for Failure to Provide an Adequate Detection and Assessment System |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71152B | OFFICIAL USE ONLY - SECURITY-RELATED INFORMATION The inspectors identified a Green cited violation of 10 CFR 73.55(i)(3)(vii) because Entergy's did not ensure intrusion detection and assessment equipment at the protected area perimeter remains operable
Region: I | Pilgrim | 17900 | 06/30/2015 08/11/2015 | 2015002-01 | Self - Revealed | FIN | Initiating Events | Green | Ineffective Corrective Action Leads to of Cavitation of Residual Heat Removal Pump |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71111.04Q | A self-revealing Green finding was identified when residual heat removal pump (RHR) 'B' experienced cavitation during refueling and maintenance outage (RFO) 20 that was a result of inadequate corrective actions associated with equipment used to determine
Region: I | Pilgrim | 17903 | 06/30/2015 08/11/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination for the X-107B EDG Results in TS Violation |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified a Green NCV 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Entergy staff performed an inadequate operability determination that assessed the X-107B emergency diesel generator (EDG) following cy
Region: I | Pilgrim | 17904 | 06/30/2015 08/11/2015 | 2015002-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Conduct Operations to Miniimze the Introduction of Residual Radioactivity to the Site |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 71124.08 | The inspectors identified a Green NCV of 10 CFR 20.1406(c) in that Entergy did not conduct operations to minimize the introduction of residual radioactivity on site. Entergy did not take action to reduce residual radioactive waste from the site in a timel
Region: I | Pilgrim | 17905 | 06/30/2015 08/11/2015 | 2015002-04 | NRC | NCV | Public Radiation Safety | Green | Failure to Properly Ship Category 2 Radioactive Material - Quantity of Concern |  | P.1 Identification | TE?: N | 05000293 Pilgrim 1 |  | 71124.08 | The inspectors identified a Green NCV of 10 CFR 71.5, "Transportation of Licensed Material," and 49 CFR 172, Subpart I, "Safety and Security Plans." Specifically, Entergy shipped a category 2 RAM-QC on public highways to a waste processor without adhering
Region: I | Pilgrim | 17899 | 03/31/2015 05/11/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Testing of Safety-Related Undervoltage Alarm Relays |  | P.1 Identification | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified an NCV of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because Entergy did not establish requirements in accordance with their test program for safety related 4160 V degraded voltag
Region: I | Pilgrim | 17881 | 03/20/2015 05/27/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Past Operability Assessment of 'C' Safety Relief Valve |  | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 93812 | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Entergy staff performed an inadequate past operability determination that assessed performance of the 'C' safety/relief valve (SRV), whic
Region: I | Pilgrim | 17885 | 03/20/2015 05/27/2015 | 2015007-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Loss of Instrument Air Abnormal Operating Procedure |  | H.1 Resources | TE?: N | 05000293 Pilgrim 1 |  | 93812 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified because Entergy failed to include appropriate operator actions to both recognize the effects of and recover systems and components important to safety within Procedure 5.3.8, "Loss of In
Region: I | Pilgrim | 17892 | 03/20/2015 05/27/2015 | 2015007-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow RCIC System Manual Restart Procedure |  | H.8 Procedure Adherence | TE?: N | 05000293 Pilgrim 1 |  | 93812 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified because the operating crew failed to implement a procedure step to open the reactor core isolation cooling (RCIC) system cooling water supply valve during a manual startup of the system.
Region: I | Pilgrim | 17893 | 03/20/2015 05/27/2015 | 2015007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Condition Adverse to Quality Associated with Core Spray Discharge Header Voiding |  | P.1 Identification | TE?: N | 05000293 Pilgrim 1 |  | 93812 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because PNPS staff failed to identify and correct conditions adverse to quality associated with the partial voiding of the 'A' core spray (CS) discharge he
Region: I | Pilgrim | 17894 | 03/20/2015 05/27/2015 | 2015007-06 | NRC | NCV | Emergency Preparedness | Green | Failure to Implement Compensatory Measures for Out-of-Service Emergency Action Level Instrumentation |  | H.7 Documentation | TE?: N | 05000293 Pilgrim 1 |  | 93812 | The inspectors identified a Green NCV of 10 CFR 50.54(q)(2) for failing to follow and maintain an emergency plan that meets the requirements of planning standards 10 CFR 50.47(b) and Appendix E. Specifically, on January 27, 2015, following a loss of instr
Region: I | Pilgrim | 17880 | 03/20/2015 05/27/2015 | 2015007-08 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Testing of the Diesel-Driven Air Compressor |  | H.6 Design Margins | TE?: N | 05000293 Pilgrim 1 |  | 93812 | A self-revealing Green finding was identified for Entergy's failure to verify that the diesel-driven air compressor (K-117) was available for service prior to the January 27, 2015 winter storm. Specifically, although K-117 was tested prior to the winter s
Region: I | Pilgrim | 17871 | 12/12/2014 01/26/2015 | 2014008-01 | NRC | FIN | Initiating Events | Green | Failure to Fully Derive the Cause of a Manual Scram |  | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 95002 | Inspectors identified a Green finding because Entergy did not fully derive the causes of the manual scram on August 22, 2013, following a loss of all feedwater. Specifically Entergy did not investigate the causes of a failed cable splice which directly ca
Region: I | Pilgrim | 17874 | 12/12/2014 01/26/2015 | 2014008-02 | NRC | NCV | Initiating Events | Green | Failure to Complete Several Corrective Actions as Required by Program Requirements |  | P.3 Resolution | TE?: N | 05000293 Pilgrim 1 |  | 95002 | The inspectors identified a Green finding for Entergy's failure to identify and correct conditions adverse to quality by implementing adequate and timely actions to address similar conditions. Specifically, inspectors identified multiple examples of failu
Region: I | Pilgrim | 17865 | 06/30/2014 08/11/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Manage a Yellow Risk Condition for Unavailable Torus Vent Valve | EA Case: 2014003 | H.13 Consistent Process | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65 paragraph (a)(4) because Entergy did not identify and manage risk for emergent maintenance on primary containment isolation valves (PCIVs). Specifically, a
Region: I | Pilgrim | 17866 | 06/30/2014 08/11/2014 | 2014003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Comply with TS Required Actions for Inoperable PCIV | EA Case: 2014003 | H.14 Conservative Bias | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification (TS) 3.7.A, "Primary Containment," because Entergy failed to comply with the TS-required actions for inoperable PCIVs. Specifically, while maintenance was being performed on an inoperable au
Region: I | Pilgrim | 17864 | 03/31/2014 05/07/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Determining Operability of the Shutdown Transformer | EA Case: 2014002 | P.2 Evaluation | TE?: N | 05000293 Pilgrim 1 |  | 71152 | Green. The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that Entergy did not correctly translate the design basis into procedures. Specifically, as of February 26, 2014, procedure 2.4.A.23
Region: I | Pilgrim | 17858 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Plant Level Maintenance Rule Monitoring |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | Green. The inspectors identified a finding (FIN) associated with licensee procedure EN-DC-204, "Maintenance Rule Scoping and Basis", because Entergy did not perform plant level monitoring in accordance with the criteria set forth therein. Specifically, th
Region: I | Pilgrim | 17448 | 12/05/2013 02/10/2014 | 2013005-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide Adequate Justification to Extend the 12-Month Review Frequency of the Emergency Preparedness Program | EA Case: 2013005 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71114.05 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50.54(t)(1), Conditions of Licenses, for failure to provide adequate justification to extend the review of the emergency preparedness program elements. Specifically, Entergy did not bas
Region: I | Pilgrim | 17856 | 10/03/2013 11/20/2013 | 2013008-01 | NRC | NCV | Initiating Events | Green | Inappropriate Fatigue Rule Waivers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 26.207(a) for Entergy's failure to issue waivers that were necessary to mitigate or prevent conditions adverse to safety, and only to address circumstances that could not have been reasonably
Region: I | Pilgrim | 17848 | 10/03/2013 11/20/2013 | 2013008-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Station Meteorological Towers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR Part 50.54(q)(2) because Entergy did not ensure that the Pilgrim Emergency Plan met the planning standards in 10 CFR 50.47(b). Specifically, on various occasions in 2012 and 2013, Pilgrim fai
Region: I | Pilgrim | 17857 | 10/03/2013 11/20/2013 | 2013008-03 | NRC | NCV | MISC | Green | Failure to Provide an Adequate Detection and Assessment System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 73.55(i)(3)(vii). This finding has a cross-cutting aspect in the area of Human Performance, Decision Making, because Entergy did not use conservative assumptions in decision making and ado
Region: I | Pilgrim | 17447 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Complete a Design Control Review for the SBO Fuel Oil Transfer System in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71151 | Green. The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not complete a design control review for the station blackout (SBO) fuel oil transfer system in a timely manner. Entergy extende
Region: I | Pilgrim | 17446 | 06/30/2013 08/08/2013 | 2013003-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedures Results in Loss of Shutdown Cooling |  | H.4(b) Procedural Compliance | TE?: N | 05000293 Pilgrim 1 |  | 71111.2 | Green. A self-revealing NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified for operators not implementing procedures to supply safety-related alternate electrical power to shutdown cooling valves during shutdown cooling operation. Spe
Region: I | Pilgrim | 17432 | 12/31/2012 01/31/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design of the SBO Fuel Oil Transfer System |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.18 | Green. The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy did not implement design control measures commensurate wit
Region: I | Pilgrim | 17438 | 12/31/2012 01/31/2013 | 2012005-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Corrective Actions for Station Blackout Battery |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green) because Entergy did not complete Shutdown Transformer Bus (A8) battery discharge testing within the required timeframe as required by procedure EN-LI-102, Corrective Acti
Region: I | Pilgrim | 17439 | 12/31/2012 01/31/2013 | 2012005-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Design Control for Station Blackout Battery |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green) because Entergy did not verify the adequacy of the design of the Station Blackout (SBO) battery as required by procedure EN-DC-126, Engineering Calculation Process. Speci
Region: I | Pilgrim | 17440 | 12/31/2012 01/31/2013 | 2012005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Extent of Condition for B-15 Safety-Related Bus After Identifying an Overload Condition on the B-14 Safety-Related Bus |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | Green. The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not identify an overload condition on the B-1
Region: I | Pilgrim | 17422 | 09/30/2012 10/31/2012 | 2012004-01 | NRC | FIN | Initiating Events | Green | Inadequate Processing of Work Package Results in Reactor Scram |  | H.3(b) Work Activity Coordination | TE?: N | 05000293 Pilgrim 1 |  | 71153 | Green. A finding of very low safety significance (Green) was identified for personnel not adequately classifying work in regards to processing an emergent work order. Specifically, personnel classified work on a reach rod position indication for valve 1
Region: I | Pilgrim | 17421 | 06/30/2012 07/23/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design of MCC-B18 with Respect to Internal Flooding |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.06 | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", because Entergy did not verify the adequacy of the design of the Motor Contro
Region: I | Pilgrim | 17416 | 03/31/2012 04/25/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope the Rod Worth Minimizer into the Maintenance Rule | EA Case: 2012002 | P.3(a) Self-Assessment | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | The inspectors identified an NCV of very low safety significance (Green) of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy did not include the Rod Worth Minimizer (RWM) system int
Region: I | Pilgrim | 17403 | 12/31/2011 02/02/2012 | 2011005-05 | NRC | FIN | Mitigating Systems | Green | Written NRC Biennial Written Examinations did not meet Qualitative Standards |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.11B | Green. The inspectors identified a Green finding of 10 CFR 55.59, "Requalification," based on a determination that greater than 20 percent of the biennial requalification written exam questions administered to licensed operators during weeks three and fou
Region: I | Pilgrim | 17394 | 10/06/2011 11/18/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of the Adequacy of the 4160 Volt Emergency Bus 95% Voltage Alarm and Load Shed Relay Design |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | Green: The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Entergy had not verified the adequacy of the 4160 volt emergency bus 95% volta
Region: I | Pilgrim | 17401 | 10/06/2011 11/18/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of Safety Related Batteries |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | Green: The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, because Entergy did not adequately perform battery discharge testing and assure that the
Region: I | Pilgrim | 17402 | 10/06/2011 11/18/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluaton of the Affect of Non Class I Equipment Internal Flooding on Redundant Safety Related Equipment |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | Green: The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Entergy did not verify the adequacy of the design with respect to ensuring tha
Region: I | Pilgrim | 17387 | 09/30/2011 11/02/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design for the 'C' Salt Service Water Pump |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.06 | Green. The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Entergy's design control measures did not ensure two-over-one seismic protection of the 'C' Salt Service Water (SSW) Pump. Specifically, Ent
Region: I | Pilgrim | 17388 | 09/30/2011 11/02/2011 | 2011004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Identify a Primary Containment System Maintenance Rule Functional Failure and Thereby Establish Monitoring Requirements for the System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | Green. The inspectors identified a Green NCV of 10 CFR 50.65, paragraph (a)(1) and (a)(2), "Requirements for Monitoring the Effectiveness of Maintenance of Nuclear Power Plants," because Entergy did not monitor the performance of the Primary Containment S
Region: I | Pilgrim | 17389 | 09/30/2011 11/02/2011 | 2011004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Accurately Assess Risk of Maintenance on Standby Gas and Secondary Containment |  | H.3(a) Work Planning | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | Green. The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) because Entergy did not assess and manage risk during elective maintenance for both 'A' and 'B' trains of the StandBy Gas Treatment (SBGT) system. Specifically, Entergy did not consult qua
Region: I | Pilgrim | 17379 | 06/30/2011 07/28/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Transient Combustible Loading in SLC Room in Excess of the Fire Hazards Analysis Limit |  | H.3(b) Work Activity Coordination | TE?: N | 05000293 Pilgrim 1 |  | 71111.05Q | -Green. The inspectors identified a Green NCV of License Condition 3.F of the Pilgrim Facility Operating License (DPR-35) for the failure to evaluate transient combustible fire loading in the Standby Liquid Control (SLC) room. Specifically, Entergy did no
Region: I | Pilgrim | 17382 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | FIN | Initiating Events | Green | Submerged Medium Voltage Cables |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71111.06 | Green. The inspectors identified a Green finding (FIN) for the improper maintenance of underground non-safety related medium voltage electric cables. The inspectors identified that Entergy allowed non-safety related medium voltage cables to remain submerg
Region: I | Pilgrim | 17380 | 06/30/2011 07/28/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Planned Maintenance and Testing on RCIC, SLC and ATS Systems |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | Green. The inspectors identified a Green NCV of 10 CFR 50.65 paragraph (a)(4) for Entergy's failure to conduct an adequate risk assessment for planned Analog Trip System (ATS) testing. Specifically, the inspectors identified that Entergy had not analyzed
Region: I | Pilgrim | 17383 | 06/30/2011 07/28/2011 | 2011003-04 | NRC | NCV | Barrier Integrity | Green | Failure to enter Technical Specifications for CHREAFS |  | H.3(b) Work Activity Coordination | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | Green. The inspectors identified a Green NCV of Technical Specification (TS) 3.7.B.2.f, "Standby Gas Treatment System and Control Room High Efficiency Air Filtration System (CRHEAFS)," for Entergy's failure to enter and perform the actions prescribed in T
Region: I | Pilgrim | 17378 | 06/30/2011 07/28/2011 | 2011003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Technical Specifications after Loss of Control Rod Indication |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | Green. The inspectors identified a Green NCV of Technical Specification (TS) 3.3.B.1 "Control Rod Operability," for Entergy's failure to enter and perform the actions prescribed in Technical Specifications after losing control rod position indication. Ent
Region: I | Pilgrim | 17345 | 04/15/2011 05/24/2011 | 2011011-01 | NRC | NCV | Barrier Integrity | Green | This inspection item is Official Use Only - Security-Related Information. See inspection report for details. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 2515/183 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Pilgrim | 17369 | 03/31/2011 05/05/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for RCIC Torus Suction Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71111.19 | Green. A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for Entergy's failure to correct a condition adverse to quality. Entergy did not correct a Reactor Core Isolation Cooling (RCIC) torus suction v
Region: I | Pilgrim | 17371 | 03/04/2011 04/15/2011 | 2011008-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Corrective Action Process for HPCI Diaphragm Degraded Condition |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000293 Pilgrim 1 |  | 71152B | GREEN. The NRC identified a finding of very low significance for Entergy's failure to follow their corrective action process in the identification, documentation, and evaluation of a degraded condition. Specifically, Entergy failed to recognize, fully d
Region: I | Pilgrim | 17370 | 03/04/2011 04/15/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Torus Air Temperature 10 CFR 50.65(a)(2) Performance Demonstration Not Met |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71152B | GREEN. The NRC identified a NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(2), for Entergy's failure to adequately demonstrate primary containment system (a)(2) performance was
Region: I | Pilgrim | 17365 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Manage a Yellow Risk Condition During HPCI Testing from the Alternate Shutdown Panel |  | H.3(a) Work Planning | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65 paragraph (a)(4) for Entergy's failure to correctly assess and manage a Yellow risk condition for planned testing of the High Pressure Coolant Injection (HPCI) system from the Alt
Region: I | Pilgrim | 17366 | 12/31/2010 02/08/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000293 Pilgrim 1 |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that Quality Control verification inspections were consistently included and correctly specified in quality-affecting procedur
Region: I | Pilgrim | 17367 | 12/31/2010 02/08/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement the experience and qualification requirements of the Quality Assurance Program. As a result, the licensee f
Region: I | Pilgrim | 17339 | 09/17/2010 10/26/2010 | 2010008-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain a Reliable Method for Transporting the SFP External Make-up Strategy Portable Fire Pump and Support Equipment. |  | H.2(d) Facilities & Equipment | TE?: N | 05000293 Pilgrim 1 |  | 71152 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Pilgrim | 17361 | 07/26/2010 10/26/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Failure to Manage a Yellow Risk Condition for an unplanned half scram |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65 paragraph (a)(4) for Entergy's failure to manage a Yellow risk condition for an unplanned half-scram. Specifically, Entergy performed an incorrect risk assessment and thereby did
Region: I | Pilgrim | 17360 | 06/30/2010 07/29/2010 | 2010003-01 | NRC | FIN | Initiating Events | Green | Submerged Medium Voltage Cables |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71111.06 | The inspectors identified a Green finding (FIN) for improper maintenance of underground non-safety related medium voltage electric cables. The inspectors identified that Entergy allowed non-safety related medium voltage cables to remain submerged in water
Region: I | Pilgrim | 17352 | 03/10/2010 05/04/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Promptly Correct Leaking Snubber Valves on the "A" Emergency Diesel Generator |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71111.19 | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Entergy's failure to promptly correct a condition adverse to quality. Specifically, Entergy did not correct defective material in their "A" Em
Region: I | Pilgrim | 17357 | 01/27/2010 05/04/2010 | 2010002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Operability Determination Process and Temporary Modification Process for Compensatory Measures Required to Maintain Operability of Secondary Containment |  | H.4(b) Procedural Compliance | TE?: N | 05000293 Pilgrim 1 |  | 71111.18 | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for Entergy's failure to accomplish procedures prescribed for activities affecting quality. Specifically, Entergy did not implem
Region: I | Pilgrim | 17350 | 10/01/2009 10/28/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish adequate procedures to prevent adverse impact due to spurious valve closure caused by fire damage. |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.05T | The inspectors identified that Entergy did not ensure that plant procedures were adequate to prevent a spurious actuation from affecting the ability to provide a source of make-up water to the reactor vessel within 20 minutes following the evacuation of t
Region: I | Pilgrim | 17335 | 09/30/2009 11/06/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Security Diesel Generator into the Maintenance Rule |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | The inspectors identified a non-cited violation of very low safety significance (Green) of 10CFR50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants", because Entergy did not include all aspects of the emergency lig
Region: I | Pilgrim | 17336 | 09/30/2009 11/06/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate for Operability of the "B" RBCCW/SSW Heat Exchanger |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified a non-cited violation of very low safety significance (Green) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings", because Entergy did not assess operability of the "B" RBCCW/SSW Heat Exchanger (HX) wh
Region: I | Pilgrim | 17338 | 09/30/2009 11/06/2009 | 2009004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Human Error Resulting in Unplanned HPCI Isolation |  | H.4(a) Human Error Prevention | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing non-cited violation of very low safety significance (Green) of TS 5.4.1, "Procedures", was identified for a procedure error which resulted in the inadvertent isolation of the High Pressure Coolant Injection (HPCI) system. Specifically, a
Region: I | Pilgrim | 17340 | 07/10/2009 02/02/2010 | 2009005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Surveillance Procedure Resulting in Failed Standby Liquid Control Train |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71111.22 | A self-revealing non-cited violation of very low safety significance (Green) of Technical Specification (TS) 5.4.1, "Procedures," was identified for inadequate procedural guidance which resulted in repeated lifting of the "A" Standby Liquid Control (SBLC)
Region: I | Pilgrim | 17333 | 05/04/2009 07/20/2009 | 2009003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedure Resulting in Damage to Refueling Mast |  | H.4(a) Human Error Prevention | TE?: N | 05000293 Pilgrim 1 |  | 71111.2 | A self-revealing non-cited violation (NCV) of Technical Specification 5.4.1 "Procedures," was identified, because Entergy's refueling bridge operators did not continuously monitor a Double Blade Guide (DBG) that was moved into the core to ensure the DBG d
Region: I | Pilgrim | 17326 | 03/31/2009 05/07/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish and Maintain Adequate Measures to Monitor Critical Parameters of the EDG Air Start System |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of very low safety significance of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy personnel did not establish and maintain measures to monitor critical design parameters t
Region: I | Pilgrim | 17332 | 03/31/2009 05/07/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Scaffolding Procedure Requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000293 Pilgrim 1 |  | 71111.15 | The inspectors identified an NCV of very low safety significance of Technical Specification 5.4.1 "Procedures," because Entergy personnel did not adequately implement procedure requirements in accordance with EN-MA-133, "Control of Scaffolding." Specifica
Region: I | Pilgrim | 17322 | 12/30/2008 02/05/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct a Risk Assessment for Emergent Maintenance on the High Pressure Coolant Injection System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) for Entergy's failure to conduct a risk assessment for emergent maintenance on the High Pressure Coolant Injection (HPCI) system injection valve. Specifically, the failure t
Region: I | Pilgrim | 17323 | 12/30/2008 02/05/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Procedural Error Resulting in Unplanned RCIC Isolation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A self-revealing Green non-cited violation (NCV) of TS 5.4.1, "Procedures", was identified for a procedure which resulted in an inadvertent isolation of the Reactor Core Isolation Cooling (RCIC) system. Specifically, the procedure was previously revised a
Region: I | Pilgrim | 17314 | 07/17/2008 07/30/2008 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Switchyard Voltage Criteria |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not perform a calculation and confirmatory test to demonstrate that the switchyar
Region: I | Pilgrim | 17312 | 06/17/2008 07/30/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for 'B' Battery Charger Circuit Breaker |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Entergy did not promptly correct deficiencies with the 'B' 125 Vdc battery charger supply
Region: I | Pilgrim | 17313 | 06/17/2008 07/30/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions in Response to an Intake De-Watering Event |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that, Entergy did not properly evaluate and take adequate corrective actions for a condition adv
Region: I | Pilgrim | 17315 | 06/17/2008 07/30/2008 | 2008007-04 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Calculation for Salt Service Water Pump Minimum Flow Rate |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not properly translate design basis parameters into specifications and procedures
Region: I | Pilgrim | 17309 | 04/03/2008 04/11/2008 | 2008006-01 | NRC | FIN | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Pilgrim | 17310 | 04/03/2008 04/11/2008 | 2008006-02 | NRC | FIN | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Pilgrim | 17311 | 04/03/2008 04/11/2008 | 2008006-03 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Pilgrim | 17305 | 03/31/2008 04/25/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Emergent Maintenance on A5 Emergency Bus Undervoltage Relays |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) for Entergy's failure to conduct an adequate risk assessment for emergent maintenance on the A5 Emergency Bus undervoltage relays. Specifically, the inspectors noted that En
Region: I | Pilgrim | 17304 | 12/31/2007 02/01/2008 | 2007005-01 | NRC | FIN | Initiating Events | Green | Improper Calibration of Vacuum Trip Switch Results in an Automatic Reactor Scram |  | H.4(a) Human Error Prevention | TE?: N | 05000293 Pilgrim 1 |  | 71153 | A Green self-revealing finding was identified for Entergy's failure to ensure the proper verification and calibration of condenser vacuum trip switch VTS-1 during refueling outage (RFO) 16. Specifically, personnel did not ensure that the proper verificati
Region: I | Pilgrim | 17301 | 09/30/2007 11/01/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish goals and monitor the performance of the HVAC system against them per 10 CFR 50.65(a)(1) |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71111.11Q | The inspector identified a NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for Entergy's failure to establish goals or monitor the performance of the Heating, Ventilation, and Air Conditioning (
Region: I | Pilgrim | 17302 | 09/30/2007 11/01/2007 | 2007004-02 | NRC | NCV | Public Radiation Safety | Green | Non-Representative Sampling of the Reactor Building Exhaust Vent |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7112201 | The inspector identified a NCV of TS 5.5.4.c, "Radioactive Effluent Controls Program," for Entergy's failure to obtain representative effluent samples. Specifically, the sample flow rate through the isokinetic nozzles for the reactor building vent was too
Region: I | Pilgrim | 17295 | 06/30/2007 08/02/2007 | 2007003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to provide adequate instructions for adjusting MO-1201-85 packing resulted in premature packing failure. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71111.12 | A self-revealing non-cited violation of very low safety significance was identified for Entergy's failure to provide adequate work instructions, as required by Pilgrim Technical Specification 5.4.1, "Procedures," to adjust packing on reactor water cleanup
Region: I | Pilgrim | 17296 | 06/30/2007 08/02/2007 | 2007003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow procedures resulted in the loss of shutdown cooling. |  | H.4(b) Procedural Compliance | TE?: N | 05000293 Pilgrim 1 |  | 71111.13 | A self-revealing non-cited violation of very low safety significance was identified for Entergy's failure to implement procedures for testing the analog trip system (ATS) as required by Pilgrim Technical Specification 5.4.1, "Procedures." Specifically, on
Region: I | Pilgrim | 17297 | 06/30/2007 08/02/2007 | 2007003-03 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent decrease in reactor vessel level due to personnel error. |  | H.3(b) Work Activity Coordination | TE?: N | 05000293 Pilgrim 1 |  | 71111.2 | A self-revealing non-cited violation of very low safety significance was identified for Entergy's failure to properly implement procedure EN-OP-102, "Protective and Caution Tagging," as required by Pilgrim Technical Specification 5.4.1, "Procedures." Spec
Region: I | Pilgrim | 17291 | 06/30/2007 08/02/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure Results in Repetitive Emergency Diesel Generator Load Oscillations. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000293 Pilgrim 1 |  | 71152B | A self-revealing Green non-cited violation (NCV) of Technical Specification 5.4.1 was identified for an inadequate procedure used to lubricate the mechanical governor linkages associated with the 'A' emergency diesel generator (EDG). The inadequately lubr
Region: I | Pilgrim | 17292 | 06/30/2007 08/02/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Effective Corrective Actions to Correct Recurring SRV Surveillance Failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000293 Pilgrim 1 |  | 71152B | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to take timely or effective corrective action to resolve repetitive safety and relief valve (SRV) surveillance test failures. Specifically, Ente
Region: I | Pilgrim | 17290 | 03/31/2007 05/07/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to thoroughly evaluate degraded condition on "B" EDG following January overhaul |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000293 Pilgrim 1 |  | 71111.19 | A Green self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for Entergy's failure to promptly correct a condition adverse to quality associated with the "B" emergency diesel generator (EDG). During the post over
Region: I | Pilgrim | 17287 | 12/31/2006 02/02/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | SL IV NCV for Inadequate 50.59 Evaluation for RFO 15 Emergency Diesel LOCA/LOOP Test Change |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000293 Pilgrim 1 |  | NONE | Green. The inspector identified a non-cited violation (NCV) for Entergy's failure to perform an adequate safety evaluation per 10 CFR 50.59. Specifically, a screening safety evaluation (SE) for surveillance 8.M.3-1, Special Test for Automatic ECCS [Emerge
Region: I | Pilgrim | 17283 | 05/19/2006 06/29/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | The team identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | Entergy used a non-conservative calculation method to determine the critical condensate storage tank (CST) water level which would preclude vortex formation at the suction of the high pressure coolant injection (HPCI) pump. The finding was more than minor
Region: I | Pilgrim | 17284 | 05/19/2006 06/29/2006 | 2006006-02 | NRC | FIN | Mitigating Systems | Green | The team identified a finding regarding Entergy's operability determination for a HPCI trip solenoid valve failure. |  |  | TE?: N | 05000293 Pilgrim 1 |  | 7111121 | The team identified a finding regarding Entergy's operability determination for a HPCI trip solenoid valve failure. Specifically, Entergy's operability evaluation technical basis did not support the specific technical specification (TS) requirement of ens
Region: I | Pilgrim | 17277 | 04/02/2006 05/12/2006 | 2006002-01 | NRC | NCV | Initiating Events | Green | Failure to evaluate failed AOG bypass valve contributes to manual reactor scram |  |  | TE?: N | 05000293 Pilgrim 1 |  | 71153 | The inspectors identified a non-cited violation (NCV) of Technical Specifications for failure to evaluate the impact of an inoperable manual bypass valve (1-HO-154) in the augmented off-gas (AOG) system. Specifically, on January 12 and March 12, 2006, whe
Region: I | Salem | 126500 | 12/31/2019 02/11/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Inadequate Control of Transient Combustible Materials in accordance with the Fire Protection Program Procedure |  | H.12 - Avoid Complacency | TE?: N | 05000272 Salem 1 05000311 Salem 2 | Protection Against External Factors | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of the Salem Unit 1 License Condition 2.C.(5) and Unit 2 License Condition 2.C.(10) when PSEG did not implement requirements in the Fire P
Region: I | Salem | 126501 | 12/31/2019 02/11/2020 | 2019004-02 | NRC | FIN | Initiating Events | Green | Inadequate Corrective Actions for Feedwater Regulating Valve Vibrations |  | P.2 - Evaluation | TE?: N | 05000272 Salem 1 05000311 Salem 2 | Equipment Performance | 71152 | The inspectors identified a Green finding (FIN) because PSEG did not adequately implement, in part, procedure LS-AA-125, Corrective Action Program (CAP), requirements to address a condition adverse to quality (CAQ) associated with a previous equipment fai
Region: I | Salem | 125787 | 09/13/2019 10/18/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Missing Preventive Maintenance for Environmental Qualification Program Components |  | NPP | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, because PSEG did not schedule and perform
Region: I | Salem | 125294 | 06/30/2019 08/06/2019 | 2019002-01 | Self - Revealed | FIN | Barrier Integrity | Green | Fuel Handling Procedures Not Followed |  | H.12 - Avoid Complacency | TE?: N | 05000272 Salem 1 05000311 Salem 2 | Human Performance | 71152 | A self-revealing Green finding (FIN) was identified because PSEG did not follow their procedures for the movement of spent fuel. Specifically, PSEG did not follow their Fuel Handling procedure, SC.RE-FR.ZZ-0001, to ensure that spent fuel assemblies (FAs)
Region: I | Salem | 125292 | 06/30/2019 08/06/2019 | 2019002-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Inadequate Procedures for the Removal of Baffle Bolts |  | H.5 - Work Management | TE?: N | 05000272 Salem 1 05000311 Salem 2 | Program & Process | 71153 | A Green self-revealing finding was identified for PSEG having inadequate procedures related to the movement of irradiated material in and around the reactor cavity during refueling operations and maintenance. Specifically, the procedures governing the con
Region: I | Salem | 124549 | 03/31/2019 05/08/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Fire Protection |  | P.3 - Resolution | TE?: N | 05000272 Salem 1 05000311 Salem 2 | Protection Against External Factors | 71152 | The inspectors identified a finding of very low safety significance (Green) involving an non-cited violation (NCV) of Salem Unit 1 License Condition 2.C.(5) and Salem Unit 2 License Condition 2.C.(10) of the respective facility operating licenses for fail
Region: I | Salem | 124601 | 03/31/2019 05/08/2019 | 2019001-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Implementation of Design Change Process on Digital Feedwater Control System |  | H.11 - Challenge the Unknown | TE?: N | 05000311 Salem 2 | Design Control | 71153 | A self-revealed, Green finding was identified when PSEG inadequately implemented a design change process on the Unit 2 advanced digital feedwater control system (ADFCS). Specifically, PSEG’s inadequate implementation of procedural requirements in CC-AA-10
Region: I | Salem | 24718 | 09/30/2018 11/13/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Chiller Maintenance Procedures |  | H.7 - Documentation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures and Programs," when PSEG did not properly preplan maintenance activities in accordance with written instructions appropriate to the circumstance
Region: I | Salem | 24719 | 09/30/2018 11/13/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Generic Letter 89-13 Program Procedure |  | P.3 - Resolution | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PSEG did not adequately follow Generic Letter (GL) 89-13 program procedure steps for p
Region: I | Salem | 24080 | 06/30/2018 07/26/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Design Change for Service Water Pumps |  | P.2 - Evaluation | TE?: N | 05000311 Salem 2 |  | 71111.18 | A self-revealing Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Appendix B, Criterion III, "Design Control," was identified because PSEG item equivalency evaluation (IEE) 80102443 did not evaluate the use of a chro
Region: I | Salem | 23551 | 03/31/2018 05/14/2018 | 2018001-01 | NRC | FIN | Mitigating Systems | Green | Implementing Procedures for Beyond Design Basis FLEX Mitigating Strategies Not Followed |  | H.5 - Work Management | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.04Q | A Green finding was identified by the inspectors for multiple examples of PSEG not following the station specific procedures that implement the Salem and HCGS Final Integrated Plans for Beyond Design Basis FLEX Mitigating Strategies, EM-SA-100-1000 and EM
Region: I | Salem | 23552 | 03/31/2018 05/14/2018 | 2018001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Step Results in Service Water Strainer Trip |  | H.5 - Work Management | TE?: N | 05000272 Salem 1 |  | 71152 | A self-revealing Green NCV of 10 CFR, Appendix B, Criterion V, was identified because PSEG procedure WC-AA-111, “Predefine Process,” Revision 8, step 4.8.11, did not adequately prescribe activities that affected the quality of the safety-related 11 SW str
Region: I | Salem | 23553 | 03/31/2018 05/14/2018 | 2018001-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Establish Containment Integrity during Plant Startup |  | H.8 - Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71153 | The inspectors determined there was a self-revealing Green NCV of TS 6.8.1, “Procedures and Programs,” when PSEG did not follow procedure S1.OP-SO.SG-0002, “Maintaining Steam Generators in Wet Layup,” Revision 10, step 5.7.7L, to close the 14 SG blowdown
Region: I | Salem | 23503 | 03/02/2018 04/09/2018 | 2018007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Testing of Emergency Diesel Generator Bypass Switches |  | P.2 - Evaluation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.05T | The team identified a finding of very low safety significance (Green) involving an NCV of Salem Unit 1 License Condition 2.C.(5) and Salem Unit 2 License Condition 2.C.(10) of the respective facility operating licenses for failure to implement and maintai
Region: I | Salem | 22654 | 12/31/2017 02/08/2018 | 2017004-01 | NRC | NCV | Barrier Integrity | Green | Non-Conformance with the Containment Thermal Insulation System was not Identified and Corrected |  | P.1 - Identification | TE?: N | 05000272 Salem 1 |  | 71111.08P | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when PSEG did not identify and correct a non-conformance with the Unit 1 containment thermal insulation system. The installed configuration did not provide
Region: I | Salem | 22663 | 12/31/2017 02/08/2018 | 2017004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Reactor Vessel Head Removal Procedure |  | P.2 - Evaluation | TE?: N | 05000272 Salem 1 |  | 71111.2 | The inspectors documented a self-revealing, Green NCV of Unit 1 Technical Specification (TS) 6.8.1, “Procedures and Programs,” for inadequate reactor vessel (RV) head removal procedures that led to the RCS level lowering out of the procedural band during
Region: I | Salem | 22678 | 12/31/2017 02/08/2018 | 2017004-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Worker Not Briefed on Dose Rates Before Entering a High Radiation Area |  | H.8 - Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71124.01 | The inspectors documented a self-revealing, Green NCV of TS 6.12.1, when a worker entered a high radiation area with dose rates greater than 100 millirem per hour at 30 centimeters, without having been informed of the area dose rates before entry. PSEG C
Region: I | Salem | 22665 | 12/31/2017 02/08/2018 | 2017004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure for a Service Water Pump Strainer Discharge Valve |  | H.7 - Documentation | TE?: N | 05000272 Salem 1 |  | 71152 | A self-revealing Green NCV of Unit 1 TS 6.8.1, “Procedures and Programs,” as described in Regulatory Guide 1.33, Revision 2, was identified when PSEG performed service water (SW) pump strainer discharge valve maintenance without adequate procedural guidan
Region: I | Salem | 22664 | 12/31/2017 02/08/2018 | 2017004-05 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Evaluation of Operating Experience for Vital Instrument Bus Inverter |  | P.5 - Operating Experience | TE?: N | 05000272 Salem 1 |  | 71152 | A self-revealing Green Finding (FIN) was identified when PSEG did not fully evaluate operating experience in accordance with LS-AA-115, “Operating Experience Procedure” and MA-AA-716-210, “Performance Centered Maintenance (PCM) Process.” Specifically, PSE
Region: I | Salem | 21692 | 09/30/2017 11/14/2017 | 2017003-02 | NRC | NCV | Barrier Integrity | Green | VIOLATION OF CONTAINMENT INTEGRITY TECHNICAL SPECIFICATION |  | H.5 - Work Management | TE?: N | 05000272 Salem 1 |  | 71111.15 | The inspectors identified a Green non-cited violation (NCV) of technical specification (TS) limiting condition for operation (LCO) 3.6.1.1, "Containment Integrity," when PSEG did not ensure that the pathway containing the air particulate detector (APD) ba
Region: I | Salem | 21693 | 09/30/2017 11/14/2017 | 2017003-03 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW MAINTENANCE PROCEDURE TO ASSURE PROPER INSTALLATION OF SERVICE WATER CHECK VALVE |  |  | TE?: N | 05000272 Salem 1 |  | 71111.22 | A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, “Procedures and Programs,” as described in Regulatory Guide 1.33, Revision 2, was identified because PSEG did not install the 12 service water (SW) accumulator injecti
Region: I | Salem | 8766 | 07/14/2017 08/14/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verification that Inter-Cabinet Bolts were Installed Between SEC and Bailey Cabinets |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.21M | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because between May 1995 to July 2017, PSEG did not verify that bolts, or other suitable connections, were installed to connect the safeguard e
Region: I | Salem | 8767 | 07/14/2017 08/14/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate PM for the EDG Room Ventilation System |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.21M | The team identified a Green non-cited violation of Technical Specification (TS) 6.8.1, "Procedures and Programs," because since January 2007, PSEG did not establish an appropriate preventive maintenance (PM) schedule for the emergency diesel generator (ED
Region: I | Salem | 8768 | 07/14/2017 08/14/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action Regarding Missed Periodic Inspections of 2C EDG AVR Card |  | P.6 Self Assessment | TE?: N | 05000311 Salem 2 |  | 71111.21M | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because between April 2008 and July 2017, PSEG failed to promptly identify and correct a condition adverse to quality associated with an aut
Region: I | Salem | 8718 | 06/30/2017 03/02/2017 | 2017009-01 | Self - Revealed | NCV | MISC | Green | Failure to Follow Troubleshooting Procedure for BIT Relief Valve Leakage |  | H.8 Procedure Adherence | TE?: N | 05000311 Salem 2 |  | 71153 | Introduction. A self-revealing, Green NCV of TS 6.8.1, "Procedures and Programs," was identified when PSEG performed troubleshooting activities that were not in accordance with documented instructions. Specifically, PSEG operators performed mechanical agi
Region: I | Salem | 8742 | 04/10/2017 04/10/2017 | 2016002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Order Planning Results in Main Generator AVR STV Relay Trip |  | H.5 Work Management | TE?: N | 05000311 Salem 2 |  | 71153 | A Green, self-revealing finding (FIN) was identified against MA-AA-716-010, "Maintenance Planning Process," Revision 18, when PSEG work orders (WOs) did not specify the appropriate procedure to perform satisfactory modification testing of the main generat
Region: I | Salem | 8758 | 03/31/2017 05/04/2017 | 2017001-01 | Self - Revealed | FIN | Mitigating Systems | Green | Loss of Unit 1C 4kV Vital Bus due to Inadequate Activity Risk Screening |  | H.5 Work Management | TE?: N | 05000272 Salem 1 |  | 71111.13 | A self-revealing Green finding (FIN) was identified when PSEG did not screen the risk associated with replacing the Unit 1C emergency diesel generator (EDG) output breaker in accordance with WC-AA-105, "Work Activity Risk Management." Specifically, on Dec
Region: I | Salem | 8759 | 03/31/2017 05/04/2017 | 2017001-02 | NRC | NCV | Initiating Events | Green | Inadequate Fire Risk Assessment and Management |  | H.5 Work Management | TE?: N | 05000272 Salem 1 |  | 71111.13 | Inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) when PSEG did not adequately assess and manage the risk of online maintenance activities associated with the 13 and 23 charging (CV
Region: I | Salem | 8760 | 03/31/2017 05/04/2017 | 2017001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Conduct Post-Maintenance Testing Required by Procedure and Work Order Resulting in Inoperable Containment Fan Coil Units |  | H.5 Work Management | TE?: N | 05000272 Salem 1 |  | 71153 | A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures and Programs;" TS 3.6.2.3, "Containment Cooling Fans;" TS 3.6.1.1, "Primary Containment Integrity;" and TS 3.0.4, "Applicability," was identified. Specific
Region: I | Salem | 8754 | 12/31/2016 02/02/2017 | 2016004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Maintenance Procedure for Steam Generator Feedwater Pump Coupling Hub Set Screw Installation |  | P.5 Operating Experience | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing Green finding (FIN) against MA-AA-716-010, "Maintenance Planning Process," step 4.2.3, Revision 18, was identified for PSEG's inadequate maintenance guidance that resulted in 11 steam generator feedwater pump (SGFP) elevated vibrations an
Region: I | Salem | 8755 | 12/31/2016 02/02/2017 | 2016004-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Surveillance Test Procedure Results in Water Hammer and Reactor Trip |  | P.2 Evaluation | TE?: N | 05000311 Salem 2 |  | 71153 | The inspectors determined there was a self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1.c, "Surveillance and test activities of safety-related equipment," when PSEG did not establish adequate procedures for restoring ser
Region: I | Salem | 8750 | 09/30/2016 11/08/2016 | 2016003-01 | Self - Revealed | FIN | Initiating Events | Green | Misclassification of and Lack of Preventative Maintenance for SWC Valve 2GW75 and Relay S62-C1 |  |  | TE?: N | 05000311 Salem 2 |  | 71153 | The inspectors documented a self-revealing, Green finding (FIN) because PSEG did not classify plant equipment in accordance with procedure ER-AA-1001, "Component Classification," Revision 0, step 4.5. Specifically, PSEG did not appropriately classify a va
Region: I | Salem | 8735 | 03/31/2016 05/10/2016 | 2016001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Chiller Failures due to Gasket Leakage |  | P.3 Resolution | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.12 | A self-revealing Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, was identified when PSEG did not assure that an identified condition adverse to quality was corrected. Specifically, PSEG closed a corrective action to address chill
Region: I | Salem | 8740 | 03/31/2016 05/10/2016 | 2016001-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Digital Feedwater Design Change Evaluation |  | H.3 Change Management | TE?: N | 05000311 Salem 2 |  | 71111.15 | A self-revealing Green finding against procedure CC-AA-103, Configuration Change Control for Permanent Physical Plant Changes, Revision 15, was identified when PSEG did not adequately evaluate a modification's effect on existing design and operating margi
Region: I | Salem | 8741 | 03/31/2016 05/10/2016 | 2016001-03 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Identification and Correction of Unsatisfactory Control Room Ventilation Charcoal Testing |  | H.4 Teamwork | TE?: N | 05000272 Salem 1 |  | 71153 | A self-revealing Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, was identified when PSEG did not promptly identify and correct a condition adverse to quality (CAQ). Specifically, PSEG did not promptly identify that negative resul
Region: I | Salem | 8732 | 12/31/2015 02/10/2016 | 2015004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Auxiliary Building Barrier Controls |  | H.5 Work Management | TE?: N | 05000311 Salem 2 |  | 71111.01 | Inspectors identified a Green NCV of TS 6.8.1, "Procedures and Programs," when PSEG improperly implemented barrier controls in accordance with procedure, CC-AA-201, "Plant Barrier Control," Revision 5, during modification activities that impacted the floo
Region: I | Salem | 8677 | 12/31/2015 02/10/2016 | 2015004-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Maintenance Effectiveness of Control Room Ventilation Radiation Monitors |  | H.14 Conservative Bias | TE?: N | 05000272 Salem 1 |  | 71111.12 | Inspectors identified a Green NCV of 10 CFR 50.65(a)(2) when Control Area Ventilation (CAV) radiation monitor performance was not being effectively controlled through appropriate preventive maintenance. Specifically, there were repetitive foil issues and
Region: I | Salem | 8733 | 12/31/2015 02/10/2016 | 2015004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Improper PM Deletion Resulted in Plant Shutdown Required by TSs |  |  | TE?: N | 05000272 Salem 1 |  | 71152 | A self-revealing Green NCV of TS 6.8.1, "Procedures and Programs," as described in Regulatory Guide 1.33, Revision 2, February 1978, was identified when PSEG did not maintain an appropriate preventive maintenance (PM) schedule for Salem containment fan co
Region: I | Salem | 8734 | 12/31/2015 02/10/2016 | 2015004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Testing on OTDT Channels |  | H.7 Documentation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," and associated NCV of TS 3.3.1.1 was identified, with two examples, for not ensuring that all testing required to demonstrate that nuclear instrumentation (NI) would perfo
Region: I | Salem | 8721 | 09/30/2015 10/22/2015 | 2015003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Establish Measures for the Selection and Review for Suitability of a TDAFW Room Cooler Temperature Switch |  | P.3 Resolution | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified when PSEG selected a temperature control switch for the auxiliary feedwater (AFW) pump area room cooler that was not suitable for its application. Specif
Region: I | Salem | 8729 | 09/30/2015 10/22/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination of Auxiliary Feedwater Flow Rate Indicator |  | H.14 Conservative Bias | TE?: N | 05000311 Salem 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when PSEG did not adequately implement procedure OP-AA-108-115, "Operability Determinations & Functionality Assessments." Specifically,
Region: I | Salem | 8730 | 09/30/2015 10/22/2015 | 2015003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Chronic Chiller Relief Valve Freon Leaks |  | H.6 Design Margins | TE?: N | 05000272 Salem 1 |  | 71111.22 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the 13 chiller tripped on freeze protection due to insufficient refrigerant. Specifically, timely corrective actions were not implemented in resp
Region: I | Salem | 8710 | 06/30/2015 07/28/2015 | 2015002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Actions For Service Water Outlet Valve |  | H.4 Teamwork | TE?: N | 05000311 Salem 2 |  | 71111.12 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified when PSEG did not implement corrective actions in a timely manner. Specifically, PSEG identified a degrading trend in the stroke time for the 25 contai
Region: I | Salem | 8711 | 06/30/2015 07/28/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Correct a Condition Adverse To Quality Associated With 12 Chiller Motor |  | P.3 Resolution | TE?: N | 05000272 Salem 1 |  | 71111.15 | A self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for PSEG's failure to take timely corrective action to correct a condition adverse to quality (CAQ)
Region: I | Salem | 8715 | 06/30/2015 07/28/2015 | 2015002-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate Seismic EAL Scheme |  | P.2(b) Implementing Operating Experience | TE?: N | 05000272 Salem 1 05000272 Salem 1 05000311 Salem 2 05000311 Salem 2 |  | 71114.06 | The inspectors identified a Green NCV of 10 CFR 50.54(q)(2) when PSEG did not maintain an adequate emergency classification and action level scheme that met the planning standards of 10 CFR 50.47(b). Specifically, PSEG did not establish an effective emerg
Region: I | Salem | 8716 | 06/30/2015 07/28/2015 | 2015002-04 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate HRA Controls |  | H.12 Avoid Complacency | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152 | The inspectors identified a Green NCV of TS 6.12, 'High Radiation Area," when PSEG did not apply appropriate controls to high radiation areas. Specifically, the Unit 1 and 2 reactor cavities in containment, which are areas that exceed 1.0 rem/hour at 30 c
Region: I | Salem | 8717 | 06/30/2015 07/28/2015 | 2015002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Breaker Preventive Maintenance Periodicity |  | P.5 Operating Experience | TE?: N | 05000272 Salem 1 |  | 71152 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," was identified because PSEG did not establish an appropriate interval to overhaul 4kV General Electric (GE) Magne-Blast breakers. As a result, the s
Region: I | Salem | 8719 | 06/30/2015 07/28/2015 | 2015002-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Chiller Maintenance Procedure |  | P.2 Evaluation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152 | The inspectors identified a Green NCV of TS 6.8.1, "Procedures and Programs," as described in Regulatory Guide (RG) 1.33, Revision 2, February 1978, when PSEG performed chiller water system maintenance activities that were not properly preplanned in accor
Region: I | Salem | 8708 | 05/22/2015 07/21/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to the Quality of the Chillers |  | P.2 Evaluation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR, Part 50, Appendix B, Criterion XVI, because PSEG did not assure that an identified condition adverse to quality was corrected. The condition adverse to quality was associated with improper maintenance of th
Region: I | Salem | 8699 | 03/31/2015 04/28/2015 | 2015001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure Adequate Negative Differential Pressure During Fuel Movements |  | H.8 Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71111.15 | The inspectors identified a Green NCV of TS 3.9.12, "Fuel Handling Area Ventilation System," when PSEG did not suspend Unit 1 fuel movement operations when the fuel handling area ventilation system was inoperable. Specifically, differential pressure excee
Region: I | Salem | 8700 | 03/31/2015 04/28/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for HELB Barrier Controls |  | P.2 Evaluation | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.19 | Inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, when PSEG did not implement adequate corrective actions from a previous Green NCV in a timeframe commensurate with its safety significance. Specifically, inadequ
Region: I | Salem | 8701 | 02/13/2015 03/12/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Post-fire Safe Shutdown Operator Manual Actions to Align Temporary Ventilation Not Assessed for Feasibility and Reliability |  |  | TE?: N | 05000272 Salem 1 |  | 71111.05T | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Salem Unit 1 Technical Specification 6.8.1.f. for failure to implement and maintain written procedures for fire protection program implementation. S1.
Region: I | Salem | 8681 | 12/31/2014 01/30/2015 | 2014005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Procedural Non-Compliance Resulted in Low Temperature Overpressure Relief Lifting |  | H.8 Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71111.15 | A self-revealing, Green NCV of TS 6.8.1, "Procedures and Programs," was identified when PSEG did not correctly implement procedures associated with Safeguard Equipment Control (SEC) surveillance testing during solid reactor coolant system (RCS) operations
Region: I | Salem | 8682 | 12/31/2014 01/30/2015 | 2014005-02 | NRC | NCV | Initiating Events | Green | Failure to Implement Procedures During Shutdown Results in ESF Actuation |  | H.8 Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71111.2 | The inspectors identified a Green NCV of TS 6.8.1, "Procedures and Programs," when PSEG operators did not implement the procedure steps to trip the main turbine, and manually initiate auxiliary feedwater (AFW), during shutdown for a refueling outage on Oc
Region: I | Salem | 8688 | 12/31/2014 01/30/2015 | 2014005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement TS Locked High Radiation Area Controls |  | P.3 Resolution | TE?: N | 05000272 Salem 1 |  | 71124.01 | The inspectors identified NCV of very low safety significance (Green) associated with failure to implement TS 6.12.2 access controls for a High Radiation Area (HRA) exhibiting accessible radiation dose rates exceeding 1 rem/hr at 30 cm. Specifically, on O
Region: I | Salem | 8689 | 12/31/2014 01/30/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Reactor Coolant Pump Turning Vane Bolt Failures |  | P.2 Evaluation | TE?: N | 05000311 Salem 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because PSEG staff did not promptly correct a condition adverse to quality related to failed Unit 2 reactor coolant pump (RCP) turning vane bolts. Specific
Region: I | Salem | 8690 | 12/31/2014 01/30/2015 | 2014005-05 | NRC | NCVIV | Initiating Events | Green | Failure to Report a Manual Reactor Trip |  |  | TE?: Y SL-IV-NCVIV | 05000272 Salem 1 |  | 71153 | Inspectors identified a Severity Level IV (SLIV) NCV of 10 CFR 50.72(b)(2)(iv)(B) when PSEG failed to make the required event notification within four hours for a valid actuation of the reactor protection system (RPS) when the reactor was critical. Inspec
Region: I | Salem | 8674 | 09/30/2014 11/03/2014 | 2014004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Improper Risk Assessment and Risk Management Actions for a Reheater Drain Valve |  | H.12 Avoid Complacency | TE?: N | 05000272 Salem 1 |  | 71111.13 | A self-revealing, Green NCV of 10 CFR 50.65(a)(4) was identified when PSEG did not properly assess and manage risk on Salem Unit 1 during an evolution with the potential to cause a reactivity change and overpower event. Specifically, while working on a mo
Region: I | Salem | 8675 | 09/30/2014 11/03/2014 | 2014004-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Corrective Action to Prevent Recurrence of Silent Steam Generator Feed Pump Coast-Downs |  |  | TE?: N | 05000272 Salem 1 |  | 71153 | A Green, self-revealing FIN was identified against NC.WM-AP.ZZ-0002, "Performance Improvement Process," Revision 6, because PSEG did not adequately correct and prevent recurrence of steam generator feedpump (SGFP) silent coast-down events. Consequently, o
Region: I | Salem | 8676 | 09/30/2014 11/03/2014 | 2014004-03 | Self - Revealed | FIN | Initiating Events | Green | Incomplete Corrective Action on Current Transformers Results in Reactor Trip |  |  | TE?: N | 05000272 Salem 1 |  | 71153 | A Green, self-revealing finding against PSEG procedure NC.WM-AP.ZZ-0002, "Performance Improvement Process," Revision 3, was identified for incomplete corrective actions when a Unit 1 main generator phase 'C' differential current lockout relay tripped and
Region: I | Salem | 8680 | 09/30/2014 11/03/2014 | 2014004-04 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Interim Corrective Actions on Current Transformers Result in Reactor Trip |  | H.14 Conservative Bias | TE?: N | 05000272 Salem 1 |  | 71153 | A Green, self-revealing finding against PSEG procedure LS-AA-120, "Issue Identification and Screening Process," Revision 12, was identified for inadequate interim corrective actions when a Unit 1 main generator phase 'A' differential current lockout relay
Region: I | Salem | 8662 | 07/24/2014 08/27/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify degraded conditions associated with the Unit 1 and Unit 2 RWST and AFWST panels. |  | P.1 Identification | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because PSEG did not promptly identify and correct conditions adverse to quality. Specifically, PSEG did not promptly identify and correct degraded c
Region: I | Salem | 8657 | 06/30/2014 08/04/2014 | 2014003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Solid Pressurizer Control Resulted in Low Temperature Overpressure Relief Lifting |  | H.11 Challenge the Unknown | TE?: N | 05000311 Salem 2 |  | 71111.15 | A self-revealing, Green non-cited violation (NCV) of TS 6.8.1, "Procedures and Programs," was identified when PSEG did not control reactor coolant system (RCS) pressure in accordance with a procedure. Consequently, on April 13, 2014, this resulted in lift
Region: I | Salem | 8660 | 06/30/2014 08/04/2014 | 2014003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Shutdown Margin Calculation Procedure to Cover certain Mispositioned Control Rod Events |  | H.8 Procedure Adherence | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.18 | The inspectors determined there was a Green, self-revealing violation of TS 6.8.1, "Procedures and Programs," as described in Regulatory Guide 1.33, Revision 2, February 1978, when PSEG did not maintain procedure SC.RE-ST.ZZ-0002, "Shutdown Margin Calcula
Region: I | Salem | 8656 | 05/04/2014 08/04/2014 | 2014003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Establish and Implement Adequate Radiation Protection Procedures |  | H.5 Work Management | TE?: N | 05000311 Salem 2 |  | 71153 | A self-revealing NCV of very low safety significance was identified for failure to establish and implement TS 6.8 required procedures. Specifically, PSEG did not establish and implement adequate procedures for transfer and control of radioactive material
Region: I | Salem | 8644 | 03/31/2014 05/09/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Fire Protection Test Procedure Resulted in Fuel Oil Spill |  | H.12 Avoid Complacency | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.05Q | The inspectors determined there was a Green, self-revealing violation of Technical Specification (TS) 6.8.1, "Procedures and Programs," as described in Regulatory Guide 1.33, Revision 2, February 1978, when PSEG failed to adequately implement procedure st
Region: I | Salem | 8645 | 03/31/2014 05/09/2014 | 2014002-02 | NRC | NCV | Initiating Events | Green | Inadequate Online Risk Assessment for an Adverse Change in Grid Conditions |  | H.4 Teamwork | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.13 | The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.65(a)(4) when PSEG inadequately assessed risk during a period of adverse grid conditions. On January 7, 2014, the regional transmission organization declared
Region: I | Salem | 8646 | 03/31/2014 05/09/2014 | 2014002-03 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment and Risk Management Actions for UV Testing |  | H.14 Conservative Bias | TE?: N | 05000311 Salem 2 |  | 71111.13 | Inspectors identified a Green NCV of 10 CFR 50.65(a)(4) when PSEG did not properly assess Unit 2 risk and implement RMAs in accordance with station procedures. PSEG conducted undervoltage (UV) surveillance testing on a 4 kilovolt (kV) vital bus without co
Region: I | Salem | 8651 | 03/31/2014 05/09/2014 | 2014002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post-Maintenance Testing of a Chiller |  | H.13 Consistent Process | TE?: N | 05000311 Salem 2 |  | 71111.19 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," was identified when PSEG did not perform adequate post-maintenance testing (PMT) of the 22 chiller. The chillers cool safety-related loads in the auxiliary building during
Region: I | Salem | 8652 | 03/31/2014 05/09/2014 | 2014002-05 | NRC | NCV | Mitigating Systems | Green | Failure to establish appropriate MR performance goals |  | H.8 Procedure Adherence | TE?: N | 05000272 Salem 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(1) associated with Unit 1. Specifically, PSEG did not establish appropriate performance goals in response to positive displacement pump (PDP) performance issues that resulted in significant emergent
Region: I | Salem | 8653 | 03/31/2014 05/09/2014 | 2014002-06 | NRC | FIN | Mitigating Systems | Green | Failure to take adequate corrective actions following a PDP failure to couple-on-demand event. |  | P.3 Resolution | TE?: N | 05000272 Salem 1 |  | 71152 | The inspectors identified a Green FIN associated with Unit 1 for PSEG's failure to take adequate corrective actions in accordance with procedure LS-AA-125, "Corrective Action Program," Attachment 1 guidance following a PDP failure to couple-on-demand even
Region: I | Salem | 8654 | 03/31/2014 05/09/2014 | 2014002-07 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Inspection of Isolated Phase Main Bus Duct Cooling Fan Sheave |  | H.4 Teamwork | TE?: N | 05000311 Salem 2 |  | 71152 | A self-revealing Green FIN was identified against PSEG procedure MA-AA-716-009, "Use of Maintenance Procedures," Revision 5, when PSEG staff did not follow "the rules of usage for Maintenance Department procedures" as applied to work on a Unit 2 isolated
Region: I | Salem | 8634 | 12/31/2013 02/06/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Fire Brigade Performance during an Unannounced Drill |  | P.3(a) Self-Assessment | TE?: N | 05000311 Salem 2 |  | 71111.05A | The inspectors identified a Green NCV of Unit 2 license condition 2.C.(10), Fire Protection, when PSEG did not adequately assess fire brigade performance during an unannounced drill on November 18, 2013, as required by the fire protection program. Specifi
Region: I | Salem | 8636 | 12/31/2013 02/06/2014 | 2013005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate HELB Barrier Controls |  | H.3(a) Work Planning | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.15 | The inspectors identified a Green NCV of TS 6.8.1, "Procedures and Programs", as described in Regulatory Guide (RG) 1.33, Revision 2, when PSEG did not properly implement high energy line break (HELB) barrier controls in accordance with CC-AA-201, Plant B
Region: I | Salem | 8637 | 08/01/2013 08/26/2013 | 2013008-01 | NRC | FIN | Initiating Events | Green | Failure to Evaluate Performance Deficiency for FIN 2011004-02 |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | The inspectors identified a Green finding (FIN) for PSEG's failure to evaluate the performance deficiency documented for FIN 2011004-02 in accordance with procedure LSAA- 1003, "NRC Inspection Preparation and Response." Specifically, PSEG failed to init
Region: I | Salem | 8638 | 08/01/2013 08/26/2013 | 2013008-02 | Self - Revealed | NCV | Mitigating Systems | Green | 13 Switchgear and penetration Area Ventilation Supply Fan Motor Bearing Failure due to Deletion of Preventative Maintenance Requirement |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified because PSEG did not complete a change to a preventative maintenance requirement for the Switchgear and Penetration Area Vent
Region: I | Salem | 8612 | 06/30/2013 07/25/2013 | 2013003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions to Address an Adverse Trend in the 2R1B-2 Radiation Monitor |  | P.1(b) Trend Performance CAP | TE?: N | 05000272 Salem 1 |  | 71111.04Q | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with PSEG failing to adequately trend an adverse condition and initiate effective corrective actions to address declining performance. Specifica
Region: I | Salem | 8617 | 06/30/2013 07/25/2013 | 2013003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Incorrect Component Installed for Containment Closure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 |  | 71111.13 | A self-revealing NCV of Unit 1 of 10 CFR Part 50, Appendix B, Criterion VIII, "Identification and Control of Materials, Parts, and Components," because PSEG did not prevent the installation and use of incorrect components. Specifically, PSEG installed an
Region: I | Salem | 8618 | 06/30/2013 07/25/2013 | 2013003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Evaluate Unit 2 Service Water Accumulator Discharge Valve IST Not Meeting Acceptance Criteria |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 71111.15 | A self revealing NCV of Salem TS 6.8.4.j, "Inservice Testing (IST)," that implements the IST program for American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 components in accordance with the ASME Operations and Maintenance (OM) code was
Region: I | Salem | 8630 | 06/30/2013 07/25/2013 | 2013003-04 | NRC | NCV | Mitigating Systems | Green | Scaffold Installed with Insufficient Separation to Safety-Related Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71111.2 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," because PSEG did not ensure adequate separation was maintained between temporary scaffolding and safety-related equipment. Specifically, the inspectors identified numero
Region: I | Salem | 8631 | 06/30/2013 07/25/2013 | 2013003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures to Identify and Control Access to a Locked High Radiation Area |  | H.3(b) Work Activity Coordination | TE?: N | 05000311 Salem 2 |  | 71124.01 | The inspectors identified a self-revealing finding of very low safety significance associated with failure to implement TS 6.8 procedures. Specifically, the inspectors identified that PSEG did not implement radiation protection procedure requirements asso
Region: I | Salem | 8632 | 06/30/2013 07/25/2013 | 2013003-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow the Loss of Main Condenser Vacuum Procedure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000272 Salem 1 |  | 71153 | A self revealing NCV of Technical Specification (TS) 6.8.1 "Procedure and Programs," resulted from operators' failure to implement the Loss of Condenser Vacuum procedure. Specifically, operators failed to follow S1.OP-AB.COND-0001, "Loss of Main Condenser
Region: I | Salem | 8607 | 03/31/2013 05/09/2013 | 2013002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correct Condition Adverse to Quality in Service Water Check Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified because PSEG did not complete corrective actions to address degraded valve bearings (i.e., installing new bearings) identified by technicians during SW
Region: I | Salem | 8608 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Install the Correct Size Zinc Anode in 11 Service Water Strainer Results in Strainer Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 |  | 71111.12 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," because PSEG did not assure that replacement zinc anodes procured for the service water (SW) strainers conformed to pr
Region: I | Salem | 8609 | 03/31/2013 05/09/2013 | 2013002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Relay Testing Instructions Cause Loss of One Offsite Power Source |  | H.3(a) Work Planning | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.12 | A self-revealing finding was identified because the work instructions used to perform relay testing on January 21, 2013, did not include the level of detail required by site work planning standards. Specifically, they did not specify the test switches tha
Region: I | Salem | 8610 | 03/31/2013 05/09/2013 | 2013002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Isolation of Service Water to all EDGs in Mode 6 |  | H.4(a) Human Error Prevention | TE?: N | 05000311 Salem 2 |  | 71153 | A self-revealing NCV of Technical Specification (TS) 6.8.1, "Procedures and Programs," was identified because PSEG personnel did not use the documentation required by site procedures to verify component position during removal of a clearance tagout. As a
Region: I | Salem | 8611 | 03/31/2013 05/09/2013 | 2013002-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Feedwater Control Valve Corrective Actions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000311 Salem 2 |  | 71153 | A self-revealing finding was identified because PSEG did not implement timely and effective corrective actions to address feedwater control valve (FCV) positioner malfunctions that occurred between 2004 and 2012, The inspectors determined that minor malfu
Region: I | Salem | 8603 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Liquid CO2 Inventory for Fire Suppression |  | H.3(b) Work Activity Coordination | TE?: N | 05000272 Salem 1 |  | 71111.05Q | The inspectors identified a Green NCV of the Unit 1 Operating License Condition 2.C because PSEG did not maintain an adequate CO2 inventory to ensure the operability of the installed deluge fire suppression system in accordance with the approved Fire Prot
Region: I | Salem | 8599 | 09/30/2012 11/08/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Injection of Auxiliary Feedwater into the 23 Steam Generator |  | H.4(a) Human Error Prevention | TE?: N | 05000311 Salem 2 |  | 71111.22 | A self-revealing NCV of Technical Specification (TS) 3.7.1.2.a, "Auxiliary Feedwater System," was identified because the 23 steam generator flow control valve from the 21 auxiliary feedwater (AFW) pump went open unexpectedly during the in-service test of
Region: I | Salem | 8584 | 06/30/2012 08/10/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | 13 Service Water Strainer Unavailabilty due to Inadequate Post Maintenance Test |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing NCV of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," was identified because the 13 service water (SW) strainer failed while in-service on March 13, 2012. PSEG failed to perform adequate post-maintenance testing (PMT) on
Region: I | Salem | 8597 | 06/30/2012 08/10/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Repeat Failures in Safety-Related Solenoid Valves in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified because PSEG did not correct a condition adverse to quality. Specifically, repeat failures of solenoid operated valves (SOVs) with voltage applied great
Region: I | Salem | 8598 | 06/30/2012 08/10/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Deficient Control of Transient Equipment in Seismic Class Auxiliary Building |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71111.15 | The inspectors identified a NCV of TS 6.8.1.a, "Procedures and Programs," because PSEG failed to properly control and store transient material within seismic class I buildings such that the equipment did not pose a hazard to safe plant operation. Specific
Region: I | Salem | 8592 | 09/30/2011 11/09/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate IST Program Evaluation of a Pressure Relief Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000311 Salem 2 |  | 71111.19 | The inspectors identified a NCV of Salem Technical Specification (TS) 6.8.4.j, "In Service Testing," that implements the in service testing program for American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 components in accordance with th
Region: I | Salem | 8593 | 09/30/2011 11/09/2011 | 2011004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Evaluate Corrective Action Options for RCP Motor Cables |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000311 Salem 2 |  | 71111.2 | A self-revealing finding of very low safety significance was identified on June 26, 2011, as Salem Unit 2 tripped following a trip of the 23 reactor coolant pump (RCP) due to a ground fault inside the 23 RCP motor junction box. PSEG determined that the ca
Region: I | Salem | 8594 | 09/30/2011 11/09/2011 | 2011004-03 | NRC | NCV | Emergency Preparedness | Green | Late State Notification of UE |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000311 Salem 2 |  | 71153 | The inspectors identified a NCV of 10 CFR 50.47, "Emergency Plans." Specifically, state officials were not notified within 15 minutes of the declaration of an Unusual Event (UE), a risk significant planning standard. PSEG has entered this issue into their
Region: I | Salem | 8586 | 07/21/2011 09/02/2011 | 2011009-01 | Self - Revealed | NCV | Initiating Events | Green | Untimely Completion of Corrective Actions Results in No. 11 Service Water Strainer Trip Due To Grassing |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000272 Salem 1 |  | 71152B | The inspectors identified a self-revealing Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because the 11 service water strainer overloads tripped on February 9, 2011, due to binding of the strainer rotating drum, w
Region: I | Salem | 8582 | 06/30/2011 08/09/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | IMPROPER CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL |  | H.3(b) Work Activity Coordination | TE?: N | 05000272 Salem 1 |  | 71111.05Q | The inspectors identified a NCV of Salem Operating License condition 2.C.5, that requires PSEG implement all provisions of the Fire Protection Program as described in the Updated Final Safety Analysis Report (UFSAR). Specifically, PSEG stored a rod drive
Region: I | Salem | 8585 | 06/30/2011 08/09/2011 | 2011003-02 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE CONTROL OF SWITCHYARD MAINTENANCE |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.13 | A self-revealing finding of very low safety significance was identified on April 1, 2011, because a 500 KV load break disconnect 3T60 failed to operate upon the restoration of switchyard maintenance. This caused a four-hour delay in the restoration from a
Region: I | Salem | 8581 | 03/31/2011 05/12/2011 | 2011002-02 | Self - Revealed | FIN | Initiating Events | Green | UNIT 1 MAIN GENERATOR VOLTAGE REGULATOR |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000272 Salem 1 |  | 71153 | A self-revealing finding of very low safety significance was identified for the failure of PSEG to resolve a long standing issue with the reliability of the Unit 1 main generator voltage regulator (VR). A failure in the Unit 1 main generator VR resulted i
Region: I | Salem | 8568 | 02/18/2011 04/04/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CALCULATIONS FOR DEGRADED VOLTAGE RELAY VOLTAGE SETPOINT |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control", because PSEG had not verified the adequacy of the design for the DVR voltage setpoint. Specifically, P
Region: I | Salem | 8575 | 02/18/2011 04/04/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM A TS REQUIRED BATTERY PERFORMANCE TEST |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of Salem Unit 1 Technical Specification (TS) Surveillance Requirement (SR) 4.8.2.5.2.h. Specifically, the team identified that PSEG did not perform a bat
Region: I | Salem | 8576 | 02/18/2011 04/04/2011 | 2011007-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IDENTIFY AND CORRECT A CONDITION ADVERSE TO QUALITY AFFECTING THE CREACS EXPANSION JOINTS |  | H.3(b) Work Activity Coordination | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action", because PSEG did not identify and correct a condition adverse to quality. Specifically, PSE
Region: I | Salem | 8567 | 12/31/2010 02/08/2011 | 2010005-01 | Self - Revealed | NCV | Mitigating Systems | Green | 13 Turbine Driven Auxiliary Feedwater Pump Trip Mechanism |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing NCV of Appendix B, Criterion V, "Instructions, Procedures, and Drawings", was identified because of two unexpected trips of the turbine trip valve (1MS52) for the 13 turbine driven auxiliary feedwater (TDAFW) pump. Specifically, adjustmen
Region: I | Salem | 8563 | 06/30/2010 08/10/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Buried AFW Discharge Piping not Tested in Accordance with 10 CFR 50.55a |  |  | TE?: N | 05000272 Salem 1 |  | 71111.08P | The inspectors identified an NCV of very low safety significance for PSEG's failure to perform auxiliary feedwater (AFW) discharge piping system pressure tests on buried piping components as required by 10 CFR 50.55a(g)(4) and the referenced American Soci
Region: I | Salem | 8566 | 06/30/2010 08/10/2010 | 2010003-02 | Self - Revealed | FIN | Initiating Events | Green | 21 Steam Generator Feed Pump Trip |  | H.4(b) Procedural Compliance | TE?: N | 05000311 Salem 2 |  | 71111.12 | A self-revealing finding of very low safety significance was identified on January 21, 2010, because a control system short circuit caused the 21 steam generator feed pump (SGFP) to trip. This caused a turbine runback and ultimately an automatic Unit 2 re
Region: I | Salem | 8562 | 03/31/2010 05/12/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Chillers Inoperability Exceeds TS Allowed Outage Time |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000272 Salem 1 |  | 71153 | A self-revealing NCV of TS 3.7.10 "Chilled Water System, Auxiliary Building Subsystem", was identified because the 12 chiller tripped on low chill water temperature during the starting of the 13 chiller for post-maintenance testing on December 7, 2010. Th
Region: I | Salem | 8560 | 12/31/2009 02/09/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Salem Unit 2 Degradation of Shutdown Cooling caused by Failure of 22RH18 |  |  | TE?: N | 05000311 Salem 2 |  | 71153 | A self-revealing NCV of TS 6.8.1.a, Procedures and Programs, was identified because 22RH18 failed while in-service on October 17, 2009. This caused a degradation of shutdown core cooling on October 18, 2009. PSEG determined that the cause of the valve fai
Region: I | Salem | 8561 | 12/31/2009 02/09/2010 | 2009005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance of the 22 CCHX Service Water Outlet Butterfly Valve |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 71111.12 | A self-revealing NCV of Technical Specification 6.8.1, Procedures and Programs, was identified because bolting between the valve body and actuator for the 22 component cooling heat exchanger (CCHX) service water isolation valve broke causing the valve to
Region: I | Salem | 8553 | 07/10/2009 08/19/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH GOALS AND MONITOR FOR (a)(1) SERVICE WATER SYSTEM |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | The inspectors identified a non-cited violation of very low safety significance of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(1), for PSEG's failure to monitor the performance of the
Region: I | Salem | 8549 | 06/30/2009 08/12/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | IMPROPER MAINTENANCE RULE SCOPING OF THE SERVICE WATER INTAKE STRUCTURE SUMP SYSTEM |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000311 Salem 2 |  | 71111.12 | The NRC identified a NCV of 10 CFR 50.65 because PSEG did not include the service water intake structure (SWIS) sump within the scope of the Salem maintenance rule program and consequently did not recognize that preventive maintenance on the SWIS sump was
Region: I | Salem | 8552 | 06/30/2009 08/12/2009 | 2009003-02 | Self - Revealed | FIN | Mitigating Systems | Green | INADEQUATE MAINTENANCE OF THE 13 AUXILIARY FEEDWATER PUMP GOVERNOR |  |  | TE?: N | 05000272 Salem 1 |  | 71111.15 | A self-revealing finding of very low safety significance was identified because PSEG did not implement adequate preventive maintenance for the turbine driven auxiliary feedwater (AFW) pump speed governor. Consequently, the governor oil conditions degraded
Region: I | Salem | 8543 | 02/13/2009 03/24/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE SPURIOUS OPERATION OF SAFETY INJECTION SIGNAL |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.05T | The team identified that PSEG failed to evaluate a single spurious operation of a safety injection signal during a main control room fire and its impact on the ability to achieve and maintain hot standby conditions. This finding was determined to be of ve
Region: I | Salem | 8536 | 12/30/2008 02/09/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | IMPROPER CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 |  | 71111.05Q | The inspectors identified a non-cited violation (NCV) of Salem Operating License condition 2.C.5, that requires that PSEG implement all provisions of the Fire Protection Program as described in the Updated Final Safety Analysis Report (UFSAR). Specificall
Region: I | Salem | 8542 | 12/30/2008 02/09/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR NO. 22 COMPONENT COOLING WATER HEAT EXCHANGER SERVICE WATER OUTLET TEMPERATURE CONTROL VALVE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 71111.12 | The inspectors identified a self-revealing NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, because the No. 22 component cooling water heat exchanger (CCWHX) service water (SW) outlet temperature control valve (22SW127) did not stroke open whe
Region: I | Salem | 8540 | 12/30/2008 02/09/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE IMPLEMENTATION OF RISK MANAGEMENT ACTIONS ASSOCIATED WITH PLANNED MAINTENANCE ON THE UNIT 2 PRESSURIZER POWER OPERATED RELIEF VALVES |  | H.4(b) Procedural Compliance | TE?: N | 05000311 Salem 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) because PSEG did not did not implement prescribed risk management actions (RMA) while both Unit 2 pressurizer (PZR) power operated relief valves (PORV) were isolated. PSEG's corrective actions in
Region: I | Salem | 8541 | 12/30/2008 02/09/2009 | 2008005-04 | Self - Revealed | FIN | Mitigating Systems | Green | INADEQUATE IDENTIFICATION OF MIDLOOP LEVEL CALIBRATION ERROR |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000272 Salem 1 |  | 71111.2 | The inspectors identified a self-revealing finding because PSEG did not use the corrective action process (CAP) to identify and correct a recurring issue with the calibration of a narrow range mid loop level transmitter. This extended the time that the re
Region: I | Salem | 8535 | 12/30/2008 02/09/2009 | 2008005-05 | Self - Revealed | NCV | Mitigating Systems | Green | SALEM UNIT 2 HIGH STEAM FLOW PROTECTION CHANNELS INOPERABLE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | NONE | A self-revealing NCV of 10 CFR 50, Appendix B, Criteria XI, "Test Control," was identified because all Unit 2 high steam flow protection channels were discovered inoperable on May 12, 2008. Specifically, following steam generator replacement on Unit 2, PS
Region: I | Salem | 8537 | 12/12/2008 01/20/2009 | 2008009-01 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR PRESSURIZER DRAINING EVOLUTION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 |  | 93812 | The inspectors identified a self-revealing Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" because PSEG did not provide operators with a procedure that contained appropriate quantitative and qualit
Region: I | Salem | 8538 | 12/12/2008 01/20/2009 | 2008009-02 | NRC | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT ACTIONS FOR A PRESSURIZER LEVEL ALARM |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 93812 | The inspectors identified a green non-cited violation of Technical Specification 6.8.1, "Procedures and Programs," because operators did not implement actions required per procedure S1.OP-AR.ZZ-0005(Q), "Overhead Annunciators Window E," in response to a "
Region: I | Salem | 8539 | 12/12/2008 01/20/2009 | 2008009-03 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS FOR OPERATING EXPERIENCE APPLICALBE TO STATION OPERATIONS |  |  | TE?: N | 05000272 Salem 1 |  | 93812 | The inspectors identified a self-revealing Green finding because on October 15, 2008, operators drained the RCS to the top of the reactor vessel hot leg without implementing the controls required to protect the source of decay heat removal for the plant.
Region: I | Salem | 8525 | 08/08/2008 09/22/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR MOTOR OPERATED VALVE CAPABILITY ASSESSMENTS |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that PSEG had used non-conservative inputs and methodologies in calculating terminal voltages
Region: I | Salem | 8526 | 08/08/2008 09/22/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR MOTOR OPERATED VALVE THERMAL OVERLOAD PROTECTION DEVICES |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that PSEG had not implemented measures to verify that thermal overloads (TOLs) on safety-rela
Region: I | Salem | 8527 | 08/08/2008 09/22/2008 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL FOR UNIT 2 CONTAINMENT SUMP VALVE DESIGN DP DETERMINATION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, in that PSEG had not validated a key design input regarding the assumed RHR pump operation time
Region: I | Salem | 8520 | 06/30/2008 08/07/2008 | 2008003-01 | Self - Revealed | NCV | Initiating Events | Green | SALEM UNIT 2 LOSS OF ALL THREE CHILLERS |  | H.4(b) Procedural Compliance | TE?: N | 05000311 Salem 2 |  | 71111.13 | A self-revealing non-cited violation of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," was identified because PSEG did not maintain adequate control of the system configuration for the Unit 2 chill water system during maintenance on the
Region: I | Salem | 8519 | 06/30/2008 08/07/2008 | 2008003-02 | Self - Revealed | NCV | Mitigating Systems | Green | SALEM UNIT 2 LOSS OF REACTOR VESSEL LEVEL INDICATION SYSTEM |  | H.3(b) Work Activity Coordination | TE?: N | 05000311 Salem 2 |  | 71111.15 | A self-revealing non-cited violation of Technical Specification (TS) 6.8.1.a, "Procedures and Programs," was identified because PSEG did not adequately maintain the calibration of the Unit 2 reactor vessel level indication system (RVLIS). Specifically, sc
Region: I | Salem | 8521 | 06/30/2008 08/07/2008 | 2008003-03 | Self - Revealed | NCV | Barrier Integrity | Green | SALEM UNIT 2 22 CFCU VALVES MISPOSITIONED |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 71111.22 | A self-revealing non-cited violation of TS 6.8.1.a, "Procedures and Programs" was identified because the 22 Containment Fan Coil Unit (CFCU) had cooling water flow to the motor cooler inadvertently isolated during a routine surveillance test. Specifically
Region: I | Salem | 8510 | 03/31/2008 04/28/2008 | 2008002-01 | Self - Revealed | NCV | Mitigating Systems | Green | 25SW24 FAILURE CAUSED 25 SERVICE WATER PUMP UNAVAILABILITY |  | P.2(b) Implementing Operating Experience | TE?: N | 05000311 Salem 2 |  | 71111.12 | The inspectors identified a self-revealing non-cited violation of Technical Specification 6.8.1.a, "Procedures and Programs." The inspectors determined that maintenance procedures for the 25 service water strainer (SWS) blow down valve (25SW24) were inade
Region: I | Salem | 8511 | 03/31/2008 04/28/2008 | 2008002-02 | Self - Revealed | NCV | Initiating Events | Green | SALEM UNIT 2 LOSS OF ALL THREE CHILLERS |  | H.4(a) Human Error Prevention | TE?: N | 05000311 Salem 2 |  | 71111.15 | The inspectors identified a self-revealing non-cited violation of Technical Specification 6.8.1.a, "Procedures and Programs " when the 23 chiller failed to start on January 22, 2008. PSEG personnel did not start the 23 chiller and verify proper operation
Region: I | Salem | 8506 | 12/29/2007 02/12/2008 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | INADEQUATE TROUBLESHOOTING FOR A FAILURE OF 13 CONTAINMENT FAN COIL UNIT TO START IN SLOW SPEED |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 6.8.1, "Procedures and Programs," on July 25, 2007, because PSEG did not conduct adequate troubleshooting and corrective maintenance following a repeat failure of the 13 containmen
Region: I | Salem | 8495 | 06/29/2007 08/14/2007 | 2007003-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO INSPECT TUBING ON THE 22 CONTROL AREA CHILLER |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000311 Salem 2 |  | 71111.12 | A self-revealing NCV for failure to comply with 10 CFR, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," was identified when operators discovered a significant leak in the copper oil filter tubing on the 22 CAC on May 1, 2007, that made t
Region: I | Salem | 7226 | 05/12/2007 08/14/2007 | 2007003-05 | Self - Revealed | FIN | Initiating Events | Green | SALEM UNIT 2 AUTOMATIC REACTOR TRIP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000311 Salem 2 |  | 71153 | A self-revealing finding for improper maintenance on a demineralizer sight glass was identified when the sight glass catastrophically failed and initiated a condensate system transient that resulted in a reactor trip. Contrary to vendor recommendations th
Region: I | Salem | 8502 | 05/01/2007 08/14/2007 | 2007003-03 | Self - Revealed | NCV | Mitigating Systems | Green | 21 CONTROL AREA CHILLER INOPERABLE DUE TO OPERATOR PROCEDURAL ERROR |  | H.4(a) Human Error Prevention | TE?: N | 05000311 Salem 2 |  | 71111.13 | A self-revealing NCV for failure to comply with 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," was identified when operators discovered the 21 CAC in an inoperable condition on May 1, 2007. In accordance with post-maintenance
Region: I | Salem | 8503 | 05/01/2007 08/14/2007 | 2007003-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT STEP 3.6.2 OF THE COMPONENT FOULING PROCEDURE |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.15 | The inspectors identified an NCV for failure to comply with 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," when operators did not implement additional log readings for service water (SW) heat exchangers (HXs) as specified by
Region: I | Salem | 7225 | 03/31/2007 05/15/2007 | 2007002-02 | Self - Revealed | NCV | Mitigating Systems | Green | 15 SERVICE WATER PUMP UNAVAILABILITY |  | H.4(a) Human Error Prevention | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because PSEG did not conduct maintenance in accordance with appropriate written procedures. Specifically, the pump packing
Region: I | Salem | 7219 | 03/23/2007 05/03/2007 | 2007006-02 | Self - Revealed | NCV | Mitigating Systems | Green | 12 CHILLER RENDERED UNAVAILABLE DUE TO INADEQUATE MAINTENANCE |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 |  | 71152B | A self-revealing non-cited violation of Technical Specification 6.8.1 was identified when improper maintenance caused the 12 control area chiller to trip and remain unavailable for approximately 70 hours on July 15, 2006. Maintenance was incorrectly perfo
Region: I | Salem | 7220 | 03/23/2007 05/03/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | REPETITIVE TRIPS OF 22 SERVICE WATER STRAINER |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000311 Salem 2 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 50, Appendix B, criterion XVI, 'Corrective Action', when the 22 service water (SW) suction strainer tripped on February 24, 2007, rendering the 22 service water pump unavailable for 44 hours to repair the
Region: I | Salem | 7222 | 03/23/2007 05/03/2007 | 2007006-04 | NRC | NCV | MISC | Green | FITNESS-FOR-DUTY (FFD) COLLECTION PERSONNEL COLLECTING FFD SAMPLES FROM CO-WORKERS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 26, Appendix A, subpart B, 2.3 (1) when the inspectors observed PSEG's fitness-for-duty (FFD) collection technicians and security officers perform urine and breath collection on co-workers on March 21, 20
Region: I | Salem | 7223 | 03/23/2007 05/03/2007 | 2007006-05 | NRC | NCV | MISC | Green | FITNESS-FOR-DUTY (FFD) COLLECTORS LEAVING FFD SPECIMENS UNATTENDED |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 26, Appendix A, Subpart B, 2.4 (g) (20) when the inspectors observed PSEG's fitness-for-duty (FFD) collection technicians leaving split FFD urine specimens in unsealed aliquot tubes and sealed specimen co
Region: I | Salem | 7214 | 12/31/2006 02/01/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE IMPLEMENTATION FOR SCAFFOLD CONSTRUCTION |  | H.4(b) Procedural Compliance | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PSEG did not adequately implement procedural controls for scaffold construction in safety-related areas. This per
Region: I | Salem | 7215 | 12/31/2006 02/01/2007 | 2006005-02 | NRC | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT EFFECTIVE CORRECTIVE ACTIONS FOR REACTOR COOLANT SYSTEM TUBING LEAKS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000311 Salem 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," in that corrective actions established in 1998 to identify, clean, and inspect Unit 2 reactor coolant system (RCS) instrument tubing were not im
Region: I | Salem | 7216 | 12/31/2006 02/01/2007 | 2006005-03 | Self - Revealed | NCV | Barrier Integrity | Green | INCORRECTLY POSITIONED FUEL ASSEMBLY |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000311 Salem 2 |  | 71111.2 | A self-revealing non-cited violation of Salem Technical Specification 6.8.1.b, "Procedures and Programs" was identified when PSEG discovered that an irradiated fuel assembly was incorrectly positioned into the spent fuel pool (SFP) and subsequently transf
Region: I | Salem | 7208 | 09/30/2006 11/09/2006 | 2006004-01 | NRC | NCV | Initiating Events | Green | 22 SERVICE WATER STRAINER TRIP |  | H.4(b) Procedural Compliance | TE?: N | 05000311 Salem 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to accomplish maintenance in accordance with procedures. PSEG maintenance personnel omitted procedure steps to ade
Region: I | Salem | 7213 | 09/30/2006 11/09/2006 | 2006004-02 | NRC | NCV | Initiating Events | Green | REACTOR COOLANT SYSTEM TUBING STRUCTURAL INTEGRITY |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000311 Salem 2 |  | 71153 | The inspectors identified a non-cited violation for PSEG's failure to follow Salem Technical Specification 3.4.11.1.b., Structural Integrity. PSEG discovered a leak on the instrument tubing for reactor coolant system loop flow transmitter 2FT416 and did n
Region: I | Salem | 7200 | 03/31/2006 04/26/2006 | 2006002-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE MAINTENANCE PRACTICES RESULT IN UNAVAILABILITY OF THE 11 CONTAINMENT FAN COIL UNIT |  |  | TE?: N | 05000272 Salem 1 |  | 71111.12 | A self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified. PSEG maintenance personnel omitted procedure steps to obtain motor vibration data at the conclusion of 11 containment fa
Region: I | Salem | 7202 | 03/31/2006 06/28/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH STATION COLD SHUTDOWN REPAIR PROCEDURES |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71111.05T | The team identified a non-cited violation (NCV) for failure to maintain equipment required for cold shutdown (CSD) repairs in the designated location. Specifically, procedure SC.MD-AB.ZZ-0001, Installation of Temporary 4KV Power Cables to CCW and RHR Moto
Region: I | Salem | 7193 | 02/17/2006 04/03/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | DEGRADED COMPONENT COOLING WATER VALVE IMPACT ON COMPONENT COOLING WATER HYDRAULIC ANALYSES |  |  | TE?: N | 05000272 Salem 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the corrective actions for a degraded condition that impacted the existing desi
Region: I | Salem | 7194 | 02/17/2006 04/03/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | LACK OF SUPPORTING ANALYSES FOR TURBINE DRIVEN AUXILIARY FEEDWATER OPERATION UNDER STATION BLACKOUT CONDITION |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The team determined that analyses did not exist to verify the availability of the auxiliary feedwater (A
Region: I | Salem | 7195 | 02/17/2006 04/03/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE SUPPORTING ANALYSES FOR AUXILIARY FEEDWATER PUMP LOW SUCTION TRIP SETPOINT |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The technical basis of the AFW pump low suction pressure trip setpoint was not available, and the setpoi
Region: I | Salem | 7197 | 02/17/2006 04/03/2006 | 2006006-04 | Self - Revealed | FIN | Mitigating Systems | Green | FAILURE OF NO. 11 SWITCHGEAR EXHAUST FAN DUE TO LACK OF PREVENTIVE MAINTENANCE PERFORMANCE |  |  | TE?: N | 05000272 Salem 1 |  | 7111121 | A self-revealing finding of very low safety significance (Green) was identified which was associated with the failure of the No. 11 Switchgear return exhaust fan breaker to close and start the fan in October 2005. Specifically, the failure occurred due to
Region: I | Salem | 7198 | 02/17/2006 04/03/2006 | 2006006-05 | NRC | NCV | Initiating Events | Green | INADEQUATE PROCEDURE FOR LOSS OF COMPONENT COOLING WATER |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of Technical Specification 6.8.1, Procedures, for an inadequate procedure to respond to a loss of component cooling water (CCW) event. The procedure was inadequa
Region: I | Salem | 7199 | 02/17/2006 04/03/2006 | 2006006-06 | NRC | NCV | Mitigating Systems | Green | RESIDUAL HEAT REMOVAL ROOM INTERNAL FLOOD PROTECTION |  |  | TE?: N | 05000311 Salem 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The Unit 2 design did not ensure that an internal auxiliary building flood, due to a postulated moderate
Region: I | Salem | 125632 | 11/05/2019 |  |  | LIV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000272 Salem 1 05000311 Salem 2 |  | 71152
Region: I | Seabrook | 126575 | 12/31/2019 02/05/2020 | 2019004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure Compliance to Ensure Representative Carbon Sampling for Containment Enclosure Emergency Air Cleanup System |  | H.8 - Procedure Adherence | TE?: N | 05000443 Seabrook 1 |  | 71111.19 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when steps for refilling carbon sample canisters for the 'B' train containment enclosure emergency air cleanup system w
Region: I | Seabrook | 126172 | 10/31/2019 11/25/2019 | 2019403-02 | NRC | NCV |  | Green | Failure to Implement Cyber Security Controls for Access Authorization Critical Digital Assets |  | H.3 - Change Management | TE?: N | 05000443 Seabrook 1 |  | 71130.10P | The team identified a Green finding and associated NCV of the Seabrook Facility Operating License Condition 2.E, for NextEra’s failure to implement and maintain in effect all provisions of the Commission-approved CSP. Specifically, NextEra did not documen
Region: I | Seabrook | 125007 | 07/03/2019 07/03/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Improperly Sized Thermal Overload Relays for Throttling Motor-Operated Valves |  | NONE | TE?: N | 05000443 Seabrook 1 | Design Control | 71111.21M | The team identified a finding of very low safety significance (Green) involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” in that NextEra did not adequately verify or check the adequacy of design, such as by the
Region: I | Seabrook | 125009 | 07/03/2019 07/03/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate 4kV Breaker Testing |  | NONE | TE?: N | 05000443 Seabrook 1 | Equipment Performance | 71111.21M | The team identified a finding of very low safety significance (Green) involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” in that NextEra’s test program did not assure that all testing required to demonstrate that
Region: I | Seabrook | 125085 | 07/03/2019 07/03/2019 | 2019010-03 | NRC | NCV | Mitigating Systems | Green | Survivability of Equipment during a Postulated Design Basis Accident Coincident with Degraded Offsite Power System Voltage |  | NONE | TE?: N | 05000443 Seabrook 1 | Design Control | 71111.21M | The team identified a finding of very low safety significance (Green) involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” in that NextEra did not verify or check the adequacy of design for setting thermal overlo
Region: I | Seabrook | 124770 | 06/30/2019 08/05/2019 | 2019002-01 | NRC | NCV | Emergency Preparedness | Green | Emergency Planning Audit Did Not Evaluate Interface With Offsite Response Organizations |  | H.1 - Resources | TE?: N | 05000443 Seabrook 1 | Offsite EP | 71114.05 | The inspector identified a Green, non-cited violation of 10 CFR 50.54(t)(2) because NextEra staff did not include an evaluation of the adequacy of the interfaces with State and local governments in a review of emergency preparedness program elements in Au
Region: I | Seabrook | 124779 | 06/30/2019 08/05/2019 | 2019002-02 | NRC | NCV | Emergency Preparedness | Green | Emergency Plan Required Drills Inadequately Documented |  | H.8 - Procedure Adherence | TE?: N | 05000443 Seabrook 1 | ERO Performance | 71114.05 | The inspector identified a Green, non-cited violation of 10 CFR 50.54(q)(2), because NextEra did not maintain the effectiveness of the station’s emergency plan. Specifically, NextEra did not follow procedure EP-AA-101-1000, Nuclear Division Drill and Exer
Region: I | Seabrook | 25928 | 12/31/2018 01/30/2019 | 2018004-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of Primary Component Cooling Water |  | H.12 - Avoid Complacency | TE?: N | 05000443 Seabrook 1 | Configuration Control | 71153 | A self-revealed Green non-cited violation (NCV) was identified when the licensee did not follow a procedure (Regulatory Guide 1.33, Appendix A) required by Technical Specification 6.7.1. Specifically, while performing procedure OS1012.04, "Primary Compon
Region: I | Seabrook | 23193 | 12/31/2017 02/12/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Licensed Operator Examination Integrity Not Ensured |  | H.1 - Resources | TE?: N | 05000443 Seabrook 1 |  | 71111.11B | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 55.49, “Integrity of Examinations and Tests,” for the failure of the licensee to ensure that the integrity of the written examinations admi
Region: I | Seabrook | 23146 | 12/31/2017 02/12/2018 | 2017004-02 | NRC | NCV | Emergency Preparedness | Green | Failure of Exercise Critique to identify a RSPS Weakness |  | H.3 - Change Management | TE?: N | 05000443 Seabrook 1 |  | 71114.06 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Reglations (10 CFR) 50.47(b)(14) and 10 CFR Part 50, Appendix E, “Emergency Planning and Preparedness for Production and Utilization Facilities,” Section IV.F.2
Region: I | Seabrook | 22689 | 12/31/2017 02/12/2018 | 2017004-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedure Implementation Results in a Manual Reactor Trip |  | H.5 - Work Management | TE?: N | 05000443 Seabrook 1 |  | 71153 | A self-revealing Green finding was identified for inadequate implementation of procedure MA 4.5, “Configuration Control,” Revision 18. Specifically, maintenance technicians failed to properly implement MA 4.5 while backfilling steam generator instrumentat
Region: I | Seabrook | 10743 | 07/13/2017 08/15/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Condition Adverse to FIre Protection Associated with Fire Safe Shutdown |  | H.1 Resources | TE?: N | 05000443 Seabrook 1 |  | 71111.05T | The team identified a Green, non-cited violation of Seabrook Station Unit 1 Facility Operating License Condition 2.F, "Fire Protection," for failure to implement and maintain in effect all provisions of the approved Fire Protection Program. Specifically,
Region: I | Seabrook | 10744 | 07/13/2017 08/15/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Test Program for Appendix R Emergency Lighting Units |  | H.5 Work Management | TE?: N | 05000443 Seabrook 1 |  | 71111.05T | The team identified a Green, non-cited violation of Seabrook License Condition 2.F, "Fire Protection," because NextEra did not implement the fire protection test program to ensure that the emergency lighting units were in conformance with design requireme
Region: I | Seabrook | 10725 | 09/02/2016 12/14/2016 | 2016007-01 | NRC | NCV | Initiating Events | Green | Innadequate Corrective Actions to Preclude Repetition of a Significant Condition Adverse to Quality |  | P.3 Resolution | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance, involving a non-cited violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion XVI, "Corrective Action," for not performing corrective actions to preclude repet
Region: I | Seabrook | 10730 | 09/02/2016 12/14/2016 | 2016007-03 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Required ASME In-Service Testing of Manual Isolation Valves for the Atmospheric Steam Dump Valve Block Valves |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance, involving a non-cited violation of Seabrook Technical Specification Surveillance Requirement 4.0.5, "Surveillance Requirements for In-Service Inspection and Testing of American Society of Mech
Region: I | Seabrook | 10717 | 06/30/2016 08/05/2016 | 2016002-01 | Self - Revealed | NCV | Initiating Events | Green | Automatic Initiation of Emergency Feedwater Resulting from Performance of Procedural Steps in a Manner Prohibited by Documented Instructions |  | H.11 Challenge the Unknown | TE?: N | 05000443 Seabrook 1 |  | 71153 | A self-revealing Green NCV of 10 CFR, Appendix B, Criterion V, "Instructions Procedures, and Drawings," was identified, because NextEra did not ensure that activities affecting quality were accomplished in accordance with documented instructions. Specific
Region: I | Seabrook | 10718 | 06/30/2016 08/05/2016 | 2016002-02 | Self - Revealed | NCV | Initiating Events | Green | Multiple Letdown Isolations Resulting from an Inadequate Procedure and the Performance of Steps Not Prescribed by Established Procedures |  | H.8 Procedure Adherence | TE?: N | 05000443 Seabrook 1 |  | 71153 | A self revealing Green NCV of 10 CFR, Appendix B, Criterion V, "Instructions Procedures, and Drawings," was identified because NextEra did not ensure that activities affecting quality were prescribed by documented procedures of a type appropriate to the c
Region: I | Seabrook | 10716 | 03/25/2016 05/06/2016 | 2016008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Complete Operabilty Determinations for ASR-Affected Structures | EA Case: 2016101 | P.3 Resolution | TE?: N | 05000443 Seabrook 1 |  | 71152 | The team identified a violation of Appendix B, Criterion V, "Instructions, Procedures, and Drawings," and NextEra Nuclear Fleet Administrative Procedure, EN-AA-203-1001, "Operability Determinations/Functionality Assessments," involving Seabrook Station st
Region: I | Seabrook | 10713 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Identification of Structural Deformation and Impacts on Associated Equipment |  | P.1 Identification | TE?: N | 05000443 Seabrook 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR, Appendix B, Criterion XVI, "Corrective Action," because NextEra did not ensure that degraded conditions were identified and entered into the corrective action process. Specifically, the inspectors identifie
Region: I | Seabrook | 10714 | 06/30/2015 08/05/2015 | 2015002-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Characterization of Prompt Operability Determination of the Containment Enclosure Building |  | P.2 Evaluation | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because NextEra did not perform an adequate POD of a safety-related plant structure. Specifically, NextEra did not appropriately categor
Region: I | Seabrook | 10709 | 12/31/2014 02/06/2015 | 2014005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Conditions Adverse to Quality in the Fuel Storage Building Structure |  | H.8 Procedure Adherence | TE?: N | 05000443 Seabrook 1 |  | 71111.12 | The inspectors identified an NCV of 10 CFR 50 Appendix B Criterion XVI, Corrective Actions, of very low safety significance because NextEra staff did not promptly identify nine visual indications of structural problems representing conditions adverse to q
Region: I | Seabrook | 10710 | 12/31/2014 02/06/2015 | 2014005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Evaluate FSB Settlement Data and the Design Basis |  | H.6 Design Margins | TE?: N | 05000443 Seabrook 1 |  | 71111.12 | The inspectors identified a violation of 10 CFR 50 Appendix B Criterion XVI, Corrective Actions, of very low safety significance because NextEra did not promptly identify a condition adverse to quality in December 2013 that involved a deviation from expec
Region: I | Seabrook | 10712 | 12/31/2014 02/06/2015 | 2014005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Periodically Calibrate REM-500 Neutron Survey Instruments |  |  | TE?: N | 05000443 Seabrook 1 |  | NONE | The inspectors identified a Green NCV of TS 6.7.1.a, "Procedures and Programs," because NextEra failed to conduct appropriate periodic calibration of neutron survey instruments. Specifically, since 1996, NextEra assumed that an operability check of certai
Region: I | Seabrook | 10705 | 07/10/2014 08/13/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Alternate Safe Shutdown Areas Affected by Smoke from Cable Spreading Room Fire |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.05T | The team identified a finding of very low safety significance, involving a non-cited violation of Seabrook Unit 1 Operating License Condition 2.F for failure to implement and maintain all aspects of the approved Fire Protection Program. Specifically, Next
Region: I | Seabrook | 10706 | 07/10/2014 08/13/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedures |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.05T | The team identified a finding of very low safety significance, involving a non-cited violation of Seabrook Unit 1 Operating License Condition 2.F for failure to implement and maintain all aspects of the approved Fire Protection Program. Specifically, Next
Region: I | Seabrook | 10700 | 06/30/2014 08/05/2014 | 2014003-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Technical Evaluation of Safety-Related Structures |  | H.8 Procedure Adherence | TE?: N | 05000443 Seabrook 1 |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) because NextEra did not perform adequate evaluations of safety-related plant structures. Specifically, additional technical evaluation and analysis was not adequately conducted on
Region: I | Seabrook | 10701 | 06/30/2014 08/05/2014 | 2014003-02 | Self - Revealed | FIN | Mitigating Systems | Green | Unexpected Main Generator Breaker Pole Closure Results in Reactor Trip |  | H.5 Work Management | TE?: N | 05000443 Seabrook 1 |  | 71153 | The inspectors identified a self-revealing finding of very low safety significance (Green), because NextEra did not ensure that adequate procedural guidance existed in ON1046.12, 'Operation of the Main Generator Breaker' to limit the likelihood of events
Region: I | Seabrook | 10699 | 03/31/2014 05/06/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Scaffolding Installed with Insufficient Separation to Safety Related Equipment |  | P.2 Evaluation | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," because NextEra did not ensure adequate separation was maintained between temporary scaffolding and safety-related equipment. Specifically, six instances of scaffol
Region: I | Seabrook | 10695 | 10/30/2013 11/19/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination Regarding Service Water Leakage and Associated TS Violation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," and an associated violation of technical specification (TS) 3.7.4, because NextEra did not
Region: I | Seabrook | 10686 | 04/26/2013 06/06/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequate Fault Protection for Safety Related Equipment from Non-Safety Related Load Fault |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of the 10CFR 50, Appendix B, Criterion III, "Design Control," in that, NextEra did not appropriately select and review, for suitability of application, a safety-
Region: I | Seabrook | 10687 | 04/26/2013 06/06/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Condensate Storage Tank Water Level Above Limits of Seismic Qualification |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that NextEra did not assure the seismic design requirements for Condensate Storage Tank (CST) were
Region: I | Seabrook | 10688 | 04/26/2013 06/06/2013 | 2013008-03 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Preventative Maintenance on the Supplemental Emergency Power System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance, in that NextEra did not perform preventative maintenance (PM) on supplemental emergency power system (SEPS) components as required by the approved engineering design modification for SEPS. As
Region: I | Seabrook | 10694 | 04/26/2013 06/06/2013 | 2013008-04 | NRC | NCV | Mitigating Systems | Green | Primary Component Cooling Water System Unavailable Following a Seismic Event |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", in that NextEra did not verify the design basis for the primary component cooling water (PC
Region: I | Seabrook | 10680 | 03/31/2013 05/01/2013 | 2013002-01 | Self - Revealed | FIN | Initiating Events | Green | Loss of DC Control Power to Switchyard #2 |  | H.4(a) Human Error Prevention | TE?: N | 05000443 Seabrook 1 |  | 71111.13 | A self-revealing finding of very low safety significance was identified for failure to follow procedures associated with switchyard maintenance activities on January 24, 2013. Specifically, in preparation for the planned maintenance on switchyard battery
Region: I | Seabrook | 10681 | 03/31/2013 05/01/2013 | 2013002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Evaluate Service Water Cooling Tower Level |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000443 Seabrook 1 |  | 71153 | A self-revealing NCV of technical specification (TS) 3.7.4 "Service Water System/Ultimate Heat Sink," resulted from operators' failure to follow procedures to evaluate a faulty SW cooling tower basin level instrument. Specifically, because NextEra personn
Region: I | Seabrook | 10664 | 12/31/2012 02/11/2013 | 2012005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correct a Condition Adverse to Quality for the L-5 FICI Connection |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000443 Seabrook 1 |  | 71111.19 | A self revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because the high pressure Swagelok fitting for the L-5 fixed in-core detection instrument failed and caused an unisolable reactor coo
Region: I | Seabrook | 10665 | 12/31/2012 02/11/2013 | 2012005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Implement Procedure Led to Reactor Coolant System Leakage from Pressurizer Safety Valve Flange |  | H.4(b) Procedural Compliance | TE?: N | 05000443 Seabrook 1 |  | 71111.19 | A self-revealing, non-cited violation of technical specification 6.7.1, "Procedures and Programs," was identified after the control room received a high discharge temperature alarm for pressurizer relief valve RC-V-116 while pressurizing the reactor coola
Region: I | Seabrook | 10656 | 09/30/2012 11/14/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Scaffold Installed with Insufficient Separation to Safety-Related Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000443 Seabrook 1 |  | 71111.2 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," because NextEra did not ensure that adequate separation was maintained between temporary scaffolding and safety-related equipment. Specifically, the inspectors identifie
Region: I | Seabrook | 10657 | 09/30/2012 11/14/2012 | 2012004-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Inadequate Process Necessary for Notification of OROs during an Emergency Declaration |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000443 Seabrook 1 |  | 71114.06 | A self-revealing NCV of 10 CFR 50.47(b)(5) and the requirements of Section lV.D.3 of Appendix E to 10 CFR 50 was identified on June 13, 2012, because NextEra did not notify the state of Massachusetts within 15 minutes of declaring an emergency at the Seab
Region: I | Seabrook | 10658 | 09/30/2012 11/14/2012 | 2012004-03 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Calibration of Respirator Fit Test Equipment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000443 Seabrook 1 |  | 71124.03 | Inspectors identified an NCV of Technical Specification (TS) 6.7.1.a, "Procedures and Programs," which requires that written procedures be established and implemented, to include administrative procedures, which includes radiation protection procedures. S
Region: I | Seabrook | 10673 | 05/07/2012 06/15/2012 | 2012007-01 | NRC | NCVIV | Barrier Integrity | Green | Inadequate 10 CFR 50.59 Evaluation |  |  | TE?: Y SL-IV-NCVIV | 05000443 Seabrook 1 |  | 71111.17T | The team identified a Severity Level IV non-cited violation of 10 CFR 50.59 in that NextEra made changes to an analysis listed in the Technical Specifications (TS) without obtaining a license amendment. The team found that prior to replacing incore probe
Region: I | Seabrook | 10651 | 01/20/2012 03/26/2012 | 2011010-02 | NRC | FIN | Mitigating Systems | Green | lnadequate Operability Determination for Degraded Concrete Structures Housing Safety-Related Equipment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | NONE | The inspectors identified a finding in that NextEra failed to fully evaluate potential structural and seismic response impacts in accordance with the requirements in NextEra procedure EN-AA-1001 after identifying a degraded and nonconforming condition rel
Region: I | Seabrook | 10641 | 12/31/2011 02/14/2012 | 2011005-01 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip Caused by Inadequate Condensate Pump Restoration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000443 Seabrook 1 |  | 71153 | A self-revealing finding was identified regarding the improper maintenance restoration of a condensate pump resulted in a reactor trip. NextEra workers aligned the B condensate pump for service following maintenance without first venting air from the pump
Region: I | Seabrook | 10639 | 09/30/2011 11/04/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Functionality Assessment for Fire Protection System | EA Case: 2011004 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.7.1.a that requires written procedures be established and implemented, including administrative procedures that define authorities and responsibilities for safe oper
Region: I | Seabrook | 10633 | 06/30/2011 08/12/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Combustible Materials |  | H.4(b) Procedural Compliance | TE?: N | 05000443 Seabrook 1 |  | 71111.05A | Green. The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.7.1.h, which requires that written procedures be established, implemented and maintained for the fire protection program. Contrary to TS 6.7.1.f, the inspectors
Region: I | Seabrook | 10636 | 06/30/2011 08/12/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Untimely Operability Determination for Degraded Concrete Structures Housing Safety-Related Equipment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.7.1.a, that requires written procedures be established, implemented and maintained, including administrative procedures that define authorities and responsibilities fo
Region: I | Seabrook | 10638 | 06/30/2011 08/12/2011 | 2011003-05 | NRC | NCV | Mitigating Systems | Green | Indequate Operability Determination for Reduced EDG HX Cooling Water Flow |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.7.1.a, which requires that written procedures be established, implemented and maintained, including administrative procedures that define authorities and responsibilit
Region: I | Seabrook | 10631 | 03/31/2011 05/12/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Condition of Control Building per 10CFR50.65(a)(1) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | 71111.12 | Inspectors identified a non-cited violation of 10 CFR 50.65(a)(1) because NextEra did not adequately monitor the condition of an in-scope structure under the Maintenance Rule (MR). Specifically, NextEra did not evaluate the results of their periodic inspe
Region: I | Seabrook | 10632 | 03/31/2011 05/12/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Classify and Monitor the Ocean Transition Structures as In-Scope per 10CFR50.65(b)(2) |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.12 | Inspectors identified a non-cited violation of 10 CFR 50.65(b)(2) because NextEra did not include certain Seabrook buildings as in-scope structures under the MR program. Specifically, NextEra did not classify the intake transition structure (ITS) and the
Region: I | Seabrook | 10626 | 05/20/2010 07/02/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Test ECCS (RHR-SI) Valve Interlocks |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | Green. The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," in that, NextEra did not assure that all testing required to demonstrate that structures, systems,
Region: I | Seabrook | 10627 | 05/20/2010 07/02/2010 | 2010006-02 | NRC | FIN | Mitigating Systems | Green | Failure to Take Timely Corrective Action for Battery Sizing Calculations for SBO Loads |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance for NextEra's failure to take effective or timely corrective actions regarding the battery sizing calculation for safety related battery loading under station blackout (SBO) conditions. Specifi
Region: I | Seabrook | 10625 | 04/15/2010 08/13/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate instructions to install test equipment caused the A EDG to be inoperable |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000443 Seabrook 1 |  | 71111.18 | A self-revealing non-cited violation of Technical Specification 6.7.1, Procedures and Programs, was identified related to the failure of the A EDG during a maintenance run per EC145293 on April 15, 2010. Specifically, NextEra did not provide adequate work
Region: I | Seabrook | 10618 | 09/30/2009 11/12/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to verify that ultimate heat sink isolation valves do not leak in excess of design basis assumptions. (Section 1R07) |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.07T | The NRC identified a non-cited violation of 10 CFR 50 Appendix-B Criteria III, Design Control, for the failure to verify that service water (SW) isolation valve leakage was within design assumptions for ultimate heat sink (UHS) water inventory. Specifical
Region: I | Seabrook | 10609 | 06/30/2008 08/04/2008 | 2008003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Tagging Procedure Caused Inadvertant Drain of 200 Gallons From RCS |  | H.3(b) Work Activity Coordination | TE?: N | 05000443 Seabrook 1 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 6.7.1.a was identified for the failure to implement written procedures governing safety-related activities. Specifically, on April 20, 2008, FPLE failed to implement tagging and configuration
Region: I | Seabrook | 10610 | 06/30/2008 08/04/2008 | 2008003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Corrective Actions to Prevent Recurrance of Mispositioned Stow-Operated Valves Caused Inadvertant Drain of 2000 Gallons From RCS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000443 Seabrook 1 |  | 71111.2 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because FPLE did not implement corrective actions to prevent recurrence of mispositioned valves caused by difficult to operate stow-operator
Region: I | Seabrook | 10611 | 06/30/2008 08/04/2008 | 2008003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control a High Radiation Area as a Locked High Radiation Area. |  | H.3(a) Work Planning | TE?: N | 05000443 Seabrook 1 |  | 7112101 | A self-revealing non cited violation of Technical Specification 6.11.2 was identified. Specifically, on May 1, 2008, FPLE failed to identify and control an existing high radiation area with dose rates greater than 1000 millirems per hour in the reactor co
Region: I | Seabrook | 10605 | 12/31/2007 02/12/2008 | 2007005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Enclosure Building Air Handling Fan Failed Due to Failure to Implement Procedure to Torque Cable Connections |  | H.4(b) Procedural Compliance | TE?: N | 05000443 Seabrook 1 |  | 71111.13 | A self-revealing, non-cited violation of Technical Specifications 6.7.1.a was identified for a failure to implement written procedures governing safety-related activities. Specifically, the requirement of maintenance procedure LX0557.04 to torque breaker
Region: I | Seabrook | 10606 | 12/31/2007 02/12/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of the Low Strength Bolts in the Residual Heat Removal System |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10CFR50, Appendix B, Criterion XVI associated with FPL's failure to identify a condition adverse to quality related to bolts in the safety-related residual heat removal (RHR) system. FPL had previously re
Region: I | Seabrook | 10603 | 04/27/2007 06/08/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate RWST level uncertainty analysis |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10CFR50, Appendix B, Criteria III, Design Control. Specifically, the instrument uncertainty calculation for the refueling water storage tank (RWST) level inst
Region: I | Seabrook | 10604 | 04/27/2007 06/08/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative TDEFWP steam admission valve stroke time test acceptance criteria |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, Test Control. The team determined that FPL did not ensure that the turbine driven emergency feedwater pump (TDEFWP) steam
Region: I | Seabrook | 10602 | 03/31/2007 04/10/2007 | 2007002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Evaluation of a Deficiency with the Alternate Cooling Water System to the Charging Pumps |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | 71152 | The inspectors identified a finding for Seabrook failing to adequately evaluate and take corrective actions to ensure the ability of alternate water sources to provide cooling to the charging pump lube oil coolers. Seabrook did not perform confirmatory te
Region: I | Seabrook | 10601 | 01/11/2007 02/16/2007 | 2006016-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective actions Result in a Repeat Failure of the "B" EDG |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000443 Seabrook 1 |  | NONE | The inspectors identified a Green non-cited violation (NCV) for the licensee's failure to comply with 10 CFR 50, Appendix B, Criteria XVI, Corrective Action. The analyses of previous "B" emergency diesel generator (EDG) voltage regulator failures were ina
Region: I | Seabrook | 10596 | 12/31/2006 01/18/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Controls of a Heavy Load Lift over the Reactor Vessel |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000443 Seabrook 1 |  | 71111.2 | The inspectors identified a non-cited violation of Technical Specification 6.7.1.a, "Procedures and Programs." On October 11, 2006, Seabrook failed to adequately establish and implement procedural controls for a heavy load lift, which resulted in a reacto
Region: I | Seabrook | 10597 | 12/31/2006 01/18/2007 | 2006005-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Compliance Results in Inadvertent Dilution during Shutdown |  | H.4(b) Procedural Compliance | TE?: N | 05000443 Seabrook 1 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 6.7.1.a, "Procedures and Programs" was identified by the inspectors. On October 25, 2006, during a cold shutdown, operators inadvertently performed a 500-gallon dilution instead of a planned
Region: I | Seabrook | 10599 | 12/07/2006 01/17/2007 | 2006006-01 | NRC | NCV | Initiating Events | Green | 10 CFR 50, Appendix B, "Corrective Actions," Failure to Promptly Identify Incorrect Analysis Assumptions Used for an Inadvertent ECCS Initiation at-power Event 10 CFR 50, Appendix B, "Corrective |  |  | TE?: N | 05000443 Seabrook 1 |  | 71152B | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," in that FPL failed to promptly identify a condition adverse to quality associated with incorrect design assumptions used for the licensing basis in the station's
Region: I | Seabrook | 10595 | 09/30/2006 10/26/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inoperable Main Steam isolation Valve for Greater than Technical Specification Allowed Outage Time |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | A Green self-revealing non-cited violation of Technical Specification (TS) 3.7.1.5, "Main Steam Line Isolation Valves" was identified by the inspectors. On June 30, 2006, operators received a control room alarm associated with a main steam isolation valve
Region: I | Seabrook | 10585 | 06/30/2006 07/26/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Degraded Floor Drains |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.06 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" in that Seabrook did not promptly identify and correct degraded cable spreading room floor hydrostatic barriers. Seabrook identified the degraded
Region: I | Seabrook | 10586 | 06/30/2006 07/26/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Untimely Identification and Evaluation of Degraded Hydrostatic Barriers |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.06 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" in that Seabrook did not take timely corrective actions for clogged drains that support safety-related systems. In 2006, Seabrook completed an ins
Region: I | Seabrook | 10592 | 06/30/2006 07/26/2006 | 2006003-03 | NRC | NCV | Initiating Events | Green | Failure to Comply with TS 3.8.2.1 when a Battery Charger was not Supplying the "B" Bus |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111114 | The inspectors identified a non-cited violation of Technical Specification (TS) 3.8.2.1, "DC (Direct Current) Sources - Operating." On June 21, 2006, the battery charger supply breaker was incorrectly opened due to a maintenance technician error. This rem
Region: I | Seabrook | 10581 | 03/31/2006 05/09/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate 10 CFR 50.59 Safety Evaluation Screen |  |  | TE?: N | 05000443 Seabrook 1 |  | 7111102 | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59; "Changes, Tests, and Experiments." Specifically, Seabrook adversely changed the bases of Technical Specification (TS) 3.4.10, "Structural Integrity," to make it applicable
Region: I | Seabrook | 10583 | 03/31/2006 05/09/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degraded Component Cooling Water Flow to Safety-Related Components |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action." In January 2006, the inspectors identified degraded component cooling water flow to the residual heat removal pump seal cooler and the enclosure
Region: I | Seabrook | 10584 | 03/31/2006 05/09/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Result in a Repeat Failure of the "B" EDG |  |  | TE?: N | 05000443 Seabrook 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action." In December of 2005, Seabrook experienced a failure of the "B" emergency diesel generator (EDG) due to a voltage excursion. Corrective actions co
Region: I | Susquehanna | 126356 | 12/31/2019 02/13/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Untimely Identification and Correction of Breaker Stab Misalignment Results In Subsequent Safety Bus Fault |  | H.14 - Conservative Bias | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 | Equipment Performance | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action." Specifically, Susquehanna failed to identify and correct a condition adverse to quality, associated with misalignment of Class 1E breaker 0B136-044 to
Region: I | Susquehanna | 126412 | 12/31/2019 02/13/2020 | 2019004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate procedural adherence for 'C' Emergency Service Water (ESW) pump flow surveillance |  | H.12 - Avoid Complacency | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 | Equipment Performance | 71153 | The inspectors documented a self-revealing Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to accomplish an activity affecting quality in
Region: I | Susquehanna | 124650 | 03/31/2019 05/13/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Engagement of the Reactor Core Isolation Cooling (RCIC) Turbine Trip Latch |  | P.5 - Operating Experience | TE?: N | 05000388 Susquehanna 2 | Procedure Quality | 71111.04Q | The inspectors identified a Green Non-Cited Violation (NCV) of 10CFR50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the procedures used to reset the RCIC turbine following surveillance testing did not include sufficient accepta
Region: I | Susquehanna | 124495 | 03/31/2019 05/13/2019 | 2019001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Swing Bus Automatic Transfer Switch Fauilure due to Improper Maintenance Activities |  | P.2 - Evaluation | TE?: N | 05000387 Susquehanna 1 | Procedure Quality | 71111.12 | A finding of very low safety significance (Green) and an associated NCV of 10CFR50 Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” were self-revealed when the safety-related automatic transfer switch (ATS) associated with the division 2
Region: I | Susquehanna | 25930 | 12/31/2018 02/13/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Standby Liquid Control Pump Failed to Achieve Design Flow |  | H.2 - Field Presence | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” were self-revealed when the licensee failed to promptly identify and correct a condition adverse to quality associated wit
Region: I | Susquehanna | 25931 | 12/31/2018 02/13/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Design Control Inadequacy with LPCI/CS Pressure Indicating Switches |  | H.13 - Consistent Process | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | A finding of very low safety significance (Green), an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” and resultant violations of Technical Specification (TS) 3.3.5.1 and 3.5.1 were self-revealed when Susquehanna did not
Region: I | Susquehanna | 1 | 12/31/2018 02/13/2019 | 2018004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Work Instructions Insufficient to Maintain Control Room Envelope In-Leakage Within Specification |  | NPP | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 | SSC and Barrier Performance | 71152 | The inspectors documented a self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for work instructions that were not sufficient to ensure the ‘A’ CREOASS filter train door gaskets were replaced in
Region: I | Susquehanna | 24095 | 06/30/2018 08/09/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Control Structure Chiller Inoperability Due to Identified Refrigerant Leaks Not Corrected |  | H.5 - Work Management | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | A Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was self-revealed when the licensee failed to promptly correct a condition adverse to quality associated with the ‘B’ control structure chiller, which re
Region: I | Susquehanna | 24055 | 06/30/2018 08/09/2018 | 2018002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Inadequate Procedure Adherence |  | H.8 - Procedure Adherence | TE?: N | 05000387 Susquehanna 1 |  | 71124.01 | A Green finding and associated NCV of TS 5.7, “High Radiation Area,” was self-revealed when two plant workers entered a posted high radiation area and one worker’s electronic dosimeter alarmed on dose rate. The workers had not been briefed for entry into
Region: I | Susquehanna | 24096 | 06/30/2018 08/09/2018 | 2018002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Justification for Deferral of Corrective Actions |  | P.3 - Resolution | TE?: N | 05000387 Susquehanna 1 |  | 71152 | The inspectors identified a Green finding and associated NCV of TS 5.4.1, “Procedures,” when the licensee failed to promptly correct numerous operable but nonconforming or degraded safety-related components. Not promptly performing corrective actions
Region: I | Susquehanna | 24389 | 06/29/2018 08/27/2018 | 2018011-01 | NRC | NCV | Barrier Integrity | Green | Failure to conduct proper testing of 125 VDC molded case circuit breakers to |  | P.5 - Operating Experience | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control.” Specifically, Susquehanna had not established a program to adequately exercise and test safety-related 125VDC MCCB since initial plant operation. Susqueha
Region: I | Susquehanna | 21654 | 09/30/2017 11/07/2017 | 2017003-01 | NRC | NCV | Barrier Integrity | Green | RBCCW PCIV Design Control Issue |  | H.7 - Documentation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green), an associated NCV of 10CFR50 Appendix B, Criterion III, “Design Control,” and a resultant violation of technical specification (TS) 3.6.1.3, Primary Containment Isolation Valves
Region: I | Susquehanna | 21655 | 09/30/2017 11/07/2017 | 2017003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Prepare Work Packages with Necessary Detail Results in Automatic Reactor Scram |  | H.12 - Avoid Complacency | TE?: N | 05000387 Susquehanna 1 |  | 71153 | The inspectors identified a self-revealing finding of very low safety significance (Green) associated with Susquehanna’s failure to ensure a work package was prepared to the detail necessary based on task difficulty as required by NDAP-QA-0502, “Work Orde
Region: I | Susquehanna | 22686 | 06/30/2017 07/31/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Fire Brigade Performance during an Unannounced Drill |  | P.6 - Self-Assessment | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.05A | The inspectors identified a Green NCV of Susquehanna Unit 1 and 2 Operating License Condition 2.C.6, Fire Protection, because Susquehanna did not adequately assess an unannounced fire brigade drill, as required by the fire protection program. Susqueha
Region: I | Susquehanna | 33260 | 06/30/2017 07/31/2017 | 2017002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk Associated with Emergent Work |  | H.13 Consistent Process | TE?: N | 05000387 Susquehanna 1 |  | 71111.13 | The inspectors identified a Green, self-revealing, NCV of 10 Code of Federal Regulations (CFR) 50.65 (a)(4) because Susquehanna failed to assess and manage the increase in risk for emergent work on the Unit 1 'A' 125 voltage direct current (VDC) battery c
Region: I | Susquehanna | 33259 | 03/31/2017 05/09/2017 | 2017001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Human Performance Error Results in Loss of Secondary Containment Safety Function |  | H.4 Teamwork | TE?: N | 05000387 Susquehanna 1 |  | 71153 | A self-revealing finding of very low safety significance (Green) and associated NCV of TS 5.4.1, "Procedures," was identified for failure to implement procedures that resulted in a secondary containment fan trip and associated loss of safety function. Sus
Region: I | Susquehanna | 33250 | 12/31/2016 02/10/2017 | 2016004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure Rates Exceed (20%) Twenty Percent for Biennial Requalification Exam |  | H.9 Training | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.11A | A self-revealing finding was identified associated with inadequate licensed operator performance during the annual licensed operator requalification operating test and biennial written examination. Specifically, 17 of 71 operators (23.9%) failed at least
Region: I | Susquehanna | 33251 | 12/31/2016 02/10/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality with LPCI Swing Bus Automatic Transfer Switches |  | P.2 Evaluation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | A finding of very low safety significance (Green) and associated NCV of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, "Corrective Action," was self-revealed when Susquehanna failed to assure that conditions adverse to quality w
Region: I | Susquehanna | 33252 | 12/31/2016 02/10/2017 | 2016004-03 | NRC | NCV | Barrier Integrity | Green | Refuel Floor Radiation Monitor Inoperable Due to being Improperly Calibrated |  | H.12 Avoid Complacency | TE?: N | 05000388 Susquehanna 2 |  | 71111.22 | A finding of very low safety significance (Green) and NCV of TS 5.4.1, "Procedures" was self-revealed when Susquehanna incorrectly calibrated the Unit 1 'B' refuel floor high exhaust duct high radiation monitor on November 15, 2014. This impacted the init
Region: I | Susquehanna | 33258 | 12/31/2016 02/10/2017 | 2016004-04 | NRC | FIN | Initiating Events | Green | Auxiliary Bus Load Shed when a Daisy Chained Neutral was Interrupted during Maintenance |  | H.5 Work Management | TE?: N | 05000387 Susquehanna 1 |  | 71153 | A finding of very low safety significance (Green) for failure to develop an adequate work plan for replacement of a voltage potential indicating light on a breaker on the Unit 2 'B' auxiliary bus was self-revealed when the Unit 2 'B' reactor recirculation
Region: I | Susquehanna | 33248 | 10/21/2016 11/23/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Specify and Maintain Safety-Related Quality Standards and Materials Essential for Reactor Core Isolation Cooling |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111121 | The team identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the failure to classify and maintain reactor core isolation cooling (RCIC) system components as
Region: I | Susquehanna | 33246 | 09/30/2016 11/07/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Breaching Internal Flood Barrier |  | H.5 Work Management | TE?: N | 05000388 Susquehanna 2 |  | 71111.06 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Susquehanna did not ensure that work instructions to breach a flood barrier appropriately incorporated design requirements for i
Region: I | Susquehanna | 33247 | 09/30/2016 11/07/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Risk Management Actions Not Adequately Implemented |  | H.12 Avoid Complacency | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) because Susquehanna did not assess and manage the increase in risk from online maintenance activities. From September 11 to 16, 2016, there were multiple affected areas that the fire protection e
Region: I | Susquehanna | 33242 | 07/22/2016 09/02/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Write a Condition Report for Degraded Conditions Which Challenged Operability of Safety Related Equipment (4OA2.1.c(1)) |  | H.4 Teamwork | TE?: N | 05000387 Susquehanna 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Susquehanna failing to identify and correct conditions adverse to quality in a timely manner. Specifically, between April 16, 2016 and April 22, 2016,
Region: I | Susquehanna | 33243 | 07/22/2016 09/02/2016 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain Quality Procedure Results in Control Room Chiller Inoperability (4OA2.1.c(2)) |  | H.8 Procedure Adherence | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to implement and maintain a quality procedure, MT-GE-021, "Chiller Maintenance and Inspection." This resulted in the safety
Region: I | Susquehanna | 33244 | 07/22/2016 09/02/2016 | 2016008-03 | NRC | FIN | Initiating Events | Green | Failure to Implement or Develop Timely Interim or Final Corrective Actions for a Degraded Condition (4OA2.1.c(3)) |  | P.3 Resolution | TE?: N | 05000388 Susquehanna 2 |  | 71152B | The inspectors documented a self-revealing finding of very low safety significance (Green) against Susquehanna procedures LS-125 Revision 4, "Corrective Action Program (CAP)," and OI-AD-096 Revision 18, "Operator Challenges," for the failure to correct an
Region: I | Susquehanna | 33245 | 07/22/2016 09/02/2016 | 2016008-04 | NRC | NCV | Initiating Events | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality on Vital 480 VAC MCCs (4OA2.1.c(4)) |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors documented a self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify and correct a condition adverse to quality. Specifically, in October and December 2006 and July 2009, Susquehanna di
Region: I | Susquehanna | 33217 | 06/30/2016 08/11/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify a Condition Adverse to Quality Associated with Primary Containment Isolation Valves |  | H.14 Conservative Bias | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | A self-revealing Green finding and associated violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," and TS 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," was identified when Susquehanna did not promptly identify a condition adv
Region: I | Susquehanna | 33221 | 06/30/2016 08/11/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality with 'A' EDG MOC Switch |  | P.2 Evaluation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | A self-revealing finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to correct a condition adverse to quality. Specifically, on March 23, 2016, the 'A' emergency die
Region: I | Susquehanna | 33222 | 06/30/2016 08/11/2016 | 2016002-03 | NRC | NCV | Mitigating Systems | Green | Failure of B EDG to Reach Rated Frequency within 10 Seconds |  | H.13 Consistent Process | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.22 | A self-revealing finding of very low safety significance (Green) and associated NCV of TS 5.4.1.a, "Procedures," was identified when Susquehanna failed to implement procedures for loading EDGs promptly following extended unloaded operation. Specifically,
Region: I | Susquehanna | 33233 | 06/30/2016 08/11/2016 | 2016002-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique an Incorrect PAR Notification |  | P.1 Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71114.06 | An NRC-identified finding of very low safety significance (Green) and associated NCV of 10 CFR 50.54(q)(2),"Emergency Plans" was identified when Susquehanna failed to identify that an incorrect notification of wind direction was made to the senior state o
Region: I | Susquehanna | 33234 | 06/30/2016 08/11/2016 | 2016002-05 | NRC | NCV | Occupational Radiation Safety | Green | Entry into a High Radiation Area without Radiological Briefing |  | P.3 Resolution | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71124.01 | A Green self-revealing NCV of TS 5.7.1, High Radiation Area Controls, was identified when a worker did not comply with a radiological posting barrier and other access control requirements for high radiation area (HRA) entry. Specifically, on December 26,
Region: I | Susquehanna | 33235 | 06/30/2016 08/11/2016 | 2016002-06 | NRC | NCV | Occupational Radiation Safety | Green | Entry into a Locked High Radiation Area without Radiological Briefing |  | H.4 Teamwork | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71124.01 | A Green self-revealing NCV of TS 5.7.2, High Radiation Area Controls, was identified when workers entered the wrong reactor unit condenser bay (Unit 2) that was posted and controlled as a locked high radiation area (LHRA). Specifically, on May 3, 2016, fo
Region: I | Susquehanna | 33239 | 06/30/2016 08/11/2016 | 2016002-07 | NRC | NCV | Mitigating Systems | Green | HPCI Overridden Prior to Manual Reactor Scram |  | H.8 Procedure Adherence | TE?: N | 05000388 Susquehanna 2 |  | 71153 | An NRC-identified finding of very low safety significance (Green) and associated NCV of TS 5.4.1.a, "Procedures," was identified when Susquehanna failed to implement procedures for controlling the high pressure coolant injection (HPCI) system. Specificall
Region: I | Susquehanna | 33210 | 03/31/2016 05/12/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk of Maintenance Activities for a SLC System Flow Surveillance |  | H.5 Work Management | TE?: N | 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) because Susquehanna did not adequately assess the risk of performing maintenance in accordance with station procedures. Specifically, Susquehanna did not assess the risk of performing a standby l
Region: I | Susquehanna | 33211 | 03/31/2016 05/12/2016 | 2016001-02 | NRC | NCV | MISC | Green | Failure to Report Loss of Safety Function as Required by 10 CFR 50.73(a)(2)(v) |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71152 | Inspectors identified a Severity Level IV NCV of 10 CFR Part 50.73 (a)(2)(v) when Susquehanna did not submit a licensee event report (LER) within 60 days of identifying that both trains of the control room emergency outside air supply system (CREOASS) wer
Region: I | Susquehanna | 33216 | 03/31/2016 05/12/2016 | 2016001-03 | NRC | NCV | Initiating Events | Green | Failure to Correct Fatigue Related Cracking of the 'B' RRP Lower Seal Cavity Vent Line |  | H.5 Work Management | TE?: N | 05000387 Susquehanna 1 |  | 71153 | A self-revealing finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for Susquehanna's failure to establish measures to assure a condition adverse to quality
Region: I | Susquehanna | 33206 | 12/31/2015 02/09/2016 | 2015004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correct a Condition Adverse to Quality Associated with an Inoperable Primary Containment Isolation Valve |  | H.11 Challenge the Unknown | TE?: N | 05000388 Susquehanna 2 |  | 71111.12 | Green. A self-revealing finding of very low safety significance (Green) and associated violations of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," and Technical Specification (TS) 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," was i
Region: I | Susquehanna | 33207 | 12/31/2015 02/09/2016 | 2015004-02 | NRC | NCV | Barrier Integrity | Green | Loss of Safety Function of SBGT and CREOASS due to Concurrently Performing Maintenance on Redundant Trains |  | H.12 Avoid Complacency | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | Green. An NRC-identified finding of very low safety significance (Green) and associated violations of TS 5.4.1, "Procedures," TS 5.5.11, "Safety Function Determination," and TS 3.7.3, "Control Room Emergency Outside Air Supply System" was identified when
Region: I | Susquehanna | 33208 | 12/31/2015 02/09/2016 | 2015004-03 | NRC | NCV | Emergency Preparedness | Green | Dose Assessment Capabilities in the Technical Support Center |  | H.7 Documentation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | Green. The inspectors identified a finding of very low safety significance (Green) and a NCV of 10 CFR 50, Appendix E, Section IV.B.1. Specifically, Susquehanna emergency plan implementing procedures did not provide the guidance for the dose assessment st
Region: I | Susquehanna | 33209 | 12/31/2015 02/09/2016 | 2015004-04 | Self - Revealed | FIN | Initiating Events | Green | Inadvertent Closure of the 'B' Inboard MSIV |  | H.11 Challenge the Unknown | TE?: N | 05000387 Susquehanna 1 |  | 71153 | Green. A self-revealing finding of very low safety significance (Green) was identified when Susquehanna did not correctly validate a deficient condition associated with the Unit 1 'B' inboard main steam isolation valve (MSIV) direct current (DC) solenoid
Region: I | Susquehanna | 32312 | 09/30/2015 11/05/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | RHR Shutdown Cooling Procedure Not Mainted Consistent with Technical Specification Requirements |  | H.3 Change Management | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.18 | Inspectors identified a finding of very low safety significance (Green) and associated NCV of SSES Unit 1 and 2 TS 5.4.1, "Procedures," because Susquehanna did not maintain the procedure for operation of the residual heat removal (RHR) shutdown cooling (S
Region: I | Susquehanna | 32313 | 09/30/2015 11/05/2015 | 2015003-02 | Self - Revealed | NCV | Mitigating Systems | Green | 'C' EDG Rendered Inoperable by Switch Manipulation during Training Simulation |  | H.12 Avoid Complacency | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | A self-revealing finding of very low safety significance (Green) and associated NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified when Susquehanna inadvertently operated the 'C' emergency diesel generator (E
Region: I | Susquehanna | 33197 | 09/30/2015 11/05/2015 | 2015003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Secondary Containment Inoperability due to Improperly Controlled Access to the Reactor Building Roof |  | H.4 Teamwork | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71151 | A self-revealing finding of very low safety significance (Green) and associated NCV of SSES Unit 1 and 2 TS 5.4.1, "Procedures," was identified because Susquehanna incorrectly implemented procedures for maintaining secondary containment integrity. Specifi
Region: I | Susquehanna | 32296 | 06/30/2015 08/10/2015 | 2015002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Assess a Non-Conforming Condition for its Impact on Component Operability |  | H.12 Avoid Complacency | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Susquehanna staff did not assess component operability following identific
Region: I | Susquehanna | 32300 | 06/30/2015 08/10/2015 | 2015002-02 | NRC | NCV | Occupational Radiation Safety | Green | Entry into a High Radiation Area without Radiological Briefing |  | H.11 Challenge the Unknown | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71124.01 | A self-revealing finding of very low safety significance (Green) and associated NCV of SSES Unit 2 TS 5.7.1 was identified because Susquehanna did not comply with a radiological posting barrier and other protective measures for HRA entry. Specifically, on
Region: I | Susquehanna | 32301 | 06/30/2015 08/10/2015 | 2015002-03 | NRC | NCV | Barrier Integrity | Green | Incorrect Implementation of the Ventilation Filter Testing Program |  | H.7 Documentation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because Susquehanna did not ensure representative samples were obtained from Engineered Safety Feature (
Region: I | Susquehanna | 32305 | 06/30/2015 08/10/2015 | 2015002-04 | NRC | NCV | Initiating Events | Green | Multiple Violations of Work Hour Limitations by Licensed Operators |  | P.1 Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 26.205, "Work Hours," because Susquehanna did not ensure that the working hours of licensed operators were maintained within regulatory limits. Specif
Region: I | Susquehanna | 32306 | 06/30/2015 08/10/2015 | 2015002-05 | NRC | NCV | Initiating Events | Green | Loss of Main Condenser Vacuum When Transitioning Steam Seals to Auxiliary Steam |  | H.12 Avoid Complacency | TE?: N | 05000388 Susquehanna 2 |  | 71153 | A self-revealing finding of very low safety significance (Green) and associated NCV of SSES Unit 2 TS 5.4.1, "Procedures," was identified because Susquehanna incorrectly implemented procedures for operation of the auxiliary steam and main turbine steam se
Region: I | Susquehanna | 32283 | 03/31/2015 05/14/2015 | 2015001-01 | NRC | NCV | Initiating Events | Green | Control of Transient Combustible Materials |  | H.5 Work Management | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.05Q | The inspectors identified a Green NCV of the PPL Unit 1 and Unit 2 Facility Operating License Condition 2.C.(6), "Fire Protection Program" (FPP), for PPL not adequately controlling the storage of transient combustibles in accordance with their fire protec
Region: I | Susquehanna | 32288 | 03/31/2015 05/14/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality on the 'B' EDG |  | P.2 Evaluation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to correct a condition adverse to quality. Specifically, despite identifying a conditi
Region: I | Susquehanna | 32289 | 03/31/2015 05/14/2015 | 2015001-03 | NRC | FIN | Mitigating Systems | Green | SBO Diesel Fuel Oil Cloud Point |  | P.2 Evaluation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) for not establishing diesel fuel oil specifications to ensure diesel-driven equipment important to safety will function during expected low ambient temperatures. Specifically, PPL
Region: I | Susquehanna | 32294 | 03/31/2015 05/14/2015 | 2015001-04 | Self - Revealed | NCV | Barrier Integrity | Green | Human Performance Errors Result in Losses of Safety Function |  | H.12 Avoid Complacency | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | A self-revealing finding of very low safety significant (Green) and associated NCV of TS 5.4.1, "Procedures," was identified for three separate examples of failing to implement work instructions or procedures that resulted in equipment inoperability and a
Region: I | Susquehanna | 32268 | 12/31/2014 02/12/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Risk Management Actions Not Implemented |  | H.5 Work Management | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a Green NCV of Title 10 Code of Federal Regulations (CFR) 50.65(a)(4) due to multiple examples of not assessing and managing the increase in risk from online maintenance activities. Specifically, on November 12, 2014, a risk asse
Region: I | Susquehanna | 32275 | 12/31/2014 02/12/2015 | 2014005-02 | NRC | NCV | Emergency Preparedness | Green | Emergency Preparedness Drill Critique Did Not Identify a Risk-Significant Planning Standard Weakness |  | H.13 Consistent Process | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71114.06 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.54(q)(2) for failing to follow and maintain an emergency plan that meets the requirements of appendix E and the planning standards of 10 CFR 50.47(b). Specifically, PPL did not ident
Region: I | Susquehanna | 32269 | 12/31/2014 02/12/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | EPA Breaker Underfrequency Setpoint Drift |  | P.2 Evaluation | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for PPL not establishing design control measures that provide for verifying or checking the adequacy of design and translating the design basis requirements i
Region: I | Susquehanna | 32277 | 09/30/2014 11/14/2014 | 2014004-01 | NRC | FIN | Initiating Events | Green | RRP Trip due to Incorrect Calibration of MG Set High Temperature Trip Setpoint |  | H.2 Field Presence | TE?: N | 05000387 Susquehanna 1 |  | 71153 | A finding of very low safety significance (Green) for inadequately implementing work instructions for the installation and calibration of the reactor recirculation pump (RRP) motor-generator (MG) set motor winding cooling air outlet temperature switch was
Region: I | Susquehanna | 32267 | 07/31/2014 09/12/2014 | 2014008-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequately Maintained Procedures for Plant Shutdown to Hot Standby led to Reactor Water Level and Power Transients. | EA Case: 2011221 | H.3 Change Management | TE?: N | 05000388 Susquehanna 2 |  | 95002 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified because PPL did not adequately maintain operating procedures for plant shutdown to hot standby. Specifically, the general operating procedure for plant shutdown
Region: I | Susquehanna | 32248 | 06/30/2014 08/13/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Conditions Adverse to Quality due to Untimely Actions to Address Extent of Condition |  | P.3 Resolution | TE?: N | 05000388 Susquehanna 2 |  | 71111.15 | An NRC-identified Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for PPL's failure to identify conditions adverse to quality by not implementing timely actions to a
Region: I | Susquehanna | 32257 | 06/21/2014 08/01/2014 | 2014009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely and Appropriate Corrective Actions to Address Carbon Steel Pipe Wall Thinning in the RHRSW and ESW Systems |  | H.13 Consistent Process | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for PPL's failure to take adequate corrective actions for a condition adverse to quality involving the emergency service water (
Region: I | Susquehanna | 32258 | 06/21/2014 08/01/2014 | 2014009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Timely Initial Operability Determinations |  | H.3 Change Management | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for PPL's failure to complete and document initial operability determinations in a timely manner in accordance with station procedures.
Region: I | Susquehanna | 32262 | 06/21/2014 08/01/2014 | 2014009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Condition Adverse to Qaulity Related to Fatigue Stress in ESW Supply Lines to RHR Pump Motor Oil Cooler |  | H.14 Conservative Bias | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," because PPL did not take measures to promptly correct an identified condition adverse to quality associated with the Emergency Service Water (ESW) su
Region: I | Susquehanna | 32263 | 06/21/2014 08/01/2014 | 2014009-04 | NRC | VIO | Emergency Preparedness | Green | Failure to take Action to Restore Degraded Emergency Actio nLevel Scheme |  | P.3 Resolution | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green cited violation of 10 CFR 50.54(q)(2) for PPL's failure to follow and maintain an emergency plan that meets the requirements of the planning standards in 10 CFR 50.47(b), in that, since October 2003, PPL did not follow an
Region: I | Susquehanna | 32247 | 03/31/2014 05/06/2014 | 2014002-02 | NRC | FIN | Initiating Events | Green | Reactor Scram due to Loss of Reactor Feed Pumps |  | H.5 Work Management | TE?: N | 05000388 Susquehanna 2 |  | 71153 | A finding of very low safety significance (Green) for failure to implement work instructions for an engineering change to the Integrated Control System (ICS) was self revealed when Unit 2 lost control of reactor vessel level on September 14, 2013, requiri
Region: I | Susquehanna | 32233 | 12/31/2013 02/14/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance for Responding to an Internal Flooding Event in ECCS Rooms |  | P.3(a) Self-Assessment | TE?: N | 05000387 Susquehanna 1 |  | 71111.06 | The inspectors identified a Green NCV of Technical Specifications (TS) 5.4.1, "Procedures," because PPL's procedures EO-000-104, "Secondary Containment Control" and ON-169-002, "Flooding in the Reactor Building" were inadequate in that actions directed in
Region: I | Susquehanna | 32239 | 12/31/2013 02/14/2014 | 2013005-03 | NRC | NCV | Barrier Integrity | Green | Missed Technical Specification Surveillance for Secondary Containment Drawdown Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because PPL did not ensure all testing required to demonstrate that structures, systems, and components will perform satisfactorily in service was identified and
Region: I | Susquehanna | 32240 | 12/31/2013 02/14/2014 | 2013005-04 | NRC | NCV | Emergency Preparedness | Green | Inadequate Instrumentation to Implement EALs for Fission Product Barrier Degradation |  | H.2(d) Facilities & Equipment | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71114.06 | The inspectors identified a Green NCV of 10 CFR 50.54, "Conditions of Licenses," paragraph (q), because PPL did not maintain the Emergency Plan to adequately meet the standards of 50.47(b). Specifically, PPL did not have temperature indication installed i
Region: I | Susquehanna | 32232 | 10/04/2013 11/18/2013 | 2013011-01 | NRC | FIN | Initiating Events | Green | Reactor Scram due to Loss of Integrated Control System |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000388 Susquehanna 2 |  | 71153 | A finding of very low safety significance (Green) for failure to evaluate and incorporate the operating experience PPL received regarding the integrated control system (ICS) was self-revealed when Unit 2 lost control of reactor vessel level on November 9,
Region: I | Susquehanna | 32222 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance for Maintaining RPV Level During Anticipated Transient Without Scram |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.11Q | The inspectors identified a Green NCV of TS 5.4.1, "Procedures," because PPL's emergency operating procedure step for terminating injection sources during a rapid depressurization required for an anticipated transient without scram (ATWS) was inadequate t
Region: I | Susquehanna | 32229 | 09/30/2013 11/14/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk of Maintenance Activities |  | H.3(a) Work Planning | TE?: N | 05000387 Susquehanna 1 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) because PPL did not adequately assess the risk of performing maintenance in accordance with station procedures. Specifically, PPL did not specify appropriate risk management actions (RMAs) while
Region: I | Susquehanna | 32230 | 09/30/2013 11/14/2013 | 2013004-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate and untimely Actioins to Address a Failed Instrument Necessary for Diagnosis of Emergency Conditions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 |  | 71152 | The inspectors identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR 50.54(q) for failing to follow and maintain an emergency plan that meets the requirements of emergency planning standard 10 CFR 50.47(b)(4). Speci
Region: I | Susquehanna | 32231 | 09/30/2013 11/14/2013 | 2013004-04 | NRC | NCV | Barrier Integrity | Green | Procedure Failed to Verify Design Requirements for RHR Suction Piping |  | P.2(b) Implementing Operating Experience | TE?: N | 05000388 Susquehanna 2 |  | 71153 | The inspectors identified a green, self-revealing, non-cited NCV of 10 CFR 50 Appendix B, Criterion 5, "Instructions, Procedures, and Drawings," which states, in part, that procedures shall include appropriate quantitative or qualitative acceptance criter
Region: I | Susquehanna | 32215 | 08/29/2013 10/01/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Operation of Safety-Related 125Vdc Molded Case Circuit Breakers |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that PPL failed to verify or check the adequacy of the design of molded case circuit
Region: I | Susquehanna | 32210 | 06/30/2013 08/14/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Assessment of Synchroscope Switch |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | Inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when PPL performed an inadequate operability determination for a synchroscope switch failure that rendered offsite power and the four emerge
Region: I | Susquehanna | 32211 | 06/30/2013 08/14/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of RPS and EOC-RPT Time Response Test |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000388 Susquehanna 2 |  | 71111.15 | Inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," because PPL staff performed unacceptable preconditioning by performing corrective maintenance prior to recording the as-found time response of the reactor protection
Region: I | Susquehanna | 32213 | 06/30/2013 08/14/2013 | 2013003-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure to Control and Monitor Reactor Coolant System Heatup Rate |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000388 Susquehanna 2 |  | 71111.22 | Inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PPL did not adequately incorporate the acceptance criteria for heatup rate specified in the plant TSs, as amplified in its basis, in
Region: I | Susquehanna | 32205 | 05/22/2013 06/17/2013 | 2013008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Implement an Effective Licensed Operator Medical Program | EA Case: 2012216 |  | TE?: Y SL-III-VIO | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | (Initial Entry) The inspectors identified: 1) an apparent violation (AV) of Title 10 of the Code of Federal Regulations (10 CFR) 55.21, "Medical Examination;" Part 55.25 "Incapacitation because of disability or illness;" Part 55.33, "Disposition of an In
Region: I | Susquehanna | 32191 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Combustible Storage in Restricted Areas Without Approval |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000388 Susquehanna 2 |  | 71111.05Q | The inspectors identified a Green NCV of Unit 2 Operating License Condition 2.C.(3), regarding its fire protection program, when PPL stored transient combustibles in restricted areas without evaluations by the site fire protection group. PPL procedure NDA
Region: I | Susquehanna | 32196 | 03/31/2013 05/14/2013 | 2013002-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Restoration from Clearance Order Results in Degradation of Main Condenser Vacuum and Plant Downpower |  | H.4(a) Human Error Prevention | TE?: N | 05000388 Susquehanna 2 |  | 71111.13 | A self-revealing NCV of very low safety significance (Green) was identified when PPL incorrectly implemented the clearance order process while returning the common offgas recombiner to service after maintenance. NDAP-QA-0322, "Energy Control Process," Rev
Region: I | Susquehanna | 32198 | 03/31/2013 05/14/2013 | 2013002-04 | NRC | FIN | Initiating Events | Green | Inaccurate USwC PI Data Submital |  | H.1(c) Communication of Decisions | TE?: Y SL-IV-FIN | 05000388 Susquehanna 2 |  | 71151 | The inspectors identified a Green Finding related to implementation of NDAP-QA-0737, "Reactor Oversight Process (ROP) Performance Indicators," Revision 9, and associated severity level (SL) IV NCV of 10 CFR 50.9(a), "Completeness and Accuracy of Informati
Region: I | Susquehanna | 32199 | 03/31/2013 05/14/2013 | 2013002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Control Room Cooling Fan Train Failure |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153 | A self-revealing NCV of 10 CFR 50 Appendix B, Criteria V "Instructions, Procedures, and Drawings," was identified because PPL did not ensure alarm response procedures (ARPs) for control room cooling fan train failures were adequate, which resulted in the
Region: I | Susquehanna | 32184 | 02/01/2013 03/21/2013 | 2013007-01 | NRC | NCV | Initiating Events | Green | Failure to maintain Adequate Feedwater Procedures |  | H.3(a) Work Planning | TE?: N | 05000388 Susquehanna 2 |  | 93812 | Inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, Procedures, related to the requirement to operate the feedwater system in accordance with procedures and implement the procedure change process. The PPL procedures implementing th
Region: I | Susquehanna | 32189 | 02/01/2013 03/21/2013 | 2013007-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish and Implement Written Procedures for Operating Plant Equipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000388 Susquehanna 2 |  | 93812 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified involving the failure to incorporate the results of a Failure Modes and Effects Analysis (FMEA) completed in January 2010 into applicable operating procedures. The FMEA identified a v
Region: I | Susquehanna | 32190 | 02/01/2013 03/21/2013 | 2013007-03 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement the Corrective Action Process |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000388 Susquehanna 2 |  | 93812 | A self-revealing finding (FIN) of very low safety significance (Green) was identified for PPL staff's failure to follow their CAP procedure, NDAP-QA-0702, "Action Request and Condition Report Process," in response to an identified issue with the FW sys
Region: I | Susquehanna | 32180 | 12/31/2012 02/13/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Effective Preventive Maintenance Under 50.65(a)(2) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000388 Susquehanna 2 |  | 71111.12 | Inspectors identified a Green NCV of 10 CFR 50.65(a)(2) for PPL staff not demonstrating that the performance of the Unit 2 125 volt direct-current (VDC) system was being effectively controlled through appropriate preventive maintenance. Specifically, PPL
Region: I | Susquehanna | 32173 | 12/31/2012 02/13/2013 | 2012005-03 | NRC | NCV | Emergency Preparedness | Green | Failure of Full-Scale Drill Critique to Identify an RSPS Weakness |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71114.06 | . Inspectors identified a Green NCV associated with emergency preparedness planning standard 10 CFR 50.47(b)(14) and the requirements of Section lV.F.2.g of 10 CFR 50, Appendix E. Specifically, PPL personnel did not identify an Emergency Response Organi
Region: I | Susquehanna | 32174 | 12/31/2012 02/13/2013 | 2012005-04 | Self - Revealed | NCV | Initiating Events | Green | Improper Stress Intensification Factor Results in Not Identifying ASME Limits for Pipe Stress Being Exceeded |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71152 | A self-revealing Green NCV of 10 CFR 50 Appendix B, Criteria III, "Design Control," was identified related to a leak on the Unit 1 'A' reactor recirculation pump suction line decontamination flange weld. Specifically, PPL personnel used an incorrect value
Region: I | Susquehanna | 32156 | 09/30/2012 11/13/2012 | 2012004-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Acts of Nature |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.01 | The inspectors identified a Green NCV of TS 5.4.1, "Procedures," when PPL did not maintain adequate procedures to respond proactively to acts of nature. Specifically, PPL's adverse weather procedure did not ensure timely risk management activities for i
Region: I | Susquehanna | 32162 | 09/30/2012 11/13/2012 | 2012004-02 | Self - Revealed | FIN | Barrier Integrity | Green | Inadequate Troubleshooting Results in Loss of Secondary Containment and Protected Equipment |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | A self-revealing Green finding against PPL procedure NDAP-QA-0510, "Troubleshooting Plant Equipment," was identified when inadequate troubleshooting caused repeated inoperability of secondary containment, an associated unplanned Unit 2 entry into a 4-hour
Region: I | Susquehanna | 32163 | 09/30/2012 11/13/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions |  | H.3(a) Work Planning | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(4) when PPL did not implement risk management actions (RMAs) during maintenance as required by station procedures. The inspectors identified multiple examples of PPL non-compliance with 10 CFR 50.65
Region: I | Susquehanna | 32164 | 09/10/2012 09/21/2012 | 2012009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Compensatory Actions for Inadequate MOV Grease Analysis Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PPL did not take appropriate action to promptly correct an identified condition adverse to quality associated with PPL's motor-operated valve (MOV) lub
Region: I | Susquehanna | 32167 | 09/10/2012 09/21/2012 | 2012009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a CAQ Associated with a Safety-Related Battery Maintenance Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PPL did not identify and correct the inadequate weekly testing procedure that resulted in the inoperability of the safety-related 24-volt battery 1D670
Region: I | Susquehanna | 32168 | 09/10/2012 09/21/2012 | 2012009-03 | NRC | NCV | Mitigating Systems | Green | Failure to identify and Correct a CAQ Associated with Reactor Recirculation Valve Exercising Surveillance Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," because PPL did not identify an inadequate recirculation valve surveillance procedure when the licensee completed the extent of condition review that was perfo
Region: I | Susquehanna | 31323 | 06/30/2012 08/10/2012 | 2012003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Secondary Containment Bypass Leakage Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for PPL's failure to prevent recurrence of a significant condition adverse to quality (SCAQ) when secondary containment bypass leakage (SCBL) was in e
Region: I | Susquehanna | 31324 | 06/30/2012 08/10/2012 | 2012003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Outboard MSIV LLRT failure Condition Adverse to Quality |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for PPL's failure to correct excessive seat leakage associated with the Unit 1 'D' outboard MSIV, HV141F028D, such that the leakage was in excess
Region: I | Susquehanna | 32155 | 06/30/2012 08/10/2012 | 2012003-04 | Self - Revealed | NCV | Barrier Integrity | Green | Improperly Performed Maintenance Impacts Secondary Containment |  | H.3(b) Work Activity Coordination | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified regarding PPL's conduct of maintenance during a Unit 1 refueling outage which impacted the operating unit, Unit 2. Specifically, improperly performed maintenance on a Unit 1 main stop va
Region: I | Susquehanna | 32148 | 06/30/2012 08/10/2012 | 2012003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to follow radiation protection procedures |  | H.3(a) Work Planning | TE?: N | 05000387 Susquehanna 1 |  | NONE | The inspector identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a, which requires that written procedures be implemented covering the activities in the applicable procedures recommended by Regulatory Guide 1.33, including proced
Region: I | Susquehanna | 31307 | 03/31/2012 05/02/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate MOV Program Implementation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding PPL's safety-related motor operated valve (MOV) program. Specifically, the program lacked a procedure, qualification, and
Region: I | Susquehanna | 31313 | 03/31/2012 05/02/2012 | 2012002-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Instrumentation to Implement EALs for Unplanned Radiological Effluent Release |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71114.06 | The inspectors identified a Green NCV of 10 CFR Part 50.54 q and 50.47(b)(4) because PPL did not have adequate instrumentation to assess and determine if an abnormal radiological effluent release was in progress such that the EAL classification process wo
Region: I | Susquehanna | 32241 | 03/31/2012 05/02/2012 | 2012002-03 | NRC | URI | Emergency Preparedness | Green | Installed Instrumentation Necessary for EAL Declaration |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 |  | 71114.06 | The inspectors identified a Green NCV of 10 CFR Part 50.54 q and 50.47(b)(4) because PPL did not have adequate instrumentation to assess and determine if an abnormal radiological effluent release was in progress such that the EAL classification process wo
Region: I | Susquehanna | 31314 | 03/31/2012 05/02/2012 | 2012002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Noncompliance with Radiological Barrier |  | H.4(a) Human Error Prevention | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | A self-revealing, Green NCV of Technical Specification (TS) 5.7.1 was identified when a worker did not comply with a radiological barrier and protective measures for high radiation area (HRA) entry. Specifically, the worker entered a HRA but was not on th
Region: I | Susquehanna | 31315 | 03/31/2012 05/02/2012 | 2012002-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | The inspectors identified a Green NCV of TS 5.4.1.a, which requires that written procedures be implemented covering the activities in the applicable procedures recommended by Regulatory Guide (RG) 1.33, including procedures for RWPs. On December 5, 2011,
Region: I | Susquehanna | 31322 | 03/21/2012 05/07/2012 | 2012008-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Gain Settings Result in Reactor Scram |  | H.3(a) Work Planning | TE?: N | 05000387 Susquehanna 1 |  | NONE | A self-revealing finding of very low safety significance was identified when Unit 1 automatically scrammed from 32 percent power on April 22, 2010, due to low reactor water level. PPL entered inadequate gain settings in the feedwater digital ICS for react
Region: I | Susquehanna | 31300 | 12/31/2011 02/14/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Work Instructions Results in C EDG Inoperability |  | H.4(a) Human Error Prevention | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | An NRC-identified Green NCV of TS 5.4.1, "Procedures," due to PPL's failure to properly plan and implement work instructions and Quality Control (QC) hold point inspections associated with a modification to the 'C' Emergency Diesel Generator (EDG) fuel pu
Region: I | Susquehanna | 31301 | 12/31/2011 02/14/2012 | 2011005-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Operability Assessment of Suppression Pool Spray |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000388 Susquehanna 2 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when PPL did not perform an adequate operability assessment for a failed suppression pool (SP) spray flow indicator in accordance w
Region: I | Susquehanna | 31305 | 12/31/2011 02/14/2012 | 2011005-03 | NRC | FIN | Initiating Events | Green | Inadequate Post-Modification Testing Results in Main Turbine Trip and Automatic Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000388 Susquehanna 2 |  | 71153 | A self-revealing finding of very low safety significance (Green) was identified when PPL personnel did not have adequate procedures to perform post-modification testing on the digital integrated control system (ICS). Specifically, scheme checks and functi
Region: I | Susquehanna | 31306 | 12/31/2011 02/14/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate RCIC Post Maintenance Testing |  | P.2(b) Implementing Operating Experience | TE?: N | 05000388 Susquehanna 2 |  | 71153 | An NRC-identified, Green NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," occurred when the Unit 2 RCIC ramp generator signal converter (RGSC) failed during maintenance but post maintenance testing (PMT) failed to identify the failure, which we
Region: I | Susquehanna | 32182 | 12/31/2011 02/14/2012 | 2011005-05 | NRC | URI | Mitigating Systems | Green | RCIC Low Reactor Pressure Surveillance Requirement |  | P.2(b) Implementing Operating Experience | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153
Region: I | Susquehanna | 31316 | 12/31/2011 02/14/2012 | 2012002-06 | NRC | URI | Occupational Radiation Safety | Green | Loss of Shield Control During Source Load |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153
Region: I | Susquehanna | 31289 | 11/08/2011 11/08/2011 | 2011004-02 | Self - Revealed | FIN | Barrier Integrity | Green | Inadequate Maintenance Practices Result in Trip of Protected Equipment Spent Fuel Pool Cooling Pump |  | H.4(a) Human Error Prevention | TE?: N | 05000388 Susquehanna 2 |  | 71111.13 | A self-revealing Green finding of NDAP-QA-0340, "Protected Equipment Program," Revision 10, was identified when the 2A fuel pool cooling (FPC) pump tripped during maintenance on the 2A FPC heat exchanger (HX). The pump and HX had been designated as protec
Region: I | Susquehanna | 31290 | 11/08/2011 11/08/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Assessment of Safety Relief Valve Seat Leakage |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000388 Susquehanna 2 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when PPL did not perform an adequate operability assessment in accordance with procedure NDAP-QA-0703, "Operability Assessments and
Region: I | Susquehanna | 31291 | 11/08/2011 11/08/2011 | 2011004-05 | NRC | NCV | Barrier Integrity | Green | Inadequate Surveillance Procedure Results in Missed Technical Specification Surveillance Requirements for Secondary Containment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.22 | An NRC-identified Green NCV of Susquehanna Unit 1 and 2 TS 5.4.1, "Procedures," was identified for an inadequate surveillance procedure for implementing Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.4 and 3.6.4.1.5. Specifically, the
Region: I | Susquehanna | 31274 | 06/30/2011 08/10/2011 | 2011003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Surveillance Procedure Results in Failure to Meet Required Action of Technical Specifications for Secondary Containment Isolation Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.04Q | The inspectors identified a Green NCV of Susquehanna Unit 1 and 2 TS 3.6.4.2, "Secondary Containment Isolation Valves" and TS 5.4.1, "Procedures" for an inadequate surveillance procedure for implementing TS Surveillance Requirements and Action Statements.
Region: I | Susquehanna | 31275 | 06/30/2011 08/10/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions during Dual Unit Elevated Risk |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR 50.65a(4) when PPL failed to manage risk as assessed on June 1, 2011. During a period of dual unit Orange risk, PPL did not adequately implement protected equipment risk management actions (RMAs) designated
Region: I | Susquehanna | 31287 | 06/30/2011 08/10/2011 | 2011003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Design Control Measures Associated with Installation of a Gland Liner in the HPCI Steam Supply Inboard Isolation Valve |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71152 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," occurred when a brass gland liner was installed in the gland for HV155F002, the high pressure coolant injection (HPCI) steam supply inboard isolation valve, without appr
Region: I | Susquehanna | 31267 | 06/24/2011 07/20/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Redundant Fire Water Pumps |  |  | TE?: N | 05000388 Susquehanna 2 |  | 71111.05T | The team identified a non-cited violation of Susquehanna Unit 1 Operating License Condition 2.C.(6), and Unit 2 Operating License Condition 2.C.(3) for the failure to implement all provisions of the approved Fire Protection Program. Specifically, PPL had
Region: I | Susquehanna | 31268 | 06/24/2011 07/20/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Test Acceptance Criteria for Fire Pump Performance Testing |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000388 Susquehanna 2 |  | 71111.05T | The team identified a non-cited violation of Susquehanna Unit 1 Operating License Condition 2.C.(6), and Unit 2 Operating License Condition 2.C.(3) for the failure to implement all provisions of the approved Fire Protection Program. Specifically, PPL esta
Region: I | Susquehanna | 31252 | 03/31/2011 05/13/2011 | 2011002-01 | NRC | FIN | Mitigating Systems | Green | RWST Level Transmitter Failure Not Entered in CAP |  | H.4(b) Procedural Compliance | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | Inspectors identified a Green finding of MT-AD-605, "Maintenance and Calibration of Installed Plant Instrumentation (IPI)," Revision 11, when as-found calibration results of the refueling water storage tank (RWST) level transmitter were discovered outside
Region: I | Susquehanna | 31253 | 03/31/2011 05/13/2011 | 2011002-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Corrective Actions Result in Loss of Drywell Cooling and Downpower |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 |  | 71111.19 | A self-revealing Green finding of NDAP-QA-0702, "Action Request and Condition Report Process," Revision 27, was identified when inadequate corrective action from the July 2010 flooding event resulted in endbell leakage from the '1A' Reactor Building (RB)
Region: I | Susquehanna | 31262 | 03/31/2011 05/13/2011 | 2011002-03 | NRC | FIN | Mitigating Systems | Green | B CS Chiller Inoperable due to Refrigerant Stacking |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | The inspectors identified a Green finding for failure to evaluate the condition of the 'B' control structure (CS) chiller after completion of SE-054-301, "Emergency Service Water/Control Structure Chilled Water System Leakage Test," Revision 12. Specifica
Region: I | Susquehanna | 31263 | 03/31/2011 05/13/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Replace Piping on B CS Chiller |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | An NRC-identified, Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified because PPL failed to correct a condition adverse to quality, an adverse trend of Freon leaks, by identifying that previous work orders (WOs) have n
Region: I | Susquehanna | 31264 | 03/31/2011 05/13/2011 | 2011002-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance Procedure Results in Steam Leak and Manual Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 |  | 71153 | A self-revealing finding of very low safety significance (Green) was identified when PPL personnel did not have adequate procedures to perform maintenance on a threaded connection on the '5C' feedwater heater (FWH) extraction steam bleeder trip valve, (BT
Region: I | Susquehanna | 31230 | 12/31/2010 02/09/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Periods of Elevated Risk for Necessary Risk Management Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000388 Susquehanna 2 |  | 71111.13 | An NRC-identified NCV of 10 CFR 50.65(a)(4) occurred when PPL failed to conduct an adequate risk assessment of online maintenance activities during the week of October 24, 2010. In one period of elevated risk on October 27, 2010, the entire duration in wh
Region: I | Susquehanna | 31231 | 12/31/2010 02/09/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Control, Calibrate and Evaluate M&TE |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | An NRC-identified NCV of 10 CFR 50, Appendix B, Criterion XII, "Control of Measuring and Test Equipment", occurred when PPL failed to control and calibrate measuring and test equipment (M&TE) at specified periods and document evaluations of missing M&TE.
Region: I | Susquehanna | 31237 | 12/31/2010 02/09/2011 | 2010005-05 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Evaluate a Non-Conforming Condition Resulted in an Alert. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000387 Susquehanna 1 |  | 71152 | A self revealing finding of Very low safety significance (Green), against PPL's CAP Procedure NDAP-QA-702, "Action Request and Condition Report Process." Specifically, a non-conforming condition with system design requirements was identified with the 'A'
Region: I | Susquehanna | 31229 | 10/08/2010 11/19/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of Safety-Related DC Circuit Breakers |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criteria XI, "Test Control," in that PPL did not ensure that test results were documented and evaluated to verify that test req
Region: I | Susquehanna | 31210 | 09/30/2010 11/12/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | HPCI and RCIC CST Low-Level Suction Transfer Made Inoperable Due to Transfer of Water from Condenser Area to CST Berm |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | The inspectors identified a Green NCV of Susquehanna Unit 1, TS 5.4.1, "Procedures," for an inadequate procedure to transfer water from the condenser area to the condensate storage tank (CST) berm. Specifically, the procedure failed to include a maximum l
Region: I | Susquehanna | 31211 | 09/30/2010 11/12/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Accurately Model the Simulator for RCIC System Operation at Reduced Flow Rates in Automatic |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.15 | An NRC-identified, Green NCV of 10 CFR 55.46(c)(1), "Plant Referenced Simulators," was identified because the Susquehanna simulator did not accurately model RCIC system response when operated in automatic flow control at less than design basis full flow.
Region: I | Susquehanna | 31217 | 09/30/2010 11/12/2010 | 2010004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Accurately Model the Simulator for RPV Level Control Using the Integrated Control System |  | H.2(d) Facilities & Equipment | TE?: N | 05000387 Susquehanna 1 |  | 71152 | A self-revealing NCV of 10 CFR 55.46(c)(1), "Plant Referenced Simulators," was identified because the Susquehanna simulator did not accurately model integrated control system (ICS) response to reactor pressure vessel (RPV) level transients. This violation
Region: I | Susquehanna | 31218 | 09/30/2010 11/12/2010 | 2010004-05 | Self - Revealed | NCV | Emergency Preparedness | Green | Inadequate Equipment to Measure Freon Concentration and Assess Threshold for an EAL Declaration |  | H.2(d) Facilities & Equipment | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153 | A Green self-revealing NCV associated with emergency planning standard 10 CFR 50.47(b)(4) was identified regarding inadequate indications for operators to determine if a threshold for an Alert Emergency Action Level (EAL) (OA7) declaration based on toxic
Region: I | Susquehanna | 31188 | 06/30/2010 08/13/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct IRM Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions", occurred when PPL failed to correct a condition adverse to quality associated with the 1D Intermediate Range Monitor (IRM) prior to a second reactor startup resulti
Region: I | Susquehanna | 31190 | 06/30/2010 08/13/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Online Risk Assessment for a Change in Plant Configuration |  | H.3(a) Work Planning | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.13 | A self-revealing, Green NCV of 10 CFR 50.65(a)(4), occurred when PPL failed to conduct an adequate risk assessment of online maintenance activities on April 22, 2010. A maintenance activity that caused the 11 B bus tie supply feeder breaker from the st
Region: I | Susquehanna | 31189 | 06/30/2010 08/13/2010 | 2010003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Condition With ESW LOOP/LOCA Timer |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix 9, Criterion XVI, "Corrective Action," in that PPL failed to correct a condition adverse to quality in a timely manner. Specifically, PPL failed to replace the emergency service water (ESW) pu
Region: I | Susquehanna | 31199 | 06/30/2010 08/13/2010 | 2010003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR 50 Appendix 9, Criterion XVI, "Corrective Action," in that PPL failed to identify and properly correct a condition adverse to quality (CAO). Specifically, PPL failed to recognize the "B" control structure
Region: I | Susquehanna | 31181 | 01/29/2010 03/15/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate PM Implementation Procedure Leading to Programmatic Deficiencies in the PM Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for PPL's failure to provide an adequate procedure to address and prevent multiple critical component preventive maintenance (PM) i
Region: I | Susquehanna | 31182 | 01/29/2010 03/15/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Non-conservative Maximum Safe Water Levels |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for PPL's failure to correct a condition adverse to quality associated with non conservative maximum safe water levels in Table 10 of Emergency Operat
Region: I | Susquehanna | 31183 | 01/29/2010 03/15/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Condition Report Process for Overdue Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for PPL's recurring failure to implement corrective action program procedural requirements. Specifically, Procedure NDAP QA 0702, "
Region: I | Susquehanna | 31184 | 01/29/2010 03/15/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Test Reactor Vessel Safety Relief Valves in Accordance with ASME Code |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50 Appendix B Criterion XI, "Test Control," for PPL's failure to appropriately implement American Society of Mechanical Engineers (ASME) Code for Operation and Maintenance of Nuclear Power Plants (OM Code) I
Region: I | Susquehanna | 31178 | 12/31/2009 02/03/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Insufficient Fire Drill Oversight to Ensure Fire Brigade Performance Deficiencies are Identified |  | P.3(a) Self-Assessment | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.05Q | The inspectors identified a Green Non-Cited Violation for the failure of fire brigade performance deficiencies to be identified and corrected during an unannounced fire drill, as required by programs set forth in Licensee Condition 2.C.3. Specifically, on
Region: I | Susquehanna | 31179 | 12/31/2009 02/03/2010 | 2009005-02 | NRC | FIN | Mitigating Systems | Green | Scenarios for NRC Annual Operating Examinations Did Not Meet Quantitative Standards for Total Malfunctions |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.11B | The inspectors identified greater finding in that 20% of the NRC annual operating exam simulator scenarios reviewed did not meet the quantitative standard for total malfunctions, 4 to 8 for a single scenario, and 10 to 14 for a scenario set established in
Region: I | Susquehanna | 31161 | 09/30/2009 11/13/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain the Fire Protection Program with Respect to the use and Storage of Combustibles in the Control Structure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000388 Susquehanna 2 |  | 71111.05Q | The inspectors identified a Green NCV of the Susquehanna, Unit 2 Operating License Condition 2.C.(3), Fire Protection for failure to administratively control combustible loading in an area on the 686' elevation of the control structure. As a result, a nor
Region: I | Susquehanna | 31172 | 09/30/2009 11/13/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Result in a Repeat Failure of Unit 1 HPCI Turbine Stop Valve |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," in that PPL did not implement timely corrective actions to preclude repetition of a significant condition adverse to quality. Specifically, actions ta
Region: I | Susquehanna | 31173 | 09/30/2009 11/13/2009 | 2009004-04 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Maintain Occupational Radiation Exposure As Low As Reasonably Achievable during the Unit 2 Refueling Outage |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000388 Susquehanna 2 |  | 7112102 | A self-revealing, Green finding was identified that involved inadequate work planning relative to the in-vessel visual inspection/ inservice inspection (IVVI/ISI) of the reactor vessel that resulted in additional unplanned collective exposure contrary to
Region: I | Susquehanna | 31159 | 06/30/2009 08/11/2009 | 2009003-01 | NRC | NCV | Initiating Events | Green | Violation of T.S. 5.5.6, IST Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | The inspectors identified a NCV of Technical Specification 5.5.6, "Inservice Testing Program," because PPL did not evaluate the cause, effect and generic concerns of safety relief valve (SRV) failures to meet the +/- 3 percent set pressure test acceptance
Region: I | Susquehanna | 31149 | 12/31/2008 01/28/2009 | 2008005-01 | NRC | FIN | Mitigating Systems | Green | Ineffective Evaluation and Incorporation of Operating Experience into the Corrective Action Program |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71153 | Green. A self-revealing finding was identified for failing to properly implement PPL procedure NDAP-QA-0725 regarding the incorporation and evaluation of operating experience (OE) into the corrective action program and control of field work. Specifically,
Region: I | Susquehanna | 31143 | 11/07/2008 12/02/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Operation of the Plant Following Evacuation of the Control Room due to a Fire |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.05T | -Green. The team identified a Green non-cited violation of Units 1 and 2 Technical Specification 5.4.1, "Procedures" for PPL's failure to establish appropriate procedure directions for operation of the plant from the remote shutdown panel following a cont
Region: I | Susquehanna | 30553 | 09/29/2008 11/14/2008 | 2008004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Equipment to Assess Threshold for Emergency Action Level |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.04Q | The inspectors identified a NCV associated with emergency planning standard 10 CFR 50.47(b)(4). The inspectors determined that a performance deficiency existed in that inadequate indications were available for operators to determine if a threshold for eme
Region: I | Susquehanna | 31142 | 09/29/2008 11/14/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | HPCI and RCIC Made Inoperable Due to Operator Actions During Shutdown |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | The inspectors identified a NCV of Susquehanna Unit 1 Technical Specifications (TS) 3.5.1 and 3.5.3 for rendering high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) inoperable during a planned shutdown. Specifically, both the
Region: I | Susquehanna | 30551 | 06/30/2008 08/13/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Corrective Actions in Response to Repeated ESW Pump Timer Failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000388 Susquehanna 2 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulation (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action" because PPL did not implement timely corrective actions for a degraded condition associated
Region: I | Susquehanna | 30550 | 03/31/2008 04/28/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Application of Work Instructions Resulted in Unavailable and Inoperable Engineering Safeguards Electrical Bus |  | H.3(a) Work Planning | TE?: N | 05000388 Susquehanna 2 |  | 71111.12 | A self-revealing, Green NCV was identified for failure to accomplish work in accordance with the appropriate instructions as required by 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, PPL did not complete the re
Region: I | Susquehanna | 30546 | 02/01/2008 03/17/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate a Deviation from BWROG EPG/SAG Resulted in an Inadequate EOP |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The NRC identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because, in the 1990s, Susquehanna failed to adequately evaluate a deviation from the Boiling Water Reactor Owner's Group Emergency P
Region: I | Susquehanna | 30547 | 02/01/2008 03/17/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | failure to Identify and Correct Inconsistencies in the Licensing Basis and the EOPs |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The NRC identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify that an inconsistency between the procedures and the design basis for suppression pool (SP) cooling was a condition adverse
Region: I | Susquehanna | 30548 | 02/01/2008 03/17/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Accurately Model the Simulator for RPV Water Level Instrumentation |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The NRC identified a Non-Cited Violation of 10 CFR 55.46(c)(1), "Plant Referenced Simulators," because the Susquehanna simulator did not accurately model reactor pressure vessel (RPV) level instrumentation following a design basis accident loss of coolant
Region: I | Susquehanna | 30549 | 02/01/2008 03/17/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | Failure to identify and Correct a Setpoint Error in the RHR and CS Operating Procedures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152B | The NRC identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify that a setpoint error in the operating procedures for safety-related systems was a condition adverse to quality (CAQ), resul
Region: I | Susquehanna | 30543 | 12/31/2007 02/14/2008 | 2007005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Design Control to Spport Fuel Rechanneling Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | A self-revealing non-cited violation of 10CFR 50 Appendix B, Criterion III, "Design Control," was identified on December 6, 2007, when PPL maintenance personnel found broken pieces of fuel spacer grid assemblies at fuel preparation machines. The damage to
Region: I | Susquehanna | 30545 | 12/31/2007 02/14/2008 | 2007005-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Occupational Radiation Exposure As Low As Reasonably Achievable During CREOAS Work |  | H.3(b) Work Activity Coordination | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7112102 | A self-revealing finding having very low safety significance was identified due to a deficiency in the area of maintaining occupational radiation exposures as low as is reasonably achievable (ALARA). ALARA and work planning for the control room emergency
Region: I | Susquehanna | 30535 | 06/30/2007 07/26/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions for an "E" Emergency Diesel Generator Jacket Water Leak |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.19 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," when PPL did not correct a condition adverse to quality, associated with a jacket water su
Region: I | Susquehanna | 30536 | 06/30/2007 07/26/2007 | 2007003-02 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Maintain Occupational Radiation Exposure As Low As reasonably Achievable During Reactor Water Cleanup Pipe Replacement Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000388 Susquehanna 2 |  | 7112102 | A self-revealing finding having very low safety significance was identified due to a deficiency in the area of maintaining occupational radiation exposures as low as is reasonably achievable (ALARA). For the Unit 2 refueling outage (2RIO13), the replaceme
Region: I | Susquehanna | 30537 | 06/30/2007 07/26/2007 | 2007003-03 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Maintain Occupational Radiation Exposure ALARA During Outage Inservice Inspection of Reactor Pressure Vessel |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000388 Susquehanna 2 |  | 7112102 | A self-revealing finding having very low safety significance was identified due to a deficiency in the area of maintaining occupational radiation exposures ALARA. For the Unit 2 refueling outage (2RIO13), the inservice inspection of the reactor pressure v
Region: I | Susquehanna | 30538 | 06/30/2007 07/26/2007 | 2007003-04 | NRC | NCV | Public Radiation Safety | Green | Violation of 10 CFR 71.5 for Inadequately Secured Transport of Condensate Pump Motors (Class 7 Material) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | An NRC-identified finding having very low safety significance was identified due to a deficiency in the radioactive material control program. On March 20, 2007, Susquehanna shipped two condensate pump motors in a sealand container as Class 7 material, sur
Region: I | Susquehanna | 30540 | 06/30/2007 07/26/2007 | 2007003-05 | NRC | NCV | Public Radiation Safety | Green | Violation of 10 CFR 71.5 for Inadequately Accounting for Activity in a Shipment of Irradiated Fuel Channels |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | NONE | A self-revealing finding having very low safety significance was identified due to a deficiency in the radioactive material control program. On June 22, 2007, while preparing to load fuel channels in a disposal liner, Susquehanna identified that a liner o
Region: I | Susquehanna | 30541 | 06/29/2007 08/03/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inoperable Pumphouse Ventilation lineup Corrective Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111121 | The inspectors identified a non cited violation (NCV) of 10CFR 50 Appendix B, Criterion III Design Control because PPL failed to ensure that the design basis for the Residual Heat Removal System (RHR) was correctly translated into specifications and proce
Region: I | Susquehanna | 30542 | 06/29/2007 08/03/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | E EDG Procedure Violation Human Performance |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111121 | The inspectors identified a non cited violation of Susquehanna Steam Electric Station (SSES) Technical Specification 5.4.1, Administrative Controls, Procedures, for failure to use procedures required by Regulatory Guide 1.33. PPL operators did not follow
Region: I | Susquehanna | 30530 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | Failure to Institute Effective Measures to Assure Special Processes (Welding) are Controlled and Accomplished |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000388 Susquehanna 2 |  | 71111.08G | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the failure to provide sufficiently detailed instructions for performing a reactor coolant system (RCS) pressure boundar
Region: I | Susquehanna | 30531 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Reactor Building Floor and Equipment Drains not Fully Scoped into the Maintenance Rule |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000387 Susquehanna 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50.65 (b)(2) because PPL did not scope an accident and transient mitigation function of the Reactor Building (RB) equipment floor drain system (EFDS) into the Maintenance Rule monitoring progr
Region: I | Susquehanna | 30528 | 12/31/2006 02/01/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate work instructions for the disassembly and inspection of IST check valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PPL did not provide adequate work instructions for the disassembly and inspection activities, required by Technic
Region: I | Susquehanna | 30529 | 12/31/2006 02/01/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for EPA Breaker Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | Inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because PPL failed to correct a long standing condition adverse to quality with regard to RPSP EPA circuit breaker problemss. The failures were
Region: I | Susquehanna | 30524 | 09/30/2006 10/31/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment |  | H.3(a) Work Planning | TE?: N | 05000388 Susquehanna 2 |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65 (a)(4), for an inadequate risk assessment. PPL did not correctly assess the risk associated with planned maintenance activities on the "A" emergency service water pump and the diesel fi
Region: I | Susquehanna | 30518 | 06/30/2006 07/28/2006 | 2006003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedures Resulted in Motor Operated Valve Failures |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71111.15 | A self-revealing non-cited violation was identified for failure to have adequate work instructions in accordance with 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings." This resulted in not identifing stem nut degradation prior t
Region: I | Susquehanna | 30519 | 06/30/2006 07/28/2006 | 2006003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Material Degradation Which Resulted in a Failure of the "C" ESW Pump Breaker |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 7111117B | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action was identified because PPL failed to adequately evaluate and correct degraded material in the "C" Emergency Service Water (ESW) pump breaker that caused a failu
Region: I | Susquehanna | 30520 | 06/30/2006 07/28/2006 | 2006003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Results in Elevated Reactor Coolant System Leakage |  |  | TE?: N | 05000388 Susquehanna 2 |  | 71111.2 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for failure to have adequate work instructions prescribed in a maintenance procedure, which resulted in a reactor coolant s
Region: I | Susquehanna | 30521 | 06/30/2006 07/28/2006 | 2006003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Design Review of PRNMS Modification Resulted in a Reactor Scram |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71111.2 | A self-revealing non-cited violation was identified for failure to comply with 10 CFR 50 Appendix B, Criterion III, Design Control. PPL did not correctly verify that the Power Range Neutron Monitoring System (PRNMS) modification would not adversely affect
Region: I | Susquehanna | 30522 | 06/30/2006 07/28/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | Ineffective Corrective Actions to Assure Training and Qualification of Workers as Required by 10 CFR 50 Appendix B, Criterion XVI |  |  | TE?: N | 05000387 Susquehanna 1 05000388 Susquehanna 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action" because PPL did not correct long standing issues related to worker qualifications. This resulted in unqualified workers performing tasks important
Region: I | Susquehanna | 30517 | 03/31/2006 05/08/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Equipment Hatch Plugs are not Watertight as Indicated in the FSAR |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71111.06 | A self-revealing non-cited violation was identified for not complying with 10 CFR 50, Appendix B, Criterion III, "Design Control." PPL did not assure that the emergency core cooling system (ECCS) compartments were water tight as described in the Final Saf
Region: I | Susquehanna | 30516 | 03/31/2006 05/08/2006 | 2006002-02 | NRC | FIN | Mitigating Systems | Green | Incomplete Corrective Actions contribute to CRD Flow control failure. |  |  | TE?: N | 05000388 Susquehanna 2 |  | 71111.12 | The inspectors identified a finding for not implementing Corrective Action procedure, NDAP-QA-702, which requires all actions to correct and prevent recurrence be completed before the closure of a condition report. Following electrolytic capacitor failure
Region: I | Susquehanna | 30514 | 02/10/2006 03/15/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Scaffolding that Affected the Safety-Related RHR Discharge Pressure Instrument Tubing Input to Automatic Depressurization System |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000388 Susquehanna 2 |  | 71152B | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify, for greater than a year, that a scaffold was constructed contacting a safety-related instrument sensing line which provided an input to
Region: I | Susquehanna | 126032 | 11/12/2019 |  |  | LIV |  | Green | Entry of two individuals into a high radiation area without appropriate qualifications, briefing, or RP escort |  |  | TE?: N | 05000387 Susquehanna 1 |  | 71152
Region: I | Three Mile Island | 124516 | 03/31/2019 05/09/2019 | 2019001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Heat Trace Calibration Procedure Resulting in Inoperable Borated Water Storage Tank Level Channel |  | P.2 - Evaluation | TE?: N | 05000289 Three Mile Island 1 | Procedure Quality | 71152 | A self-revealing Green non-cited violation of Technical Specification 6.8.1 was identified for inadequate procedures resulting in the freezing of a borated water storage tank (BWST) level transmitter instrument line.
Region: I | Three Mile Island | 24699 | 09/30/2018 11/08/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | 1A Emergency Diesel Generator Lube Oil Leak Caused by Untimely Corrective Actions |  | NPP | TE?: N | 05000289 Three Mile Island 1 |  | 71111.22 | A self-revealing Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action," was identified for failure to develop and implement adequate corrective actions to ensure the availability and reliability of the 1A emergency diesel
Region: I | Three Mile Island | 25922 | 02/19/2018 06/26/2018 | 2018012-01 | NRC | UNKN | Initiating Events | Green | Failure to Establish Appropriate Corrective Actions Associated with a Degraded Non-Safety Related Piping System |  | P.2 - Evaluation | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The NRC identified a Green finding when Exelon failed to establish appropriate corrective actions for a non-safety related system in the vicinity of safety-related equipment from 2010 to 2018. Specifically, failure to fix non-safety related piping resulte
Region: I | Three Mile Island | 22630 | 12/31/2017 01/25/2018 | 2017004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to correct degraded control rod connections |  | P.2 - Evaluation | TE?: N | 05000289 Three Mile Island 1 |  | 71111.12 | The inspectors documented a green self-revealing finding involving the failure to follow LS-AA-125, “Corrective Action Program,” Revision 14. Specifically, the licensee failed to take appropriate corrective actions to correct aging control rod drive mecha
Region: I | Three Mile Island | 34650 | 07/11/2017 07/11/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Deficiency in Implementing Controls for Pre-Staging of Material in the Reactor Building |  | H.2 Field Presence | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action Program," because Exelon did not effectively correct a condition adverse to quality regar
Region: I | Three Mile Island | 34649 | 09/30/2016 11/07/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Internal Flooding Risk Not Evaluated |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152 | Green. The inspectors identified an NCV of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion III, "Design Control," in that Exelon did not ensure the availability of the emergency diesel generator (EDG) following a seismic event. The in
Region: I | Three Mile Island | 34087 | 03/31/2016 04/28/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Deficient Design Control of ECCS Level Transmitter Instrument Line Heat Trace Causes Freezing and Inoperability |  | H.8 Procedure Adherence | TE?: N | 05000289 Three Mile Island 1 |  | 71111.01 | A self-revealing non-cited violation of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," was identified for failure to establish and implement adequate design control measures to assure that the bora
Region: I | Three Mile Island | 34086 | 12/31/2015 02/01/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Trend Vibration Data for Safety Related River Water Pump |  | P.2 Evaluation | TE?: N | 05000289 Three Mile Island 1 |  | 71111.12 | The inspectors identified a self-revealing finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion XVI, "Corrective Action Program," because Exelon did not identify and correct a condition ad
Region: I | Three Mile Island | 34083 | 09/30/2015 11/02/2015 | 2015003-01 | NRC | FIN | Mitigating Systems | Green | Internal Flooding Licensing Basis Commitment Not Met |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71111.06 | Green. The inspectors identified a finding because Exelon failed to meet a commitment made during original licensing to mitigate an internal flooding event. Specifically, Exelon committed to making changes to the fire water supply system to mitigate the i
Region: I | Three Mile Island | 34082 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Failure to Maintain Turbine Bypass Valve Simulator Modeling |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71111.2 | Green. A self-revealing NCV of 10 CFR Part 55.46(c), "Plant-Referenced Simulators," was identified for Exelon's failure to ensure that the plant-referenced simulator demonstrated expected plant response to normal, transient, and accident conditions to whi
Region: I | Three Mile Island | 32201 | 02/27/2015 04/07/2015 | 2015007-01 | NRC | NCV | Barrier Integrity | Green | Deficient Design Control for Verifying Reactor Building Fan Assembly Capability to Perform Design Basis Function |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The NRC identified an NCV of Title 10 of the CFR, Part 50, Appendix B, Criterion III, "Design Control," for failure to establish and implement adequate design control measures to assure that the reactor building (RB) fan assemblies were capable of perfo
Region: I | Three Mile Island | 34081 | 02/27/2015 04/07/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Untimely Identification and Correction of Degraded BWST Level Transmitter Cold Weather Protection Equipment |  | H.8 Procedure Adherence | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The NRC identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct degraded borated water storage tank (BWST) level transmitter instru
Region: I | Three Mile Island | 32200 | 09/30/2014 11/13/2014 | 2014004-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000289 Three Mile Island 1 |  | NONE | Green. The inspectors identified an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.54(q)(2), 10 CFR 50.47(b)(10), and 10 CFR 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the Three Mile Island Nuclear Station
Region: I | Three Mile Island | 34074 | 06/30/2014 08/04/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Risk Mitigation Actions Not Performed for Excavation of Nuclear River System Cable Conduits |  | H.5 Work Management | TE?: N | 05000289 Three Mile Island 1 |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR Part 50.65(a)(4), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," because Exelon did not im
Region: I | Three Mile Island | 34076 | 05/23/2014 06/27/2014 | 2014009-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions for a Condition Adverse to Quality that Caused the Failure of Two Primary Isolation Valaves |  | P.2 Evaluation | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified a finding of very low safety significance involving an NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion XVI, "Corrective Action," because Exelon did not take adequate corrective actions to add
Region: I | Three Mile Island | 34066 | 03/31/2014 05/14/2014 | 2014002-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a 10 CFR 50.59 Evaluation for the BWST Seismic Qualification |  | P.5 Operating Experience | TE?: Y SL-IV-NCVIV | 05000289 Three Mile Island 1 |  | 71111.04Q | Green/SL-IV. The inspectors identified a Severity Level IV (SL-IV), Non-Cited Violation of 10 CFR 50.59, "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for Exelon's failure to perform a 50.59 evaluatio
Region: I | Three Mile Island | 34072 | 03/31/2014 05/14/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Loss of Air Intake Tunnel Sump Pump Function due to Inadequate Work Execution |  | H.8 Procedure Adherence | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05Q | Green. The inspectors identified a finding of very low safety significant (Green) for Exelon's failure to follow work order instructions in accordance with MA-AA-716-011, "Work Execution and Close Out," during planned maintenance activities on the air int
Region: I | Three Mile Island | 34073 | 03/31/2014 05/14/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Restore Station Blackout Diesel Generator Cooling Water Lineup following Maintenance and Testing Activities |  | H.7 Documentation | TE?: N | 05000289 Three Mile Island 1 |  | 71111.22 | Green. A self-revealing non-cited violation (NCV) of 10 CFR 50.63, "Loss of All Alternating Current Power," was identified for Exelon's failure to properly restore the station blackout (SBO) diesel generator system following maintenance and testing activi
Region: I | Three Mile Island | 34061 | 12/31/2013 02/10/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Material Storage in Reactor Building |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | 71111.2 | Green. The inspectors identified a Green non-cited violation of Technical Specification 6.8.1 for Exelon's failure to implement procedure requirements governing storage of equipment in Class 1 structures. Specifically, Exelon stored unsecured material, on
Region: I | Three Mile Island | 34065 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Leak Rate Testing on Close Loop Piping |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71111.22 | Green. The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix J, Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors, for Exelon's failure to establish an adequate program that leak tested components penetrati
Region: I | Three Mile Island | 34058 | 03/31/2013 04/29/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Combustible Loading near the 'B' CST within FHAR Limits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05Q | [Draft] Green. The inspectors identified a Green non-cited violation (NCV) of license condition DPR-50 section 2.C.(4), Fire Protection, for Exelon's failure to maintain transient combustible loading within fire loading limits near the 'B' condensate stor
Region: I | Three Mile Island | 34049 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Adequacy of Reactor Building Seismic Gap Flood Seal |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000289 Three Mile Island 1 |  | 71152 | Green. The inspectors identified a non-cited violation (NCV) of General Design Criterion 2, "Performance Standards," because Exelon had not established measures to ensure that the seismic gap flood seal was adequate to remain watertight during a probable
Region: I | Three Mile Island | 34050 | 12/31/2012 02/11/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Licensing Basis Flood Barrier and Support Equipment Deficiencies in Intake Screen and Pump House |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000289 Three Mile Island 1 |  | NONE | Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, in that Exelon failed to identify and correct conditions adverse to quality regarding the licensing basis external flood barrier inte
Region: I | Three Mile Island | 34048 | 09/30/2012 11/14/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Combustible Loading in the BWST Tunnel within FHAR Limits |  | H.3(b) Work Activity Coordination | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of license condition DPR-50, section 2.C.(4), Fire Protection, for Exelon storing transient combustibles in excess of the fire loading allowed near the borated water storage tank (BWST). Specific
Region: I | Three Mile Island | 34040 | 05/25/2012 07/05/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with ESAS relay replacement |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Exelon's failure to implement prompt corrective actions following the ident
Region: I | Three Mile Island | 34023 | 03/31/2012 05/01/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Compensatory Actions for Out-of-Service Appendix 'R' Heat Exchanger |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000289 Three Mile Island 1 |  | 71111.04Q | Green. The inspectors identified a non-cited violation of license condition DPR-50 section 2.C.(4), Fire Protection, for Exelon's failure to implement compensatory actions during planned maintenance on the 'A' nuclear service heat exchanger (NS-C-1A). S
Region: I | Three Mile Island | 34026 | 03/31/2012 05/01/2012 | 2012002-02 | NRC | NCV | Initiating Events | Green | Inadequate Inspection of RCP Flanges |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000289 Three Mile Island 1 |  | NONE | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, because Exelon did not specify, in writing, the exact inspection scope and criteria for boric acid inspections of the re
Region: I | Three Mile Island | 34027 | 03/31/2012 05/01/2012 | 2012002-03 | NRC | FIN | Initiating Events | Green | Inadequate System Monitoring Results in Multiple IA-P-4 Trips |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.12 | Green. A self-revealing finding was identified for inadequate performance monitoring of instrument air compressor number four (IA-P-4) in accordance with ER-AA-2003, System Performance Monitoring and Analysis. Specifically, performance monitoring action
Region: I | Three Mile Island | 34028 | 03/31/2012 05/01/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Maintenance Risk Evaluation for DH-V-3 Planned Maintenance |  | H.3(a) Work Planning | TE?: N | 05000289 Three Mile Island 1 |  | 71111.13 | Green. The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(4), Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, for Exelon's failure to adequately assess and manage the impact to plant risk during a p
Region: I | Three Mile Island | 34032 | 03/30/2012 05/08/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Nonconservative Differential Pressure Value used in DHR/LPI Motor Operated Valves Design Analysis |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Exelon had not verified the adequacy of their design with respect to ensuring the c
Region: I | Three Mile Island | 34033 | 03/30/2012 05/08/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate TOL Sizing Evaluation for Jogging/Throttling Valves |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Exelon had not verified the adequacy of the design regarding motor operated valve (
Region: I | Three Mile Island | 34034 | 03/30/2012 05/08/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Battery Sizing Calculation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because Exelon did not verify the adequacy of design with respect to the Battery 1A sizing
Region: I | Three Mile Island | 34039 | 03/30/2012 05/08/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design and Maintenance of SBO Diesel Generator Battery |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50.63, "Loss of all Alternating Current Power," because Exelon did not ensure that necessary support systems had sufficient capability to mitig
Region: I | Three Mile Island | 34005 | 12/31/2011 02/08/2012 | 2011005-01 | NRC | URI | Barrier Integrity | Green | Inspect and Disposition Leakage Event from B RCP Flange from 1R19 |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000289 Three Mile Island 1 |  | 71111.08P | Introduction: The NRC inspectors identified an unresolved item (URI), because Exelon did not implement boric acid inspections of the reactor coolant system (RCS) thermal barrier flange joints of reactor coolant pumps (RCP) RC-P-1A, RC-P-1B, RC-P-1C and RC
Region: I | Three Mile Island | 34000 | 12/31/2011 02/08/2012 | 2011005-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Inadequate Control of Reactor Coolant Let-down and Clean-up to Minimize Occupational Radiation Dose |  | H.3(a) Work Planning | TE?: N | 05000289 Three Mile Island 1 |  | 71124.02 | A self-revealing finding was identified because Exelon did not effectively manage and control Unit 1 reactor coolant let-down and clean-up during shutdown and cool-down in support of the 2011 TMI Unit 1 refueling and maintenance outage (T1R19) to maximize
Region: I | Three Mile Island | 34001 | 12/31/2011 02/08/2012 | 2011005-05 | NRC | NCV | Initiating Events | Green | Failure to Identify a Non-Conservative Technical Specification following Revision to River Stage Discharge Analysis |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, was identified because Exelon did not identify and correct a condition adverse to quality regarding the impact of a revised river stage discharge anal
Region: I | Three Mile Island | 34021 | 08/31/2011 09/12/2011 | 2011503-01 | NRC | NCV | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: I | Three Mile Island | 34022 | 08/31/2011 09/12/2011 | 2011503-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: I | Three Mile Island | 33988 | 12/31/2010 02/03/2011 | 2010005-01 | NRC | FIN | Initiating Events | Green | Inadequate Preventive Maintenance for Signal Converter Causes Turbine Trip and Plant Transient |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000289 Three Mile Island 1 |  | 71111.12 | A self-revealing Green finding was identified, because station personnel did not establish a periodic task to calibrate and/or replace the integrated control system (ICS) to digital turbine control system (DTCS) signal convertor, a critical component, in
Region: I | Three Mile Island | 33989 | 12/31/2010 02/03/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Deficient Internal and External Flood Barrier Inspection Program |  | P.2(b) Implementing Operating Experience | TE?: N | 05000289 Three Mile Island 1 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings for deficient internal and external flood barrier inspection procedures. Specifically, no instructions, procedures, or
Region: I | Three Mile Island | 33987 | 09/30/2010 11/01/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Deficient Control of Transient Material in Seismic Class I Buildings |  | H.4(b) Procedural Compliance | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of Technical Specification 6.8.1 for failure to properly control and store transient material within seismic Class I buildings such that the equipment did not pose a hazard to nuclear safety or s
Region: I | Three Mile Island | 33984 | 07/29/2010 09/10/2010 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Deficient Extent Of Condition Evaluation for a 2007 'B' EDG Scavenging Air Box Gasket Leak Which Affected the Reliability and Availability of the 'A EDG |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) involving a NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for a deficient evaluation of a failed 'B' emergency diesel generator (EDG) scavenging air box g
Region: I | Three Mile Island | 33985 | 07/29/2010 09/10/2010 | 2010009-02 | NRC | NCV | Mitigating Systems | Green | MSSV Design Basis Calculations Inaccurate |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," associated with MSSV capacity calculations revised in 1988 to support a power uprate amendment. The MSSV capacity calculations erroneously referenced the as-p
Region: I | Three Mile Island | 33986 | 07/29/2010 09/10/2010 | 2010009-03 | Self - Revealed | NCV | Mitigating Systems | Green | Multiple MSSVs test failures due to improper evaluation of Operating Experience. |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | A self-revealing Green NCV of TMI Technical Specification (TS) 3.4.1.2.3 was identified for having greater than three main steam safety valves (MSSVs) inoperable for greater than the allowed outage time with reactor power greater than 5%. MSSV testing pri
Region: I | Three Mile Island | 33936 | 07/29/2010 09/10/2010 | 2010009-04 | NRC | URI | Mitigating Systems | Green | Potential Concern Regarding TMI's Internal and External Flood Protection Barriers and Mitigation Strategies |  | P.2(b) Implementing Operating Experience | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The team identified that Exelon was not meeting the requirements of USFSAR Section 2.6.5 and of 10 CFR 50.65 because TMI did not have an effective program to monitor the condition of flood seal penetrations into safety-related structures. This has been a
Region: I | Three Mile Island | 33981 | 03/12/2010 04/15/2010 | 2010007-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Use Process or Engineering Controls Caused Airborne Radioactivity |  | H.3(a) Work Planning | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR 20.1701 was identified because Exelon did not use process or other engineering controls, to the extent practicable, to control the concentration of radioactive materials in air. Specifically, process or
Region: I | Three Mile Island | 33982 | 03/12/2010 04/15/2010 | 2010007-02 | NRC | NCV | Public Radiation Safety | Green | Deficient Design Change Implementation and Controls Resulted In Unfiltered Radioactivity Release to the Environment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | A self-revealing NCV of Technical Specification 6.8 was identified because Exelon did not properly establish and implement procedures for control of radioactivity to limit materials released to the environment and limit personnel exposure as specified in
Region: I | Three Mile Island | 33983 | 03/12/2010 04/15/2010 | 2010007-03 | NRC | NCV | Public Radiation Safety | Green | Untimely Corrective Action to Stop Unfiltered Radiological Release |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | The inspectors identified an NCV of Technical Specification 6.11 because from November 16 through November 21, 2009, Exelon did not implement timely follow-up and corrective action to minimize radioactivity released to the environment as required radiatio
Region: I | Three Mile Island | 33980 | 12/31/2009 02/02/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000289/2009005-01, Potential CO2 Migration Outside the Relay Room Fire Area |  |  | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a Green, non-cited violation of the Three Mile Island operating license for not adequately considering the effects of CO2 toxicity. Specifically, for a fire in the relay room which causes a CO2 initiation and a control room evacu
Region: I | Three Mile Island | 33973 | 06/30/2009 07/31/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Deficient Coordination of Work Activities Resulted in NR-P-1C Becoming Inoperable |  | H.3(b) Work Activity Coordination | TE?: N | 05000289 Three Mile Island 1 |  | 71111.13 | A self-revealing NCV of Technical Specification 6.8.1.a was identified for failure to properly plan and coordinate maintenance and operational activities affecting safety related components. Specifically, station personnel did not properly coordinate impl
Region: I | Three Mile Island | 33974 | 06/30/2009 07/31/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Deficient Inspections, Evaluation, and Remediation of Submerged Underground Electrical Cables |  | P.2(b) Implementing Operating Experience | TE?: N | 05000289 Three Mile Island 1 |  | 71152 | The inspectors identified an NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for failure to establish and accomplish appropriate work instructions and procedures to inspect underground elect
Region: I | Three Mile Island | 33967 | 06/26/2009 08/10/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess Seismic Qualification of Stop Logs |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The team determined Exelon did not evaluate the adequacy of the river water stop logs in the Intake Screen and Pump House (ISPH) structure, to ensure that l
Region: I | Three Mile Island | 33969 | 06/26/2009 08/10/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Install Amptector Bypass Jumper for Load Center Breaker |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, Drawings, in that Exelon failed to include appropriate quantitative or qualitative acceptance criteria for determining that important activities have been sati
Region: I | Three Mile Island | 33963 | 03/31/2009 05/13/2009 | 2009002-01 | NRC | NCV | Barrier Integrity | Green | Instrument Accuracy Not Verified Prior to Performing Containment Penetration Local Leak Rate Testing | EA Case: 2009011 | H.4(b) Procedural Compliance | TE?: N | 05000289 Three Mile Island 1 |  | 71111.19 | The inspectors identified an NCV of Technical Specification 6.8.5 which requires the Reactor Building Leak Rate Testing Program to be properly implemented. Specifically, station personnel repeatedly used temperature instruments that did not meet accuracy
Region: I | Three Mile Island | 33960 | 09/29/2008 11/04/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Deficient Implementation of Fire Barrier Seal Inspection Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000289 Three Mile Island 1 |  | 71111.15 | The inspectors identified an NCV of Technical Specification (TS) 6.8.1.e, which requires that written procedures covering the Fire Protection program be properly implemented. Specifically, fire seal inspections performed in August and October 2007 did not
Region: I | Three Mile Island | 33961 | 09/29/2008 11/04/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Reference Test Conditions for MU-P-1B Not Established in Accordance with ASME OM Code |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.22 | The inspectors identified an NCV of TS 4.2.2 for improper implementation of applicable American Society of Mechanical Engineers (ASME) Operation and Maintenance (OM) Code requirements for quarterly in-service testing (IST) of the 'B' makeup pump (MU-P-1B)
Region: I | Three Mile Island | 33954 | 09/12/2008 10/07/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Use of Elevators by Fire Brigade Members |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05T | The team identified that AmerGen allowed fire brigade members to use elevators during response to a fire, when the power or control to the elevator could be lost as a result of a fire. This finding was determined to be of very low safety significance (Gre
Region: I | Three Mile Island | 33955 | 09/12/2008 10/07/2008 | 2008009-02 | NRC | URI | Mitigating Systems | Green | Potential CO2 Migration Outside the Relay Room Fire Area |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05T | The team identified a potential concern regarding operation of the carbon dioxide (CO2) extinguishing system for the relay room. Specifically, the potential may exist for CO2 to migrate outside the relay room and affect the ability of operators to perform
Region: I | Three Mile Island | 33950 | 04/18/2008 06/02/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Stage Equipment Required by Abnormal Operating Procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a NCV of Technical Specification (TS) 6.8.1, which requires that written procedures be implemented as recommended in Appendix A of Regulatory Guide (RG) 1.33, including abnormal operating procedures (AOPs) for loss of service wat
Region: I | Three Mile Island | 33951 | 04/18/2008 06/02/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Increased EDG Fuel Oil Consumption Into Design Basis Calculations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, AmerGen did not ensure that fuel consumption calculations included the additional fuel needed for allowable emergency diesel generator (EDG) freq
Region: I | Three Mile Island | 33952 | 04/18/2008 06/02/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Meet ASME OM Code Data Collection Requirement for Comprehensive IST |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a NCV of TS 4.2.2 for the failure to implement applicable American Society of Mechanical Engineers (ASME) Operation and Maintenance (OM) Code requirements for comprehensive in-service testing (IST) of the 'A' and 'B' decay heat r
Region: I | Three Mile Island | 33953 | 04/18/2008 06/02/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Require Emergency Lighting Units (ELUs) |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000289 Three Mile Island 1 |  | NONE | The inspectors identified a NCV of License Condition 2.c(4) and 10 CFR 50, Appendix R, Section III.J, which require that emergency lighting units (ELUs) with at least an eight-hour battery power supply be provided in areas needed for operation of safe shu
Region: I | Three Mile Island | 33943 | 12/31/2007 02/12/2008 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | Ineffective Corrective Actions for Failure to Maintain Structural Design Clearances Inside Reactor Building Containment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 71111.15 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for ineffective corrective actions to a previously identified NCV regarding a failure to maintain structural design clearances inside the rea
Region: I | Three Mile Island | 33947 | 12/31/2007 02/12/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Deficient Control of Reactor Coolant System Vent Area During Mid-Loop Operation |  | H.3(b) Work Activity Coordination | TE?: N | 05000289 Three Mile Island 1 |  | 71111.2 | The inspectors identified a NCV of TS 6.8.1a for failure to maintain the appropriate reactor coolant system (RCS) vent area required by station procedures during mid-loop operation. The reduced vent area degraded operators' ability to add water to the RCS
Region: I | Three Mile Island | 33383 | 12/31/2007 02/12/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Deficient Procedure Causes Failure to Perform Surveillance Testing of Valves in Accordance with ASME OM Code |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000289 Three Mile Island 1 |  | 71111.22 | The inspectors identified an NCV of TS 4.2.2 for failure to test eight safety-related valves in accordance with American Society of Mechanical Engineers Operations & Maintenance (ASME OM) Code requirements. Procedure OP-TM-211-211 contained no procedural
Region: I | Three Mile Island | 33948 | 12/31/2007 02/12/2008 | 2007005-05 | NRC | NCV | Mitigating Systems | Green | Deficient Control of Temporary Ventilation During Mid-Loop Operation Leads to Unusual Event |  | H.3(b) Work Activity Coordination | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | A self-revealing NCV of TS 6.8.1.a was identified for failure to properly coordinate maintenance and operational activities associated with installing the OTSG primary lower manways during mid-loop operation. Installation of the OTSG lower manway cover, w
Region: I | Three Mile Island | 33944 | 12/31/2007 02/12/2008 | 2007005-06 | NRC | NCV | Barrier Integrity | Green | Damaged Control Rod Assembly Due to Deficient Fuel Handling Practices |  | H.4(b) Procedural Compliance | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | A self-revealing NCV of Technical Specification (TS) 6.8.1.c was identified for failure to properly implement procedures to safely move control rod assemblies (CRAs) within the spent fuel pool (SFP). Fuel handling operators did not monitor the control mas
Region: I | Three Mile Island | 33945 | 12/31/2007 02/12/2008 | 2007005-07 | NRC | NCV | Barrier Integrity | Green | Damaged Fuel Assembly Due to Deficient Fuel Handling Practices |  | H.4(a) Human Error Prevention | TE?: N | 05000289 Three Mile Island 1 |  | 71153 | A self-revealing NCV of TS 6.8.1.c was identified for failure to properly establish and implement procedures to safely reload fuel into the reactor vessel core. Fuel handling operators proceeded to insert a FA without properly verifying the fuel movement
Region: I | Three Mile Island | 33940 | 04/20/2007 05/15/2007 | 2007502-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Adequately Critique and Identify a Performance Problem Associated with the Process of Event Classification. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000289 Three Mile Island 1 |  | 71114.01 | A Green NRC-identified non-cited violation (NCV) of 10 CFR 50.47(b)(14) and 10 CFR Part 50, Appendix E, Section IV.F.2.g, was identified for failure of the licensee's exercise critique process to identify a weakness associated with a risk significant plan
Region: I | Three Mile Island | 33941 | 03/15/2007 04/02/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Manual Capability for EFW Flow Control Valves |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee could not provide demonstrative evidence that design control measures
Region: I | Three Mile Island | 33942 | 03/15/2007 04/02/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for EDG Loading |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000289 Three Mile Island 1 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10CFR50, Appendix B, Criterion III, Design Control. Specifically, AmerGen did not consider the effects of frequency variation on diesel generator load
Region: I | Three Mile Island | 33934 | 12/31/2006 01/31/2007 | 2006006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inattentiveness to Duty by a Shift Manager |  |  | TE?: N | 05000289 Three Mile Island 1 |  | NONE | A self-revealing violation of Technical Specification 6.8.1 occurred on Sunday, December 11, 2005 at 3:45 AM when the on-duty Operations Shift Manager, a licensed senior reactor operator, was observed by three control room operators to be inattentive to d
Region: I | Three Mile Island | 33935 | 12/31/2006 01/31/2007 | 2006006-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow FFD Procedures |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000289 Three Mile Island 1 |  | NONE | A self-revealing violation of 10 CFR Part 26, "Fitness For Duty Programs" occurred on Sunday, December 11, 2005 at 3:45 AM when three control room operators failed to follow station procedures and initiate actions to have an inattentive Operations Shift M
Region: I | Three Mile Island | 33933 | 09/30/2006 11/02/2006 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Unreliable BWST Level Alarm Instrument. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000289 Three Mile Island 1 |  | 71111.19 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI "Corrective Action" for untimely action to correct degraded performance of the borated water storage tank (BWST) low level alarm. Differential pressure ins
Region: I | Three Mile Island | 33406 | 03/31/2006 05/09/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Deficient Work Instructions and Maintenance Implementation on Control Building Chiller |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152 | The inspectors identified a non-cited violation (NCV) of Technical Specification 6.8.1 in that station personnel did not properly establish and implement work instructions for replacement of the 'B' control building chiller (AH-C-4B) expansion joints. Spe
Region: I | Three Mile Island | 33412 | 03/31/2006 05/15/2006 | 2006007-01 | NRC | NCV | Initiating Events | Green | Deficient Abnormal Operating Procedures for Loss of Vital 120 Volt Electrical Bus, Loss of 4160 Volt Bus, and Loss of NSCCW |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.8.1, for failure to adequately establish and implement procedures required by Regulatory Guide 1.33, Section 6, "Procedures for Combating Emergencies and Other Signifi
Region: I | Three Mile Island | 33413 | 03/31/2006 05/15/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Inservice Testing Reference Values Not Reestablished as Required by ASME Code Following Maintenance to Decay Heat, NSCCW, and Emergency Feedwater Pumps |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The team identified an NCV of 10 CFR 50.55a.(f)(4)(ii) "Codes and Standards," which requires, in part, that testing of safety-related pumps meet the requirements of the American Society of Mechanical Engineers (ASME) Operation and Maintenance (OM) Code re
Region: I | Three Mile Island | 33924 | 03/31/2006 05/15/2006 | 2006007-03 | NRC | NCV | Barrier Integrity | Green | Inservice Test Failure Not Identified and Evaluated for Containment Isolation Check Valve |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified an NCV of 10 CFR 50.55a.(f)(4)(ii) "Codes and Standards" which requires, in part, that testing of safety-related check valves meet the requirements of the American Society of Mechanical Engineers (ASME) Operation and Maintenance
Region: I | Three Mile Island | 33925 | 03/31/2006 05/15/2006 | 2006007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate and Correct Indications of Air in 'A' Decay Heat Removal System |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for a deficient evaluation that resulted in ineffective corrective actions for indications of air in the Decay Heat (DH) system following maintenance. The
Region: I | Three Mile Island | 33926 | 03/31/2006 05/15/2006 | 2006007-05 | NRC | NCV | Mitigating Systems | Green | Deficient Test Procedure Causes Air Introduction to Emergency Core Cooling Systems |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71152B | The inspectors identified an NCV of TS 6.8.1.a for deficient surveillance procedures that resulted in the introduction of air into the sodium hydroxide (NAOH) piping to several emergency core cooling systems (ECCS) during in-service testing (IST) activiti
Region: I | Three Mile Island | 125640 | 11/06/2019 |  |  | LIV |  | Green | Failure to Maintain Functional Fire Seal Barrier |  |  | TE?: N | 05000289 Three Mile Island 1 |  | 71111.05Q
Region: I | Vermont Yankee | 1996 | 03/31/2015 02/12/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Calculation Assumption Led to Reduced Reactor Vessel Level While in Cold Shutdown |  | H.11 Challenge the Unknown | TE?: N | 05000271 Vermont Yankee |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, because Entergy did not establish measures to assure the design basis was correctly translated into procedures and instructions. Specifically, an incorrect assumption
Region: I | Vermont Yankee | 1993 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Compensatory Continuous Fire Watches Not Implemented as Required |  | P.3 Resolution | TE?: N | 05000271 Vermont Yankee |  | 71111.05Q | The inspectors identified a Green NCV of operating license condition 3.F, Fire Protection Program, because Entergy did not implement and maintain in effect all provisions of the NRC approved fire protection program. Specifically, Entergy did not implement
Region: I | Vermont Yankee | 1994 | 12/31/2014 02/10/2015 | 2014005-02 | NRC | NCV | Emergency Preparedness | Green | Misclassification of Emergency Conditions Based on Radiological Criteria |  | H.9 Training | TE?: N | 05000271 Vermont Yankee |  | 71111.06 | The inspectors identified a Green NCV of 10 CFR 50.54(q), "Emergency Plans," because Entergy's emergency action level (EAL) classification process could result in a misclassification, a deficiency related to a risk significant planning standard. Specifica
Region: I | Vermont Yankee | 1995 | 12/31/2014 02/10/2015 | 2014005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inoperable Emergency Diesel Generator |  |  | TE?: N | 05000271 Vermont Yankee |  | 71153 | The inspectors identified a self-revealing Green NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy did not properly implement the prescribed maintenance instr
Region: I | Vermont Yankee | 1983 | 09/30/2014 10/27/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failures to Promptly Identify Through-Wall Leakage from Service Water Piping to Emergency Diesel Generators |  | H.1 Resources | TE?: N | 05000271 Vermont Yankee |  | 71111.04Q | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly identify conditions adverse to quality related to the service water system. Specifically, observable through-wall leaks th
Region: I | Vermont Yankee | 1984 | 09/30/2014 10/27/2014 | 2014004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Submit Reactor Building Crane Digital Control System Modification for Approval |  | H.12 Avoid Complacency | TE?: N | 05000271 Vermont Yankee |  | 71111.18 | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.59, "Changes, Tests and Experiments," when Entergy made changes to the reactor b
Region: I | Vermont Yankee | 1992 | 09/30/2014 10/27/2014 | 2014004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Results in Inoperable Containment Isolation Valve |  | H.8 Procedure Adherence | TE?: N | 05000271 Vermont Yankee |  | 71152 | The inspectors identified a self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because Entergy staff did not implement the prescribed maintenance instructions during the refurbishment of the air-opera
Region: I | Vermont Yankee | 1977 | 04/03/2014 05/16/2014 | 2014007-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Design Control of SBO Loading Calculation |  | H.8 Procedure Adherence | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a finding of very low safety significance (Green), in that Entergy did not ensure correct implementation of their design control process when establishing the capacity requirement for the new Station Blackout (SBO) alternate alternatin
Region: I | Vermont Yankee | 1966 | 03/31/2014 05/08/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Unavailability of the Fire Water to Service Water Crosstie |  | H.11 Challenge the Unknown | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | The inspectors identified an NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph a(1), because Entergy did not evaluate the fire protection system for (a)(1) classification even though the
Region: I | Vermont Yankee | 1961 | 12/31/2013 02/06/2014 | 2013005-01 | Self - Revealed | VIO | Mitigating Systems | Green | Inadequate Corrective Actions to Restore Switchgear Room Flood Boundary |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.06 | A self-revealing, cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy did not promptly correct two separate conditions adverse to quality related to flood protection of the switchgear rooms. Specifi
Region: I | Vermont Yankee | 1964 | 12/31/2013 02/06/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Isolating All Nitrogen Supply to the Containment Instrument Air System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | The inspectors identified a NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(4), for Entergy's failure to conduct an adequate risk assessment prior to isolating the nitrogen supply
Region: I | Vermont Yankee | 1956 | 09/30/2013 11/05/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Unavailability of the "B" Control Rod Drive Equipment Train |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | The inspectors identified a NCV of Title 10 Code of Federal Regulations (10 CFR) 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy did not monitor the performance of the "B" control rod drive (C
Region: I | Vermont Yankee | 1959 | 09/30/2013 11/05/2013 | 2013004-02 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During Refueling Activities |  | H.3(a) Work Planning | TE?: N | 05000271 Vermont Yankee |  | 71124.02 | A self-revealing finding was identified because Entergy inadequately planned and controlled work while performing reactor reassembly and reactor cavity decontamination activities during refueling outage (RFO) 30 resulting in excessive unintended occupatio
Region: I | Vermont Yankee | 1960 | 09/30/2013 11/05/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Operator Error Results in Diesel Generator Overload |  | H.4(a) Human Error Prevention | TE?: N | 05000271 Vermont Yankee |  | 71152 | A self-revealing NCV of Technical Specification 6.4, "Procedures," was identified because Entergy overloaded the "B" emergency diesel generator to 130 percent of its sustained load rating. Specifically, an auxiliary operator (AO) took the speed droop swit
Region: I | Vermont Yankee | 1942 | 06/30/2013 08/09/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Sealing Flood Pathways into the Electrical Switchgear Rooms |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 71111.01 | Two examples of a self-revealing, non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," were identified because Entergy did not promptly identify and correct conditions adverse to quality related to flood protection of the switc
Region: I | Vermont Yankee | 1945 | 06/30/2013 08/09/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Compensatory Measures Required for a Barrier Breach Permit for the "A" Emergency Diesel Generator Room |  | H.3(b) Work Activity Coordination | TE?: N | 05000271 Vermont Yankee |  | 71111.04Q | The inspectors identified a Green NCV of TS 6.4, "Procedures," because Entergy did not implement a barrier breach permit required by procedure. Specifically, Entergy personnel created three open penetrations to the "A" emergency diesel generator (EDG) roo
Region: I | Vermont Yankee | 1946 | 06/30/2013 08/09/2013 | 2013003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure for Configuration Control Results in a Dislodged Secondary Containment Blowout Panel Due to Reactor Building Ventilation System Pressurization |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.2 | A self-revealing, Green, NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Entergy did not establish a procedure controlling plant equipment appropriate to the circumstances for activities affecting
Region: I | Vermont Yankee | 1954 | 06/28/2013 07/31/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Improper Maintenance Rule Scoping of the Reactor Building HVAC System |  |  | TE?: N | 05000271 Vermont Yankee |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50.65(b)(2) because Entergy did not properly scope the reactor building heating, ventilation and air conditioning (HVAC) system within the station's maintenance rule program. Specifically, the inspectors det
Region: I | Vermont Yankee | 1936 | 03/31/2013 04/19/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Appendix R Fire Door Not Latching Closed Due to Misalignment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 71111.04Q | The inspectors identified an NCV of operating license condition 3.F, fire protection program, because Entergy did not correct a degraded latch on a three-hour rated fire door on the entrance to the "B" emergency diesel generator (EDG) room, and as a resul
Region: I | Vermont Yankee | 1937 | 03/31/2013 04/19/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Compensatory Measures Associated with a Temporary Modification |  | H.3(b) Work Activity Coordination | TE?: N | 05000271 Vermont Yankee |  | 71111.18 | The inspectors identified an NCV of Technical Specification 6.4, "Procedures," because procedure OPOP-SW-2181, "Service Water/ Alternate Cooling System," was inadequate. Specifically, the step in the procedure to identify and isolate sources of water lost
Region: I | Vermont Yankee | 1940 | 03/31/2013 04/19/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Maintaining Operability of the Low Pressure Coolant Injection Battery UPS-1A |  | P.2(b) Implementing Operating Experience | TE?: N | 05000271 Vermont Yankee |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Entergy did not promptly correct an adverse condition resulting in the failure of the "B-UPS-1A" low pressure coolant injection (LPCI) uninterruptible p
Region: I | Vermont Yankee | 1941 | 03/31/2013 04/19/2013 | 2013002-04 | NRC | NCV | Mitigating Systems | Green | Failure of the "B" Emergency Diesel Generator from Jacket Water Leakage Due to Inadequate Corrective Action |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000271 Vermont Yankee |  | 71111.19 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy did not promptly correct an adverse condition resulting in the failure of the "B" EDG. Specifically, Entergy personnel did not promptly repla
Region: I | Vermont Yankee | 1929 | 10/16/2012 10/31/2012 | 2012004-01 | Self - Revealed | FIN | Initiating Events | Green | Incorrect Assessment of Equipment Condition Resulted in Single Recirculation Loop Operation |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | A self-revealing finding was identified because Entergy failed to implement a preventive maintenance procedure. Specifically, Entergy personnel classified the discovery status code for the minor motor inspection on the "A" recirculation pump motor generat
Region: I | Vermont Yankee | 1930 | 10/16/2012 10/31/2012 | 2012004-02 | NRC | NCV | Barrier Integrity | Green | Dedicated Operators Required for Operability under Applied Administrative Controls Left Immediate Vicinity of Open Valves |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000271 Vermont Yankee |  | 71111.22 | The inspectors identified an NCV of technical specification (TS) 6.4, "Procedures," for Entergy's failure to implement a surveillance activity in accordance with the written procedure. Specifically, the inspectors identified that during a surveillance tes
Region: I | Vermont Yankee | 1924 | 06/30/2012 07/26/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Isolating the Condensate Pumps' Minimum Flow Line's Automatic Flow Control Valve |  | H.2(d) Facilities & Equipment | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(4), for Entergy's failure to conduct an adequate risk assessment prior to isolatin
Region: I | Vermont Yankee | 1928 | 06/30/2012 07/26/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Not Considering the Increased Risk of a Plant Transient when Securing a Feedwater Pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | The inspectors identified a NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(4) for Entergy's failure to conduct an adequate risk assessment prior to securing the "C" feedwater pump
Region: I | Vermont Yankee | 1922 | 03/31/2012 04/16/2012 | 2012002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of the "B" UPS Tachometer Coupling Due to Age and Inadequate Corrective Actions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | A self-revealing, NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy did not promptly correct an adverse condition resulting in the failure of the "B" uninterruptible power system (UPS) motor generator (MG) set
Region: I | Vermont Yankee | 1923 | 03/31/2012 04/16/2012 | 2012002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of the "D" Service Water Pump Due to Low Oil and Inadequate Corrective Actions |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 71111.19 | A self-revealing, NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," was identified because Entergy personnel did not promptly correct an adverse condition resulting in the unplanned unavailability of the "D" service water pump. Specifically
Region: I | Vermont Yankee | 1919 | 12/31/2011 01/27/2012 | 2011005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Trip of an Emergency Diesel Generator's Fuel Rack |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | A self-revealing NCV of very low safety significance of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Entergy personnel used instructions that were not appropriate to the circumstances resulting in an
Region: I | Vermont Yankee | 1921 | 12/31/2011 01/27/2012 | 2011005-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Incomplete Inventory for Spent Resin Shipment |  | H.3(b) Work Activity Coordination | TE?: N | 05000271 Vermont Yankee |  | 71152 | A self-revealing NCV of very low safety significance of 10 CFR 20.1501 was identified because Entergy personnel failed to indicate the total radionuclide activity on the radioactive waste manifest for a radioactive waste shipment. 10 CFR 20.1501 requires
Region: I | Vermont Yankee | 1920 | 10/11/2011 01/27/2012 | 2011005-02 | Self - Revealed | NCV | Initiating Events | Green | Loss of Shutdown Cooling due to Tag Out Error |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.2 | A self-revealing NCV of very low safety significance of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because drawing B-191301, Sheet 576, "Control Wiring Diagram - Emergency Heater Drain Valve Diagram"
Region: I | Vermont Yankee | 1915 | 02/16/2011 04/29/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Steam Leak on High Pressure Coolant Injection (HPCI) During Surveillance Testing |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000271 Vermont Yankee |  | 71153 | A self-revealing, Green NCV of Technical Specification 6.4, "Procedures," was identified in which maintenance and planning personnel did not involve engineering personnel as required by Entergy procedure EN-MA-101, "Fundamentals of Maintenance," Revision
Region: I | Vermont Yankee | 1914 | 01/02/2011 04/29/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Foreign Material Exclusion Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71111.19 | . A self-revealing, non-cited violation (NCV) of very low safety significance (Green) of Technical Specifications 6.4, "Procedures," was identified for inadequate implementation of Entergy procedure EN-MA-118, "Foreign Material Exclusion," Revision 6, whi
Region: I | Vermont Yankee | 1907 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000271 Vermont Yankee |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that Quality Control verification inspections were consistently included and correctly specified in quality-affecting procedur
Region: I | Vermont Yankee | 1912 | 12/31/2010 02/08/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000271 Vermont Yankee |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement the experience and qualification requirements of the Quality Assurance Program. As a result, the licensee f
Region: I | Vermont Yankee | 1905 | 10/01/2010 11/08/2010 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | Fire Scenario Resulting in Loss of Reactor Core Isolation Cooling System |  |  | TE?: N | 05000271 Vermont Yankee |  | 71111.05T | The team identified a Green, Non-Cited Violation of the Vermont Yankee Nuclear Power Station Facility Operating License, Condition 3.F, in that Entergy failed to implement and maintain in effect all provisions of the approved Fire Protection Program as
Region: I | Vermont Yankee | 1904 | 09/30/2010 10/27/2010 | 2010004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Isolation of Reactor Core Isolation Cooling (RCIC) During Surveillance Testing |  | H.4(a) Human Error Prevention | TE?: N | 05000271 Vermont Yankee |  | 71152 | A self-revealing, Green, non-cited violation (NCV) of Technical Specification 6.4, "Procedures," was identified in which technicians incorrectly performed reactor core isolation cooling (RCIC) surveillance test operating procedure (OP) 4365, "RCIC Steam L
Region: I | Vermont Yankee | 1899 | 06/30/2010 07/29/2010 | 2010003-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of RCS Inventory During Emergency Core Cooling System (ECCS) Testing Due to Inadequate Test Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.2 | A self-revealing NCV of very low safety significance (Green) of TS 6.4, "Procedures," was identified when operators inadvertently drained water from the RPV during integrated ECCS testing. Specifically, Entergy failed to establish the initial plant condit
Region: I | Vermont Yankee | 1727 | 03/30/2010 05/10/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | High Pressure Coolant Injection Inoperable Due to Spurious Suction Valve Swap and Technical Specification Actions Not Performed |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | The inspectors identified an NCV of very low safety significance (Green) of technical specification 3.5.E, "High Pressure Coolant Injection (HPCI) System," because Entergy staff failed to identify that HPCI was inoperable, enter the required limiting cond
Region: I | Vermont Yankee | 1897 | 03/30/2010 05/10/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Surveillance Testing Not Risk Assessed in Accordance with 10 CFR 50.65 |  | H.3(a) Work Planning | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | . The inspectors identified an NCV of very low safety significance (Green) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because Entergy staff did not assess and manage the increase in risk due to
Region: I | Vermont Yankee | 1898 | 03/30/2010 05/10/2010 | 2010002-03 | NRC | NCV | Initiating Events | Green | Inadequate Design Control for Continuously Submerged Underground Cables |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000271 Vermont Yankee |  | 71152 | . The inspectors identified an NCV of very low safety significance (Green) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because Entergy did not select and review safety-related cables suitable for application in the environment in which
Region: I | Vermont Yankee | 1725 | 12/31/2009 01/25/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Entergy did not assess and manage the increase in risk that resulted from maintenance activities that impacted the availability of the low pressure coolant injection (LPCI) subsystem |  | H.3(a) Work Planning | TE?: N | 05000271 Vermont Yankee |  | 71111.13 | On December 4, 2009, Entergy conducted a test of the high pressure coolant injection (HPCI) system as a retest following maintenance activities. Operations personnel placed both trains of the residual heat removal (RHR) system in the torus cooling mode to
Region: I | Vermont Yankee | 1717 | 09/30/2009 11/09/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to initiate corrective action condition reports for all deficient items identified during cooling tower inspections. |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," in that Entergy did not initiate corrective action condition reports (CRs) for all deficient items identified during Cooling Tower
Region: I | Vermont Yankee | 1715 | 06/03/2009 06/03/2009 | 2009006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Actions for a HPCI System Functional Failure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000271 Vermont Yankee |  | 71152B | The team identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for Entergy's failure to take adequate corrective actions for a condition adverse to quality involving an issue that had the potential to n
Region: I | Vermont Yankee | 1710 | 03/31/2009 05/01/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to write a condition report (CR) for an adverse condition associated with water accumulating in the turbine building supply fan housing plenum area. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | The inspectors identified a Green non-cited violation (NCV) of Vermont Yankee Technical Specifications Section 6.4, "Procedures," for Vermont Yankee's failure to take action to correct a specific and foreseen malfunction of a plant component. Specifically
Region: I | Vermont Yankee | 1711 | 03/31/2009 05/01/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to perform procedurally required engineering evaluations for scaffolding. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000271 Vermont Yankee |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for Vermont Yankee's failure to routinely perform procedurally required engineering evaluations for scaffold bracing attached to pi
Region: I | Vermont Yankee | 1702 | 10/31/2008 09/26/2008 | 2008006-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Preventative Maintenence Program for Reactor Building Crane |  |  | TE?: N | 05000271 Vermont Yankee |  | NONE | A self-revealing Finding of very low safety significance was identified for Entergy not fully developing an adequate preventive maintenance (PM) program for the reactor building crane (RBC). As a result, on May 12, 2008, when the first loaded spent fuel s
Region: I | Vermont Yankee | 1709 | 10/08/2008 10/10/2008 | 2008009-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Change Review Causes Failure of Circulating Water System Pipe Supports |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 93812 | A self-revealing finding of very low safety significance was identified because Entergy did not verify the technical adequacy of a design change prior to placing the circulating water system piping in east cooling tower cell 1-1 in service. As a result, f
Region: I | Vermont Yankee | 1699 | 08/15/2008 09/26/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of Safety Related Batteries |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," in that, Entergy did not properly document and evaluate safety related battery test results. Specifically
Region: I | Vermont Yankee | 1700 | 08/15/2008 09/26/2008 | 2008008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Emergency Diesel Generator Load Testing |  |  | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, Entergy did not ensure that the design basis, as defined in calculations and the Updated
Region: I | Vermont Yankee | 1701 | 08/15/2008 09/26/2008 | 2008008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Station Blackout Load Shedding |  |  | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50.63, "Loss of all Alternating Current Power," in that, Entergy did not ensure that adequate battery capacity would be available during a stat
Region: I | Vermont Yankee | 1698 | 06/30/2008 08/06/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | Ineffective Reactor Building Crane Maintenance |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | The NRC identified a non-cited violation for Entergy's failure to take timely corrective action, as required by 10CFR50.65(a)(1), after the reactor building crane (RBC) exceeded reliability performance goals. Specifically, from April 12, 2007, when the RB
Region: I | Vermont Yankee | 1691 | 04/10/2008 05/14/2008 | 2008007-01 | NRC | FIN | Mitigating Systems | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(d) Facilities & Equipment | TE?: N | 05000271 Vermont Yankee |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: I | Vermont Yankee | 1692 | 04/10/2008 05/14/2008 | 2008007-02 | NRC | NCV | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Vermont Yankee | 1693 | 04/10/2008 05/14/2008 | 2008007-03 | NRC | FIN | Barrier Integrity | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: I | Vermont Yankee | 1694 | 04/10/2008 05/14/2008 | 2008007-04 | NRC | NCV | Mitigating Systems | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: I | Vermont Yankee | 1695 | 04/10/2008 05/14/2008 | 2008007-05 | NRC | NCV | Mitigating Systems | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: I | Vermont Yankee | 1696 | 03/31/2008 04/30/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Inadequate Work Order Results in Unplanned "A" Service Water Pump Inoperability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | A self-revealing non-cited violation (NCV) of Technical Specification 6.4, "Procedures," was identified for Entergy's failure to provide an adequate procedure for setting the "A" service water (SW) pump lower motor guide bearing during its replacement in
Region: I | Vermont Yankee | 1688 | 09/28/2007 11/07/2007 | 2007004-01 | NRC | NCV | Initiating Events | Green | Inadequate Inspection program Resulted in a Partial Collapse of a Non-Safety Related Cooling Tower Cell |  | P.2(b) Implementing Operating Experience | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | . A self-revealing NCV of TS 6.4, "Procedures," was identified for Entergy's failure to effectively incorporate readily available industry operating experience (OE) into the cooling tower (CT) inspection program and processes. Specifically, Entergy had no
Region: I | Vermont Yankee | 1689 | 09/28/2007 11/07/2007 | 2007004-02 | NRC | FIN | Initiating Events | Green | Reactor Scram During Troubleshooting Due to Inadequate Main TSV Preventive Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | A self-revealing Finding of very low safety significance was identified for Entergy's failure to specify adequate preventive maintenance (PM) for main turbine stop valve number two (TSV-2). As a result, during troubleshooting activities on the TSV-2 bypas
Region: I | Vermont Yankee | 1671 | 03/31/2007 05/02/2007 | 2007002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Establish Minimum Thread Engagement for the "A" SW Pump Packing Gland Studs Results in Unplanned Unavailability |  |  | TE?: N | 05000271 Vermont Yankee |  | 71111.12 | . A self-revealing finding was identified because Entergy mechanics did not meet station expectations for establishing minimum thread engagement when installing packing gland studs into the "A" service water pump stuffing box during the replacement of pum
Region: I | Vermont Yankee | 1677 | 03/31/2007 05/02/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Associated with CST Vortexing Analysis |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000271 Vermont Yankee |  | 71111.15 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control." Specifically, Entergy did not use an appropriate method for calculating the effects of vortexing within the condensate storage tank which could have impacted high
Region: I | Vermont Yankee | 1678 | 03/31/2007 05/02/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Unplanned "A" Emergency Diesel Generator Shutdown and Unavailability |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71111.22 | . A self-revealing NCV of Vermont Yankee Technical Specification 6.4, "Procedures," was identified when operators failed to follow a surveillance procedure for the emergency diesel generator fuel oil transfer system. As a result, the "A" diesel automatica
Region: I | Vermont Yankee | 1679 | 03/31/2007 05/02/2007 | 2007002-04 | Self - Revealed | FIN | Initiating Events | Green | Error Made by Electrical Maintenance Department Technicians Results in the Need for a Reactor Power Reduction |  | H.4(b) Procedural Compliance | TE?: N | 05000271 Vermont Yankee |  | 71153 | A self-revealing finding was identified due to a procedure performance error made by Electrical Maintenance Department technicians while performing switchyard testing. As a result, one of three 345 kilovolt offsite power lines and one of two 115 kilovolt
Region: I | Vermont Yankee | 1669 | 09/30/2006 10/30/2006 | 2006004-01 | NRC | FIN | Initiating Events | Green | Vermont Yankee Did Not Correct Conditions Leading to the Continued Accumulation of Dust on Non-Safety Related Electrical Bus Grounding Resistors |  |  | TE?: N | 05000271 Vermont Yankee |  | 71153 | A self-revealing finding was identified because Vermont Yankee did not correct a previously identified condition that allowed the continued accumulation of dust on non-safety related 4160 Volt electrical bus 2 grounding resistor banks. This accumulation o
Region: I | Vermont Yankee | 1670 | 09/30/2006 10/30/2006 | 2006004-02 | NRC | FIN | Mitigating Systems | Green | Entergy Did Not Incorporate Industry Operating Experience into the Preventive Maintenance Strategies for the "A" RBCCW Pump Motor |  | P.2(b) Implementing Operating Experience | TE?: N | 05000271 Vermont Yankee |  | 71153 | A self-revealing finding of very low safety significance was identified because Entergy did not effectively incorporate existing industry operating experience into the preventive maintenance (PM) strategy for the "A" reactor building closed cooling water
Region: I | Vermont Yankee | 1663 | 08/18/2006 09/29/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Appendix R Power Supply Surveillance Test |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a green, non-cited violation of 10CFR50, Appendix R (App R), General Requirements for failure to create and schedule surveillances to ensure App R components were operable. The team reviewed two modifications related to the replacement
Region: I | Vermont Yankee | 1664 | 08/18/2006 09/29/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Clogged SW Strainer Procedure |  |  | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a green, non-cited violation of Technical Specification 6.4 Procedures, for Entergy's failure to establish an adequate procedure to address degraded service water (SW) flow conditions. The station's Loss of Service Water procedure perm
Region: I | Vermont Yankee | 1668 | 08/18/2006 09/29/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for HPCI/RCIC Terry Turbine Controller Flow Oscillations |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000271 Vermont Yankee |  | 7111121 | The team identified a green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to take actions to correct a condition adverse to quality related to significant flow oscillations caused by the Terry turbine flow/sp
Region: II | Browns Ferry | 126243 | 12/31/2019 02/11/2020 | 2019004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Site Procedures Results in Smoldering of Main Feed Water System Electrical Wires |  | H.4 - Teamwork | TE?: N | 05000260 Browns Ferry 2 | Protection Against External Factors | 71153 | A self-revealed Green finding was identified when the licensee failed to follow their general operating instruction for breakers, 0-GOI-300-2, "Electrical." Specifically, the licensee failed to inspect a 250V molded case circuit breaker prior to re-closi
Region: II | Browns Ferry | 126475 | 12/31/2019 02/11/2020 | 2019004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 1 High Pressure Coolant Injection System Declared Inoperable due to Steam Supply Isolation |  | H.5 - Work Management | TE?: N | 05000259 Browns Ferry 1 | Equipment Performance | 71153 | A self-revealed Green finding and associated NCV of TS 5.4.1, "Procedures," was identified when the licensee failed to comply with NPG-SPP-22.206, "Verification Program," which resulted in the inadvertent isolation and inoperability of Unit 1 HPCI.
Region: II | Browns Ferry | 126476 | 12/31/2019 02/11/2020 | 2019004-03 | Self - Revealed | NCV | Initiating Events | Green | Unit 2 Automatic Reactor Scram during Startup due to Intermediate Range Monitor Noise |  | P.5 - Operating Experience | TE?: N | 05000260 Browns Ferry 2 | Equipment Performance | 71153 | A self-revealed Green finding and NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to correct an electrical noise issue associated with the neutron monitoring system, which resulted in a Unit
Region: II | Browns Ferry | 125100 | 06/30/2019 08/12/2019 | 2019002-01 | Self - Revealed | FIN | Initiating Events | Green | Improper Operation of Automatic Voltage Regulator Results in Reactor SCRAM |  | H.12 - Avoid Complacency | TE?: N | 05000296 Browns Ferry 3 | Protection Against External Factors | 71153 | A self-revealed Finding of Browns Ferry procedure 3-OI-47 "Turbine-Generator System" was identified for the failure to properly operate the Unit 3 Automatic Voltage Regulator (AVR) while adjusting the reactive load on the main generator in order to lower
Region: II | Browns Ferry | 124652 | 03/31/2019 05/09/2019 | 2019001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to establish and implement adequate procedures for diving activities and the underwater storage of highly radioactive materials. |  | H.12 - Avoid Complacency | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 | Program & Process | 71124.01 | A self-revealed, Green, Non-cited Violation of Technical Specification 5.4.1.a, “Procedures”, was identified for multiple examples of the failure to establish and implement adequate procedures for the control of diving activities and the storage of ra
Region: II | Browns Ferry | 124583 | 03/31/2019 05/09/2019 | 2019001-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to backwash and drain RWCU demineralizers prior to perform a system breach. |  | H.11 - Challenge the Unknown | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 | Program & Process | 71124.01 | A self-revealed, Green, Non-cited Violation (NCV) of Technical Specification (TS) 5.4.1.a, “Procedures” was identified for failure to implement procedure NPG-SPP-10.2, “Clearance Procedure to Safely Control Energy.” Specifically, the licensee failed to ve
Region: II | Browns Ferry | 124515 | 03/01/2019 04/12/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain CO2 Barriers |  | H.11 - Challenge the Unknown | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05XT | The NRC identified a Green NCV of Operating License Condition 2.C.(13) for Unit 1, 2.C.(14) for Unit 2 and 2.C(7) for Unit 3, for the licensee's failure to identify and document non-functional CO2 doors in the Corrective Action Program.
Region: II | Browns Ferry | 25962 | 12/31/2018 01/31/2019 | 2018004-01 | Self - Revealed | FIN | Mitigating Systems | Green | High Crew Failure Rate During Annual Requalification |  | H.8 - Procedure Adherence | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 | Human Performance | 71111.11A | A self-revealing Green Finding was identified for a performance deficiency against the expected knowledge and abilities of licensed operators as demonstrated during the requalification examinations required by 10 CFR 55.59(a)(2). Specifically, the license
Region: II | Browns Ferry | 25965 | 12/31/2018 01/31/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Control the Design of the High Pressure Coolant Injection (HPCI) Containment Isolation Circuitry |  | NPP | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 | Design Control | 71153 | A self-revealing Green non-cited violation of 10 CFR 50 Appendix B, Criterion III “Design Control”, was identified for the failure to control the design of the HPCI containment isolation circuitry. Specifically, the licensee added additional relays to the
Region: II | Browns Ferry | 25966 | 12/31/2018 01/31/2019 | 2018004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Surveillance Test Procedures to Check Battery Category C Limits |  | NPP | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 | Procedure Quality | 71153 | A self-revealing Green non-cited violation of TS 5.4.1.a, “Procedures,” required, in part, that written procedures be established, implemented, and maintained covering Emergency Power Sources (e.g., diesel generator, batteries) related to procedures recom
Region: II | Browns Ferry | 25963 | 11/16/2018 01/23/2019 | 2018050-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Adequate Radiation Surveys |  | H.5 - Work Management | TE?: N | 05000259 Browns Ferry 1 |  | 93812 | A self-revealing, Green, Non-cited Violation (NCV) of Title 10 Code of Federal Regulations (10 CFR) 20.1501, “Surveys and Monitoring: General,” was identified when TVA failed to perform adequate surveys of the Unit 1 refuel floor equipment pit during divi
Region: II | Browns Ferry | 24423 | 08/23/2018 10/03/2018 | 2018012-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correct an inoperable 250V Shutdown Board Battery Charger |  | NPP | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | Performance Deficiency: The failure to correct a condition adverse to quality was a performance deficiency (PD). Specifically, in 2014 the 250V Shutdown Board Battery Charger was entered into the CAP as a CAQ, but no actions were taken to correct the cond
Region: II | Browns Ferry | 24111 | 06/30/2018 08/09/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Procedures to prevent Over Pressurizing the HPCI System |  | P.3 - Resolution | TE?: N | 05000259 Browns Ferry 1 |  | 71152 | A self-revealed, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified for failure to establish procedures appropriate to the circumstances to preclude over pressurizing the High Pr
Region: II | Browns Ferry | 23534 | 02/24/2018 05/08/2018 | 2018001-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area (HRA) |  | H.8 - Procedure Adherence | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | A self-revealing, Green, Non-cited Violation (NCV) of Technical Specification (TS) 5.7.1, was identified for a worker who entered a HRA without proper authorization. Specifically, the worker entered the Unit 3 A & C Residual Heat Removal (RHR) heat exchan
Region: II | Browns Ferry | 23512 | 02/20/2018 05/08/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post-Maintenance Testing of 4kV Breaker Stationary Switches |  | H.1 - Resources | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.19 | A self-revealing, Green, NCV of 10 CFR Part 50 Appendix B, Criterion V, was identified when the licensee failed to perform an adequate post-maintenance test in accordance with NPG-SPP-06.3, “Pre-/Post-Maintenance Testing.” Specifically, the post m
Region: II | Browns Ferry | 23535 | 02/18/2018 05/08/2018 | 2018001-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Implement Controls for Locked High Radiation Area (LHRA) Access |  | H.4 - Teamwork | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | A self-revealing, Green, NCV of TS 5.7.2, was identified for the failure to control access to a LHRA. Specifically, a worker installed and climbed a ladder in the Unit 3 drywell without RP personnel present. In doing so, the worker accessed an area with d
Region: II | Browns Ferry | 23176 | 12/31/2017 02/07/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Determination of Operability for the HPCI System |  | P.2 - Evaluation | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | Green. Two examples of an NRC identified NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" were identified for the licensee's failure to properly implement operability evaluation requirements for degraded High Pressu
Region: II | Browns Ferry | 23177 | 12/31/2017 02/07/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an IDO without delay for 3A EDG after Observing Indications of a Degraded Condition |  | H.13 - Consistent Process | TE?: N | 05000296 Browns Ferry 3 |  | 71111.15 | Green. The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, for failure to perform an immediate operability determination (IDO) for 3A Emergency Diesel Generator (EDG) upon discovering a degra
Region: II | Browns Ferry | 21639 | 09/30/2017 10/31/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Measures to Ensure the Watertight Integrity of the Diesel Generator Buildings |  | P.6 - Self-Assessment | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.01 | An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V was identified for the licensee's failure to prescribe instructions and appropriate acceptance criteria for diesel generator building door inspections. This design requ
Region: II | Browns Ferry | 21640 | 09/30/2017 10/31/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Intake Building Flood Barrier |  | H.12 - Avoid Complacency | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152 | An NRC identified NCV of Technical Specification (TS) 5.4.1, “Procedures,” was identified for the failure to follow BFN procedure MCI-0-023-PMP003, Emergency Equipment Cooling Water (EECW) and Residual Heat Removal Service Water Pump (RHRSW) Removal and R
Region: II | Browns Ferry | 23513 | 09/24/2017 05/08/2018 | 2018001-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Configuration Control of HPCI Valve Design Issues |  | NPP | TE?: N | 05000296 Browns Ferry 3 |  | 71152 | A self-revealing, Green, NCV of 10 CFR Part 50, Appendix B, Criterion III, was identified when the licensee failed to ensure adequate control of valve design configurations in accordance with NPG-SPP-9.3, "Plant Modifications and Engineering Change Contro
Region: II | Browns Ferry | 3717 | 06/30/2017 07/26/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Risk Evaluation for Postulated Fires Affecting EECW Strainers |  | H.12 - Avoid Complacency | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05A | An NRC-identified non-cited violation of 10 CFR 50.48(c) and NFPA 805, Section 2.4.2.4 was identified for the licensee's failure to perform an adequate engineering analysis to determine the effects of fire on the ability to achieve the nuclear safety perf
Region: II | Browns Ferry | 22309 | 06/30/2017 07/26/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Non Conservative Assumptions in Emergency Drain Capacity Design Review |  | NPP | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 71111.06 | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion III was identified for the licensee's failure to verify the adequacy of the Unit 1 and 2 diesel building emergency drain pipe to mitigate a postulated internal flood. Specifically,
Region: II | Browns Ferry | 3718 | 06/30/2017 07/26/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Assure EECW Design Basis Capability |  | H.6 Design Margins | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.22 | An NRC-identified non-cited violation of 10 CFR Part 50, Appendix B, Criterion III was identified for the licensee's failure to correctly translate the design basis of the EECW system into technical instruction 0-TI-579(EECW). The effects of instrument un
Region: II | Browns Ferry | 3716 | 06/30/2017 07/26/2017 | 2017002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Corrective Actions to Prevent the Recurrence of a Reactor Scram Due to IRM spiking |  | H.11 Challenge the Unknown | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was reviewed for the licensee's failure to establish measures to assure that corrective action was taken to preclude repetition of a significant
Region: II | Browns Ferry | 3711 | 03/31/2017 05/10/2017 | 2017001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Take Corrective Actions to Preclude a Repeat Failure of a Containment Isolation Valve |  |  | TE?: N | 05000260 Browns Ferry 2 |  | 71111.15 | An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's inadequate corrective actions to preclude repetition (CAPR) of a significant condition adverse to quality (SCAQ). The
Region: II | Browns Ferry | 3713 | 03/31/2017 05/10/2017 | 2017001-02 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area |  | H.4 Teamwork | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | . A self-revealing non-cited violation (NCV) of TS 5.7.1 was identified for a worker who entered a High Radiation Area (HRA) (Unit 1 reactor building steam tunnel) without proper authorization. This performance deficiency was determined to be greater than
Region: II | Browns Ferry | 3714 | 03/31/2017 05/10/2017 | 2017001-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Airborne Radioactivity Surveys |  | H.12 Avoid Complacency | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | An inspector-identified non-cited violation (NCV) of TS 5.4.1 was identified for the licensee's failure to obtain an air sample while performing work in an area with smearable contamination levels greater than 50,000 disintegrations per minute (DPM) per 1
Region: II | Browns Ferry | 3712 | 03/31/2017 05/10/2017 | 2017001-04 | NRC | NCV | Mitigating Systems | Green | Incorrect Tap Settings for 480 Volt Shutdown Transformer Results in Inoperability of Associated 480V Shutdown Boards |  |  | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | An NRC identified non-cited violation of 10 CFR Part 50, Appendix B, Criterion VI, "Document Control," was identified after maintenance on safety related 4kv to 480 volt transformers TS1A and TS1B (Unit 1) resulted in the windings tap setting being miscon
Region: II | Browns Ferry | 3708 | 10/17/2016 02/08/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Prompt Determination of Operability for the HPCI System |  | P.2 Evaluation | TE?: N | 05000296 Browns Ferry 3 |  | 71152 | An NRC identified NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for the licensee's failure to accomplish the Prompt Determination of Operability (PDO) for CR 1039036 in accordance with the requirem
Region: II | Browns Ferry | 3692 | 09/30/2016 11/09/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Piping Clearances After MOV Modification |  |  | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.04Q | An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for the licensee's failure to ensure sufficient clearance was available following a replacement of the Core Spr
Region: II | Browns Ferry | 3693 | 09/30/2016 11/09/2016 | 2016003-02 | NRC | NCV | Initiating Events | Green | Failure to Implement Compensatory Roving Fire Watch |  | H.3 Change Management | TE?: N | 05000260 Browns Ferry 2 |  | 71111.05Q | An NRC identified non-cited violation (NCV) of Renewed License Number DPR-52, condition 2.C.(14) was identified for the licensee's failure to implement and maintain in effect all provisions of the approved fire protection program that comply with 10 CFR 5
Region: II | Browns Ferry | 3694 | 09/30/2016 11/09/2016 | 2016003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain the High Pressure Fire Protection System Piping |  | P.5 Operating Experience | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | A self-revealing Non-cited Violation (NCV) of Technical Specification (TS) 5.4.1.d, Fire Protection Program Implementation, was identified for the licensee's failure to maintain the integrity of the high pressure fire protection piping. The licensee's imm
Region: II | Browns Ferry | 3704 | 09/30/2016 11/09/2016 | 2016003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Prompt Determination of Operability for HPCI Steam Line Inboard Isolation Valve |  | H.6 Design Margins | TE?: N | 05000259 Browns Ferry 1 |  | 71152 | An NRC identified NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" was identified for the licensee's failure to promptly identify conditions adverse to quality associated with the prompt determination of operability (PDO) for CR 10610
Region: II | Browns Ferry | 3705 | 09/30/2016 11/09/2016 | 2016003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Alternate Depressurization Valve Inoperable Longer than the Allowed Outage Time |  | P.1 Identification | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing NCV of TS 3.5.1, Emergency Core Cooling Systems, Condition E in that an inoperable Automatic Depressurization System (ADS) valve function existed longer than the allowed technical specification time. The licensee implemented corrective ac
Region: II | Browns Ferry | 3706 | 09/30/2016 11/09/2016 | 2016003-06 | Self - Revealed | NCV | Mitigating Systems | Green | Main Steam Relief Valves Inoperable Longer than Allowed Outage Time |  | P.3 Resolution | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing NCV of TS 3.4.3, Safety Relief Valves was identified for two required MSRVs being inoperable longer than the allowed outage time and follow on action completion time. The licensee's immediate corrective action was to replace all Unit 3 MS
Region: II | Browns Ferry | 3687 | 08/12/2016 09/26/2016 | 2016011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate All Targets Within the Zone of Influence of Ignition Sources |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The NRC identified a violation of 10 CFR 50.48(c) for the licensee's failure to address in the Fire Probabilistic Risk Assessment (Fire PRA) the risk contribution associated with all potentially risk significant fire scenarios for a given fire compartme
Region: II | Browns Ferry | 3688 | 08/12/2016 09/26/2016 | 2016011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Identify and Evaluate All Circuit Failures for NSCA Credited Equipment |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The NRC identified a violation of 10 CFR 50.48(c) for the licensee's failure to properly identify circuits required for the nuclear safety function. Specifically, the licensee's Nuclear Safety Capability Assessment (NSCA) failed to identify that fire-in
Region: II | Browns Ferry | 3707 | 07/31/2016 02/08/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Reassembly Procedure for HPCI Steam Line Inboard Isolation Valve Actuator |  | H.8 Procedure Adherence | TE?: N | 05000259 Browns Ferry 1 |  | 71111.15 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings " was identified for the licensee's failure to provide sufficient detail, in this case, appropriate to the work activity in proc
Region: II | Browns Ferry | 3675 | 06/30/2016 08/11/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Failure to Provide Adequate Maintenance Results in Loss of Core Flow While Shutdown |  | H.7 Documentation | TE?: N | 05000296 Browns Ferry 3 |  | 71111.19 | A self-revealing, finding associated with the licensee's failure to provide adequate work instructions for performing maintenance on the discharge valves for 3A and 3B Recirculation Pump motors. This resulted in three consecutive pump trips and a complete
Region: II | Browns Ferry | 3676 | 06/30/2016 08/11/2016 | 2016002-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Declare Notification of Unusual Event |  | H.8 Procedure Adherence | TE?: N | 05000296 Browns Ferry 3 |  | 71114.05 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50.54(q)(2), when the licensee failed to declare a Notification of Unusual Event (NOUE) within 15 minutes of entry conditions being met. Specif
Region: II | Browns Ferry | 3684 | 04/15/2016 05/25/2016 | 2016010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include Required Gasket Replacement in Limit Switch Surveillance Procedure |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.21N | An NRC-identified non-cited violation (NCV) of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to include vendor requirements for maintaining the environ
Region: II | Browns Ferry | 3664 | 03/31/2016 05/13/2016 | 2016001-01 | NRC | FIN | Mitigating Systems | Green | Unacceptable Preconditioning of RCIC Valve Prior to ASME In-Service Testing |  | H.13 Consistent Process | TE?: N | 05000260 Browns Ferry 2 |  | 71111.22 | An NRC identified finding (FIN) for failure to meet TVA procedure NETP-116.3, "Inservice Testing Program Preconditioning Guidelines," because unacceptable preconditioning of the Unit 2 Reactor Core Isolation Cooling (RCIC) steam supply valve occurred prio
Region: II | Browns Ferry | 3665 | 03/31/2016 05/13/2016 | 2016001-02 | NRC | NCV | Emergency Preparedness | Green | Failure to adequately maintain emergency plan implementing procedures |  | P.2 Evaluation | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71114.06 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50.54(q)(2), for the licensee's failure to maintain the effectiveness of its emergency plan by ensuring procedures for use by the emergency re
Region: II | Browns Ferry | 3668 | 03/31/2016 05/13/2016 | 2016001-03 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area |  | H.8 Procedure Adherence | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | A self-revealing, Non-cited Violation (NCV) of Technical Specification (TS) 5.7.1, was identified for a worker who entered a High Radiation Area (HRA) without proper authorization. Specifically, the worker entered a posted HRA located outside the Radwaste
Region: II | Browns Ferry | 3669 | 03/31/2016 05/13/2016 | 2016001-04 | NRC | NCV | Occupational Radiation Safety | Green | Unposted High Radiation Areas |  | H.8 Procedure Adherence | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.01 | A self-revealing, NCV of 10 CFR 20.1902(b), with two examples, was identified for the failure to post multiple HRAs. Specifically, areas within the Unit 2 (U2) Control Rod Drive Rebuild Room and U2 Reactor Water Cleanup Holding Pump Room contained dose ra
Region: II | Browns Ferry | 3670 | 03/31/2016 05/13/2016 | 2016001-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Include the Correct Proper Shipping Name on Radioactive Material Shipping Papers |  | H.9 Training | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.08 | The inspectors identified a NCV of 10 CFR 71.5 for the failure to include the correct Proper Shipping Name (PSN) on radioactive material shipping papers in accordance with the requirements of Department of Transportation (DOT) regulation 49 CFR 172.202. T
Region: II | Browns Ferry | 3671 | 03/31/2016 05/13/2016 | 2016001-06 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Applicable Technical Specification Action Statement for a PCIV |  | H.9 Training | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | . An NRC identified non-cited violation (NCV) of Technical Specification (TS) 5.4.1, Procedures, for the licensee's failure to implement OPDP-8, Operability Determinations and LCO Tracking. Specifically, the licensee failed to track the applicability of c
Region: II | Browns Ferry | 3678 | 02/25/2016 03/25/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Conditions Adverse to QUality Associated with RHRSW Room Flood Barriers |  | H.14 Conservative Bias | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152B | An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to promptly identify conditions adverse to quality associated with deficient flood barrier penetrations in
Region: II | Browns Ferry | 3643 | 12/31/2015 02/12/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Assess and Manage Risk During Planned Maintenance Activities |  | H.4 Teamwork | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.13 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50.65(a)(4) was identified for the licensee's failure to properly assess and manage the risk associated with performing maintenance on the Standby Gas Treatment (SBGT) system piping . Specifically,
Region: II | Browns Ferry | 3645 | 12/31/2015 02/12/2016 | 2015004-04 | NRC | NCV | Mitigating Systems | Green | Failure of 2A RHR Pump to Start from the Control Room due to a Loose Fastener |  | H.8 Procedure Adherence | TE?: N | 05000260 Browns Ferry 2 |  | NONE | A self-revealing NCV of TS 5.4.1.a was identified for the licensee's failure to use appropriate maintenance procedures to ensure appropriate system start functions worked after maintenance activities on the 2A Residual Heat Removal (RHR) Pump breaker. Spe
Region: II | Browns Ferry | 3646 | 12/31/2015 02/12/2016 | 2015004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain The Design Packing Features of the Unit 2 HPCI Turbine Steam Admission Valve |  | H.13 Consistent Process | TE?: N | 05000260 Browns Ferry 2 05000260 Browns Ferry 2 |  | 71111.15 | A self-revealing Non-Cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control was identified for the licensee's failure to properly install the Unit 2 High Pressure Coolant Injection (HPCI) turbine steam admission valve packing a
Region: II | Browns Ferry | 3653 | 12/31/2015 02/12/2016 | 2015004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Significant Steam Leak on the Unit 2 HPCI Turbine Steam Admission Valve |  | P.3 Resolution | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A self-revealing Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Actions, was identified for the licensee's failure to take corrective action following the discovery of a significant steam leak from the packing gland of
Region: II | Browns Ferry | 3654 | 12/18/2015 02/01/2016 | 2015007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Specify Adequate Instrument Ranges for MSIV Leakage Testing |  | P.1 Identification | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.21M | A NRC identified NCV of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XI, "Test Control," was identified for the failure to specify adequate test instrumentation for performing MSIV leak rate testing. Specifically, the licensee tes
Region: II | Browns Ferry | 3655 | 12/18/2015 02/01/2016 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to develop a PM schedule that specified inspection of the EDG neutral grounding resistor |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.21M | A NRC-identified non-cited violation (NCV) of Technical Specifications (TS) 5.4.1 was identified for the failure to develop a preventive maintenance (PM) schedule that specified inspection of the Emergency Diesel Generators (EDG) neutral grounding resi
Region: II | Browns Ferry | 3662 | 09/30/2015 11/09/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify a Condition Adverse to Quality Associated with HPCI Turbine Exhaust System |  | P.2 Evaluation | TE?: N | 05000296 Browns Ferry 3 |  | 71152 | Green. An NRC identified NCV of 10 CFR Part 50, Appendix B, Criterion XVI was identified for the licensee's failure to establish measures to promptly identify a condition adverse to quality involving the malfunction of the High Pressure Coolant Injectio
Region: II | Browns Ferry | 3620 | 03/31/2015 05/12/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide Adequate Acceptance Criteria for ECCS Venting Surveillance |  | H.11 Challenge the Unknown | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.04S | Green. An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identifed for the licensee's failure to maintain adequate procedure acceptance criteria and cautions to verify ope
Region: II | Browns Ferry | 3621 | 03/31/2015 05/12/2015 | 2015001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to have Simulator Fidelity with D EDG Control Switch |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 71111.11Q | Green. A Self Revealing NCV of 10 CFR 55.46(c)(1), "Simulation Facilities," was identified because the licensee failed to demonstrate simulator fidelity associated with D EDG control switch. The licensee's immediate corrective actions were to replace the
Region: II | Browns Ferry | 3622 | 03/31/2015 05/12/2015 | 2015001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain an Operating Procedure Resulted in the D EDG Exceeding its Technical Specification Allowed Outage Time |  | H.1 Resources | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 71111.15 | Green. A Self Revealing NCV of 10 CFR Part 50 Appendix B, Criterion V "Instructions, Procedures, and Drawings" was identified for the licensee's failure to maintain an adequate operating procedure for the D Emergency Diesel Generator (EDG) that resulted i
Region: II | Browns Ferry | 3623 | 03/31/2015 05/12/2015 | 2015001-04 | NRC | NCV | Barrier Integrity | Green | Failure to Satisfy TS LCO 3.6.1.3 |  | P.1 Identification | TE?: N | 05000296 Browns Ferry 3 |  | 71111.15 | Green. An NRC identified NCV of Technical Specification Limiting Condition of Operation (TS LCO) 3.6.1.3 was identified for the licensee's failure to satisfy the TS LCO. Specifically, the licensee failed to satisfy the LCO in two instances because two tra
Region: II | Browns Ferry | 3624 | 03/31/2015 05/12/2015 | 2015001-05 | NRC | NCVIV | MISC | Green | Failure to Reflect Changes to Facility and Procedures in Final Safety Analysis Report Periodic Revisions |  |  | TE?: Y SL-IV-NCVIV | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.18 | Severity Level IV. An NRC identified non-cited violation (NCV) of 10 CFR 50.71(e)(4) was identified for the licensee's failure to reflect all changes made in the facility or procedures as described in the Final Safety Analysis Report (FSAR) up to a maximu
Region: II | Browns Ferry | 3625 | 03/31/2015 05/12/2015 | 2015001-06 | NRC | NCVIV | MISC | Green | Failure to Report Condition Prohibited by Technical Specifications |  |  | TE?: Y SL-IV-NCVIV | 05000296 Browns Ferry 3 |  | 71152 | Severity Level IV. An NRC identified non-cited violation (NCV) of 10 CFR 50.73(a)(2)(i)(B) was identified for the licensee's failure to report, within 60 days of discovery, a condition which was prohibited by the plant's Technical Specifications (TS). Spe
Region: II | Browns Ferry | 3618 | 12/31/2014 02/11/2015 | 2014005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Required Continued Monitoring of a Degraded Condition |  | P.2 Evaluation | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.06 | . The NRC identified a finding (FIN) associated with the licensee's failure to evaluate continued operation for an established and growing crack in the "A" Residual Heat Removal Service Water (RHRSW) pump room floor. The licensee failed to provide justifi
Region: II | Browns Ferry | 3619 | 12/31/2014 02/11/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Satisfactory Performance of the Automatic Depressurization System Air Accumulators |  |  | TE?: N | 05000259 Browns Ferry 1 |  | 71111.19 | A self revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XI, Test Control, was identified for the licensee's failure to correctly demonstrate that Unit 1 Automatic Depressurization System (ADS) valve 1-PCV-1-19 would perform satisfac
Region: II | Browns Ferry | 3608 | 09/30/2014 10/30/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain Fire Doors in their Rated Configuration (Section 1R05) |  | P.4 Trending | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05Q | The NRC identified a Green non-cited violation (NCV) of Browns Ferry Operating License Conditions 2.C for the licensee's failure to maintain fire doors in their rated configuration required by the Fire Protection Report. Specifically, the licensee failed
Region: II | Browns Ferry | 3615 | 09/30/2014 10/30/2014 | 2014004-03 | NRC | NCV | Mitigating Systems | Green | TRM Allowances for Electric Board Room Air Conditioning Units conflicting with Technical Specifications (Section 1R15.1) |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | The NRC identified a Severity Level IV (SL-IV) NCV of 10 CFR 50.90, "Application for amendment of license, construction permit, or early site permit," and an associated Green NCV of Technical Specification (TS) 3.8.7 "Distribution System - Operating" for
Region: II | Browns Ferry | 3616 | 09/30/2014 10/30/2014 | 2014004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate NPSH Calculations for Standby Liquid Control Pumps (Section 1R15.2) |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | The NRC identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to maintain adequate control measures for verifying or checking the adequacy of design of the Standby Liquid Co
Region: II | Browns Ferry | 3607 | 06/30/2014 07/30/2014 | 2014003-01 | NRC | FIN | Mitigating Systems | Green | RHRSW pump power cables submerged in water |  | P.3 Resolution | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.06 | An NRC-identified finding was identified for the licensee's failure to adhere to TVA General Specification 40 (G-40) for Installation, Modification, and Maintenance of Electrical Systems, section 3.5.7, which required standing water in Handholes be kept b
Region: II | Browns Ferry | 3593 | 03/31/2014 04/30/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | Failure to perform MSIV as-found leakage test under suitable conditions | EA Case: 2014005 | H.7 Documentation | TE?: N | 05000296 Browns Ferry 3 |  | 71111.15 | An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XI, "Test Control," was identified for the licensee's failure to establish adequate written procedures for the test program to determine MSIV as-found leakage that met the req
Region: II | Browns Ferry | 3594 | 03/31/2014 04/30/2014 | 2014002-04 | NRC | NCV | Mitigating Systems | Green | Failure to control transient combustible in designated high risk areas | EA Case: 2014005 | H.3 Change Management | TE?: N | 05000259 Browns Ferry 1 05000296 Browns Ferry 3 |  | 71152 | An NRC-identified non-cited violation (NCV) of the T.S. 5.4.1.d, Fire Protection Program Implementation, was identified for the licensee's failure to control transient combustible materials in designated high risk areas in Unit 1 and Unit 3. The licensee'
Region: II | Browns Ferry | 3606 | 02/28/2014 04/10/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify the root cause of the failure of the 1B standby liquid control pump breaker |  | P.2 Evaluation | TE?: N | 05000259 Browns Ferry 1 |  | NONE | An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to adequately identify the root cause for a significant condition adverse to quality as defined in NPG-S
Region: II | Browns Ferry | 3595 | 12/31/2013 02/14/2014 | 2013005-01 | NRC | NCV | Initiating Events | Green | Failure to document service water freeze protection deficiencies | EA Case: 2014005 | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.01 | The NRC identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Procedures, for the licensee's failure to implement 0-GOI-200-1, Freeze Protection Inspection. Specifically, the licensee failed to enter freeze protection discrepancies
Region: II | Browns Ferry | 3604 | 12/31/2013 02/14/2014 | 2013005-05 | NRC | NCV | Mitigating Systems | Green | Failure to maintain emergency diesel room floor drains | EA Case: 2014005 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152 | The NRC-identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to establish measures to ensure the EDG floor drains maintained the capability of performing their intended function as desc
Region: II | Browns Ferry | 3586 | 11/08/2013 12/19/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate compensatory actions to minimize the effects of impaired fire proteciton equipment on fire safe shutdown |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of Browns Ferry Nuclear Plant (BFN) Unit Nos. 1, 2, and 3 Technical Specification 5.4.1.d for the failure to establish procedural guidance to implement compensatory measures for the high pressure
Region: II | Browns Ferry | 3587 | 11/08/2013 12/19/2013 | 2013010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate evaluation of combustible material control fire protection program change |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The inspectors identified a Severity Level IV, non-cited violation (NCV) of Browns Ferry Nuclear Plant (BFN) Renewed Facility Operating License Conditions 2.C.(13), (14), and (7) for Units 1, 2, and 3, respectively, and an associated finding of very low s
Region: II | Browns Ferry | 3588 | 11/08/2013 12/19/2013 | 2013010-03 | NRC | NCV | Mitigating Systems | Green | Failure to meet the requirements of large fire and explosion mitigation strategies |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of Browns Ferry Nuclear Plant (BFN) Units 1, 2 and 3, Renewed Operating License Conditions 2.C(4)(b)(7), 2.C(6)(b)(7) and 2.C(10)(b)(7) respectively, for the licensee's failure to meet the requir
Region: II | Browns Ferry | 3582 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to enter Technical Specification for residual heat removal service water maintenance | EA Case: 2013235 | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.13 | The NRC identified a non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.a, Procedures, for the licensee's failure to follow OPDP-8, Operability Determination Process and Limiting Conditions for Operation Tracking. Specifically, the licensee
Region: II | Browns Ferry | 3273 | 09/30/2013 11/14/2013 | 2013004-02 | NRC | FIN | Mitigating Systems | Green | Failure to clean the safety related pump pit once per two cycles |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | An NRC identified finding (FIN) was identified for the licensee's exceeding the maximum allowed periodicity for inspecting and cleaning the Residual Heat Removal Service Water (RHRSW) pump pit per Raw Water Corrosion Program procedure (NPG-SPP 9.7.3).
Region: II | Browns Ferry | 1743 | 09/30/2013 11/14/2013 | 2013004-03 | NRC | FIN | Initiating Events | Green | Failure to properly screen and classify corrective action program, problem evaluation reports |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | The NRC identified a Green finding for the licensee's failure to properly screen and classify corrective action program (CAP) problem evaluation reports (PER's) in accordance with NPG-SPP-03.1.4, Corrective Action Program Screening and Oversight. Specific
Region: II | Browns Ferry | 3579 | 06/30/2013 08/14/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to perform post maintenance testing on the 2E 480V RMOV board |  | H.3(b) Work Activity Coordination | TE?: N | 05000260 Browns Ferry 2 05000260 Browns Ferry 2 |  | 71153 | A self-revealing non-cited violation (NCV) of Technical Specifications 3.5.1, Emergency Core Cooling Systems (ECCS) and Reactor Core Isolation Cooling (RCIC) System was identified associated with the licensee's failure to perform a post maintenance test (
Region: II | Browns Ferry | 3302 | 06/04/2013 06/25/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to verify the capability of HPCI to achieve required flow and pressure within 30 seconds under accident conditions |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to ensure that post-maintenance and post-modification testing of the high pressure cooling injection (HPCI) pump adequately demonstra
Region: II | Browns Ferry | 3303 | 06/04/2013 06/25/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate the effects of the fialure of non-class 1 load center transformer cooling fans on the class 1 4160-480V load center transformers and 480V shutdown boards |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," involving the failure to evaluate the effects of a postulated failure of the load center transformer non-safety-related, non-Class 1E cooling fans, whi
Region: II | Browns Ferry | 3304 | 06/04/2013 06/25/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to use worst case 4160 VAC bus voltage in desgin calculations |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to perform analyses demonstrating that the degraded voltage relay (DVR) set points specified in technical specifications (TS) w
Region: II | Browns Ferry | 3311 | 06/04/2013 06/25/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to adequately identify, evaluate, and correct the EECW strainers degraded/non-conforming condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and take corrective actions to address a non-conforming condition adverse to quality related to three
Region: II | Browns Ferry | 3313 | 05/24/2013 08/22/2013 | 2013011-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform evaluation of non-conforming material during commercial grade dedication of safety-related bearings |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion III, Design Control in that the licensee did not adequately evaluate a commercial grade dedication (CGD) of bearings prior to installing the bearings in a safety-rela
Region: II | Browns Ferry | 3536 | 05/24/2013 08/22/2013 | 2013011-02 | NRC | NCV | Mitigating Systems | Green | Failure to follow procedure during implementation of plant modifications to the residual heat removal and core spray systems |  | H.3(b) Work Activity Coordination | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings for the licensee's failure to maintain effective configuration control as required by Procedure NPG-SPP-09.3, Rev. 13, "Plant Mod
Region: II | Browns Ferry | 3537 | 05/24/2013 08/22/2013 | 2013011-03 | NRC | NCV | Barrier Integrity | Green | Failure to perform 10 CFR 50.59 evaluation intergranular stress corrosion cracking examination on ASME code class 1 piping weld |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000260 Browns Ferry 2 |  | 95003 | The team identified a Severity Level IV non-cited violation of 10 CFR 50.59, Changes, Tests, and Experiments, for the licensee's failure to perform an evaluation of a change to the facility as described in the Updated Final Safety Analysis Report (UFSAR)
Region: II | Browns Ferry | 3538 | 05/24/2013 08/22/2013 | 2013011-04 | Self - Revealed | NCV | Mitigating Systems | Green | Two BFN assistant unit operators closed and danger tagged the A1 RHRSW pump manual discharge valve instead of the required A2 RHRSW pump discharge valve |  | H.4(a) Human Error Prevention | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green, self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures." The team determined that BFN's clearance and tagging application related to the planned A2 residual heat removal service water (RHRS
Region: II | Browns Ferry | 3539 | 05/24/2013 08/22/2013 | 2013011-05 | NRC | NCV | Mitigating Systems | Green | Maintenance personnel not following clearance procedure violation |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures." The team determined that the maintenance Primary Authorized Employee (PAE) did not verify that all blocking points were danger tagged to ensure work
Region: II | Browns Ferry | 3540 | 05/24/2013 08/22/2013 | 2013011-06 | NRC | NCV | Mitigating Systems | Green | Conduct of operations procedure violation |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 95003 | The team identified a Green, non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures." The team determined that assistant unit operators' (AUOs) failure to comply with Procedure OPDP-1, Rev. 26, "Conduct of Operations," Sections 4.2 K
Region: II | Browns Ferry | 3541 | 05/24/2013 08/22/2013 | 2013011-07 | NRC | NCV | Mitigating Systems | Green | Failure to adequately implement procedure 3-SR-3.3.8.2.1(B) |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a non-cited violation of Technical Specification (TS) 5.4.1, which requires written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33, Revision 2, Appendix A, dated Febru
Region: II | Browns Ferry | 3545 | 05/24/2013 08/22/2013 | 2013011-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to manage emergent risk condition during A1 and A2 RHRSW inoperability |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a self-revealing, Green non-cited violation (NCV) of 10 CFR 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," due to BFN's failure to adequately manage the impact of an emergent risk
Region: II | Browns Ferry | 3546 | 05/24/2013 08/22/2013 | 2013011-09 | NRC | NCV | Barrier Integrity | Green | Failure to control a modification to the seismically mounted control room ceiling ligh diffusers |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green, NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to control deviations from the as built control room envelope design for seismically mounted ceilin
Region: II | Browns Ferry | 3557 | 05/24/2013 08/22/2013 | 2013011-10 | NRC | NCV | Mitigating Systems | Green | Requirements for concurrent verification, independent verification and peer checks |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green, non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures." The team determined that BFN's Requirements for Concurrent Verification, Independent Verification, and Peer Checks were not consistently applied to
Region: II | Browns Ferry | 3558 | 05/24/2013 08/22/2013 | 2013011-11 | NRC | NCV | Initiating Events | Green | Inadequate corrective actions to address programmatic procedure quality issue |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," due to BFNs failure to take corrective action to preclude repetition of a significant condition adverse to quality regarding procedure quality.
Region: II | Browns Ferry | 3559 | 05/24/2013 08/22/2013 | 2013011-12 | NRC | NCV | Mitigating Systems | Green | Deficient acceptance criteria for main battery bank 1 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 |  | 95003 | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, for the licensee's failure to incorporate appropriate quantitative acceptance criteria into a station battery inspection Procedure. Specifically,
Region: II | Browns Ferry | 3565 | 05/24/2013 08/22/2013 | 2013011-13 | NRC | NCV | Mitigating Systems | Green | Failure to translate the design into procedure 3-SR-3.3.8.2.1(B) |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate seismic uncertainties into acceptance criteria and measuring and test equipment accuracy requirements i
Region: II | Browns Ferry | 3566 | 05/24/2013 08/22/2013 | 2013011-14 | NRC | NCV | Mitigating Systems | Green | Failure to implement an adequate test program for RHRSWS and EECS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a non-cited violation of 10CFR50, Appendix B, Criterion XI, Test Control, because the licensee did not establish a test program for Residual Heat Removal Service Water (RHRSW) and Emergency Equipment Cooling Water (EECW) pumps such tha
Region: II | Browns Ferry | 3567 | 05/24/2013 08/22/2013 | 2013011-15 | NRC | NCV | Mitigating Systems | Green | Deficient design control for RHR service water freeze protection |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, involving the failure to maintain adequate design control measures associated with the residual heat remove service water (RHRSW) system freeze p
Region: II | Browns Ferry | 3577 | 05/24/2013 08/22/2013 | 2013011-16 | NRC | NCV | Initiating Events | Green | Failure to establish qualified ultrasonic examination procedures |  | P.2(b) Implementing Operating Experience | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 95003 | The team identified a NCV of 10 CFR 50, Appendix B, Criterion IX, Control of Special Processes for the licensee's failure to control non-destructive examination (NDE) activities by not having qualified NDE procedures required by applicable codes, standard
Region: II | Browns Ferry | 3291 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement preventive maintenance program |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | A self-revealing Apparent Violation (AV) of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to establish an adequate preventive maintenance program as required by procedure NPG-SPP-06.2,
Region: II | Browns Ferry | 3281 | 09/30/2012 11/13/2012 | 2012004-01 | NRC | NCV | Emergency Preparedness | Green | Loss of seismic monitoring capability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.54(q)(2) for the licensee's failure to follow and maintain an emergency plan that meets the requirements of emergency planning standard 10 CFR 50.47(b)(4). Specifically, due to a plant mod
Region: II | Browns Ferry | 3282 | 09/30/2012 11/13/2012 | 2012004-02 | Self - Revealed | FIN | Initiating Events | Green | Automatic reactor scram due to inadequate design review of relay setting |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to provide an adequate design review of vendor calculations as required by TVA-NQA-PLN89-A, Nuclear Quality Assurance Plan which resulted in the 3A Unit Station Service Transformer (
Region: II | Browns Ferry | 3290 | 09/30/2012 11/13/2012 | 2012004-03 | Self - Revealed | FIN | Initiating Events | Green | Automatic reactor scram due to inadequate testing of current transformer |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to adequately test a Unit 3 main turbine generator current transformer (CT) as required by TVA-NQA-PLN89-A, Nuclear Quality Assurance Plan which resulted in the improper wiring of th
Region: II | Browns Ferry | 3274 | 06/30/2012 08/14/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain flood barrier results in inoperable safety related pumps |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.15 | An NRC-identified non-cited violation (NCV) of the Technical Specifications 5.4.1.a was identified for the licensee's failure to maintain an Emergency Equipment Cooling Water (EECW) pump flood barrier in accordance with written procedures which resulted i
Region: II | Browns Ferry | 3275 | 06/30/2012 08/14/2012 | 2012003-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to properly prepare a DOT type A package for transport |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.08 | A self-revealing non-cited violation (NCV) of 10 CFR 71.5, Transportation of Licensed Material, was identified by inspectors for the licensee's failure to comply with Department of Transportation (DOT) regulations during shipment of radioactive materials.
Region: II | Browns Ferry | 3276 | 06/30/2012 08/14/2012 | 2012003-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to implement DOT type A package closure requirements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71124.08 | A self-revealing non-cited violation (NCV) of 10 CFR 71.5, Transportation of Licensed Material, was identified by inspectors for the licensee's failure to comply with Department of Transportation (DOT) regulations during shipment of radioactive materials.
Region: II | Browns Ferry | 3280 | 06/30/2012 08/14/2012 | 2012003-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to establish preventive maintenance for Unit 2 and 3 main control room annunciator power supplies |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to perform preventive maintenance on the Unit 3 Main Control Room (MCR) annunciator power supplies. As a result, a power supply failed which led to a fire in annunciator panel 3-X-55
Region: II | Browns Ferry | 3262 | 05/14/2012 05/28/2012 | 2012007-01 | NRC | FIN | Mitigating Systems | Green | Failure to follow NRC commitment management procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a Green finding (FIN) for the licensee's failure to follow procedure NPG-SPP-03.3, Rev.001, "NRC Commitment Management." Specifically, the procedure states, in part, that each responsible organization ensures commitment implement
Region: II | Browns Ferry | 3263 | 05/14/2012 05/28/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to establish adequate compensatory measures for non-conforming fire barriers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a Green NCV of Browns Ferry Operating License Conditions 2.C(13), 2.C(14) and 2.C(7), for Units 1, 2, and 3, respectively, for the licensee's failure to establish adequate compensatory measures for non-conforming fire barriers,
Region: II | Browns Ferry | 3269 | 05/14/2012 05/28/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Failure to implement appropriate safe shutdown instructions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a Green non-cited violation of 10 CFR 50 Appendix B, Criteria XVI, Corrective Action, for the licensee's failure to assure conditions adverse to quality associated with the establishment and implementation of four new Safe Shutdo
Region: II | Browns Ferry | 3270 | 05/14/2012 05/28/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct appropriate safe shutdown instructions |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish procedures appropriate to the circumstances for combating plant fires. Specifically, four new Safe Sh
Region: II | Browns Ferry | 3238 | 03/31/2012 04/29/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequatley implement impaired fire barrier and detector controls |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05Q | The NRC identified a non-cited violation of Technical Specification 5.4.1.d, Fire Protection Program, for the licensee's failure to adequately implement Limiting Conditions For Operation in accordance with Fire Protection Report Volume 1, Fire Protection
Region: II | Browns Ferry | 3239 | 03/31/2012 04/29/2012 | 2012002-02 | NRC | NCV | Initiating Events | Green | Failure to immediately report a plant fire |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71153 | The NRC identified a non-cited violation of Technical Specification 5.4.1.d, Fire Protection Program implementation associated with the licensee's failure to report a fire in the Unit 1 Turbine Building to the main control room (MCR). Specifically, the fa
Region: II | Browns Ferry | 3240 | 03/31/2012 04/29/2012 | 2012002-03 | NRC | NCV | Barrier Integrity | Green | Failure to ensure ECCS design calculation does not exceed maximum clad tempoerature |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The NRC identified a Green non-cited violation of 10CFR 50.46, Acceptance criteria for emergency core cooling systems for light-water nuclear power reactors, for the licensee's failure to ensure that the ECCS was satisfactorily designed such that the maxi
Region: II | Browns Ferry | 3236 | 12/31/2011 02/13/2012 | 2011005-02 | Self - Revealed | FIN | Barrier Integrity | Green | Unit 1 TS 3.0.3 entry caused by the failure of RPS M-G set 1B |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to adequately evaluate historically high vibrations on the Unit 1 Reactor Protection System (RPS) Motor Generator (M-G) Set 1B. Consequently, the impact of high vibrations was not co
Region: II | Browns Ferry | 3237 | 12/31/2011 02/13/2012 | 2011005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to control temporary equipment resulted in a fire |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71153 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures and Drawings was identified for the licensee's failure to install and maintain adequate control of temporary lighting in the intake cable tunnel as require
Region: II | Browns Ferry | 3261 | 12/30/2011 02/28/2012 | 2011012-01 | NRC | NCV | Mitigating Systems | Green | Degraded electrolytic capacitor test results not entered into corrective action program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The team identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for the failure to promptly identify and correct a condition adverse to quality relat
Region: II | Browns Ferry | 3242 | 10/03/2011 11/17/2011 | 2011011-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement requirements of the inservice testing program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a NCV of very low safety significance for the licensee's failure to implement a procedure required by Technical Specification (TS) 5.5.6, Inservice Testing Program. Specifically, inspectors determined that TVA did not adequately
Region: II | Browns Ferry | 3252 | 10/03/2011 11/17/2011 | 2011011-02 | NRC | NCV | Mitigating Systems | Green | Failure to reestablish motor operated valve design basis capability after performing modifications to the valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50.55a(b)(3)(ii), for the licensee's failure to adequately reestablish the design basis capability of multiple Motor Operated Valves (MOV
Region: II | Browns Ferry | 3253 | 10/03/2011 11/17/2011 | 2011011-03 | NRC | NCV | Mitigating Systems | Green | Inadequate funcional evaluations performed to support operability of overthrust motor operated valves |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000259 Browns Ferry 1 |  | NONE | The inspectors identified an NCV of very low safety significance involving the licensee's failure to implement a procedure as required by 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The inspectors determined that TVA faile
Region: II | Browns Ferry | 3232 | 09/30/2011 11/14/2011 | 2011004-01 | NRC | NCV | Initiating Events | Green | Failure to control transient conmbustible materials in the Unit 1 reactor building |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 |  | 71111.05Q | A NRC-identified non-cited violation of the Technical Specifications 5.4.1.d, Fire Protection Program Implementation, was identified for the licensee's failure to control transient combustible materials in a designated exclusion area between Fire Zones 1-
Region: II | Browns Ferry | 3234 | 09/30/2011 11/14/2011 | 2011004-03 | Self - Revealed | NCV | Initiating Events | Green | Unit 1 loss of shutdown cooling caused by emergency diesel generator output breaker trip |  | P.3(a) Self-Assessment | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | A self-revealing non-cited violation of Technical Specifications 5.4.1.a was identified for the licensee's failure to establish an adequate maintenance procedure to ensure appropriate calibration and alignment of the Emergency Diesel Generator (EDG) overs
Region: II | Browns Ferry | 3235 | 09/30/2011 11/14/2011 | 2011004-04 | Self - Revealed | NCV | Initiating Events | Green | Unit 3 loss of shutdown cooling during primary containment isolation system relay replacement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing non-cited violation of Technical Specifications 5.4.1.a was identified for the licensee's failure to establish adequate work order instructions for maintenance activities on CR120A relays associated with the Unit 3 Primary Containment Iso
Region: II | Browns Ferry | 3229 | 06/30/2011 08/08/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to take corrective actions to preclude a repetitive functional failure of an EDG due to excessive heat exchanger fouling |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.07A | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to take prompt corrective actions to preclude repetition of a significant condition adverse to quality (SCAQ) that r
Region: II | Browns Ferry | 3230 | 06/30/2011 08/08/2011 | 2011003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Over-pressurization of high pressure coolant injection system due to stuck open HPCI system testable check valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 |  | 71111.15 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criteria XVI, Corrective Action, was identified for the licensee's failure to promptly correct a condition adverse to quality related to Unit 1 High Pressure Coolant Injection (HPCI) system tes
Region: II | Browns Ferry | 3222 | 03/31/2011 05/13/2011 | 2011002-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of reactor water level during Unit 2 reactor reassembly due to a mispositioned valve |  | H.3(b) Work Activity Coordination | TE?: N | 05000260 Browns Ferry 2 |  | 71111.2 | A self-revealing non-cited violation of Technical Specifications (TS) 5.4.1.a was identified for the licensee's failure to adequately implement operations instruction 2-OI-74, Residual Heat Removal System, to ensure the reactor cavity draindown flow path
Region: II | Browns Ferry | 3224 | 03/31/2011 05/13/2011 | 2011002-02 | NRC | NCV | Initiating Events | Green | Inadequate corrective actions to address Unit 3 CR120A PCIS relays taht exceeded their recommended service life |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000296 Browns Ferry 3 |  | 71152 | An NRC identified non-cited violation of 10 CFR 50 Appendix B, Criteria XVI, Corrective Action, was identified for the licensee's failure to correct a condition adverse to quality related to Unit 3 primary containment isolation system (PCIS) logic relays
Region: II | Browns Ferry | 3225 | 03/31/2011 05/13/2011 | 2011002-03 | NRC | NCV | Barrier Integrity | Green | Inadequate TS 5.5.2 program for primary coolant leaks outside containment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152 | An NRC identified non-cited violation of Technical Specifications (TS) 5.5.2, Primary Coolant Sources Outside Containment was identified for the licensee's failure to establish, implement, and maintain an adequate program for minimizing primary coolant le
Region: II | Browns Ferry | 3226 | 03/31/2011 05/13/2011 | 2011002-04 | NRC | FIN | Initiating Events | Green | Failure to identify adverse trend resulted in reactor scram |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to adequately evaluate and take the required actions established by site standards to address an adverse system performance trend that had degraded below acceptable levels associated
Region: II | Browns Ferry | 3218 | 12/31/2010 02/09/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Degraded 1C RHR motor rendered one RHR sybsystem inoperable beyond the TS allowed outage time |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 |  | 71111.2 | -Green. A self-revealing non-cited violation (NCV) of Unit 1 Technical Specifications (TS) Limiting Condition for Operations (LCO) 3.6.2.3, Suppression Pool Cooling was identified for the licensee's failure to correct a degraded condition of the 1C Residu
Region: II | Browns Ferry | 3192 | 09/30/2010 10/29/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately assess online risk associated with maintenance activities on risk significant SSCs |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50.65 (a)(4), for inadequate risk assessments of on-line risk associated with ongoing maintenance activities. Specifically, on July 21 and then again on September 16, 2010, the inspectors foun
Region: II | Browns Ferry | 3202 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Initiating Events | Green | Failure to adequately test molded case circuit breakers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to establish a preventive maintenance (PM) test program for safety-related molded case circuit breakers (MCCBs) to demonstrate these b
Region: II | Browns Ferry | 3203 | 09/30/2010 10/29/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Failure to perform functional evaluations for gas identified during venting |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | An NRC-identified Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to perform functional evaluations in accordance with procedure NEDP-22, Functional
Region: II | Browns Ferry | 3204 | 09/24/2010 11/08/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure To Correct The EECW Valves Throttled Below Analyzed Condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000260 Browns Ferry 2 |  | 71152B | Green: The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to adequately evaluate and take prompt corrective actions to address a condition adverse to quality related to
Region: II | Browns Ferry | 3205 | 09/24/2010 11/08/2010 | 2010006-02 | NRC | FIN | Initiating Events | Green | Failure to Implement the Provisions of Preventative Maintenance (PM) Program Which Contributed to a Manual Reactor Scram |  | H.4(b) Procedural Compliance | TE?: N | 05000296 Browns Ferry 3 |  | 71152B | Green: The inspectors identified a finding for the licensee's failure to implement the applicable provisions of the Tennessee Valley Authority (TVA) Preventative Maintenance (PM) Program to replace the coil in the solenoid valve controlling the opening of
Region: II | Browns Ferry | 3206 | 09/24/2010 11/08/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with the 2D Residual Heat Removal (RHR) Room Cooler (Section 40A2.a.3.3) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000260 Browns Ferry 2 |  | 71152B | Green: The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to correct a condition adverse to quality by failing to implement adequate corrective actions to address degradat
Region: II | Browns Ferry | 3207 | 09/24/2010 11/08/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated Cooling Water Flow Degradation in the 1B Core Spray Room Cooler (Section 40A2.a.3.4) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 |  | 71152B | Green: The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to correct a condition adverse to quality and implement adequate corrective actions for the degraded 1B Core Spra
Region: II | Browns Ferry | 3215 | 09/24/2010 11/08/2010 | 2010006-05 | NRC | NCV | Mitigating Systems | Green | Failure to maintain an Adequate Surveillance Procedure to Prevent an Unplanned HPCI Isolation (Section 40A2.a.3.5) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000260 Browns Ferry 2 |  | 71152B | Green: The inspectors identified a self-revealing non-cited violation of Technical Specifications 5.4.1.a, Procedures, for an inadequate surveillance procedure used to test High Pressure Coolant Injection (HPCI) pressure switches that led to an unplanned
Region: II | Browns Ferry | 3216 | 09/24/2010 11/08/2010 | 2010006-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure for Siemens Horizontal Vacuum Circuit Breakers Circuit Breakers (Section 40A2.a.3.6) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000296 Browns Ferry 3 |  | 71152B | Green: The inspectors identified a non-cited violation of Technical Specification (TS) 5.4.1for the licensee's failure to have adequate preventative maintenance procedures for Siemens Horizontal Vacuum Circuit Breakers. Plant procedure EPI-0-000-BKR015, 4
Region: II | Browns Ferry | 3188 | 06/30/2010 10/29/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Use of Waivers to Exceed 10 CFR 26 Work Hour Limitations |  | H.4(b) Procedural Compliance | TE?: N | 05000296 Browns Ferry 3 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR 26.207(a) for improper execution of the waiver process for authorizing waivers of the "72 hours in any seven day period" work hour limitation required by 10 CFR 26.205(d), for contractors performing
Region: II | Browns Ferry | 3189 | 06/30/2010 10/29/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 3 RCIC System Inoperable Beyond the Technical Specifications Allowed Outage Time |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A self-revealing non-cited violation of Unit 3 Technical Specifications (TS) Limiting Condition for Operation 3.5.3, Reactor Core Isolation Cooling (RCIC) System, was identified for the licensee's failure to comply with the TS required actions for an inop
Region: II | Browns Ferry | 3163 | 03/31/2010 04/30/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to effectively maintain performance of the A3 EECW pump as required by 10 CFR |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2) for failure to demonstrate that the performance of the A3 Emergency Equipment Cooling Water (EECW) pump was effectively controlled by preventive maintenance (PM) such that the pump remai
Region: II | Browns Ferry | 3164 | 03/31/2010 04/30/2010 | 2010002-02 | NRC | NCV | Barrier Integrity | Green | New fuel receipt inspection and refueling operations supervised by non-qualified senior reactor operators |  | H.4(b) Procedural Compliance | TE?: N | 05000296 Browns Ferry 3 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specifications 5.4.1.a for the failure to comply with operating procedures for Unit 3 new fuel receipt inspection and refueling operations that required the Fuel Handling Supervisor (FHS) to be t
Region: II | Browns Ferry | 3165 | 03/31/2010 04/30/2010 | 2010002-03 | NRC | NCV | Initiating Events | Green | Operators failed to correctly monitor and assess RPV beltline temperatures during RPV hydrostatic/in-service leak test |  | H.4(a) Human Error Prevention | TE?: N | 05000296 Browns Ferry 3 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specifications (TS) 5.4.1.a for failure to follow surveillance procedure 3-SR-3.4.9.1(2), Reactor Vessel Shell Temperature and Reactor Coolant Pressure Monitoring during In-service Hydrostatic Le
Region: II | Browns Ferry | 3169 | 03/31/2010 04/30/2010 | 2010002-04 | NRC | NCV | Initiating Events | Green | Inadequate surveillance procedure to ensure all releveant RPV metal temperatures were monitored during RPV hydrostatic/in-service leak testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000296 Browns Ferry 3 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specifications (TS) 5.4.1.a for failure to establish an adequate surveillance procedure to ensure all relevant reactor pressure vessel (RPV) metal temperatures of all four RPV regions were being
Region: II | Browns Ferry | 3170 | 03/31/2010 04/30/2010 | 2010002-05 | NRC | NCV | Mitigating Systems | Green | Untimely corrective actions to restore compliance of EECW pump in-service testing with ASME OM code requirements |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to promptly recognize, and then correct in a timely manner, non-conforming conditions involving the in-service testing (IST) requirement
Region: II | Browns Ferry | 3142 | 12/31/2009 02/02/2010 | 2009005-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Operating Procedures Cause Partial Loss of Reactor Feedwater Which Results In Unit 2 Manual Reactor Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A Green self-revealing noncited violation of Technical Specifications 5.4.1.a was identified for failure to adequately maintain the accuracy of critical operating procedures for Power Maneuvering, and Reactor Feedwater (RFW) and Condensate System operatio
Region: II | Browns Ferry | 3143 | 12/31/2009 02/02/2010 | 2009005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 RCIC System Inoperable Beyond the Technical Specification Allowed Outage Time |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A Green self-revealing non-cited violation of Unit 2 Technical Specifications (TS) Limiting Condition for Operation 3.5.3, Reactor Core Isolation Cooling (RCIC) System, was identified for the licensee's failure to comply with the TS required actions for a
Region: II | Browns Ferry | 3185 | 12/28/2009 02/09/2010 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Violation of Technical Specification 5.4.1 for Failure to Develop Adequate Procedures to Ensure Tornado Depressurization Protection of the Emergency Diesel Generators |  | P.2(b) Implementing Operating Experience | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The inspectors identified a Green non-cited violation (NCV) of TS 5.4.1 for the failure to have an adequate procedure that would ensure tornado depressurization protection of the emergency diesel generators (EDGs). Abnormal Operating Instruction, 0-AOI-10
Region: II | Browns Ferry | 3186 | 12/28/2009 02/09/2010 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Violation of 10CFR50, Appendix B, Criterion V for Inadequate Procedure for Emergency Equipment Cooling Water System Flow Balancing |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to provide adequate guidance in existing procedures utilized for flow balancing of the emergency e
Region: II | Browns Ferry | 3144 | 10/09/2009 01/20/2010 | 2009009-01 | NRC | NCV | Mitigating Systems | Green | Deficiencies with Emergency Lighting Units |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The team identified a Green non-cited violation of Browns Ferry Units 1, 2, and 3 Operating License Conditions 2.C(13), 2.C(14), and 2.C(7), respectively, for the licensee's failure to maintain in effect all provisions of the NRC-approved fire protection
Region: II | Browns Ferry | 3148 | 10/09/2009 01/20/2010 | 2009009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Compensatory measures for an Out-of-Service Hose Station |  | H.3(a) Work Planning | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The team identified a Green non-cited violation of Browns Ferry Units 1, 2, and 3 Operating License Conditions 2.C(13), 2.C(14), and 2.C(7), respectively, for the licensee's failure to maintain in effect all provisions of the NRC-approved fire protection
Region: II | Browns Ferry | 3127 | 07/17/2009 08/21/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Standby Gas Treatment Subsystem 'A' Inoperable Beyond the Technical Specification Allowed Outage Time (Section 4OA2.a) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71152B | -Green. A Green, self-revealing, non-cited violation (NCV) of Technical Specification (TS) limiting condition for operation (LCO) 3.6.4.3, "Standby Gas Treatment (SGT) System", was identified for the licensee's failure to comply with the LCO required acti
Region: II | Browns Ferry | 3114 | 06/30/2009 07/30/2009 | 2009003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to assess and manage shutdown risk associated with outage activities |  | H.3(b) Work Activity Coordination | TE?: N | 05000260 Browns Ferry 2 |  | 71111.13 | A Green self-revealing noncited violation of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified for failure to adequately assess and manage shutdown risk associated with mainten
Region: II | Browns Ferry | 3115 | 06/30/2009 07/30/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Failure to perform an adequate risk assessment during severe weather conditions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 |  | 71111.13 | A Green non-cited violation of 10 CFR Part 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified when the licensee failed to consider the impact of severe weather conditions on plant risk. Spe
Region: II | Browns Ferry | 3116 | 06/30/2009 07/30/2009 | 2009003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to comply with the requirements of an RWP by entering a posted high radiation area |  | H.4(a) Human Error Prevention | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7112101 | A Green self-revealing non-cited violation (NCV) of TS 5.4.1, Procedures, was identified for a radiation worker who failed to follow the requirements of RWP 09270081 as required by procedure RCI 9.1, Radiation Work Permits, Rev. 57. The licensee has enter
Region: II | Browns Ferry | 3126 | 06/30/2009 07/30/2009 | 2009003-05 | NRC | FIN | Initiating Events | Green | Untimely actions to resolve excessive IBC system condensation results in U1 reactor scram |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 |  | 71152 | A Green self-revealing finding was identified for a failure to implement corrective actions in a timely manner to address excessive isophase bus cooling system condensation that resulted in a Unit 1 reactor scram caused by water accumulation in the isopha
Region: II | Browns Ferry | 2899 | 03/21/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Procedure Causes Loss of Unit 1 RHR System Safety Function (Section 1R22) Inadequate Surveillance Procedure Causes Loss of Unit 1 RHR System Safety Function |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 |  | 71111.22 | Green. A self-revealing non-cited violation of Technical Specification 5.4.1, "Procedures", was identified for an incorrect Unit 1 surveillance procedure that instructed technicians to install a jumper in the wrong location which resulted in the inadverte
Region: II | Browns Ferry | 2897 | 12/31/2008 01/30/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Requalification Examination Integrity |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR 55.49 for engaging in an activity that compromised, or would have compromised but for detection by the inspectors, the integrity of examinations required by 10 CFR 55.59 that were administered in 2
Region: II | Browns Ferry | 3106 | 10/28/2008 04/30/2009 | 2009002-03 | Self - Revealed | NCV | Initiating Events | Green | Unit 1 RPV Flange Leak Due To Lack of Prompt Identification and Resolution |  |  | TE?: N | 05000259 Browns Ferry 1 |  | 71152 | Green. A Green self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI was identified for not promptly identifying and correcting a condition adverse to quality associated with steam cuts and/or defects in the Unit 1 reactor pressure ve
Region: II | Browns Ferry | 2895 | 10/24/2008 12/22/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify an Adverse Trend for Vibration-induced, Failed or Degraded Unit 2 and 3 RHR Hx SW Outlet FCVs |  | P.1(b) Trend Performance CAP | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | An NRC-identified, Green, non-cited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," was identified for the licensee's failure, between April 2000 and January 2008, to carry out the Nuclear Quality Assurance Plan policy in th
Region: II | Browns Ferry | 3107 | 10/04/2008 04/30/2009 | 2009002-04 | Self - Revealed | FIN | Initiating Events | Green | Main Generator Voltage Regulator Relay Failure Results in Unit 2 Reactor Scram |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | Green. A Green self-revealing finding was identified for inadequate design control and replacement of the 43A relay in the Unit 2 main generator voltage regulator control circuit that resulted in a reactor scram due to a main turbine generator trip from a
Region: II | Browns Ferry | 2889 | 06/30/2008 08/07/2008 | 2008003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post, Barricade, and Control Access to a High Radiation Area During Power Ascension |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 |  | 7112101 | A Green, self-revealing non-cited violation of Technical Specification (TS) 5.7.1 was identified for the licensee's failure to conspicuously post, barricade, and control access to a high radiation area (HRA) with dose rates not exceeding 1.0 rem per hour
Region: II | Browns Ferry | 2892 | 06/30/2008 08/07/2008 | 2008003-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Secure Stored Radioactive Material from Unauthorized Removal |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7112203 | A Green, self-revealing non-cited violation of 10 CFR 20.1801 was identified for the licensee's failure to secure stored radioactive material from unauthorized removal. On August 14, 2007, a shipment of "clean" scrap metal from Browns Ferry alarmed the tr
Region: II | Browns Ferry | 2888 | 06/30/2008 08/07/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Deficiencies in Degraded Flood Protection Doors |  | H.4(b) Procedural Compliance | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to identify and correct deficiencies in watertight doors that protect the safety-related Residual Heat Removal Service Wa
Region: II | Browns Ferry | 2893 | 05/02/2008 05/30/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | NCV withdrawn by letter dated Jan. 20, 2009 (Failure to prevent recurrence of stem-to-disc separation events in residual heat removal service water heat exchanger outlet valves) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000260 Browns Ferry 2 |  | 93812 | THIS NON-CITED VIOLATION HAS BEEN WITHDRAWN (LETTER JAN. 20, 2009) The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, for the licensee's failure in March, 2000, to take action to preclude repetition of stem-t
Region: II | Browns Ferry | 2884 | 12/31/2007 01/30/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | Untimely Corrective Actions To Resolve Leaking Recirculation Flow Transmitter Fitting Resulted In Unit 1 Reactor Scram |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion XVI, for untimely corrective actions to ensure that repairs were initiated to correct the Unit 1 Recirculation System flow transmitter fitting 1-FT-68-81B prior to th
Region: II | Browns Ferry | 2885 | 12/31/2007 01/30/2008 | 2007005-02 | NRC | FIN | Initiating Events | Green | Unisolable EHC Leak Due To Fretting From Missing Pipe Support Isolator Blocks Caused Unit 1 Reactor Scram |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | A Green self-revealing finding was identified for inadequate pre-startup walkdowns of the Unit 1 Electro-Hydraulic Control (EHC) system that failed to identify critical pipe support components were missing from an EHC line which directly resulted in a man
Region: II | Browns Ferry | 2886 | 12/31/2007 01/30/2008 | 2007005-03 | NRC | FIN | Initiating Events | Green | Untimely Corrective Actions To Resolve Moisture Separator Level Switch Vulnerabilities Resulted In Unit 1 Reactor Scram |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | A Green self-revealing finding was identified for incomplete and untimely corrective actions that allowed for a repeat Unit 1 turbine trip and reactor scram due to previously identified oversized moisture separator high level dump valves. The stems of the
Region: II | Browns Ferry | 2887 | 12/31/2007 01/30/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions To Ensure Sufficient Alternate Shutdown Cooling Flow During Appendix R Events |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71153 | The inspectors identified a Green noncited violation of Unit 2 License Condition 2.C (14), and Unit 3 License Condition 2.C (7), Fire Protection Report, Appendix R Safe Shutdown Program, for failing to establish the required compensatory measures to provi
Region: II | Browns Ferry | 2881 | 12/14/2007 01/25/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform ASME Inspections of Safety-Related Piping. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The inspectors identified a Green non-cited violation of 10 CFR 50.55a(g)4 Codes and Standards. Specifically, the licensee failed to perform required code inspections of accessible portions of safety-related piping. The licensee entered this issue into th
Region: II | Browns Ferry | 2882 | 12/14/2007 01/25/2008 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Corrective Actions for Cable Submersion Were Not Effective. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7111121 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee failed to correct a cable submergence issue which resulted in the failure of a safety-related cable. This findi
Region: II | Browns Ferry | 2877 | 10/09/2007 10/09/2007 | 2007008-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Recognize an Inoperable RCIC Steam Flow Isolation Instrument |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 |  | 71152B | A green self-revealing non-cited violation (NCV) of Technical Specification (TS) 3.3.6.1 was identified for failing to recognize an inoperable Reactor Core Isolation Cooling (RCIC) steam flow isolation instrument resulting in exceeding the TS allowed out
Region: II | Browns Ferry | 2874 | 09/30/2007 10/30/2007 | 2007004-01 | Self - Revealed | FIN | Initiating Events | Green | Unisolable Electro-hydraulic Control System Leak Due To Improperly Installed Compression Fitting Causes Unit 1 Reactor Scram |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | Green. A Green self-revealing finding was identified for poor work practices and inadequate licensee oversight. This allowed for the improper installation of a critical compression fitting on the Unit 1 Electro-Hydraulic Control (EHC) system that caused a
Region: II | Browns Ferry | 2875 | 09/30/2007 10/30/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Reactor Trip Function on Turbine Stop Valve Closure Not Enabled at 30% Rated Thermal Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | Green. A Green self-revealing noncited violation of Unit 1 Technical Specifications (TS) 3.3.1.1 and Table 3.3.1.1-1, Reactor Protection System Instrumentation, Function 8, Turbine Stop Valve Closure and Function 9, Turbine Control Valve Fast Closure - Tr
Region: II | Browns Ferry | 2876 | 09/30/2007 10/30/2007 | 2007004-03 | Self - Revealed | FIN | Initiating Events | Green | Moisture Separator Level Control System Failure Due To Improperly Installed Compression Fitting Causes Unit 1 Reactor Scram |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000259 Browns Ferry 1 |  | 71153 | Green. A Green self-revealing finding was identified for poor work practices and inadequate oversight that allowed for the improper installation of a critical compression fitting on the Feedwater Heater and Moisture Separator Level Control panel that caus
Region: II | Browns Ferry | 2864 | 06/30/2007 07/30/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Online Risk Assessment of Unit 2 Startup With All Three RFPs Out of Service (Section 1R13) |  | H.3(a) Work Planning | TE?: N | 05000260 Browns Ferry 2 |  | 71111.13 | Green. The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(4) for the licensee's failure to conduct an adequate risk assessment prior to and during the startup of Unit 2 with all three reactor feedwater pumps (RFP) uncoupled and out o
Region: II | Browns Ferry | 2871 | 06/30/2007 07/30/2007 | 2007003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Non-Conservative APRM/LPRM Gain Settings Result in Neutron Flux Setdown Setpoint in Excess of TS Limit (Section 1R15) |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 |  | 71111.15 | Green. A self-revealing Green noncited violation was identified for a violation of Unit 1 Technical Specifications 3.3.1.1.A.1 and Table 3.3.1.1-1, Function 2a, Reactor Protection System Instrumentation, on two separate occasions when Unit 1 entered Mode
Region: II | Browns Ferry | 2872 | 06/30/2007 07/30/2007 | 2007003-04 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Instructions For Isolating Condensate Demineralizer System Causes a Unit 3 Reactor Scram (Section 4OA3.5) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | Green. A Green self-revealing finding was identified for use of an inadequate work order instructions during an online modification of the Unit 3 Condensate Demineralizer System control logic that caused an inadvertent isolation of condensate flow which d
Region: II | Browns Ferry | 2873 | 06/30/2007 07/30/2007 | 2007003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow the Freeze Seal Procedure and Procedural Inadequacy (Section 4OA5.3) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | Green. The inspectors identified a Green noncited violation of 10CFR50, Appendix B, Criterion V, for inadequate procedure and failure to follow quality-related procedure MSI-0-000-PLG001, Installation of Freeze Seals, while installing a freeze seal on the
Region: II | Browns Ferry | 2847 | 03/31/2007 04/30/2007 | 2007002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Two Examples of Failure to Perform Adequate Surveys. |  | H.3(b) Work Activity Coordination | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 |  | 7112101 | Two examples of a Green self-revealing non-cited violation of 10 CFR 20.1501(a)(2)(i) were identified for failure to conduct surveys that were reasonable under the circumstances to evaluate the magnitude and extent of radiation levels in areas where work
Region: II | Browns Ferry | 2848 | 03/31/2007 04/30/2007 | 2007002-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Properly Prepare a Radioactive Materials Package for Shipment |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 7112202 | A Green self-revealing non-cited violation of 10 CFR 71.5 was identified for failure to properly package radiological material such that, under conditions normally incident to transportation, the radiation levels at the external surface of the package wou
Region: II | Browns Ferry | 2849 | 03/31/2007 04/30/2007 | 2007002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Resolve Deficiencies in SBO Mitigation Capabilities |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000260 Browns Ferry 2 |  | 71152 | The inspectors identified a Green non-cited violation of 10CFR50, Appendix B, Criterion XVI, for ineffective corrective actions by the licensee to ensure that the operating emergency diesel generators (EDGs) during a Unit 2 Station Blackout (SBO) event wo
Region: II | Browns Ferry | 2854 | 03/31/2007 04/30/2007 | 2007002-05 | NRC | NCV | MISC | Green | Work Hours for I&C Mechanics Exceeded Overtime Limits Without Prior Authorization |  |  | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a Green non-cited violation of Technical Specification 5.2.2.d due to inadequate management oversight and awareness of the administrative requirements for controlling overtime which resulted in multiple instances of Instrumentati
Region: II | Browns Ferry | 2855 | 03/31/2007 04/30/2007 | 2007002-06 | NRC | NCV | Barrier Integrity | Green | Operation of Unit 2 Outside the Limits Allowed by the Power-Flow Map |  | H.4(b) Procedural Compliance | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | The inspectors identified a Green non-cited violation of TS 5.4.1.a for the operators' failure to maintain Unit 2 core flow within the bounds of the Core Power/Flow Map established by operating procedures. When notified, the licensee promptly reduced reac
Region: II | Browns Ferry | 2838 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Lack of Assured Cooling Water for Emergency Diesel Generators During SBO Conditions |  |  | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | NONE | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, that affected Units 2 and 3. The licensee's calculations and procedures did not adequately implement the plant's licensing basis for Station Bla
Region: II | Browns Ferry | 2834 | 09/15/2006 10/30/2006 | 2006014-02 | NRC | NCV | Mitigating Systems | Green | Safe Shutdown Instruction Directs Operators to Connect 4 KV SD BD "A" to a Potentially Fire-Induced Fault in FA 8 |  |  | TE?: N | 05000260 Browns Ferry 2 |  | 71111.05T | The team identified a non-cited violation (NCV) of Unit 2 Operating License Condition 2.C.14 for an inadequate Safe Shutdown Instruction (SSI) which directed the operator to align credited 4 kV Shutdown Board (SD BD) "A" to its alternate supply (Shutdown
Region: II | Browns Ferry | 2835 | 09/15/2006 10/30/2006 | 2006014-04 | NRC | NCV | Mitigating Systems | Green | Cellular Phone Communications Unreliable for Alternate Shutdown in FA16 |  |  | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05T | The team identified a non-cited violation (NCV) of Unit 2 Operating License Condition 2.C.14 and Unit 3 Operating License Condition 2.C.7 for failure to have adequate communications to implement alternate shutdown for a fire in fire area (FA) 16 using pro
Region: II | Browns Ferry | 2818 | 06/30/2006 07/25/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Required Fire Watches |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71111.05Q | A Green non-cited violation of TS 5.4.1.d, Fire Protection Program Implementation, was identified by the inspectors for the licensee's failure to implement compensatory measures (i.e., roving fire watches) as prescribed by the Browns Ferry Fire Protection
Region: II | Browns Ferry | 2821 | 06/30/2006 07/25/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | Ineffective Maintenance To Ensure Performance Of Unit 3 Drywell Equipment Hatch 1A To Fulfill Its Maintenance Rule Function |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000296 Browns Ferry 3 |  | 71111.12 | A Green non-cited violation of 10 CFR 50.65(a)(2) was identified by the inspectors due to the licensee's failure to maintain effective control of the Unit 3 Drywell Equipment Hatch 1A leak tightness through their preventative maintenance program, and thei
Region: II | Browns Ferry | 2822 | 06/30/2006 07/25/2006 | 2006003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Primary Containment Leak Via The 2A RHR Heat Exchanger In Excess Of Analyzed Limits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A Green self-revealing non-cited violation of TS 3.6.1.1 was identified due to the licensee's failure to adequately evaluate the significance of a leak from the Unit 2 2A Residual Heat Removal heat exchanger that would have constituted a direct pathway fr
Region: II | Browns Ferry | 2823 | 06/30/2006 07/25/2006 | 2006003-04 | Self - Revealed | FIN | Initiating Events | Green | Improper Return To Service of 500 KV Trinity Transmission Line Results in Unit 3 Reactor Scram |  |  | TE?: N | 05000296 Browns Ferry 3 |  | 71153 | A Green self-revealing finding was identified for failure to correctly implement an offsite switching order by transmission system personnel that resulted in a Unit 3 reactor scram. This issue was documented in the licensee's corrective action program as
Region: II | Browns Ferry | 2814 | 03/31/2006 04/28/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform An Adequate Risk Assessment |  |  | TE?: N | 05000260 Browns Ferry 2 |  | 71111.13 | A Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified by the inspectors for the licensee's failure to conduct an adequate risk assessment of the Unit 2 systems, and Unit 3 systems affecting Unit 2, that were taken out of service for sched
Region: II | Browns Ferry | 2816 | 03/31/2006 04/28/2006 | 2006002-03 | Self - Revealed | FIN | Initiating Events | Green | Poor Workmanship and Inadequate Work Instructions for Maintenance on the 2C Reactor Feedwater Pump That Resulted in a Reactor Scram |  |  | TE?: N | 05000260 Browns Ferry 2 |  | 71153 | A Green self-revealing Finding (FIN) was identified for inadequate work instructions and poor work practices associated with maintenance on the 2C reactor feedwater pump that resulted in a Unit 2 reactor trip. This issue was documented in the licensee's c
Region: II | Browns Ferry | 125485 | 08/12/2019 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71114.04
Region: II | Browns Ferry | 126590 | 12/18/2019 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation |  |  | TE?: N | 05000259 Browns Ferry 1 05000260 Browns Ferry 2 05000296 Browns Ferry 3 |  | 71130.05
Region: II | Brunswick | 125809 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain the Effectiveness of the Emergency Plan |  | H.3 - Change Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 | Procedure Quality | 71114.04 | The inspectors determined that the licensee’s failure to maintain their Emergency Plan was a performance deficiency. Specifically, from May 2004 to July 2018, the licensee failed to maintain the correct site-specific delta-T value used in their dose asses
Region: II | Brunswick | 125717 | 09/13/2019 10/16/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Size and Evaluate the Acceptability of MOV Thermal Overloads |  | NPP | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 | Design Control | 71111.21M | The team identified a Green finding and associated Non-cited Violation (NCV) of Title 10 of the Code of Federal Regulations Part 50 (10 CFR 50), Appendix B, Criterion III, "Design Control," for the licensee's failure to translate design basis MOV requirem
Region: II | Brunswick | 125721 | 09/13/2019 10/16/2019 | 2019011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Calculation Control Process |  | H.3 - Change Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.21M | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of Title 10 of the Code of Federal Regulations Part 50 (10 CFR 50), Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow t
Region: II | Brunswick | 125487 | 06/30/2019 08/09/2019 | 2019002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Start of the No. 1 Emergency Diesel Generator (EDG) |  | H.5 - Work Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 | Configuration Control | 71111.13 | A self-revealed Green NCV of TS 5.4.1a, was identified for the licensee’s failure to implement the procedural guidance associated with maintenance on the No. 1 emergency diesel generator (EDG-1).
Region: II | Brunswick | 124787 | 06/30/2019 08/09/2019 | 2019002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to periodically calibrate radiation monitoring equipment. |  | H.3 - Change Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71124.05 | The inspectors identified a Green NCV of 10 CFR 20.1501(c) for failure to periodically calibrate area radiation monitoring equipment used to perform dose rate measurements. Specifically, on or around July 13, 2017, the licensee discontinued periodic calib
Region: II | Brunswick | 125190 | 06/30/2019 08/09/2019 | 2019002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Resulted in Inoperable Safety Relief Valves |  | H.1 - Resources | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 | Equipment Performance | 71153 | A self-revealed Green non-cited violation (NCV) of TS 3.4.3, “Safety/Relief Valves (SRVs)”, was identified when the licensee discovered two of the 11 safety relief valves (SRVs) as-found lift set points were outside of the +/- 3 percent pressure band requ
Region: II | Brunswick | 125490 | 06/30/2019 08/09/2019 | 2019002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Unit 1 Reactor Coolant System Leak Due to Reference Leg Failure |  | NPP | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 | Design Control | 71153 | A self-revealed Green NCV of 10CFR50 Appendix B, Criterion III, design control, was identified for the licensee’s failure to adequately address material incompatibilities of Titanium-Nickel (TiNi) couplings located in a hydrogen environment.
Region: II | Brunswick | 124476 | 03/31/2019 05/14/2019 | 2019001-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Instruction Used to Perform Vessel Nozzle Flushing |  | H.5 - Work Management | TE?: N | 05000324 Brunswick 2 | Configuration Control | 71111.2 | A self-revealing Green NCV of TS 5.4.1a, Procedures, was identified for the licensee’s failure to implement adequate work instructions for flushing the reactor pressure vessel (RPV) nozzles on Unit 2, which resulted in a temporary loss of shutdown cooling
Region: II | Brunswick | 124886 | 03/31/2019 05/14/2019 | 2019001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Spent Fuel Pool Cooling Due to the Failure to Evaluate Risk of a Maintenance Activity |  | H.12 - Avoid Complacency | TE?: N | 05000325 Brunswick 1 | Human Performance | 71111.2 | A self-revealed Green NCV of 10 CFR 50.65(a)(4) was identified for the licensee’s failure to adequately evaluate the risk of a maintenance activity.
Region: II | Brunswick | 24098 | 06/30/2018 07/23/2018 | 2018002-01 | Self - Revealed | FIN | Initiating Events | Green | Automatic Reactor Trip due to Perceived Loss of Stator Cooling Water |  | H.3 - Change Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing Green finding (FIN) was identified for the failure to properly implement a modification to the turbine control system (TCS). The modification ultimately resulted in an automatic reactor trip on April 7, 2018, due to a turbine trip caused
Region: II | Brunswick | 24051 | 05/10/2018 10/02/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Justify Qualified Life Extension of ASCO Solenoid Operated Valves |  | NPP | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.21N | The NRC identified a Green finding and associated non-cited violation of 10 CFR 50.49(e)(5) for the licensee’s failure to justify life extensions of ASCO solenoid operated valves (SOVs). The inspectors identified two examples where the licensee did not ju
Region: II | Brunswick | 24052 | 05/10/2018 10/02/2018 | 2018011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Effects of MOV Space Heaters on Qualified Life |  | NPP | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.21N | The NRC identified a Green finding and associated non-cited violation of 10 CFR 50.49(e)(5) for the licensee’s failure to evaluate the effects of additional heat rise on the qualified life of Limitorque controls. The failure to address the degrading
Region: II | Brunswick | 23946 | 03/31/2018 05/02/2018 | 2018001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Instruction to Perform Inspections on Emergency Ventilation Dampers |  | H.5 - Work Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing Green NCV of TS 5.4.1a, Procedures, was identified when the licensee failed to properly provide adequate work instructions associated with the control room emergency damper inspections. Specifically, the licensee disconnected the damper a
Region: II | Brunswick | 23216 | 12/31/2017 01/29/2018 | 2017004-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of Emergency 4160V Bus Due to Failure to Implement Procedure |  | H.8 - Procedure Adherence | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing non-cited violation (NCV) was identified for the licensee’s failure to properly transfer power to the E-4 4160 volt emergency bus from the E-4 emergency diesel generator (EDG), to the normal switchgear bus 2C, as required by procedure 0OP
Region: II | Brunswick | 6715 | 05/26/2017 07/06/2017 | 2017009-01 | NRC | NCV | Mitigating Systems | Green | Inoperability of EDG1 due to Cyclic Fatigue Failure of Hydraulic Fuel Rack Control |  |  | TE?: N | 05000325 Brunswick 1 |  | NONE | A self-revealing Green non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion XVI, "Corrective Actions," was identified on February 19, 2017, when emergency diesel generator (EDG) number one was determined to be inoperable due to an oil leak on the l
Region: II | Brunswick | 6697 | 03/31/2017 05/05/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Nonfunctional Sprinklers in the Service Water Building Without Compensatory Measures |  | H.2 Field Presence | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of License Condition 2.B.(6), Fire Protection Program, was identified for the licensee's failure to implement compensatory measures for nonfunctional sprinklers. Specifically, from January 11, 2017, until
Region: II | Brunswick | 6698 | 03/31/2017 05/05/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control a Temporary Fire Ignition Source Near the Unit 2 Standby Liquid Control Pump Motor and Cables |  | H.4 Teamwork | TE?: N | 05000324 Brunswick 2 |  | 71111.05Q | An NRC-identified Green NCV of License Condition 2.B.(6), Fire Protection Program, was identified for the licensee's failure to adequately control fire ignition sources in the Unit 2 standby liquid control (SLC) pump area in accordance with licensee proce
Region: II | Brunswick | 6709 | 03/31/2017 05/05/2017 | 2017001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Install Flood Barrier Seals Around the EDG 2 Four-Day Fuel Oil Tank Vents |  | H.6 Design Margins | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.18 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the failure of the licensee to install flood barrier seals around the emergency diesel generator (EDG) 2, four-day fuel oil tank vent as described
Region: II | Brunswick | 6710 | 03/31/2017 05/05/2017 | 2017001-04 | NRC | NCV | Barrier Integrity | Green | Failure to Enter the Technical Specification for an Inoperable 1D Control Room Air Conditioning Unit |  | P.3 Resolution | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | An NRC-identified Green NCV of Technical Specification (TS) 3.7.4, Control Room Air Conditioning (AC) System, was identified for the failure to declare the 1D control room AC unit inoperable. Specifically, on December 1, 2016, the licensee failed to decla
Region: II | Brunswick | 6711 | 02/17/2017 03/28/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Nonfunctional Fire Door |  | P.2 Evaluation | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.05XT | The NRC identified a Green non-cited violation (NCV) of Brunswick Operating License Condition (OLC) 2.B(6) for Units 1 and 2, for the licensee's failure to correct a nonfunctional fire door in the diesel generator (DG) building. Specifically, on three occ
Region: II | Brunswick | 6680 | 09/30/2016 11/09/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions during Elevated Risk |  | H.8 Procedure Adherence | TE?: N | 05000324 Brunswick 2 |  | 71111.13 | An NRC-identified Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified for the failure of the licensee to implement all necessary prescribed risk management actions (RMAs) during a 2A residual heat removal (RHR) and residual heat removal s
Region: II | Brunswick | 6681 | 09/30/2016 11/09/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure to Perform Preventive Maintenance on the HPCI Auxiliary Oil Pump Motor Overload Relay |  | H.5 Work Management | TE?: N | 05000324 Brunswick 2 |  | 71111.15 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1a, Procedures, was identified for the failure of the licensee to have an adequate procedure for preventive maintenance (PM) on the Unit 2 high pressure coolant injection (HPCI) auxiliary oil
Region: II | Brunswick | 6684 | 09/30/2016 11/09/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for the 2B RHRSW Subsystem Operability Test |  | H.11 Challenge the Unknown | TE?: N | 05000324 Brunswick 2 |  | 71111.22 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure of the licensee to have an adequate procedure for the 2B RHRSW pump operability test. Specifically, from July 12,
Region: II | Brunswick | 6674 | 06/30/2016 08/11/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identity Broken Auto Start Control Relay on Emergency Diesel Generator 1 |  | P.1 Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.15 | An NRC-identified Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified because the licensee failed to promptly identify and correct a condition adverse to quality (CAQ) on emergency diesel generat
Region: II | Brunswick | 6679 | 06/30/2016 08/11/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify or Check the Adequacy of Design of the EDG 3 Auto-Start Circuitry |  | P.1 Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.19 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to verify or check the adequacy of design of the EDG 3 emergency auto-start circuitry. Specifically, on October 24, 2011, th
Region: II | Brunswick | 6673 | 05/31/2016 07/13/2016 | 2016008-01 | NRC | FIN | Initiating Events | Green | Inadequate Procedures to Perform Maintenance on the SAT Non-segregated Bus and the 1B RRP VFD Cables |  | H.12 Avoid Complacency | TE?: N | 05000325 Brunswick 1 |  | 71111.12 | A self-revealing finding with two examples was identified for the licensee's failure to have adequate procedures to perform maintenance on the startup auxiliary transformer (SAT) non-segregated bus duct and the 1B Reactor Recirculation Pump (RRP) variable
Region: II | Brunswick | 6672 | 03/31/2016 04/28/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct 2B NSW Pump Strainer Drag |  | P.2 Evaluation | TE?: N | 05000324 Brunswick 2 |  | 71152 | The inspectors identified a Green non-cited (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, because the licensee failed to identify and correct a condition adverse to quality associated with the 2B nuclear service water (NSW) pump s
Region: II | Brunswick | 6670 | 12/31/2015 02/01/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for the 2C RHRSW Booster Pump Motor Bearings |  | H.11 Challenge the Unknown | TE?: N | 05000324 Brunswick 2 |  | 71111.19 | A self-revealing Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure of the licensee to have an adequate procedure for the 2C residual heat removal service wate
Region: II | Brunswick | 6649 | 06/30/2015 07/31/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Barrier Seals in the Unit 2 Cable Accessway |  |  | TE?: N | 05000324 Brunswick 2 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of License Condition 2.B.(6), Fire Protection Program, was identified for the licensee's failure to maintain the 3 hour fire seals in the Unit 2 cable access way. Specifically, three cables in the Unit 2 c
Region: II | Brunswick | 6650 | 06/30/2015 07/31/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for the 1B Conventional Service Water Pump Strainer Repair |  | H.7 Documentation | TE?: N | 05000325 Brunswick 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to have an adequate procedure to perform maintenance on the 1B conventional service water (CSW) pump
Region: II | Brunswick | 6651 | 06/30/2015 07/31/2015 | 2015002-03 | NRC | FIN | Mitigating Systems | Green | Failure to Perform an Adequate Extent of Condition Review for the 1C Conventional Service Water Pump Strainer |  | P.2 Evaluation | TE?: N | 05000324 Brunswick 2 |  | 71111.19 | An NRC-identified Green finding of licensee procedure CAP-NGGC-0205, Condition Evaluation and Corrective Action Process, was identified for the licensee's failure to perform an adequate extent of condition review for the 1C CSW pump strainer stop collar c
Region: II | Brunswick | 6653 | 06/18/2015 07/26/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to Quality |  | P.2 Evaluation | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152B | An NRC-identified Green non-cited violation (NCV) of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for licensee failure to identify conditions adverse to quality during the evaluation of an
Region: II | Brunswick | 6654 | 06/18/2015 07/26/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Insufficient Material Evaluation of Commercially Dedicated Allen Bradley Relays |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152B | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control was identified for the licensee's inadequate commercial grade dedication technical evaluation that resulted in non-conforming relays being installed in the control ci
Region: II | Brunswick | 6638 | 12/31/2014 01/30/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Protect Emergency Diesel Generator 4-Day Fuel Oil Tank Ventilation Piping from Tornado Missiles |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.15 | The NRC-identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, Design Control, for the failure to ensure adequate tornado missile protection for the emergency diesel generat
Region: II | Brunswick | 6639 | 12/31/2014 01/30/2015 | 2014005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Emergency Diesel Generator No. 3 Monthly Load Test Surveillance Procedure |  | H.12 Avoid Complacency | TE?: N | 05000324 Brunswick 2 |  | 71111.22 | A Green self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure to conduct the number 3 EDG monthly load test in accordance with the prescribed technical specification surveilla
Region: II | Brunswick | 6631 | 09/30/2014 11/04/2014 | 2014004-01 | NRC | FIN | Initiating Events | Green | Inadequate Procedure to Perform Core Ground Checks on the Common Bus C Transformer |  |  | TE?: N | 05000325 Brunswick 1 |  | 71111.12 | A self-revealing Green finding of Licensee Procedure 0PM-XMR001, ITE Substation Transformers, was identified for the failure to have an adequate procedure to perform preventative maintenance on the Common Bus C 4160/480V Transformer. Specifically, between
Region: II | Brunswick | 6635 | 09/30/2014 11/04/2014 | 2014004-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Post a High Radiation Area |  | H.4 Teamwork | TE?: N | 05000324 Brunswick 2 |  | NONE | A Green self-revealing NCV of TS 5.7.1 was identified for the failure to post a high radiation area (HRA). Specifically, on September 25, 2014, the licensee failed to post the Unit 2 high pressure coolant injection (HPCI) pump room as a HRA during a HPCI
Region: II | Brunswick | 6636 | 09/30/2014 11/04/2014 | 2014004-04 | NRC | FIN | Mitigating Systems | Green | Failure to Correct SLC Tank Level Indication Degradation |  | H.5 Work Management | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | An NRC-identified Green finding of Licensee Procedure AD-PI-ALL-0100, Corrective Action Program (CAP), was identified for the failure of the licensee to identify and correct a condition adverse to quality with the Unit 2 standby liquid control (SLC) contr
Region: II | Brunswick | 6629 | 06/30/2014 08/04/2014 | 2014003-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain a Standard Emergency Action Level Scheme for Flooding |  | H.1 Resources | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.01 | An NRC-identified Green NCV of 10 CFR 50.54(q)(2), 10 CFR 50.47(b)(4), and the requirements of Appendix E to 10 CFR Part 50, was identified for the failure of the licensee to maintain the effectiveness of the emergency plan. Specifically, from November 6,
Region: II | Brunswick | 6630 | 06/30/2014 08/04/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Flood Protection Features in the Maintenance Rule Program |  | P.3 Resolution | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | An NRC-identified Green non-cited violation (NCV) of 10 CFR 50.65(b)(2)(ii) was identified for the failure of the licensee to scope flood protection features in the maintenance rule (MR) program. Specifically, from July 10, 1996, to May 8, 2014, the licen
Region: II | Brunswick | 6610 | 12/31/2013 02/04/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Required Service Water Flow to the Emergency Diesel Generators |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the failure of the licensee to verify the adequacy of design of the emergency diesel generator (EDG) service water flow. Specifically, from May 1,
Region: II | Brunswick | 6618 | 12/31/2013 02/04/2014 | 2013005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure to Perform Preventative Maintenance on the Residual Heat Removal Room Coolers |  |  | TE?: N | 05000325 Brunswick 1 |  | 71111.19 | A self-revealing Green NCV of TS 5.4.1a, Procedures, was identified for the failure of the licensee to have an adequate procedure for preventative maintenance on the 1B residual heat removal (RHR) room cooler damper limit switch. Specifically, between May
Region: II | Brunswick | 6619 | 12/31/2013 03/21/2014 | 2013010-01 | NRC | VIO | Mitigating Systems | Green | Failure to Identify and Correct Flood Protection Degradation in Safety-Related Buildings | EA Case: 2014048 | H.2 Field Presence | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.01 | The NRC identified an AV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, with two examples. The first example involved the failure of the licensee to promptly identify and correct conditions adverse to quality associated with flood protec
Region: II | Brunswick | 6622 | 12/31/2013 03/21/2014 | 2013010-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Procedures for Inspecting Flood Protection Doors and Performing Functionality Assessments |  | H.7 Documentation | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.01 | An NRC-identified Green finding for the failure to meet the requirements of licensee procedure PRO-NGGC-0201, NGG Procedure Writer's Guide, was identified with two examples. Specifically, the licensee failed to provide an adequate procedure with appropria
Region: II | Brunswick | 6623 | 12/31/2013 03/21/2014 | 2013010-03 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Functionality Assessments for flood Protection Features |  | H.8 Procedure Adherence | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.01 | An NRC-identified Green finding was identified for the failure of the licensee to follow Procedure OPS-NGGC-1305, Operability Determinations, to perform functionality assessments for degraded or non-conforming flood protection features. Specifically, the
Region: II | Brunswick | 6600 | 10/23/2013 12/03/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for the Class 1E Station Battery Service Capacity Test Procedure |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to incorporate adequate acceptance criteria in the Class 1E station battery service test procedures. This failure to incorpor
Region: II | Brunswick | 6604 | 10/23/2013 12/03/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate DC System Calculations - Three Examples |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with three examples, for the licensee's failure to properly incorporate the design and licensing bases for the 125 volt direct current system into de
Region: II | Brunswick | 6605 | 10/23/2013 12/03/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of the Service Water Intake Structure Ventilation System |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of the service water intake structure ventilation design through calculational methods. This failur
Region: II | Brunswick | 6606 | 10/23/2013 12/03/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Safety-related Components in the Maintenance Rule Program |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.65(b)(1), for the licensee's failure to scope the safety-related service water intake structure exhaust fan dampers into the Maintenance Rule program. This failure to scope safety-related service wate
Region: II | Brunswick | 6607 | 10/23/2013 12/03/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Plant Procedure Directing the Performance of Preventive Maintenance on Safety-related Dampers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow plant procedures specifying requirements for preventive maintenance of safety-related damp
Region: II | Brunswick | 6608 | 10/23/2013 12/03/2013 | 2013007-06 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Evaluation of Vibration on 2A RHR Heat Exchanger Bypass Valve |  |  | TE?: N | 05000324 Brunswick 2 |  | 7111121 | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the licensee's failure to verify or check the adequacy of design of the Unit 2 A residual heat removal heat exchanger bypass valve 2-E1
Region: II | Brunswick | 6598 | 09/30/2013 11/13/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct nuclear service water pump shaft degradation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.15 | An NRC identified Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the failure of the licensee to identify and correct a condition adverse to quality (CAQ) on the 1B nuclear service water pump
Region: II | Brunswick | 6599 | 09/30/2013 11/13/2013 | 2013004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate preventative maintenance procedure for the service water pump breakers |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.19 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure of the licensee to have an adequate preventative maintenance procedure for the service water pump breakers. Specifical
Region: II | Brunswick | 6578 | 06/30/2013 08/08/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Have Adequate Installation and Testing Instructions for the EDG Overspeed Boost Cylinder. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure of the licensee to have adequate installation and testing instructions for the EDG control oil system overspeed boost
Region: II | Brunswick | 6579 | 06/30/2013 08/08/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Lubricate the 1B Residual Heat Removal Cooler Damper |  | H.4(b) Procedural Compliance | TE?: N | 05000325 Brunswick 1 |  | 71111.12 | -An NRC-identified Green NCV of TS 5.4.1a, Procedures, was identified for the failure of the licensee to follow the procedure to properly lubricate the 1B RHR room cooler damper The licensee lubricated the damper and returned the room cooler to operable,
Region: II | Brunswick | 6580 | 06/30/2013 08/08/2013 | 2013003-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Work Order to Perform a Modification to the Control Room Emergency Ventilation System |  | H.3(b) Work Activity Coordination | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | An NRC-identified Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified, for the licensee's failure to have an adequate instruction or procedure to perform a modification to the contro
Region: II | Brunswick | 6581 | 06/30/2013 08/08/2013 | 2013003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions during Elevated Risk |  | H.3(a) Work Planning | TE?: N | 05000324 Brunswick 2 |  | 71111.13 | -An NRC-identified Green NCV of 10 CFR 50.65(a)(4) was identified for the failure of the licensee to manage the increase in risk that resulted from the E6 bus outage. Specifically, between May 19, 2013 and May 21, 2013, the licensee did not manage the inc
Region: II | Brunswick | 6588 | 06/30/2013 08/08/2013 | 2013003-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Allowable Jacket Water Leak Rate |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the failure of the licensee to verify the adequacy of the design acceptance criteria for jacket water leakage to ensure EDG 3 could meet the design bas
Region: II | Brunswick | 6591 | 06/30/2013 08/08/2013 | 2013003-08 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Have an Adequate Procedure for Preventative Maintenance on a SCRAM Contactor Coil |  |  | TE?: N | 05000324 Brunswick 2 |  | 71111.19 | A self-revealing Green NCV of TS 5.4.1a, Procedures, was identified for the failure of the licensee to have an adequate procedure incorporating a preventative maintenance schedule which specifies inspection or replacement of the RPS coil contactor 2-C72B-
Region: II | Brunswick | 6574 | 03/31/2013 04/30/2013 | 2013002-01 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure for Variable Frequency Drive Reactor Recirculation Pump Design Modification. |  | H.3(b) Work Activity Coordination | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.18 | An NRC-identified Green finding was identified for the failure of the licensee to follow Procedure EGR-NGGC-0005, Engineering Change (EC), when performing the variable frequency drive (VFD) modification for the reactor recirculation pumps (RRPs). Specific
Region: II | Brunswick | 6571 | 12/31/2012 02/08/2013 | 2012005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure for the EDG Jacket Water Pump Wear Ring Tolerances |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.19 | -Green. A self-revealing Green NCV of Technical Specification (TS) 5.4.1a, Procedures, was identified because the licensee did not have an adequate maintenance procedure to perform work on the emergency diesel generator (EDG) 3 engine-driven jacket water
Region: II | Brunswick | 6572 | 12/31/2012 02/08/2013 | 2012005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design of EDG 2 ASSD Switch A1 |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | -Green. The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion III, Design Control, for failure to assure that the design basis for EDG 2 Alternate Safe Shutdown (ASSD) Switch A1 was correctly translated into specifications and drawings.
Region: II | Brunswick | 6573 | 12/31/2012 02/08/2013 | 2012005-05 | NRC | FIN | Initiating Events | Green | Inadequate Maintenance Procedure for Fluorescent Lights over Safety-related Equipment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 2515/188 | -Green. The inspectors identified a Green finding for the licensee not having an adequate procedure for maintenance on fluorescent lights over safety-related equipment. Specifically, between plant startup and August 29, 2012, the licensee did not have ins
Region: II | Brunswick | 6567 | 09/30/2012 11/07/2012 | 2012004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Secondary Containment Operable During an OPDRV Activity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000325 Brunswick 1 |  | 71111.2 | The inspectors identified a Green non-cited violation (NCV) of TS 3.6.4.1, Secondary Containment because the licensee did not maintain secondary containment operable as required during a maintenance activity considered an operation with a potential for dr
Region: II | Brunswick | 6568 | 09/30/2012 11/07/2012 | 2012004-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to Maintain Reliability and Availability of Emergency Response Equipment for Emergency Response Facilities |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | A self-revealing Green NCV of 10 CFR 50.54(q)(2) was identified for the licensee's failure to properly evaluate or consider the impact to emergency response facilities of design change ESR98-00436 which was implemented in 1999. This resulted in the loss o
Region: II | Brunswick | 6563 | 06/30/2012 07/30/2012 | 2012003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to follow plant procedure caused loss of E1 bus |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, Procedures, was identified when the licensee failed to follow procedure 0MST-DG11R, Diesel Generator 1 Loading Test. During the preparation for the test, procedural steps were not performed
Region: II | Brunswick | 6556 | 04/04/2012 04/23/2012 | 2012007-01 | NRC | NCV | Initiating Events | Green | Failure to Properly Assemble Reactor Vessel Head Following Maintenance Outage |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000324 Brunswick 2 |  | 71153 | A self-revealing (Green) non-cited violation (NCV) of 10 CFR 50, Appendix B Criterion V, Instructions, Procedures, and Drawings was identified for failure to properly implement plant procedures for reactor pressure vessel (RPV) reassembly following the Un
Region: II | Brunswick | 6557 | 04/04/2012 04/23/2012 | 2012007-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a Post Maintenance Test After Reactor Pressure Vessel Assembly |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000324 Brunswick 2 |  | 71153 | A self-revealing (Green) non-cited violation (NCV) of 10 CFR 50, Appendix B Criterion V, Instructions, Procedures, and Drawings was identified for failure to properly implement plant procedure 0PLP-20, Post Maintenance Testing, after reactor pressure v
Region: II | Brunswick | 6562 | 04/04/2012 04/23/2012 | 2012007-03 | NRC | NCV | Initiating Events | Green | Failure to Perform Adequate Training for Reactor Vessel Reassembly |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000324 Brunswick 2 |  | 71153 | NRC inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B Criterion V, Instructions, Procedures, and Drawings for failure to properly implement plant procedure TRN-NGGC-1000, Conduct of Training for training and qualifications o
Region: II | Brunswick | 6551 | 03/31/2012 04/26/2012 | 2012002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Refrigerant Leak in the Instrument Air Dryer System |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criteria XVI, Corrective Action, was identified for the licensee's failure to promptly identify and correct a condition adverse to quality related to the Control Room Air Conditioning (AC) syst
Region: II | Brunswick | 6544 | 12/31/2011 01/27/2012 | 2011005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Bearing Oil Level Resulted in Residual Heat Removal Service Water Pump Failure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000324 Brunswick 2 |  | 71111.12 | Green. A self-revealing Green non-cited violation of TS 5.4.1, Procedures, was identified for failure to implement procedural requirements for verifying lubrication levels on the 2B RHRSW Booster pump. This finding resulted in failure of the 2B RHRSW Boos
Region: II | Brunswick | 6538 | 09/30/2011 11/14/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Configuration Control Resulted in Rainwater Intrusion into the Unit 2 Reactor Building |  | H.3(a) Work Planning | TE?: N | 05000324 Brunswick 2 |  | 71111.06 | A self-revealing Green non-cited violation of TS 5.4.1, Procedures, was identified for failure to implement procedural requirements of the equipment configuration control program to ensure that temporary power cables routed through an open manhole and int
Region: II | Brunswick | 6539 | 09/30/2011 11/14/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Control Building Air Conditioning Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | The inspectors identified a Green non-cited violation of 10 CFR 50 Appendix B, Criteria XVI, Corrective Action, for the licensee's failure to promptly identify and correct a condition adverse to quality related to the Control Room Air Conditioning (AC) sy
Region: II | Brunswick | 6540 | 09/30/2011 11/14/2011 | 2011004-03 | Self - Revealed | FIN | Barrier Integrity | Green | Inadequate Maintenance Results in Containment Isolation Valve Failure |  |  | TE?: N | 05000324 Brunswick 2 |  | 71111.12 | A self-revealing Green finding was identified for inadequate maintenance on the overload relay of the unit 2 reactor water cleanup (RWCU) system inlet isolation valve 2-G31-F001. As a result of the inadequate maintenance, the overload relay actuated durin
Region: II | Brunswick | 6528 | 06/30/2011 07/27/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Adequately Evaluate And Correct A Condition Adverse To Quality Involving A Manufacturing Defect Of Barton Model 199 Dual Dampener Differential Pressure Units |  |  | TE?: N | 05000325 Brunswick 1 |  | 71111.15 | -Green. A self revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" was identified for failure to promptly correct a condition adverse to quality regarding a manufacturing defect of a Barton Model 199 dual dampen
Region: II | Brunswick | 6525 | 03/31/2011 05/13/2011 | 2011002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to follow procedures for analyzing radiological air samples for the presence of alpha emitters |  | H.3(b) Work Activity Coordination | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | NONE | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1, Procedures, for the failure of the licensee to perform initial alpha activity analysis of air samples indicating greater than 0.3 Derived Air Concentration (DAC)
Region: II | Brunswick | 6529 | 01/21/2011 02/24/2011 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze MOV Operation with Transient Voltages |  | H.4(b) Procedural Compliance | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to use conservative motor control center (MCC) voltage inputs when calculating motor actuator output torque and con
Region: II | Brunswick | 6533 | 01/21/2011 02/24/2011 | 2010008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Isolation Override Circuitry Testing Deficiencies |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to assure that conditions adverse to quality, such as deficiencies, were promptly identified and corrected. Specifica
Region: II | Brunswick | 6534 | 01/21/2011 02/24/2011 | 2010008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Appropriate Corrective Actions for Deficiencies with Opening a Service Water Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 7111121 | Green. The team identified a non-cited violation of Technical Specification (TS) 5.4.1, Procedures, for the licensee's failure to maintain adequate abnormal operating procedures (AOP) for opening a service water cross-tie valve during a loss of offsite po
Region: II | Brunswick | 6520 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct a condition adverse to quality involving corrosion-related failures in the emergency diesel generator starting/control air system |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000324 Brunswick 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for failure to promptly correct a condition adverse to quality regarding moisture and corrosion buildup in carbon steel components used in the emergency
Region: II | Brunswick | 6519 | 09/17/2010 10/20/2010 | 2010007-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to timely activate ERDS |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | NONE | A self-revealing, very low safety significance (Green), non-cited violation (NCV) of 10 CFR 50.72(a)(4) was identified. The Emergency Response Data System (ERDS) was not activated until 80 minutes after the Alert declaration due to a lack of on-shift staf
Region: II | Brunswick | 6511 | 06/30/2010 07/27/2010 | 2010003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Change Results in an Automatic Reactor Scram |  |  | TE?: N | 05000325 Brunswick 1 |  | 71153 | Green. A self-revealing Green finding was identified for an inadequate design change to the Unit 1 feedwater flow instrument sensing lines (Plant Modification (PM) 77-039). As a result of the inadequate design change, pressure pulsation dampeners (snubber
Region: II | Brunswick | 6502 | 03/31/2010 04/28/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures During Reactor Head Disassembly |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000325 Brunswick 1 |  | 71111.2 | A self-revealing Green NCV of Technical Specifications (TS) 5.4.1, Procedures, was identified when reactor head piping was disconnected prior to swapping shutdown range reactor water level transmitters resulting in inaccurate water level indication. The p
Region: II | Brunswick | 6509 | 03/31/2010 04/28/2010 | 2010002-02 | NRC | NCV | Initiating Events | Green | Inadequate Risk Evaluation for Removing the 1A South Condenser from Service |  | H.3(a) Work Planning | TE?: N | 05000325 Brunswick 1 |  | 71111.2 | The inspectors identified a Green NCV of 10 CFR Part 50.65 (a)(4), Requirements for monitoring the Effectiveness of Maintenance at Nuclear Power Plants, after Unit 1 experienced a loss of normal reactor feedwater as a result of an abnormal plant configura
Region: II | Brunswick | 6510 | 03/31/2010 04/28/2010 | 2010002-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Ensure Representative Sampling of Particulate Effluents Released from the Reactor Building Roof Vent |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | NONE | The inspectors identified a Green NCV of 10 CFR 20.1302(a) for failure to ensure surveys of particulate radioactive materials in effluents released to unrestricted areas from the reactor building roof vent were adequate to demonstrate compliance with dose
Region: II | Brunswick | 6488 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure To Identify and Correct Degraded Fire Protection Sprinklers |  | H.4(b) Procedural Compliance | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation of Brunswick Steam Electric Plant (BSEP) Unit 1 Updated Facility Operating License DPR-71, and the Unit 2 Updated Facility Operating License DPR-62, Condition 2.B.(6), for the licensee's failure to ide
Region: II | Brunswick | 6489 | 12/31/2009 01/28/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Failure To Adequately Implement Design Control Measures For The Fire Protection Program |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation of BSEP Unit 1 Updated Facility Operating License DPR-71, and the Unit 2 Updated Facility Operating License DPR-62, Condition 2.B.(6), for the licensee's failure to implement adequate design control me
Region: II | Brunswick | 6501 | 12/31/2009 01/28/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Inadequately Monitored Maintenance Rule MOV |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(1), Requirements for monitoring the effectiveness of maintenance at nuclear power plants, for the licensee's failure to monitor the performance or condition of motor-operated valve (MOV) MS-V28 in a
Region: II | Brunswick | 6487 | 10/20/2009 11/24/2009 | 2009011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Instructions for Maintaining Cleanliness During Emergency Diesel Generator Governor Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 93812 | Green. The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, Procedures, for inadequate cleanliness and flushing procedures for maintaining cleanliness during maintenance on the emergency diesel generator (EDG) governors. This proce
Region: II | Brunswick | 6474 | 09/30/2009 10/30/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Annunciator Response Procedure for HPCI Vacuum Tank High Level |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 |  | 71153 | A self-revealing Green non-cited violation of TS 5.4.1, Procedures, was identified for an inadequate annunciator response procedure to respond to a high level in the high pressure coolant injection (HPCI) vacuum tank when the barometric condensate pump is
Region: II | Brunswick | 6480 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Plant Procedure Caused Loss of E2 Bus |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71153 | A self-revealing Green non-cited violation of Technical Specification (TS) 5.4.1, Procedures, was identified when the licensee failed to follow procedure 0PICCNV023, Calibration of Westinghouse & Scientific Columbus Teleductors. During the performance of
Region: II | Brunswick | 6481 | 09/30/2009 10/30/2009 | 2009004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Surveillance Test Performed on Incorrect Loop of RHR |  | H.4(b) Procedural Compliance | TE?: N | 05000325 Brunswick 1 |  | 71111.22 | A self-revealing Green non-cited violation of TS 5.4.1, Procedures, was identified when the licensee failed to follow work order instructions contained in work order 1280322. This work order directed technicians to perform testing on the B loop of the Uni
Region: II | Brunswick | 6482 | 09/30/2009 10/30/2009 | 2009004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Installation Instructions for Emergency Diesel Generator Service Water Expansion Joint Control Units |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.18 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to specify an appropriate quality standard for the installation of the control units on the emergency diesel generator ja
Region: II | Brunswick | 6485 | 09/30/2009 10/30/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Include Risk Significant Maintenance in the Site Risk Profile |  | H.3(a) Work Planning | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR Part 50.65 (a)(4), when the licensee removed the severe accident mitigation guideline (SAMG) diesel generators from service without considering the change in the online plant risk. Online pla
Region: II | Brunswick | 6486 | 09/30/2009 10/30/2009 | 2009004-06 | NRC | NCV | Mitigating Systems | Green | Capability of Emergency Diesel Generator Ventilation System to Meet Design and Licensing Requirements |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | NONE | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to translate a key analytical assumption related to operation of the emergency diesel building back draft and check dampers in
Region: II | Brunswick | 6466 | 06/30/2009 07/30/2009 | 2009003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Plant Procedures During Performance of a Reactor Pressure Vessel Hydrostatic Test |  | H.4(b) Procedural Compliance | TE?: N | 05000324 Brunswick 2 |  | 71111.2 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1.a, Administrative Control (Procedures), was identified when the licensee failed to follow plant procedure OPT-80.1, Reactor Pressure Vessel (RPV) ASME Section XI Pressure Test during Unit 2
Region: II | Brunswick | 6455 | 03/31/2009 04/30/2009 | 2009002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Condition Adverse to Quality Affecting the Operability of the Standby Gas Treatment Train B |  |  | TE?: N | 05000325 Brunswick 1 |  | 71111.06 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" which states in part, that for conditions adverse to quality, measures shall assure that the cause of the condition is determined and
Region: II | Brunswick | 6456 | 03/31/2009 04/30/2009 | 2009002-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a 10 CFR 50.59 Evaluation for a Plant Modification |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.18 | The inspectors identified a severity level IV NCV of 10 CFR 50.59, "Changes, Tests, and Experiments" for failing to perform a written safety evaluation prior to implementing a change to the facility as described in the Updated Final Safety Analysis Report
Region: II | Brunswick | 6460 | 03/31/2009 04/30/2009 | 2009002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures During Reactor Head Disassembly |  | H.3(b) Work Activity Coordination | TE?: N | 05000324 Brunswick 2 |  | 71111.2 | A self-revealing Green NCV of TS 5.4.1, Procedures, was identified when reactor head piping was disconnected prior to swapping shutdown range reactor water level transmitters resulting in inaccurate water level indication. The plant procedure for disconne
Region: II | Brunswick | 6461 | 03/31/2009 04/30/2009 | 2009002-04 | Self - Revealed | NCV | Initiating Events | Green | Unauthorized Maintenance Results in Loss of Shutdown Cooling |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 |  | 71111.2 | A self-revealing Green NCV of TS 5.4.1, Procedures, was identified when the licensee changed the position of 2-E11-F009, the shutdown cooling (SDC) inboard suction throttle valve, without following a procedure. On March 26, Unit 2 was in Mode 5 in a refue
Region: II | Brunswick | 6462 | 03/31/2009 04/30/2009 | 2009002-05 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Maintenance Procedure for the Control Room Air Conditioning and Emergency Ventilation Instrument Air System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, Procedures, was identified for inadequate maintenance procedures for the control room air conditioning and emergency ventilation system instrument air dryer. As a result, on January 21, 200
Region: II | Brunswick | 6447 | 12/31/2008 01/30/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Plant Procedures for Assembly of Safety Relief Valves |  | H.4(b) Procedural Compliance | TE?: N | 05000324 Brunswick 2 |  | 71153 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, Procedures, was identified when the licensee failed to correctly reassemble the pilot valve for the Unit 2 Safety Relief Valve (SRV) H. The plant procedure for assembly of the pilot valve,
Region: II | Brunswick | 6448 | 12/31/2008 01/30/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Prompt Corrective Actions for Low Oil Level in the 2B RHRSW Booster Pump |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000324 Brunswick 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" for failure to assure that a condition adverse to quality was promptly corrected, which resulted in the licensee declaring the 2B residual heat removal ser
Region: II | Brunswick | 6449 | 12/31/2008 01/30/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Inadvertent Rack Out of the 2A Core Spray Pump Circuit Breaker |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 |  | 71153 | A self-revealing Green NCV of TS 5.4.1, "Procedures," was identified for failure to comply with clearance order 180845 and 2OP-50, Plant Electric System Operating Procedure, Section 8.1, Racking Out a 4 KV Breaker." Specifically, the 2A Core Spray pump br
Region: II | Brunswick | 6454 | 12/31/2008 01/30/2009 | 2008005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Perform Biennial Written Examination for a Licensed Operator |  | H.4(b) Procedural Compliance | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR Part 55.59(a)(2) for failure to correctly evaluate and grade a written examination during the biennial requalification examination for licensed operators. The licensee operations training staff inc
Region: II | Brunswick | 6441 | 06/30/2008 07/30/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Performing Maintenance on the Control Room AC Subsystem |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.18 | A self-revealing Green non-cited violation of Technical Specification 5.4.1 was identified for an inadequate procedure used to specify configuration controls during a maintenance activity. The configuration management program implementation procedure, ADM
Region: II | Brunswick | 6442 | 06/30/2008 07/30/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calibration Procedure for the Conventional Service Water Relays |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000325 Brunswick 1 |  | 71111.19 | A self-revealing Green non-cited violation of Technical Specification 5.4.1 was identified for an inadequate procedure used for the calibration of the conventional service water pump logic relays in September 2007. Specifically, procedure 0PM-RLY-001, PM
Region: II | Brunswick | 6444 | 06/30/2008 07/30/2008 | 2008003-04 | NRC | FIN | Public Radiation Safety | Green | Failure to Conduct Adequate and Timely Evaluations of Onsite Groundwater Monitoring Well Tritium Concentration Trend Data |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | The inspectors identified a Green finding (FIN) for failure to properly evaluate the potential causes of increased tritium (H-3) concentrations in groundwater samples collected and reviewed in accordance with Brunswick procedure E&RC-3250, "Environmental
Region: II | Brunswick | 6432 | 02/29/2008 04/09/2008 | 2008006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correct a Condition Adverse to Quality Involving an MSIV Design Deficiency |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, for failure to correct a condition adverse to quality (i.e., design deficiency) which led to multiple and repetitive failures of the main stea
Region: II | Brunswick | 6433 | 02/29/2008 04/09/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate and Correct a Condition Adverse to Quality Involving Service Water Fouling of the 1A RHR Heat Exchanger |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000325 Brunswick 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the inadequate evaluation and corrective actions to address a condition adverse to quality involving degraded performance of the 1A Resid
Region: II | Brunswick | 6423 | 10/15/2007 11/16/2007 | 2007011-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Fisher Model 9100 Unbonded Butterfly Valve Failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 93812 | The inspectors identified an NCV of 10 CFR 50 Appendix B, Criterion XVI, for failure to promptly identify and correct a condition adverse to quality related to foreign material in the service water system (SW) resulting from Fisher butterfly valve rubber
Region: II | Brunswick | 6431 | 10/15/2007 11/16/2007 | 2007011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Loose Parts Analysis / Operability Evaluation for Fisher Butterfly Valve Taper Pin |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000325 Brunswick 1 |  | 93812 | The inspectors identified an NCV of 10 CFR 50 Appendix B, Criterion V, for an inadequate loose parts analysis / operability evaluation performed following the failure of SW valve 1-SW-V105 to open on July 26, 2005, due to the loss of both taper pins which
Region: II | Brunswick | 6419 | 09/30/2007 10/29/2007 | 2007004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Diesel Generator Trip Due to Failure to Follow Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 |  | 71111.22 | A self-revealing Green non-cited violation (NCV) of Technical Specification 5.4.1 was identified for failure to follow the Diesel Generator monthly load test procedure (0PT-12.2D) which resulted in Diesel Generator number 4 tripping on reverse power and l
Region: II | Brunswick | 6421 | 08/30/2007 10/11/2007 | 2007010-02 | NRC | NCV | Mitigating Systems | Green | Goal Setting and Monitoring not Performed for an Emergency Diesel Generator |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000325 Brunswick 1 |  | 95002 | The team identified a Green non-cited violation (NCV) of 10 CFR 50.65 (maintenance rule) for failure to demonstrate that the performance or condition of structures, systems, or components is being effectively controlled through the performance of appropri
Region: II | Brunswick | 6414 | 06/30/2007 07/30/2007 | 2007003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate Operating Experience into Plant Procedures and Training |  | P.2(b) Implementing Operating Experience | TE?: N | 05000324 Brunswick 2 |  | 71152 | A self-revealing non-cited violation of 10CFR50, Appendix B, Criterion XVI, Corrective Action, was identified for failing to incorporate operating experience into appropriate precautions and operating limitations for single recirculation loop operation in
Region: II | Brunswick | 6407 | 03/31/2007 04/30/2007 | 2007002-01 | Self - Revealed | NCV | Initiating Events | Green | Incorrect Fuel Assembly Moved to Core |  | H.4(a) Human Error Prevention | TE?: N | 05000324 Brunswick 2 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 5.4.1, Administrative Controls (Procedures) was identified for failing to follow the Core Component Sequence Sheet for Refueling Outage B218R1 during fuel movement on Unit 2. This resulted in
Region: II | Brunswick | 6404 | 02/23/2007 03/23/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate and Correct Condition Adverse to Quality Resulting in 2C CSW Pump Failure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000324 Brunswick 2 |  | 71152B | A self-revealing, non-cited violation of 10CFR50, Appendix B, Criteria XVI, "Corrective Action," was identified for the failure to take adequate corrective actions to prevent a failure of the 2C Conventional Service Water (CSW) pump on July 26, 2006, due
Region: II | Brunswick | 6400 | 12/31/2006 01/30/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Work Management Process |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000325 Brunswick 1 |  | 71111.12 | A self-revealing non-cited violation of Technical Specification 5.4.1, Administrative Controls (Procedures), was identified for failing to follow the work management process for the performance of minor maintenance. Minor maintenance was performed on a Un
Region: II | Brunswick | 6403 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Calibrate Service Water Pump Discharge Pressure Gages |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71111.12 | An NRC-identified non-cited violation of 10CFR50, Appendix B, Criteria XII, Control of Measuring and Test Equipment, was identified for failing to periodically calibrate the Units 1 and 2 service water pump discharge pressure gages. As a result, the quali
Region: II | Brunswick | 6395 | 09/30/2006 10/30/2006 | 2006004-01 | NRC | NCV | Emergency Preparedness | Green | Potential Reduction in Effectiveness of Emergency Plan |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152 | An NRC-identified non-cited violation of 10 CFR 50.54(q) was identified for the failure to determine if the introduction or the increasing of air into the offgas flowpath for the purpose of reducing steam jet air ejector radiation monitor readings would r
Region: II | Brunswick | 6396 | 09/30/2006 10/30/2006 | 2006004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Condenser Air Removal and Off-gas Recombiner System Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000325 Brunswick 1 |  | 71152 | An NRC-identified non-cited violation of Technical Specification 5.4.1, Administrative Controls (Procedures), was identified for the failure to adhere to procedure requirements when operators injected service air into the steam jet air ejectors and the of
Region: II | Brunswick | 6388 | 06/30/2006 07/28/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Engineering Change Procedure Resulting in Inoperable Reactor Core Isolation Cooling System |  |  | TE?: N | 05000324 Brunswick 2 |  | 71111.04Q | An NRC-identified non-cited violation was identified for failure to meet Technical Specification (TS) 5.4.1, Procedures. Specifically, the temporary modification process was not followed when implementing a temporary change to the Unit 2 reactor core isol
Region: II | Brunswick | 6386 | 03/31/2006 04/30/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Evaluate Core Spray Header Piping Flaw |  |  | TE?: N | 05000325 Brunswick 1 |  | NONE | An NRC-identified non-cited violation of Technical Specification 3.5.1, Emergency Core Cooling Systems (ECCS) and Reactor Core Isolation Cooling System, was identified for failure to appropriately evaluate and take corrective measures for a pre-existing f
Region: II | Brunswick | 6387 | 03/31/2006 04/30/2006 | 2006002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Resulting in Condensate System Transient |  |  | TE?: N | 05000325 Brunswick 1 |  | 71152 | A self-revealing non-cited violation of Technical Specification 5.4.1, Administrative Controls (Procedures), was identified for failure to properly implement requirements for procedure adherence when rinsing a Unit 1 condensate deep bed demineralizer. Pro
Region: II | Brunswick | 126528 | 02/11/2020 |  |  | LIV |  | Green | Failure to use proper data from the meteorological tower for dose assessments |  |  | TE?: N | 05000324 Brunswick 2 05000325 Brunswick 1 |  | 71152
Region: II | Catawba | 126613 | 12/31/2019 01/27/2020 | 2019004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadvertent Actuation of Unit 2 Containment Spray |  | H.8 - Procedure Adherence | TE?: N | 05000414 Catawba 2 |  | 71111.2 | A self-revealing Green NCV of Technical Specification 5.4.1, “Procedures,” was identified for the licensee’s failure to implement AD-OP-ALL-0204, “Plant Status Control,” during the operation of the Unit 2 containment spray (NS) system. Specifically, on O
Region: II | Catawba | 126323 | 11/21/2019 01/28/2020 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Qualify GEMS Level Transmitters for Submergence |  | NPP | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 | Equipment Performance | 71111.21N | The inspectors identified a Green finding and Non-cited Violation (NCV) of 10 CFR 50.49(f) when the licensee failed to demonstrate the GEMS containment sump level transmitter NILT5270 would meet its specified values for one year post-accident during subme
Region: II | Catawba | 126337 | 11/21/2019 01/28/2020 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Qualification of Conduit Sealant Compatibility for Electrical Wires and Cables |  | NPP | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 | Equipment Performance | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR 50.49(f) when the licensee failed to demonstrate the qualification of the conduit sealant and cable/wire interfaces utilizing Scotchcast Epoxy 9 in accordance wit
Region: II | Catawba | 126339 | 11/21/2019 01/28/2020 | 2019010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Assess Radiation and Thermal Degradation Effects of Replacement Sealant Equivalency |  | H.8 - Procedure Adherence | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 | Equipment Performance | 71111.21N | The inspectors identified a Green finding and Non-cited Violation (NCV) of 10 CFR 50.49(f) when the licensee failed to demonstrate that the qualification of Scotchcast Epoxy 9 was applicable to Scotchcast Epoxy 9N in accordance with Section 5.5.7 of proce
Region: II | Catawba | 125750 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Declare Motor Driven Auxiliary Feedwater Pumps Inoperable When Technical Specification Support System was Out Of Service |  | H.14 - Conservative Bias | TE?: N | 05000413 Catawba 1 | Equipment Performance | 71111.06 | Introduction: The inspectors identified a Green finding and associated NCV of TS 3.7.5, “Auxiliary Feedwater System,” for the failure to declare the Unit 1 motor driven auxiliary feedwater pumps (MDAFW) pumps inoperable and comply with the associated acti
Region: II | Catawba | 125778 | 09/30/2019 11/07/2019 | 2019003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Selected Licensee Commitment (SLC) 16.6-5 |  | H.8 - Procedure Adherence | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 | Configuration Control | 71111.15 | Introduction: The inspectors identified a Green finding and associated NCV of TS 5.4.1, “Procedures,” for Units 1 and 2 when the licensee failed to comply with SLC 16.6-5, “Residual Heat Removal/ Containment Spray Sump Pump (ND/NS) Interlock.” Specifical
Region: II | Catawba | 125980 | 09/30/2019 11/07/2019 | 2019003-03 | NRC | NCV | Mitigating Systems | Green | Failure to take Technical Specification Actions with Two Trains of Component Cooling Inoperable and Failure to Submit an Associated 8-hour NRC Report |  | H.14 - Conservative Bias | TE?: Y SL-IV-NCV | 05000414 Catawba 2 | Equipment Performance | 71111.15 | Introduction: The inspectors identified a Green finding and associated Severity Level IV NCV of TS 3.7.7 “Component Cooling Water System (KC),” for a failure to take TS actions for two inoperable trains of KC and of 10 CFR 50.72(b)(3)(v)(A, B, and D) for
Region: II | Catawba | 126114 | 06/30/2019 08/14/2019 | 2019002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Post Modification Testing Following a Design Change to the Nuclear Service Water System |  | H.3 - Change Management | TE?: N | 05000413 Catawba 1 | Equipment Performance | 71111.22
Region: II | Catawba | 124624 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Monitor and Control a Reactivity Change Results in Violation of Unit 1 License Condition |  | H.8 - Procedure Adherence | TE?: N | 05000413 Catawba 1 |  | 71111.11Q | The inspectors determined a self-revealing Green non-cited violation (NCV) of Catawba Unit 1 Facility Operating License (NPF–35), Condition 2.C. (1), “Maximum Power Level,” occurred on February 12, 2019. Licensed reactor operators in the control room fail
Region: II | Catawba | 24639 | 09/30/2018 10/18/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Maintenance Procedure Results in Damage to the 2A EDG During Testing |  | H.8 - Procedure Adherence | TE?: N | 05000414 Catawba 2 |  | 71153 | A Green self-revealed NCV of Technical Specification 5.4.1.a, “Procedures,” was identified for Catawba’s failure to follow procedure TE-MN-ALL-0202, “Transformer and Apparatus Testing,” during maintenance on the 2A EDG. Specifically, the licensee’s failur
Region: II | Catawba | 24396 | 08/03/2018 09/17/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Engineering Analyses to Support Design Basis Requirements |  | NPP | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.21M | The team identified four examples of a Green non-cited violation of title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control”. Specifically, Catawba failed to verify the electrical design of safety-related switchgear for
Region: II | Catawba | 24397 | 08/03/2018 09/17/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Operability of the VZ and RN Systems were not Assured |  | NPP | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.21M | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control” for the failure to assure that applicable regulatory requirements for the safety-related service water pump house environmental controls were
Region: II | Catawba | 24148 | 06/30/2018 07/24/2018 | 2018002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Identify and Correct CAQ Associated with Failure of the 2B Seal Water Injection Filter O-ring |  | P.2 - Evaluation | TE?: N | 05000414 Catawba 2 |  | 71111.12 | A self-revealed Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified for the licensee’s failure to promptly identify and correct a condition adverse to quality associated with the failure of 2B seal water injection f
Region: II | Catawba | 24149 | 06/30/2018 07/24/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000413 Catawba 1 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct a condition adverse to quality associated with low resistance readings for core exit therm
Region: II | Catawba | 23537 | 03/31/2018 04/27/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to ensure conditions adverse to quality managed outside of the CAP are corrected. |  | P.3 - Resolution | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71152 | The inspectors identified a Green NCV of Title 10 CFR 50, Appendix B, Criterion XVI, “Corrective Actions,” for the licensee’s failure to adequately establish measures to correct CAQ. Specifically, the licensee failed to establish controls to ensure that C
Region: II | Catawba | 23187 | 12/31/2017 01/26/2018 | 2017004-01 | NRC | NCV | Public Radiation Safety | Green | Inadequate testing of fuel pool ventilation radiation monitors. |  | H.3 - Change Management | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.15 | An NRC identified Green non-cited violation (NCV) of Technical Specification (TS) 5.4.1, “Procedures,” was identified for the licensee’s failure to establish and maintain a procedure for testing the Unit 1 and 2 process and area radiation monitoring syste
Region: II | Catawba | 23189 | 12/31/2017 01/26/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Failure to follow administrative procedures. |  | H.8 - Procedure Adherence | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71152 | The NRC identified a Green NCV of TS 5.4.1, “Procedures.” Specifically, the licensee failed to follow procedure AD-HU-ALL-004, “Preparation and Work Instruction Use and Adherence.” As a result, the licensee: (1) replaced a pressurizer heater breaker with
Region: II | Catawba | 20264 | 02/03/2017 03/17/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Translate Design Requirements into Operating Procedures for NW System |  | P.2 Evaluation | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.17T | Green: The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the limiting high pressure design requirement of the containment valve
Region: II | Catawba | 20263 | 12/31/2016 01/31/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to follow lockout relay testing procedure. |  | H.8 Procedure Adherence | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.2 | Green: A self-revealing Green non cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," was identified for the licensee's failure to follow procedure IP/2/A/4971/086, "2ETA 4160V Switchgear Lockout Relays," during relay testing, resul
Region: II | Catawba | 20254 | 06/30/2016 07/19/2016 | 2016002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to adequately implement RHR operating procedure. |  | H.4 Teamwork | TE?: N | 05000413 Catawba 1 |  | 71111.15 | Green: A self-revealing Green NCV of Technical Specifications (TS) 5.4.1.a, "Procedures," was identified for the licensee's failure to adequately implement a procedure for the operation of the Unit 1 residual heat removal (RHR) system. As a result, the br
Region: II | Catawba | 20255 | 06/30/2016 07/19/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to implement effective corrective actions to prevent DG connecting bearing rod rotations. |  | P.2 Evaluation | TE?: N | 05000413 Catawba 1 |  | 71152 | Green: An NRC identified Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to implement effective corrective actions to prevent repetition of a significant condition adverse to quality regard
Region: II | Catawba | 19840 | 12/31/2015 01/27/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Implement In-service Test Procedure for the Unit 1 Standby Makeup Pump |  | H.12 Avoid Complacency | TE?: N | 05000413 Catawba 1 |  | 71111.22 | Green. A Green self-revealing non-cited violation of Technical Specification (TS) 5.4.1, "Procedures," was identified for the licensee's failure to adequately implement their in-service test procedure for the Unit 1 standby makeup pump (SMP). Operators pe
Region: II | Catawba | 19839 | 09/30/2015 10/30/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Replace a Frequently Operated Sliding Link |  | P.3 Resolution | TE?: N | 05000414 Catawba 2 |  | 71153 | -Green: An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to promptly implement corrective actions to replace a frequently operated sliding link associated w
Region: II | Catawba | 19837 | 06/19/2015 07/15/2015 | 2015012-01 | NRC | NCV | Initiating Events | Green | Failure to Analyze the Spurious Operation of Control Room Area Ventilation Valves and the Adverse Impact on Control Room Habitability |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.05T | Green: The NRC identified an NCV of the Unit 1 and 2 Catawba Nuclear Station (CNS) Facility Operating License, Condition 2.C.5, for the failure to analyze the spurious operation of two motor operated valves (MOVs) in the control room area ventilation sy
Region: II | Catawba | 19838 | 06/19/2015 07/15/2015 | 2015012-02 | NRC | NCVIV | Mitigating Systems | Green | Fire Protection Program Change did not meet CNS License Condition Requirement 2.C.5 for Units 1 and 2. |  |  | TE?: Y SL-IV-NCVIV | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.05T | Green: The NRC identified a non-cited Severity Level IV violation of the Unit 1 and 2 CNS Facility Operating License, Condition 2.C.5, for the failure to implement and maintain in effect all provisions of the approved fire protection program (FPP). Spec
Region: II | Catawba | 19835 | 09/30/2014 10/22/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Impairment Requirements for a Degraded Committed Fire Barrier |  | P.1 Identification | TE?: N | 05000414 Catawba 2 |  | 71111.05Q | Green: An NRC-identified non-cited violation (NCV) of the Unit 2 Facility Operating License, Condition 2.C.5, Fire Protection Program, was identified for failure to implement and maintain all provisions of the approved fire protection program. The inspect
Region: II | Catawba | 19836 | 09/30/2014 10/22/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement a Prompt Determination of Operability for Diesel Generator Lube Oil Temperature |  | P.2 Evaluation | TE?: N | 05000413 Catawba 1 |  | 71153 | Green: A NRC-identified non-cited violation (NCV) was identified for the licensee's failure to adequately implement their administrative procedure for operability/functionality assessments as applied to the evaluation of Unit 1 diesel connecting rod beari
Region: II | Catawba | 19831 | 12/31/2013 01/23/2014 | 2013005-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Control Transient Combustible Materials in Accordance with the Fire Protection Program |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000414 Catawba 2 |  | 71111.05Q | An NRC-identified NCV of the Fire Protection Program (FPP) required by 10 CFR 50.48 and License Condition 2.C.5, was identified for failing to adequately implement transient combustible controls. Transient combustible material stored adjacent to the B rod
Region: II | Catawba | 19827 | 09/30/2013 10/28/2013 | 2013004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadvertent operation of the Unit 1 standby makeup pump |  |  | TE?: N | 05000413 Catawba 1 |  | 71153 | A self-revealing finding was identified for inadvertent operation of the Unit 1 Standby Makeup Pump (SMP) during the performance of a job performance measure (JPM). The licensed operator performing the JPM operated plant equipment which was contrary to pr
Region: II | Catawba | 19825 | 06/30/2013 07/26/2013 | 2013003-01 | NRC | NCV | Barrier Integrity | Green | Failure to inspect control room door seal |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.15 | -Green: An NRC-identified non-cited violation (NCV) of Technical Specifications, 5.5.16, Control Room Envelope Habitability Program, was identified for failure to implement and maintain all provisions of the program. The seals on the control room doors we
Region: II | Catawba | 19826 | 05/24/2013 06/18/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Deficiencies in the Emergency Lighting System Preventive Maintenance Program |  | P.1(b) Trend Performance CAP | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50.65, Maintenance Rule, for the licensee's failure to identify and correct deficiencies in the 8-hour emergency light preventive maintenance program. The licensee entered the issu
Region: II | Catawba | 19816 | 09/30/2012 10/26/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate 3 hour fire barrier between essential switchgear rooms |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of the Unit 1 and 2 Facility Operating Licenses, Condition 2.C.5, Fire Protection Program, was identified for failure to implement and maintain all provisions of the approved fire protection program. The i
Region: II | Catawba | 19817 | 09/30/2012 10/26/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to maintain requalification examination integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.11Q | An NRC-identified non-cited violation (NCV) of 10 CFR 55.49, Integrity of examinations and tests, was identified for the licensee's failure to adhere to examination procedure standards that allow no more than 50 percent scenario overlap between examinatio
Region: II | Catawba | 19818 | 09/14/2012 10/18/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Adequate Test to Ensure Minimum SMP Flow Requirements |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a non-cited violation of Catawba Nuclear Station Units 1 and 2 License Condition 2.C.5, "Fire Protection Program," for the licensee's failure to establish a leakage acceptance criteria past check valves that supported minimum, post-f
Region: II | Catawba | 19822 | 09/14/2012 10/18/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Procedure to Ensure EQ MOV Cycle Limit Is Not Exceeded |  | P.2(b) Implementing Operating Experience | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish a procedure to ensure that the requirements in EQMM 1393.01-A01-00, "Environmental Qualifica
Region: II | Catawba | 19815 | 06/30/2012 07/27/2012 | 2012003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to adequatley implement tagout procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000414 Catawba 2 |  | 71111.2 | A self-revealing non-cited violation (NCV) of TS 5.4.1, Procedures, was identified when the licensee failed to follow NSD 500, Red Tags/Configuration Control Tags. The licensee implemented a tagout that was not supported by plant conditions which resulted
Region: II | Catawba | 19808 | 06/18/2012 07/25/2012 | 2012009-02 | NRC | NCV | Mitigating Systems | Green | Unit 2 Offsite Power Circuits Inoperable Due to Improper Unit 1 Zone G Modification | EA Case: 2012153 |  | TE?: N | 05000414 Catawba 2 |  | 93812 | Self-revealing findings were identified for the licensee's failure to follow EDM-141, Procurement Specifications for Services. The licensee did not identify the need for the blocking feature for the instantaneous underfrequency protective function in both
Region: II | Catawba | 19809 | 06/18/2012 07/25/2012 | 2012009-03 | NRC | NCV | Mitigating Systems | Green | Improper Unit 2 Zone G Modification |  |  | TE?: N | 05000414 Catawba 2 |  | 93812 | A self-revealing finding was identified for the licensee's failure to follow EDM-141, Procurement Specifications for Services. The licensee did not identify the blocking feature for the instantaneous underfrequency protective function in both the vendor s
Region: II | Catawba | 19806 | 03/31/2012 04/26/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Safety-Related Manhole Sump Pump Discharge Outlet Blockage |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000413 Catawba 1 |  | 71111.06 | Green. A NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to implement the requirements of their modification program. Surface grading work for the nuclear s
Region: II | Catawba | 19800 | 09/30/2011 10/28/2011 | 2011004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Implement Tagout Procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000413 Catawba 1 |  | 71153 | A self-revealing finding was identified for the licensee's failure to adequately implement their administrative tagout procedure resulting in the isolation of main feedwater while Unit 1 was in Mode 4. The licensee's corrective actions included revisions
Region: II | Catawba | 19798 | 06/30/2011 07/27/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Failure to adequately control energized temporary power sources with transient fire loads |  | H.3(a) Work Planning | TE?: N | 05000413 Catawba 1 |  | 71111.05Q | An NRC-identified non-cited violation of the Fire Protection Program (FPP) was identified when the licensee failed to evaluate 600V temporary power sources installed in a housekeeping area with approved transient combustibles as required by NSD 313, Contr
Region: II | Catawba | 19799 | 06/30/2011 07/27/2011 | 2011003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate procedures for obtaining lube oil samples from the 2B NI pump |  | H.4(a) Human Error Prevention | TE?: N | 05000414 Catawba 2 |  | 71111.12 | A self-revealing non-cited violation was identified for the licensee's failure to provide adequate instructions for obtaining oil samples on the 2B safety injection (NI) pump. As a result, maintenance technicians inserted a plastic tube into the pump gear
Region: II | Catawba | 19796 | 03/31/2011 04/26/2011 | 2011002-01 | NRC | NCV | Emergency Preparedness | Green | Failure to update bases for EAL changes |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71114.04 | An NRC-identified NCV of 10 CFR 50.54(q) with two examples was identified for failing to maintain emergency plans that meet the requirements of 10 CFR 50.47(b)(4). The licensee failed to revise the Emergency Action Level (EAL) basis which potentially impa
Region: II | Catawba | 19792 | 12/31/2010 01/28/2011 | 2010005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to barricade and conspicuously post HRAs in Unit 2 lower containment |  | H.3(a) Work Planning | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | NONE | -Green. A self-revealing NCV of Technical Specification (TS) 5.7.1, High Radiation Area (HRA), was identified for the failure to barricade and conspicuously post HRAs inside Unit 2 lower containment. The inspectors determined that the failure to adequa
Region: II | Catawba | 19793 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to maintain retrievable quality related records |  | H.4(a) Human Error Prevention | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | NONE | An NRC-identified NCV of 10 CFR 50, Appendix B, Criterion XVII, "Quality Assurance Records," was identified for the failure to maintain retrievable records of activities affecting quality. Several work orders from the fall of 2009 were irretrievably lost
Region: II | Catawba | 19788 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Failure to adequately control transient combustible material in accordance with the fire protection program |  | H.4(b) Procedural Compliance | TE?: N | 05000414 Catawba 2 |  | 71111.05Q | An NRC-identified Green NCV of the Fire Protection Program (FPP) was identified when transient combustible materials of greater than 15 pounds and located near an ignition source were stored in the Unit 2 electrical penetration room without prior review a
Region: II | Catawba | 19782 | 06/30/2010 07/23/2010 | 2010003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Enter a Steam Leak on Safety Related Main Steam Piping in the Corrective Action Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000413 Catawba 1 |  | 71152 | -Green. An NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to adequately identify and correct a steam leak on a safety-related portion of the Main Steam sy
Region: II | Catawba | 19784 | 06/28/2010 08/10/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Emergency Lighting Units Not Installed as Required by the Fire Protection Program |  | H.2(d) Facilities & Equipment | TE?: N | 05000413 Catawba 1 |  | 71111.05T | Green: The inspectors identified a non-cited violation of Catawba Unit 1 Operating License Condition 2.C(5), in that the licensee failed to install emergency lighting units (ELUs) in accordance with the approved fire protection program. Specifically, ELUs
Region: II | Catawba | 19778 | 12/31/2009 01/28/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Underground Fuel Oil Storage Tank Vent Tornado Missile Protection |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | NONE | A NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion III, was identified in that the installed emergency diesel generator (EDG) fuel oil storage tank vents did not meet the design basis of bending without crimping. The licensee completed correct
Region: II | Catawba | 19777 | 10/15/2009 11/20/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to monitor the turbine-driven auxiliary feedwater pump sump valves for units 1 and 2 |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.65(a)(1) for the licensee's failure to monitor the turbine-driven auxiliary feedwater pump (CAPT) sump valves for Units 1 and 2. PIPs C-09-05020 and C-09-04390 initiated immediate corrective actions,
Region: II | Catawba | 19775 | 09/30/2009 09/25/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform required hourly fire watch patrols | EA Case: 2009198 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000413 Catawba 1 |  | NONE | The NRC identified a non-cited violation of 10 CFR 50.48 when a contract fire watch employee failed to complete fire watch surveillances on twelve occasions. The fire watch employee pre-signed the fire watch Impairment and Compensatory Measures (ICM) form
Region: II | Catawba | 19774 | 03/31/2009 04/28/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to translate design requirements into a maintenance program to ensure Component Cooling Water system operability was maintained over the design life of the plant (Section 4OA3.1) |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71153 | -Green: A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to translate the design basis for the Component Cooling Water (KC) heat exchanger Nuclear Service Water (RN) outlet
Region: II | Catawba | 19764 | 12/31/2008 01/27/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Risk Management Actions Associated With Planned Maintenance on the Unit 2 A Train KC Heat Exchanger |  | H.3(b) Work Activity Coordination | TE?: N | 05000414 Catawba 2 |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(4) for the licensee's failure to provide sufficient details for equipment protection in the approved Critical Activity Plan. In addition, the risk mitigation actions contained in the
Region: II | Catawba | 19765 | 12/19/2008 01/16/2009 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate System Leakage Tests (Section 4OA2.a.3) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71152B | The team identified a Green non-cited violation (NCV) for a failure to comply with 10CFR50.55a(g)(4) in that, the licensee failed to perform adequate system leakage tests of buried Nuclear Service Water (RN) piping repairs. This issue was entered into the
Region: II | Catawba | 19762 | 03/31/2008 04/24/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify an Inoperable CRACWS Chiller Prior to Removing the Remaining Chiller from Service Placed Both Units in TS 3.0.3 for Approximately 110 minutes (Section 4OA2.2(2)) |  | H.4(b) Procedural Compliance | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71152 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a, for the failure to adequately establish and implement procedures required by Regulatory Guide 1.33, Appendix A, Section 1.b, Administrative Procedures. Specifically,
Region: II | Catawba | 19751 | 12/31/2007 01/31/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required ASME Code Section XI Leakage Testing |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.08P | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.55a(g)(4) for the failure to perform periodic leakage testing of buried piping portions of the service water system as required by Section XI of the ASME Code for the second 10-year
Region: II | Catawba | 19756 | 12/31/2007 01/31/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Develop a Lift Plan and Risk Management Actions for the Replacement of Piping Over a Safety-Related SSC |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000414 Catawba 2 |  | 71111.13 | The inspectors identified a Green NCV of 10CR50.65(a)(4) for the failure to manage and minimize the risk associated with the replacement of portions of the nuclear service water (RN) system. More specifically, the licensee failed to develop a Complex Lift
Region: II | Catawba | 19757 | 12/31/2007 01/31/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Inspections of the Unit 2 ECCS Containment Sump Installation Failed to Identify Deficiencies Prior to Declaring the Safety-Related Structure Operable |  | H.4(a) Human Error Prevention | TE?: N | 05000414 Catawba 2 |  | 7111117A | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion X, Inspections, for the licensee's failure to adequately implement inspections of the new Unit 2 emergency core cooling system (ECCS) containment sump to ensure it was installed in
Region: II | Catawba | 19758 | 12/31/2007 01/31/2008 | 2007005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify and Correct a Significant Condition Adverse to Quality Affecting the Ability of Both CRAVS Chillers to Operate as Designed Following a SBO due to Inadequate Troubleshootin |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly identify and correct a significant condition adverse to quality affecting the ability of both control room area ventil
Region: II | Catawba | 19754 | 08/03/2007 09/14/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Barrier Penetration Seal |  |  | TE?: N | 05000413 Catawba 1 |  | 71111.05T | Inspectors identified a non-cited violation (NCV) of Unit 1 Operating License Condition 2.C.(5) for the licensee's failure to replace or reinstall a 3" x 3" section of fiberboard damming material on the outside surface of the silicone foam fire barrier pe
Region: II | Catawba | 19755 | 08/03/2007 09/14/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | ELU Replacement Batteries Not Tested After Installation |  | H.4(b) Procedural Compliance | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.05T | Inspectors identified a non-cited violation (NCV) of Units 1 and 2 Operating License Condition 2.C.(5) for failure to follow the emergency battery lighting maintenance and testing procedure IP/0/B/3540/002, Emergency Battery Lighting Periodic Maintenance
Region: II | Catawba | 19748 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Risk Management Actions Associated With Planned Maintenance on the Unit 2 B Train KC Heat Exchanger |  | H.3(b) Work Activity Coordination | TE?: N | 05000414 Catawba 2 |  | 71111.13 | Inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(4) for the licensee's failure to effectively implement the risk mitigation actions contained in the approved Critical Evolution Plan associated with work on the Unit 2 B Train Component
Region: II | Catawba | 19749 | 06/30/2007 07/30/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Risk Management Actions Associated With the Excavation of the RN Supply Headers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.13 | Inspectors identified a NCV of 10 CFR 50.65(a)(4) for the licensee's failure to develop and implement an effective Complex Evolution Plan associated with excavation and inspection of the nuclear service water (RN) supply headers in order to manage and min
Region: II | Catawba | 19750 | 06/30/2007 07/30/2007 | 2007003-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Design and Implementation of Modifications to the Hydrogen Igniter System on Catawba Units 1 and 2 |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111117A | Inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to effectively design and implement a modification that replaced the containment hydrogen ignition system's glow plugs with upgraded glow coils
Region: II | Catawba | 19752 | 06/30/2007 07/30/2007 | 2007003-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Test Procedure Used to Verify the Operability of the Hydrogen Igniter System Glow Coils on Catawba Units 1 and 2 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111117A | Inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for the licensee's failure to ensure that surveillance procedures were adequate to verify the operability of the newly-installed hydrogen igniter glow coils on Catawba Units
Region: II | Catawba | 19753 | 06/30/2007 07/30/2007 | 2007003-05 | NRC | NCV | Initiating Events | Green | Failure to Perform Required Weld Inspections on the Fuel Handling Cask Cranes |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111117A | Inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to effectively implement the requirement to fully inspect fuel handling cask crane welds in accordance with Updated Final Safety Analysis Repor
Region: II | Catawba | 19741 | 04/20/2007 05/29/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for CA System Air Entrainment Issue Identified in PIP C-97-01579 |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to perform adequate corrective action associated with an air entrainment issue in
Region: II | Catawba | 19742 | 04/20/2007 05/29/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate and Timely Corrective Action to Identify and Resolve an Equipment Design Deficiency of the Alternate Power Supply for the 125 VDC Vital I&C Distribution Center 1EDF |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to perform adequate and timely corrective actions to resolve a potential equipmen
Region: II | Catawba | 19743 | 04/20/2007 05/29/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Analyzing the Impact of Updated Vendor Technical Information on Reactor Trip Breaker Maintenance and Inspection Procedures |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 7111121 | The team identified a finding of very low safety significance (Green) involving a non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for failure to follow procedure NSD 319, Vendor Technical Information Prog
Region: II | Catawba | 19736 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Examinations of 1A ND Heat Exchanger Inlet and Outlet Welds |  | H.3(a) Work Planning | TE?: N | 05000413 Catawba 1 |  | 71111.08P | The inspectors identified a finding involving an NCV of 10 CFR Part 50.55a(g)(4)ii for failure to perform a volumetric examination of the 1A Residual Heat Removal (ND) heat exchanger as required by Section XI of the American Society of Mechanical Engineer
Region: II | Catawba | 19734 | 12/31/2006 01/30/2007 | 2006005-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Recognition, Assessment and Management of the Increased Shutdown Risk Associated With the Failure of the 1B KF Pump with the Core in the Spent Fuel Pool and the 1A DG Inoperable |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.13 | The inspectors identified a green NCV of 10 CFR 50.65(a)(4) for the licensee failing to adequately recognize, assess, and manage the increased risk resulting from the failure of the single operable spent fuel pool cooling pump with the opposite train's em
Region: II | Catawba | 19735 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | NCV | Barrier Integrity | Green | Failure to implement adequate design control for ice condenser lower inlet doors |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, and Criterion XI, Test Control, for the licensee's failure to have design documentation to support the ice condenser lower inlet door surveillance procedure tes
Region: II | Catawba | 19740 | 12/31/2006 01/30/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Recurring Scaffolding Installation Deficiencies |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to identify and implement effective corrective actions to prevent recurring deficiencies associated with the erection of scaffoldi
Region: II | Catawba | 19732 | 12/01/2006 01/05/2007 | 2006010-02 | NRC | NCV | Mitigating Systems | Green | Failure to establish a procedure for mitigating the consequences of an external flooding event. |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | NONE | A non-cited violation of TS 5.4.1b was identified for failing to establish procedures required by Regulatory Guide 1.33, Appendix A, Section 6, Procedures for Combating Emergencies and Other Significant Events. Specifically, no procedure existed to combat
Region: II | Catawba | 19733 | 12/01/2006 01/05/2007 | 2006010-03 | NRC | FIN | Mitigating Systems | Green | Failure to conduct an adquate extent of condition review following multiple water intrusion events to ensure risk significant SSC's were proted from loss due to flooding. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | NONE | An NRC identified finding was identified for the licensee's failure to conduct adequate extent of condition reviews following multiple water intrusion events at the site by limiting the focus of the reviews to only safety-related structures, systems, and
Region: II | Catawba | 19729 | 09/30/2006 10/26/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Senior Reactor Operator Operating Examinations |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.11B | An NRC-identified NCV of 10 CFR 55.59 was identified for failure to adequately examine Senior Reactor Operators (SROs). Job Performance Measures (JPMs) that contained immediate operator actions was excluded from the sample of JPMs used to examine SROs.
Region: II | Catawba | 19730 | 09/30/2006 10/26/2006 | 2006004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to maintain design control over installation of seals in below-grade electrical conduits. |  |  | TE?: N | 05000413 Catawba 1 |  | 71153 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified when the licensee failed to maintain appropriate design control in ensuring below-grade electrical conduits were properly sealed to prevent w
Region: II | Catawba | 19726 | 06/30/2006 07/28/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Periodic Inspection Procedures for Seals on Below-Grade Electrical Conduits Entering Plant Areas Containing Safety-Related Equipment. |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.12 | The inspectors identified an NCV of Technical Specifications 5.4.1.b, for failure to adequately establish and implement procedures required by Regulatory Guide 1.33, Appendix A, Section 9, Procedures for Performing Maintenance. Specifically, no procedure
Region: II | Catawba | 19725 | 03/31/2006 05/15/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment and Management Associated With Planned Nuclear Service Water System Maintenance |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71111.13 | An NRC-identified non-cited violation was identified for the failure to adequately assess and manage the risk pertaining to a portion of the maintenance activities associated with the removal of the A train of nuclear service water (RN) from service for a
Region: II | Catawba | 19724 | 03/31/2006 05/15/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Derating Selected Emergency Lighting Units Required for Post-Fire Safe Shutdown |  |  | TE?: N | 05000414 Catawba 2 |  | NONE | The inspectors identified a non-cited violation of Catawba Nuclear Station Operating License Condition 2.C.5, Fire Protection Program. The licensee made a change to the approved fire protection program which had the potential to affect post-fire safe shut
Region: II | Catawba | 124800 | 05/07/2019 |  |  | LIV |  | Green | Failure to meet the CSP, Section 3.1.6, “Mitigation of Vulnerabilities and Application of Cyber Security Controls |  |  | TE?: N | 05000413 Catawba 1 05000414 Catawba 2 |  | 71130.10P
Region: II | Catawba | 20265 | 07/24/2017 | 2017002-01 | NRC | NCV | MISC | Green | 10 CFR 50.59 evaluation of a change to an engineered safety features actuation (ESFAS) test procedure. |  |  | TE?: N | 05000413 Catawba 1 |  | 71111.15 | The inspectors identified a URI associated with the implementation of a procedure change to the Unit 1 auxiliary shutdown panel (ASP) room air conditioning system. Additional information is needed to determine if a performance deficiency exists. In Nov
Region: II | Farley | 125695 | 10/08/2019 10/11/2019 |  |  | LIV |  | Green | Failure to Control Physical Access Points to The MET Tower and Control Communication Paths from The MET Tower to The Level 3 Plant Computer |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71130.10P
Region: II | Farley | 125806 | 09/30/2019 11/07/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 1 turbine driven auxiliary feed water pump steam supply vavle failure |  | NPP | TE?: N | 05000348 Farley 1 | Equipment Performance | 71111.15 | A self-revealed green finding and associated non-cited violation (NCV) of Technical Specification 5.4.1, “Procedures” was identified when the licensee failed to follow procedural guidance in 2012 for work that affected the performance of the Unit 1 turbin
Region: II | Farley | 125290 | 06/30/2019 08/08/2019 | 2019002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiological Surveys Adequate to Identify and Control a High Radiation Area with Dose Rates Greater than 1,000 millirem/hour @ 30 centimeters |  | H.5 - Work Management | TE?: N | 05000348 Farley 1 05000364 Farley 2 | Human Performance | 71124.01 | A self-revealing, Green, Non-Cited Violation of 10 CFR 20.1501 and Technical Specifications (TS) 5.7.2 “High Radiation Area,” was identified when a worker received a dose rate alarm upon entering an unlocked and unguarded high radiation area (HRA) with do
Region: II | Farley | 125272 | 06/30/2019 08/08/2019 | 2019002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inoperable Containment Isolation Valve due to Design Control Error |  | H.3 - Change Management | TE?: N | 05000364 Farley 2 | Design Control | 71153 | A self-revealed, Green, Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, “Design Control’, was identified for the licensee’s failure to translate design requirements for a unit 2 containment isolation valve modification into instructions or pr
Region: II | Farley | 38860 | 12/31/2018 02/13/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | 2B emergency diesel generator oil leak |  | H.8 - Procedure Adherence | TE?: N | 05000364 Farley 2 |  | 71111.15 | A green self-revealed non-cited violation (NCV) of Technical Specification 5.4.1, “Procedures” was identified for the failure to follow procedural guidance on October 29, 2018 for work that affected the performance of the ‘2B’ emergency diesel generator.
Region: II | Farley | 25900 | 11/09/2018 12/20/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to determine the full range of environmental conditions for MCCs U & V |  | NPP | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.21N | For their environmental qualification (EQ) program, the licensee is committed to the Division of Reactor (DOR) guidelines for Unit 1 and NUREG 0588 CAT II for Unit 2. The licensee is committed to Regulatory Guide (RG) 1.89 for all replacement componen
Region: II | Farley | 25899 | 11/09/2018 12/20/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to replace or provide ongoing qualification for the Boston Insulated Wire (BIW) cables at the end of their qualified life |  | NPP | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.21N | For their environmental qualification (EQ) program, the licensee is committed to the Division of Reactor (DOR) guidelines for Unit 1 and NUREG 0588 CAT II for Unit 2. The licensee is committed to Regulatory Guide (RG) 1.89 for all replacement componen
Region: II | Farley | 24395 | 08/03/2018 09/11/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to ensure fire barrier penetrations (including fire dampers) in fire zones protecting |  | H.8 - Procedure Adherence | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.05XT | The NRC identified a Green finding and associated non-cited violation (NCV) of the Farley’s Renewed Operating License Condition 2.C.(4) – Fire Protection for U1 and 2.C.(6) – Fire Protection for U2. This finding was identified for failure to maintain al
Region: II | Farley | 24129 | 06/30/2018 08/08/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperability of 1B Charging pump due to vibration |  | H.1 - Resources | TE?: N | 05000348 Farley 1 |  | 71111.12 | A green self-revealed NCV of TS 5.4.1, “Procedures” was identified for the failure to provide adequate work order (WO) instructions in work order SNC531734 for the ‘1B’ charging pump preventive maintenance on January 31, 2017. Excess grease in the pump sh
Region: II | Farley | 24130 | 06/30/2018 08/08/2018 | 2018002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to develop adequate PM for diesel generator relays |  | P.3 - Resolution | TE?: N | 05000348 Farley 1 |  | 71111.19 | A green self-revealed violation of Technical Specifications 5.4.1, “Procedures” was identified on May 16, 2018 when the 1B diesel generator (DG) failed to adequately load during a subsequent restart while performing FNP-1-STP-80.6, “Diesel Generator 1B 24
Region: II | Farley | 24136 | 06/30/2018 08/08/2018 | 2018002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Calibrate Portable Radiation Survey Instruments |  | H.1 - Resources | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71124.05 | A NRC-identified, green, NCV of 10 CFR 20.1501(c) was identified for the licensee’s failure to periodically calibrate portable instruments for the radiation measured. Specifically, high-range Geiger-Mueller (GM) survey instruments were not being calibrate
Region: II | Farley | 24137 | 06/30/2018 08/08/2018 | 2018002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement timely corrective actions for charging pump discharge check valves |  | H.10 - Bases for Decisions | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | A green self-revealed NCV of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action” was identified for the licensee’s failure to promptly identify and correct a condition adverse to quality associated with the Unit 1 and 2 charging pump discharge check
Region: II | Farley | 24138 | 06/30/2018 08/08/2018 | 2018002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of a Main Steam Isolation Valve on the ‘C’ Steam Line |  | H.1 - Resources | TE?: N | 05000348 Farley 1 |  | 71152 | A green self-revealed NCV of Technical Specifications 5.4.1, “Procedures” was identified for the failure of the licensee to provide adequate procedural guidance in FNP-0-MP-39.0, “Main Steam Isolation Valve Disassembly and Reassembly” to maintenance perso
Region: II | Farley | 23988 | 05/08/2018 05/08/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to conduct an In-service Testing (IST) surveillance on the 2B charging pump discharge check valve |  | H.9 - Training | TE?: N | 05000364 Farley 2 |  | 71111.15 | A Green self-revealed NCV of 10 CFR 50, Appendix B, Criterion XI, “Test Control,” was identified for the failure to test the ‘2B’ charging pump discharge check valve, Q2VE21V122B, in accordance with IST requirements. Specifically, licensee procedure F
Region: II | Farley | 25919 | 03/30/2018 05/23/2018 | 2018013-01 | Self - Revealed | NOV | Occupational Radiation Safety | Green | Interference with the operation of a respirator | EA Case: EA-17-187 | H.5 - Work Management | TE?: Y SL-IV-NOV | 05000348 Farley 1 |  | 71124 | A self-revealing, Green, Finding and associated Severity Level IV Notice of Violation (NOV) of 10 CFR 20.1703 (a), (b) and (e) and plant Technical Specification (TS) 5.4.1, was identified when licensee personnel altered respiratory protective equipment in
Region: II | Farley | 23212 | 12/31/2017 02/12/2018 | 2017004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to evaluate impacts on the 2C RCP oil collection system |  | P.2 - Evaluation | TE?: N | 05000364 Farley 2 |  | 71111.05Q | Green. Self-revealing finding was identified for the licensee’s failure to evaluate the impacts to the Unit 2 Reactor Coolant Pump (RCP) 2C oil collection system when a service water leak was identified on the Unit 2 RCP motor air coolers. As a result
Region: II | Farley | 23213 | 12/31/2017 02/12/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Failure to maintain an operable Oil Collection System on RCP 2B |  | H.6 - Design Margins | TE?: N | 05000364 Farley 2 |  | 71111.2 | Green. NRC identified NCV of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 (NFPA 805), Section 3.3.12, was identified for the licensee’s failure to maintain the Unit 2 Reactor Coolant Pump (RCP) 2B oil collection system in an o
Region: II | Farley | 23214 | 12/31/2017 02/12/2018 | 2017004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulted in Inoperable TDAFW pump |  | H.12 - Avoid Complacency | TE?: N | 05000348 Farley 1 |  | 71152 | Green. Self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a, “Procedures,” was identified when the Unit 1 TDAFW uninterruptible power supplies (UPS) swapped to a bypass power source during maintenance on November 5, 2017. A
Region: II | Farley | 23230 | 10/27/2017 10/27/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform adequate corrective maintenance on the 2B EDG |  | H.14 - Conservative Bias | TE?: N | 05000364 Farley 2 |  | 71153 | The NRC identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a, “Procedures,” for the licensee’s failure to implement corrective maintenance work order instructions to identify and replace piping as necessary for a degraded threa
Region: II | Farley | 22352 | 09/29/2017 11/08/2017 | 2017009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Complete Corrective Action to Preclude Repetition of a Significant Conditions Adverse to Quality |  | H.8 - Procedure Adherence | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152B | The NRC identified non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for failure to ensure that a corrective action taken to preclude repetition (CAPR) of a significant condition adverse to quality would be impleme
Region: II | Farley | 11160 | 06/30/2017 08/04/2017 | 2017002-01 | NRC | NCV | Emergency Preparedness | Green | NCVFailure to Declare an Unusual Event During an Actual Event |  | H.9 Training | TE?: N | 05000348 Farley 1 |  | 71114.05 | Green: The inspectors identified a self-revealing non-cited violation (NCV) for failure to declare a Notification of Unusual Event (NOUE) during an actual event. Specifically, on November 1, 2016, Farley Unit 1 experienced conditions that met Emergency Ac
Region: II | Farley | 11161 | 06/30/2017 08/04/2017 | 2017002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedure Resulted in Inoperable PRF System Boundary (1R15) |  | H.4 Teamwork | TE?: N | 05000348 Farley 1 |  | 71111.15 | Green: A Green NRC-identified NCV of TS. 5.4.1.a, Procedures, was identified when inspectors found the 1A containment spray (CS) pump room door (door 106) open on May 12, 2017 without the required dedicated individual to close the door. As a result, the p
Region: II | Farley | 11440 | 06/27/2017 06/27/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Time Requirement into the Time Critical Operator Action Program Procedure (Section 1R21.b.1) |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.21M | Green: The NRC identified a non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the design basis time limit for the alignment of the emergen
Region: II | Farley | 11441 | 06/27/2017 06/27/2017 | 2017007-02 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Actions for Check Valve Q2E21V0026 (Section 1R21.b.2) |  | H.14 Conservative Bias | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.21M | Green: The NRC identified a non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to implement timely corrective actions to change the classification of
Region: II | Farley | 11153 | 03/31/2017 05/01/2017 | 2017001-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to perform PM task resulted in MSIV closure |  | P.4 Trending | TE?: N | 05000348 Farley 1 |  | 71153 | Green. A self-revealing finding was identified for the failure to maintain a preventive maintenance (PM) task to replace the main steam isolation valve (MSIV) test solenoid valves in accordance with the PM basis. As a result, test solenoid valve N1N11SV33
Region: II | Farley | 11146 | 12/31/2016 01/27/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Install an Oil Collection System on Reactor Coolant Pump Motors |  | H.8 Procedure Adherence | TE?: N | 05000348 Farley 1 |  | 71111.05Q | Green: A NRC-identified NCV of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 (NFPA 805), Section 3.3.12, was identified for the licensee's failure to comply with code requirements for design and installation of the Unit 1 Reactor C
Region: II | Farley | 11147 | 12/31/2016 01/27/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate NTTF Flooding Walkdowns |  | H.8 Procedure Adherence | TE?: N | 05000348 Farley 1 |  | 71152 | Green: A NRC-identified NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, was identified because the licensee failed to identify and correct conditions adverse to quality associated with the flood protection design basis of the Unit 1 Auxil
Region: II | Farley | 11151 | 12/31/2016 01/27/2017 | 2016004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Resulted in Automatic Reactor Trip and Safety Injection |  | H.8 Procedure Adherence | TE?: N | 05000348 Farley 1 |  | 71153 | Green: A self-revealing NCV of Technical Specification 5.4, "Procedures" was identified on October 1, 2016 when the Unit 1 operations shift crew failed to comply with annunciator response procedure FNP-1-ARP-1.9, Ver. 50 for the "JC4" annunciator. Conditi
Region: II | Farley | 11138 | 09/30/2016 11/02/2016 | 2016003-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Comply with NFPA-13 for Pre-action Fire Suppression System 1A-36 and Provide NRC Staff Complete and Accurate Information (1R05) |  |  | TE?: Y SL-IV-NCVIV | 05000348 Farley 1 05000364 Farley 2 |  | 71111.05Q | Green: An NRC-identified Severity Level IV NCV of 10 CFR 50.9(a), "Completeness and accuracy of information," and an associated Green NCV of 10 CFR 50.48(c) and National Fire Protection Association Standard (NFPA) 805, Section 3.9.1, was identified for th
Region: II | Farley | 11139 | 09/30/2016 11/02/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Requalification Examination Integrity (1R11) |  | H.1 Resources | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.11B | Green: An NRC-identified non-cited violation (NCV) of 10 CFR 55.49, "Integrity of examinations and tests," was identified for the licensee's failure to adhere to examination procedure standards that require the use of sequestering and examination security
Region: II | Farley | 11145 | 09/30/2016 11/02/2016 | 2016003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Preventive maintenance on Circuit Breaker Cell Switch (4OA3.2) |  | H.2 Field Presence | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71153 | Green: An NRC-identified, non-cited violation of Technical Specification (TS) 3.8.9 "Distribution Systems - Operating," occurred when the shared 600 VAC 1-2R load center (LC) was inoperable for longer than allowed by technical specifications for Unit 1. T
Region: II | Farley | 11134 | 06/30/2016 08/12/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform TS Surveillance Requirements for Safety-Related Batteries (4OA2) |  | H.1 Resources | TE?: N | 05000348 Farley 1 |  | 71152 | Green: An NRC-identified non-cited violation of Technical Specification (TS) 5.4.1 "Procedures", was identified with two examples. The licensee failed to implement and maintain surveillance test procedures for surveillance requirements (SR) 3.8.4.4 and SR
Region: II | Farley | 11152 | 05/03/2016 10/04/2016 | 2016008-01 | NRC | VIO | Occupational Radiation Safety | Green | Inaccurate Training Records | EA Case: 2016110 | H.2 Field Presence | TE?: Y SL-V-VIO | 05000348 Farley 1 05000364 Farley 2 |  | NONE | Severity Level IV/Green: The licensee identified a violation of 10 CFR 50.9(a) requirements and an associated finding of very low significance when it was determined that an employee deliberately completed requalification examinations for other employee
Region: II | Farley | 11137 | 02/04/2016 03/18/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Design Assumptions Associated with the Operation of the Atmospheric Relief Valves |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.17T | Green. The NRC identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to verify design assumptions associated with the operation of the atmospheric relief valves (ARVs) following a steam generato
Region: II | Farley | 11133 | 12/31/2015 02/03/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Instructions for the 2A Service Water Pump Motor Cable Connections |  | P.2 Evaluation | TE?: N | 05000364 Farley 2 |  | 71111.12 | A self-revealing, non-cited violation of Technical Specification 5.4 "Procedures," was identified for the failure to provide an adequate procedure for installing the 2A service water (SW) pump motor cable connections. As a result, the connection degraded
Region: II | Farley | 11131 | 09/30/2015 11/03/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate or Test EMI/RFI Effect for Solid State Protection System Power Supply |  |  | TE?: N | 05000348 Farley 1 |  | NONE | An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the licensee's failure to evaluate or test the Electro Magnetic Interference/Radio Frequency Interference (EMI/RFI) effects of the So
Region: II | Farley | 11130 | 09/30/2015 11/03/2015 | 2015003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to properly implement design change |  | H.5 Work Management | TE?: N | 05000348 Farley 1 |  | 71153 | A self-revealing finding was identified for the licensee's failure to conduct adequate functional testing during implementation of a design change. Incorrect installation of protective relaying circuitry for the 1B Unit Auxiliary Transformer (UAT) was not
Region: II | Farley | 11119 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Install an Oil Collection System on Reactor Coolant Pump Motors |  | P.2 Evaluation | TE?: N | 05000348 Farley 1 |  | 71111.05Q | An NRC-identified, Green non-cited violation of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 (NFPA 805), Section 3.3.12, was identified for the licensee's failure to comply with code requirements for design and installation of the
Region: II | Farley | 11124 | 06/30/2015 08/05/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Impacts of Degraded Condition on the Unit 1 TDAFW Pump |  | H.11 Challenge the Unknown | TE?: N | 05000348 Farley 1 |  | 71111.15 | An NRC-identified, Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified with two examples. First, for the May 17, 2015, failure to evaluate the operability impact of condensate water in th
Region: II | Farley | 11125 | 06/30/2015 08/05/2015 | 2015002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Survey for Radiological Conditions |  | H.5 Work Management | TE?: N | 05000348 Farley 1 |  | 71124.01 | A self-revealing, Green non-cited violation of 10 CFR 20.1501(a) was identified for the failure to perform radiological surveys in Unit 1 containment to ensure that the potential radiological hazards and extent of radiation levels were evaluated which res
Region: II | Farley | 11106 | 03/31/2015 05/08/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify deficiencies during a fire drill |  | H.8 Procedure Adherence | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.05A | A NRC-identified NCV of Farley Nuclear Plant, Unit 1, Operating License Condition 2.C.(4), and Unit 2, Operating License Condition 2.C.(6), "Fire Protection" was identified for the licensee's failed to identify deficiencies during a fire drill as required
Region: II | Farley | 11116 | 03/31/2015 05/08/2015 | 2015001-02 | NRC | FIN | Mitigating Systems | Green | Failure to maintain AFW pump room watertight doors |  |  | TE?: N | 05000348 Farley 1 |  | 71111.06 | A NRC-identified finding was identified for the licensee's failure to maintain the doors for the "1A" and "1B" motor-driven auxiliary feed water (AFW) pump room in a watertight configuration as required by the facility's updated final safety analysis repo
Region: II | Farley | 11117 | 03/31/2015 05/08/2015 | 2015001-03 | NRC | NCV | Mitigating Systems | Green | Failure to ensure rolling fire doors would automatically close |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | A NRC-Identified NCV of Farley Nuclear Plant, Unit 1, Operating License Condition 2.C. (4), and Unit 2, Operating License Condition 2.C.(6), "Fire Protection" was identified for the licensee's failure to install rolling steel fire doors in the Appendix R
Region: II | Farley | 11118 | 03/31/2015 05/08/2015 | 2015001-04 | NRC | NCV | Mitigating Systems | Green | Failure to ensure DG rolling fire doors were labeled fire doors |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | A NRC-identified NCV of Farley Nuclear Plant, Unit 1, Operating License Condition 2.C.(4), and Unit 2, Operating License Condition 2.C.(6), "Fire Protection" was identified for the licensee's failure to install rolling steel fire doors in the Appendix R 3
Region: II | Farley | 11109 | 12/31/2014 02/09/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Rolling Fire Doors on Units 1 and 2 Complied with Fire Code |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | An NRC identified non-cited violation (NCV) of Farley Nuclear Plant, Unit 1, Operating License Condition 2.C.(4), and Unit 2, Operating License Condition 2.C.(6), "Fire Protection" was identified for the licensee's failure to install rolling steel fire do
Region: II | Farley | 11110 | 12/31/2014 02/09/2015 | 2014005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to perform an adequate risk assessment led to a manual reactor trip of Unit 2 |  |  | TE?: N | 05000364 Farley 2 |  | 71153 | A self-revealing non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, was identified for the licensee's failure to properly assess and manage the increase in risk that resulted f
Region: II | Farley | 11108 | 09/30/2014 10/28/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for Steam Generator Steam Flow Channel Checks |  | H.14 Conservative Bias | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.15 | Green. A NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the licensee's failure to include appropriate quantitative acceptance criteria for determining that i
Region: II | Farley | 11126 | 08/01/2014 09/15/2014 | 2014009-01 | NRC | NCV | Mitigating Systems | Green | Installation of 1.5-hour UL Labeled Fire Door in a Required 3-hour Fire Barrier on Unit 2 |  | H.12 Avoid Complacency | TE?: N | 05000364 Farley 2 |  | 71111.05T | A Green NRC-identified non-cited violation (NCV) of Unit 2 Operating License Condition (OLC) 2.C. (6), Fire Protection, was identified for the failure to ensure that a fire door that was part of a fire barrier was provided with a 3-hour labeled door as re
Region: II | Farley | 11078 | 06/06/2014 07/28/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of the CCW Miscellaneous User Isolation Valves |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate operability evaluation following the discovery that the componen
Region: II | Farley | 11081 | 06/06/2014 07/28/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with IEEE 308-1971 for the Required Independence of 120 Volt Vital AC Distribution System Channels |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to demonstrate compliance with IEEE 308-1971 for the required independence of 120V vital AC distribution syst
Region: II | Farley | 11082 | 06/06/2014 07/28/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Lack of Validated Time Critical Operator Actions Analyses |  | P.2 Evaluation | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct a lack of documented verification and validation for time critical operator actions which
Region: II | Farley | 11083 | 06/06/2014 07/28/2014 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Acceptance Criterion for UHS Temperature Did Not Consider Instrument Uncertainty |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to include an appropriate acceptance criterion for ultimate heat sink (UHS) temperatu
Region: II | Farley | 11090 | 06/06/2014 07/28/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criterion for Testing of Check Valves |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50.55a(f), "Inservice testing requirements," subsection (4), American Society of Mechanical Engineers Operation and Maintenance of Nuclear Power Plants code, Subsection ISTC-5221, "Check
Region: II | Farley | 11091 | 06/06/2014 07/28/2014 | 2014007-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Characterization of IST Program Valves |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50.55a(f), "Inservice testing requirements," subsection (4), American Society of Mechanical Engineers Operation and Maintenance of Nuclear Power Plants code, Subsection ISTC-1300, "Valve
Region: II | Farley | 11104 | 06/06/2014 07/28/2014 | 2014007-09 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that the RHR System Would Be Capable to Mitigate a MODE 4 LOCA |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure the residual heat removal (RHR) system would be capable to respond to a MODE 4 loss of coolant a
Region: II | Farley | 11074 | 03/31/2014 05/14/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to properly conduct cold weather contigency procedures |  | H.8 Procedure Adherence | TE?: N | 05000364 Farley 2 |  | 71111.01 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to implement cold weather preparation procedures prior to the onset of anticipated below-
Region: II | Farley | 11076 | 03/31/2014 05/14/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Lack of acceptance criteria for nuclear instrument channel checks |  | H.1 Resources | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.15 | The inspectors identified an NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the licensee's failure to include appropriate quantitative or qualitative acceptance criteria for determining that important
Region: II | Farley | 11077 | 03/31/2014 05/14/2014 | 2014002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement fire protection program requirements |  | H.3 Change Management | TE?: N | 05000364 Farley 2 |  | 71111.19 | A self-revealing NCV of TS 5.4.1.c, "Fire Protection Program Implementation," was identified for the licensee's failure to establish and implement adequate procedures required to maintain functionality of the Unit 2 auxiliary building fire protection syst
Region: II | Farley | 11063 | 09/30/2013 10/29/2013 | 2013004-01 | NRC | NCV | Initiating Events | Green | Failure to control transient combustible materials in the Unit 2 auxiliary building |  | H.4(b) Procedural Compliance | TE?: N | 05000364 Farley 2 |  | 71111.05Q | The NRC identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1.c, "Fire Protection Program Implementation," for failing to properly control combustible material in fire risk-significant areas without a continuous fire watch as requir
Region: II | Farley | 11067 | 09/30/2013 10/29/2013 | 2013004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement fire protection program requirements |  | H.3(b) Work Activity Coordination | TE?: N | 05000348 Farley 1 |  | 71152 | A self-revealing NCV of TS 5.4.1.c, "Fire Protection Program Implementation," was identified, because the licensee failed to implement written procedures to cover activities of the Fire Protection Program as documented in Appendix 9B of the updated final
Region: II | Farley | 11062 | 06/30/2013 08/01/2013 | 2013003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to properly maintain procedures to ensure reactor vessel head vent path was preserved |  | H.4(a) Human Error Prevention | TE?: N | 05000364 Farley 2 |  | 71111.2 | Green. A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1,"Procedures," was identified for the licensee's failure to establish procedures recommended in Regulatory Guide (RG) 1.33. Specifically, the licensee did not properly
Region: II | Farley | 11055 | 03/31/2013 05/02/2013 | 2013002-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform 50.59 Evaluation for Replacement of TDAFW Pump Governor |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-IV-NCVIV | 05000348 Farley 1 05000364 Farley 2 |  | 71111.17T | Green. An NRC-identified Green finding and associated Severity Level IV, NCV, of 10 CFR 50.59(d)(1), were identified for the failure to perform an evaluation of a turbine-driven auxiliary feed water (TDAFW) pump governor modification on Units 1 and 2 agai
Region: II | Farley | 11051 | 09/30/2012 10/30/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Damaged wiring and resistors in the static exciter and voltage regulator circuit of 1C EDG |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000348 Farley 1 |  | 71111.12 | A Green self revealing NCV of TS 5.4.1.a, Procedures, was identified for the failure to accomplish the installation of the auxiliary contacts of the K1 relay associated with the 1C emergency diesel generator (EDG) in accordance with station work order SNC
Region: II | Farley | 11052 | 09/30/2012 10/30/2012 | 2012004-02 | Self - Revealed | NCV | Initiating Events | Green | Loss of shutdown cooling due to an unplanned loss of Train A 4160v safety related switchgear |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000348 Farley 1 |  | 71153 | A Green self revealing non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.a, Procedures, was identified for the failure to accomplish shutdown of the 1-2A emergency diesel generator (EDG) in accordance with station procedure FNP-1-STP-40.0.
Region: II | Farley | 11042 | 06/30/2012 07/20/2012 | 2012003-01 | NRC | NCV | Barrier Integrity | Green | Failure to perform ISI general visual examinations of containment moisture barrier associated with containment liner leak chase test connection threaded pipe plugs |  |  | TE?: N | 05000348 Farley 1 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50.55a, "Codes and Standards," involving the licensee's failure to properly apply Subsection IWE of ASME Section XI for conducting general visual examinations of the metal-to-metal pipe
Region: II | Farley | 11043 | 06/30/2012 07/20/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to implement design control measures to verify the adequacy of CST design |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | NONE | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to implement design control measures to verify the adequacy of design inputs, assumptions, or limiting plant condit
Region: II | Farley | 11049 | 06/30/2012 07/20/2012 | 2012003-03 | NRC | FIN | Occupational Radiation Safety | Green | Failure to monitor for auxiliary building airborne radioactivity levels as described in the FSAR |  | H.2(d) Facilities & Equipment | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71124.05 | The inspectors identified a Green finding for failure to meet the FSAR continuous online radiation monitor design bases as described in FSAR Section 12.2.4, Airborne Radioactivity Monitoring. Specifically, six of the nine continuous online radiation monit
Region: II | Farley | 11050 | 06/30/2012 07/20/2012 | 2012003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent transfer of approximately 5000 gallons of borated water from the RWST to the RCS refueling cabity and spent fuel pool |  | H.3(b) Work Activity Coordination | TE?: N | 05000348 Farley 1 |  | 71152 | A self-revealing Green non-cited violation of Technical Specification 5.4.1, Procedures, was identified for the licensee's failure to adhere to the information contained within clearance 1-DT-24-E21-03211. This failure resulted in the unplanned transfer o
Region: II | Farley | 11009 | 12/08/2011 12/19/2011 | 2011010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Control Measures to Verify the Adequacy of CST Design |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," (with two examples) for the licensee's failure to implement design control measures to verify the adequacy of design inputs, assumptions, or
Region: II | Farley | 11014 | 12/08/2011 12/19/2011 | 2011010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Control Measures to Verify the Adequacy of AFW Design |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to implement design control measures to verify the adequacy of design inputs, assumptions, or limiting plant conditions which
Region: II | Farley | 11015 | 12/08/2011 12/19/2011 | 2011010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedural Guidance for Controlling Steam Generator and Pressurizer Level During Loss of Air Events |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," for the licensee's failure to provide adequate procedural guidance for controlling steam generator (SG) and pressurizer level during loss of instrume
Region: II | Farley | 11017 | 12/08/2011 12/19/2011 | 2011010-05 | NRC | URI | Mitigating Systems | Green | Non-Conservative Assumptions Regarding AFW Net Positive Suction Head |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | The team determined that additional information and/or evaluation by the licensee were required to determine if operation of the AFW system during a loss of instrument air event (as described above) was consistent with system design basis assumptions a
Region: II | Farley | 11022 | 12/08/2011 12/19/2011 | 2011010-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate the Design Basis into Procedures for Minimum CCW Flow to the RHR Seal Coolers and Minimum Flow Requirements for the AFW Pumps |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," involving two examples. In the first example, the licensee failed to translate the minimum Component Cooling Water (CCW) flow for the Residua
Region: II | Farley | 11023 | 12/08/2011 12/19/2011 | 2011010-07 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor or Perform Effective Preventive Maintenance on the 2C EDG Exhaust Fan Louvers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to perform condition monitoring or otherwise implement an appropriat
Region: II | Farley | 11024 | 12/08/2011 12/19/2011 | 2011010-08 | NRC | NCV | Mitigating Systems | Green | Failure to Develop an Adequate Procedure to Test the Turbine Driven Auxiliary Feedwater Pump Discharge Check Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000348 Farley 1 |  | 7111121 | Green. The team identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish an adequate test procedure used to demonstrate that the Turbine Driven Aux
Region: II | Farley | 11008 | 11/30/2011 01/27/2012 | 2011014-01 | NRC | NCV | Mitigating Systems | Green | TDAFW Pump Inoperable due to Improper Control of Station Drawings |  | H.3(b) Work Activity Coordination | TE?: N | 05000364 Farley 2 |  | NONE | Green: A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control was identified for the licensee's failure to correctly update their design drawing for the Unit 2 Turbine Driven Auxiliary Feedwater (TDAFW) pump ele
Region: II | Farley | 11001 | 09/30/2011 10/28/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to properly pre-plan maintenance activities whle conducting tagout operations on the 2C charging pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000364 Farley 2 |  | 71111.12 | A self-revealing NCV of Technical Specification (TS) 5.4.1a was identified for the licensee's failure to implement procedures recommended in Regulatory Guide (RG) 1.33. Specifically, the licensee did not properly pre-plan maintenance tagout activities on
Region: II | Farley | 10992 | 05/24/2011 06/08/2011 | 2011012-01 | NRC | NCV | Initiating Events | Green | Flame Detected on the 1A RCP Handswitch |  | H.4(a) Human Error Prevention | TE?: N | 05000348 Farley 1 |  | NONE | TBD. A self-revealing finding and apparent violation of Technical Specification 5.4, Procedures, was identified for failing to maintain the configuration of the 1A RCP oil lift pump system in accordance with plant design and drawings. The licensee incorre
Region: II | Farley | 10986 | 03/31/2011 04/29/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to maintain safety-related cables in a non-submerged environment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000348 Farley 1 |  | 71111.06 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to implement measures to assure safety-related cables remained in an environment for which they were certified. Safety-related ca
Region: II | Farley | 10561 | 12/31/2010 01/27/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Station Guidance on Use of Extension Cords and Placement of Equipment in Safety-Related Cable Trays (Section 1R05) |  | H.4(b) Procedural Compliance | TE?: N | 05000364 Farley 2 |  | 71111.05Q | An NRC identified NCV of Technical Specification (T.S.) 5.4.1 was identified for failure to follow station maintenance procedures related to the use of extension cords, which resulted in an energized smoke eductor and its extension cord located within one
Region: II | Farley | 10982 | 12/31/2010 01/27/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Effectively Implement Risk Management Activities Results in Loss of Single Train of Shutdown Core Cooling (Section 4OA2.2.b.1) |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000348 Farley 1 |  | NONE | A self-revealing NCV of 10 CFR 50.65(a)(4) revealed itself when Unit 1 train 'A' RHR was lost because the licensee failed to identify and assess the loss of a plant significant component during plant repairs. On October 15, 2010, Unit 1 was in a refueling
Region: II | Farley | 10560 | 09/30/2010 10/29/2010 | 2010004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate procedure leads to LOSP on Unit 2 4160 volt safety related bus |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000364 Farley 2 |  | NONE | Green. A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensees' failure to modify surveillance test procedure FNP-2-STP-40.0, Safety Injection with Loss of Off-site Power (LOSP)
Region: II | Farley | 10551 | 06/30/2010 07/30/2010 | 2010003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to perform adequate surveys to identify potential radiological hazards during reactor cavity drain down |  | H.3(a) Work Planning | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | NONE | -Green A self-revealing non-cited violation (NCV) of 10 CFR Part 20.1501(a) was identified for failure to perform adequate surveys to identify rising radiation levels during the lowering of water level in the reactor cavity. This resulted in an uncontroll
Region: II | Farley | 10552 | 06/30/2010 07/30/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to maintain safety-related cables in a non-submerged environment |  | P.1(b) Trend Performance CAP | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | -Green An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to implement measures to assure that safety-related cables remained in an environment for which they were certified. Safe
Region: II | Farley | 10550 | 04/15/2010 06/02/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate controls for service water pump procurement |  |  | TE?: N | 05000364 Farley 2 |  | NONE | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," was identified for the licensee's failure to establish measures to assure that the 2E service water pump (SWP) in
Region: II | Farley | 10543 | 03/31/2010 04/29/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | Failure to control combustible material in a no intervening combustible allowed area of the plant |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000348 Farley 1 |  | 71111.05Q | An NRC-identified NCV of License Condition 2.C.(4) was identified for the failure to control combustible material in the Unit 1 Component Cooling Water (CCW) Pump area as required by the licensee's administrative controls program. Workers left combustible
Region: II | Farley | 10547 | 03/31/2010 04/29/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to re-evaluate significant changes in assumption to prompt operability determination of Unit 2 TDAFW pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000364 Farley 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings for the failure to implement procedure NMP-AD-012, Operability Determinations and Functionality Assessments. Specifically, the licensee fai
Region: II | Farley | 10548 | 03/31/2010 04/29/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Violatin of technical specification 5.4.1 for failure to maintain procedures for full flow recirculation after a loss of coolant accident |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.17T | The inspectors identified a Green NCV of TS 5.4.1 for the failure to maintain emergency procedure FNP-1/2-ESP-1.3, Transfer to Cold Leg Recirculation, Rev. 19. ESP-1.3 contained a step to verify containment sump level was sufficient to adequately cover th
Region: II | Farley | 10549 | 03/31/2010 04/29/2010 | 2010002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to maintain control of combustible material |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000348 Farley 1 |  | 71153 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified for the licensee's failure to maintain combustible material a distance of 35 feet or greater from the "hot work" area as required by station
Region: II | Farley | 10523 | 12/31/2009 01/29/2010 | 2009005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify A Credible Source of Flooding in the Internal Flooding Evaluation of Record |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.06 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, identified for licensee's failure to identify a credible source of flooding in their internal flooding evaluation of record (performed in 1999). On March 27, 2009, a licensee fl
Region: II | Farley | 10528 | 12/31/2009 01/29/2010 | 2009005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Maintenance Inspections of Safety-Related Switchgear |  | H.3(b) Work Activity Coordination | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.12 | A self-revealing NCV of TS 5.4.1, Procedures, was identified for failure to implement preventative maintenance inspections on the 1-2L 600 volt load center as specified by FNP-0-EMP-1322.10, Maintenance and Cleaning of Westinghouse Switchgear. Failure to
Region: II | Farley | 10529 | 12/31/2009 01/29/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | 1-2R 600 Volt Load Center Operability |  | H.4(b) Procedural Compliance | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.15 | NRC-identified NCV of TS 3.8.9 was identified forfailure to meet LCO of maintaining 2 trains of AC vital bus electrical power distribution subsystems operable. Licensee failed to evaluate plant conditions and identify 1-2R 600 vlc was unable to meet surve
Region: II | Farley | 10530 | 12/31/2009 01/29/2010 | 2009005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Performance Monitoring of SWP Seismic Supports |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | NONE | Self-revealing NCV of 10CFR50.65(a)(1) identified for failure to perform monitoring of SWIS seismic rings resulting in inability of 2A,B,C&E SWP seismic rings to perform their func.b/c of fastener degradation. Licensee entered CR into CAP as 2009109700 an
Region: II | Farley | 10531 | 12/31/2009 01/29/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | Load Sequencer Operability during EDG Surveillance Tests |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71153 | NRC identified Green NCV of 10CFR50, Appendix B, Criterion III, Design Control, for failure to translate EDG system inoperable during test performance. Licensee entered issue into CAP as CR2008105195 & is taking corrective action to modify the EDG LOSP ci
Region: II | Farley | 10539 | 11/20/2009 12/31/2009 | 2009007-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for the B Train SSPS System Testing |  |  | TE?: N | 05000348 Farley 1 |  | 71152B | A seal-reaviling Green NCV of 10 CFR 50 Appendix B, Criterion V was identified for an inadequate procedure for testing the 'B' train SSPS. While Unit 1 was in Mode 5 and N31 source range instrumentation was tagged out and unavailable, the licensee perform
Region: II | Farley | 10521 | 09/30/2009 10/30/2009 | 2009004-01 | NRC | URI | Mitigating Systems | Green | Failure to Implement Performance Monitoring of Service Water Pump Seismic Supports |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.12
Region: II | Farley | 10527 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Surveillance Test Instructions to Prevent Over-Speed of the TDAFW Pump |  | H.4(b) Procedural Compliance | TE?: N | 05000348 Farley 1 |  | 71111.22 | Green. A self-revealing NCV of Technical Specification (TS) 5.4.1, Procedures, was identified for failure to implement surveillance test procedure instructions for starting the Unit 1 TDAFW pump. The failure resulted in an over-speed trip and inoperabilit
Region: II | Farley | 10522 | 09/30/2009 10/30/2009 | 2009004-03 | NRC | URI | Mitigating Systems | Green | Load Sequencer Operability during EDG Surveillance Tests |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152
Region: II | Farley | 10520 | 09/30/2009 10/30/2009 | 2009004-04 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Procedures Used to Prevent Seismic Interaction with Safety-Related Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000348 Farley 1 |  | 71153 | Green. A self-revealing finding was identified for a failure to implement procedures to ensure that temporary equipment carts were immobilized in order to prevent inadvertent contact with safety related equipment. Specifically, the Unit 1 'H' bus protecti
Region: II | Farley | 10495 | 09/30/2009 10/30/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Degraded Emergency Air System Conditions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | NONE | Green. A self revealing NCV of 10 CFR 50.65(a)(1), Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, was identified for failure to monitor and maintain the emergency air system's capability to operate the steam generato
Region: II | Farley | 10512 | 06/30/2009 07/28/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Procedures for SG Blowdown Isolation Valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.19 | Green. An NRC identified NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, was identified for failure to establish adequate procedures to verify automatic closure of the Unit 1 and Unit 2 Steam Generator blowdown (SGBD) isolation valves. This find
Region: II | Farley | 10513 | 06/30/2009 07/28/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Test Procedures for Verification of Steam Dump Arming From Reactor Trip (P-4) Signal and P-4 Contact Verification |  | H.3(b) Work Activity Coordination | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.22 | Green. A self-revealing NCV of TS 5.4.1.a. for failure to implement FNP-1-STP- 33.8, Verification of Steam Dump Arming from Reactor Trip (P-4) Signal and P-4 Contact Verification, was identified when licensee personnel took actions not directed by the pro
Region: II | Farley | 10514 | 06/30/2009 07/28/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Include Water Tight Doors in the Scope of the Maintenance Rule |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | Green. An NRC identified NCV of 10 CFR 50.65 (b) was identified for failure to include the Auxiliary Building water-tight doors within the scope of the maintenance rule (MR) monitoring program. During routine plant inspections, the inspectors noticed degr
Region: II | Farley | 10511 | 03/31/2009 04/30/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate maintenance instructions results in inoperability of the TDAFW pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000364 Farley 2 |  | 71111.19 | A self-revealing, Green non-cited violation of TS 5.4.1 was identified for inadequate work instructions used to perform corrective maintenance on the Unit 2 TDAFW pump 'A' UPS which resulted in an inoperability of the TDAFW pump. This finding has been ent
Region: II | Farley | 10507 | 02/27/2009 04/09/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of SW Capability to Concurrently Provide System Design Basis Cooling Requirements and the AFW Alternate Water Source. |  | H.4(a) Human Error Prevention | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121 | Green: The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee failed to establish measures to verify the design capability of
Region: II | Farley | 10526 | 02/27/2009 04/09/2009 | 2009006-02 | NRC | URI | Mitigating Systems | Green | Degraded Emergency Air System Conditions |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 7111121
Region: II | Farley | 10500 | 04/04/2008 05/13/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Fire Procedure Credits Unreliable Indication |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.4.1, Procedures, in that Units 1 and 2 post-fire safe shutdown abnormal operating procedures AOP 28.1, Fire or Inadvertent Fire Protection System Actuation in the Cable Spreading Room,
Region: II | Farley | 10501 | 04/04/2008 05/13/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Areas Where OMAs Are Performed Did Not Have ELUs Installed |  |  | TE?: N | 05000364 Farley 2 |  | 71111.05T | The team identified a non-cited violation of Farley Unit 2 Operating License Condition 2.C.(6), for the licensee's failure to fully implement the approved fire protection program, in that emergency lighting units (ELUs) were not installed in all areas whe
Region: II | Farley | 10504 | 04/04/2008 05/13/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | ELU Test Failures Were Not Documented In CRs As Required By Procedure |  |  | TE?: N | 05000364 Farley 2 |  | 71111.05T | The team identified a non-cited violation of Farley Unit 2 Operating License Condition 2.C.(6), for the licensee's failure to fully implement test control requirements incorporated in approved plant procedures associated with the periodic testing of emerg
Region: II | Farley | 10494 | 03/30/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Installation of a Maintenance Jumper for the 2C CCW Pump Cell Switch |  |  | TE?: N | 05000364 Farley 2 |  | 71111.15 | The NRC identified a Green NCV of 10 CFR 50 Appendix B, Criterion III for failing to implement measures to verify design adequacy resulting in the installation of a maintenance jumper on the cell switch for the Unit 2 2C Component Cooling Water (CCW) pump
Region: II | Farley | 10498 | 03/30/2008 04/30/2008 | 2008002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of CCW 4160 Circuit Breaker to Operate When Demanded Due to Ineffective Corrective Actions |  |  | TE?: N | 05000348 Farley 1 |  | 71153 | A self-revealing Green NCV of 10 CFR 50 Appendix B, Criterion XVI was identified for inadequate corrective actions which resulted in the 1C CCW Pump's circuit breaker failing to operate when required. The combination of inadequate tolerances, manipulation
Region: II | Farley | 10499 | 03/30/2008 04/30/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent the Installation of a Nonconforming Breaker into the Cubicle for the 1C CCW Pump |  | H.4(b) Procedural Compliance | TE?: N | 05000348 Farley 1 |  | 71153 | The NRC identified a Green NCV of 10 CFR 50 Appendix B, Criterion XV for failing to properly control nonconforming components resulting in the installation of a 4160 volt breaker for the Unit 1 1C CCW pump with a stop bolt gap dimension not meeting vendor
Region: II | Farley | 10487 | 12/31/2007 01/30/2008 | 2007005-02 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess Risk Resulting in Unit 2 Reactor Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | The NRC inspectors identified a Green NCV for inadequate risk assessment which resulted in a Unit 2 reactor trip when performing switchyard relay testing. This event has been entered into the licensee's corrective action program (CAP) as Condition Report
Region: II | Farley | 10488 | 12/31/2007 01/30/2008 | 2007005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Two ECCS Trains Operable Due to Gas Accumulation in the Charging Pump Suction Piping |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000364 Farley 2 |  | 71153 | A self-revealing NCV was identified for gas binding of the 2A CCP that resulted in a failure to maintain the 'A' train of HHSI in an operable condition, in accordance with T.S. 3.5.2, ECCS. This event has been entered into the licensee's CAP as CR 2005112
Region: II | Farley | 10479 | 08/24/2007 09/21/2007 | 2007006-02 | NRC | FIN | MISC | Green | Biennial Identification and Resolution of Problems Inspection Results |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152B | One finding of very low safety significance (Green) was identified. The licensee was generally effective in identifying problems at a low threshold and entering them into the corrective action program. The licensee properly prioritized issues entered into
Region: II | Farley | 10483 | 08/24/2007 09/21/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify the Complete Population of Service Water Valves Affected by the System's Corrosive Environment and Correct the Condition |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152B | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for a failure to promptly identify and correct a condition adverse to quality. In November 2004, the licensee identified that the carbon stee
Region: II | Farley | 10485 | 07/16/2007 08/17/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Breaker Failures and Subsequent Corrective Actions. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 95001 | The NRC identified a Green non-cited violation with two examples of 10 CFR 50, Appendix B, Criterion XVI, for failing to promptly identify and correct a condition adverse to quality. For the first example, weaknesses with the thoroughness of evaluations f
Region: II | Farley | 10476 | 12/31/2006 01/29/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Main Steam Isolation Valve Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000348 Farley 1 |  | 71153 | An NRC-identified non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Actions, was identified for failure to correct repetitive failures of main steam isolation valves (MSIVs). The April 2006 failure of the three Unit 1 outboard MSIVs t
Region: II | Farley | 10477 | 12/31/2006 01/29/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Fire Procedure Failed to Ensure that AC Power Would Be Available |  |  | TE?: N | 05000364 Farley 2 |  | NONE | An NRC-identified non-cited violation of Unit 2 License Condition C(6), Fire Protection, was identified. Operator actions to isolate the control power for AC power distribution breakers from the effects of a fire in the main control room were included in
Region: II | Farley | 10470 | 06/30/2006 07/27/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures for Containment Closeout |  |  | TE?: N | 05000348 Farley 1 |  | 71111.2 | Green. A Green non-cited violation (NCV) of Technical Specification 5.4, Procedures, was identified by the NRC for failure to follow procedural guidance associated with removal of debris in containment. The licensee performed a containment inspection; how
Region: II | Farley | 10473 | 06/30/2006 07/27/2006 | 2006003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Control Contractors Results in Fuel Transfer System Damage |  |  | TE?: N | 05000348 Farley 1 |  | 71111.2 | A Green self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion VII, Control of Purchased Material, Equipment, and Services, was identified for failure to control adequately contractors during the Unit 1 refueling outage that resulted
Region: II | Farley | 10474 | 06/30/2006 07/27/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Pump Code Requirements/Details |  |  | TE?: N | 05000364 Farley 2 |  | 71152 | A Green non-cited violation (NCV) of 10 CFR 50.55a (a) (2) was identified by the NRC for the licensee failing to comply with the ASME Boiler and Pressure Vessel Code, Section XI, for Class 2 Components. The licensee failed to meet the ASME Code requiremen
Region: II | Farley | 10468 | 03/31/2006 04/28/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Conditions Resulting in the Unrecognized Inoperability of the 1-2A Emergency Diesel Generator |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000348 Farley 1 |  | 71153 | A Green, NRC-identified, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XIV, Corrective Actions, was identified for failure to promptly identify and correct a failure of the 1F (Unit 1 Train A Engineered Safety Feature) 4-kV bus synchroscop
Region: II | Farley | 24429 | 11/09/2018 |  | Licensee - Identified | LIV |  | Green | Failure to Establish Compensatory Measures as Required by Procedure 71152 |  |  | TE?: N | 05000348 Farley 1 05000364 Farley 2 |  | 71152 | January 16, 2018 through August 28, 2018, the licensee failed to establish compensatory measures (fire watches) as required by licensee procedure FNP-0-SOP-0.4 on thirteen occasions. The cause of the fire watch discrepancies were mainly because Farley Ope
Region: II | Farley | 11162 | 08/04/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulted in Inoperable 2B Diesel Generator (1R22) |  | H.14 Conservative Bias | TE?: N | 05000364 Farley 2 |  | 71111.22 | To Be Determine (TBD): The NRC identified apparent violation (AV) of Technical Specification (TS) 5.4.1, "Procedures," for the licensee's failure to implement corrective maintenance work order instructions to identify and replace a degraded jacket water f
Region: II | Harris | 125824 | 09/30/2019 10/24/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Effective Corrective Actions to Preclude Repetition of a Significant Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000400 Harris 1 | Equipment Performance | 71153 | A self-revealing Green non-cited violation (NCV) of 10CFR50, Appendix B, Criterion XVI, “Corrective Actions,” was identified for the licensee’s failure to implement effective corrective actions to preclude repetition of a significant condition adverse to
Region: II | Harris | 124662 | 03/22/2019 05/02/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Three Examples of Failure Develop a Valid Mathematical Model for ASCO Solenoid Valves |  | NPP | TE?: N | 05000400 Harris 1 | Design Control | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV), with three examples, of 10 CFR 50.49(e)(5) for the licensee’s failure to model the effects of thermal insulation, oven characteristics, and differences between nitrogen an
Region: II | Harris | 24669 | 09/30/2018 10/26/2018 | 2018003-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement Adequate Periodic Exercising of Turbine Trip Solenoid Operated Valves |  | P.5 - Operating Experience | TE?: N | 05000400 Harris 1 |  | 71152 | A self-revealing Green finding was identified for the licensee’s failure to establish and implement adequate preventive maintenance (PM) for exercising the turbine electro-hydraulic auto-stop trip (AST) solenoid operated valves (SOVs) in accordance with p
Region: II | Harris | 24125 | 06/30/2018 08/10/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality For a Through-Wall Leak in the ESW Screen Wash Piping |  | P.1 - Identification | TE?: N | 05000400 Harris 1 |  | 71111.04Q | An NRC-identified Green NCV of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, “Corrective Actions,” was identified for the licensee’s failure to promptly identify and correct a condition adverse to quality involving through-wall
Region: II | Harris | 24126 | 06/30/2018 08/10/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Brigade Performance Assessment of Announced Fire Drill |  | P.6 - Self-Assessment | TE?: N | 05000400 Harris 1 |  | 71111.05Q | An NRC-identified Green NCV of 10 CFR 50.48(c) and National Fire Protection Association Standard (NFPA) Standard 805, Section 3.4.3, “Training and Drills,” was identified for the licensee’s failure to adequately assess the fire brigade performance during
Region: II | Harris | 24140 | 06/30/2018 08/10/2018 | 2018002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Adequate Steam Generator Blowdown Demineralizer Control Procedures |  | H.12 - Avoid Complacency | TE?: N | 05000400 Harris 1 |  | 71152 | A self-revealing Green NCV of Technical Specifications (TS) 6.8.1.a, “Procedures and Programs,” was identified for licensee’s failure to establish and implement adequate steam generator blowdown demineralizer control operating procedures resulting in exce
Region: II | Harris | 24141 | 06/30/2018 08/10/2018 | 2018002-05 | NRC | NCV | Initiating Events | Green | Failure to Follow Secondary Water Chemistry Plan for Elevated Levels of Secondary Water Impurities |  | H.8 - Procedure Adherence | TE?: N | 05000400 Harris 1 |  | 71152 | An NRC-identified Green NCV of TS 6.8.4.c, “Secondary Water Chemistry,” was identified for the licensee’s failure to follow secondary water chemistry control requirements in accordance with procedure CSD-CP-HNP-0002, Harris Secondary Water Chemistry Strat
Region: II | Harris | 24142 | 06/30/2018 08/10/2018 | 2018002-06 | NRC | NCV | Emergency Preparedness | Green | Failure to Implement Viable Compensatory Actions with Seismic Monitoring System Out of Service for Planned Preventive Maintenance |  | H.5 - Work Management | TE?: N | 05000400 Harris 1 |  | 71152 | An NRC-identified Green NCV of 10 CFR 50.54(q)(2) was identified for the licensee’s failure to follow and maintain the effectiveness of its emergency plan that meets the requirements of the risk-significant emergency planning standard 10 CFR 50.47(b)(4).
Region: II | Harris | 16756 | 09/30/2016 11/01/2016 | 2016003-02 | NRC | NCV | MISC | Green | Failure to Conduct and Document Fatigue Assessments for Contract Personnel |  | H.7 Documentation | TE?: N | 05000400 Harris 1 |  | 71152 | Inspectors identified a Green non-cited violation (NCV) of 10 CFR 26.27, Written Policy and Procedures, for the failure to conduct and document fatigue assessments for self-declared fatigued contractors, and other contract personnel called in to supplemen
Region: II | Harris | 16754 | 03/31/2016 04/19/2016 | 2016001-01 | NRC | FIN | Mitigating Systems | Green | NRC Biennial Written Examinations Did Not Meet Qualitative Standards |  |  | TE?: N | 05000400 Harris 1 |  | NONE | . The inspectors identified a finding of very low safety significance associated with 10 CFR 55.59, "Requalification," based on a determination that greater than 20 percent of the written examination questions administered to licensed operators during th
Region: II | Harris | 16748 | 12/31/2015 01/27/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | 'B' ESW System Safety-Related Cables Submerged in Water |  | H.5 Work Management | TE?: N | 05000400 Harris 1 |  | 71111.06 | A self-revealing Green non-cited violation (NCV) of Criterion III, Design Control, Appendix B of 10 CFR Part 50, occurred due to the licensee's failure to maintain Class 1E (safety-related) electrical cables in an environment for which they are designed.
Region: II | Harris | 16749 | 12/31/2015 01/27/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Post-Maintenance Testing |  | H.10 Bases for Decisions | TE?: N | 05000400 Harris 1 |  | 71111.19 | A self-revealing Green NCV of Criterion XI, Test Control, Appendix B of 10 CFR Part 50, occurred due to the licensee's failure to perform adequate post-maintenance testing on the essential services chilled water (ESCW) chillers. Specifically, on multiple
Region: II | Harris | 16750 | 12/10/2015 12/22/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish As-found Testing on 6.9kV Vacuum Breakers |  |  | TE?: N | 05000400 Harris 1 |  | 71111.17T | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a periodic as-found testing program of safety-related 6.9kV vacuum breakers in accordance with applicable desi
Region: II | Harris | 16753 | 10/01/2015 11/13/2015 | 2015008-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Follow EPM-410 Procedure |  | P.3 Resolution | TE?: N | 05000400 Harris 1 |  | 71152B | An NRC-identified Green NCV of 10 CFR 50.54(q)(2) was identified, for the licensee's failure to follow and maintain, in effect, the Emergency Plan when performing monthly testing of the Technical Support Center (TSC). Specifically, the licensee failed to
Region: II | Harris | 16734 | 09/30/2015 10/30/2015 | 2015003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Clearance and Tagging Procedure |  | H.8 Procedure Adherence | TE?: N | 05000400 Harris 1 |  | 71111.06 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, Procedures and Programs, for the licensee's inadequate implementation of procedure AD-OP-ALL-0200, Clearance and Tagging, when the licensee failed to establish an appropriate clearance boun
Region: II | Harris | 16736 | 09/30/2015 10/30/2015 | 2015003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Adequate Corrective Actions |  | H.6 Design Margins | TE?: N | 05000400 Harris 1 |  | 71111.12 | A self-revealing green finding was identified for failure to implement adequate corrective actions for the repeated failure of PS-4175, low pressure steam inlet crossover pressure switch in accordance with licensee procedure AD-PI-ALL-0100, Corrective Act
Region: II | Harris | 16745 | 09/30/2015 10/30/2015 | 2015003-04 | Self - Revealed | NCV | Initiating Events | Green | Loss of "A" ESW Train |  | H.6 Design Margins | TE?: N | 05000400 Harris 1 |  | 71111.18 | A self-revealing green NCV of 10 CFR 50, Appendix B, Quality Assurance Criteria for Nuclear Power Plants and Fuel Reprocessing Plants, Criterion III, Design Control, was identified for failure to implement design control measures that verify adequacy of d
Region: II | Harris | 16746 | 09/30/2015 10/30/2015 | 2015003-05 | NRC | NCV | Initiating Events | Green | Failure to implement EQ Program Requirements |  | P.3 Resolution | TE?: N | 05000400 Harris 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to identify and correct a condition adverse to quality affecting the Environmental Qualification (EQ) Program. Specifically, the licensee failed
Region: II | Harris | 16721 | 06/30/2015 07/29/2015 | 2015002-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Emergency Assessment Capability |  | P.2 Evaluation | TE?: N | 05000400 Harris 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR 50.54(q)(2) was identified for the licensee's failure to maintain adequate equipment for assessing and monitoring actual or potential offsite consequences of a radiological emergency condition as required by 10 CFR 50
Region: II | Harris | 16728 | 06/30/2015 07/29/2015 | 2015002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement the Control Room Area HVAC System Procedure |  | H.8 Procedure Adherence | TE?: N | 05000400 Harris 1 |  | 71111.15 | An NRC-identified Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, Procedures and Programs, was identified for the licensee's inadequate implementation of procedure OP-173, Control Room Area HVAC System. Specifically, the licensee fa
Region: II | Harris | 16729 | 06/30/2015 07/29/2015 | 2015002-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Post Modification Testing of 1CZ-1 and 1CZ-2 HMCP Breakers |  | H.5 Work Management | TE?: N | 05000400 Harris 1 |  | 71111.18 | An NRC-identified Green NCV of TS 6.8.1, Procedures and Programs, was identified for the licensee's failure to perform adequate post modification tests (PMTs) on Motor Circuit Protectors (HMCP) breakers for dampers 1CZ-1 and 1CZ-2 as required by procedure
Region: II | Harris | 16717 | 12/31/2014 01/27/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Equipment Clearance Procedure |  | H.11 Challenge the Unknown | TE?: N | 05000400 Harris 1 |  | 71111.15 | The NRC identified a Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1, Procedures and Programs, for the licensee's inadequate implementation of procedure OPS-NGGC-1301, Equipment Clearance, when they failed to identify required compen
Region: II | Harris | 16715 | 09/30/2014 10/30/2014 | 2014004-02 | NRC | NCV | Emergency Preparedness | Green | Loss of Emergency Planning Sirens |  | H.8 Procedure Adherence | TE?: N | 05000400 Harris 1 |  | 71152 | The NRC identified a Green NCV associated with emergency preparedness planning standard 10 CFR 50.47(b)(5), which requires in part, that the means to provide alert and notification and clear instruction to the populace within the plume exposure pathway Em
Region: II | Harris | 16705 | 07/25/2014 09/03/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Test That Verified Interlock Capability |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a test program to assure that the interlocks between the Charging/Safety Injection (CSI) pump alternate
Region: II | Harris | 16706 | 07/25/2014 09/03/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Procedural Limitations Based on Design Requirements of the Emergency Diesel Generators |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that applicable regulatory requirements in technical specification surveillance requirement 4.8.1.1.2.e.
Region: II | Harris | 16712 | 07/25/2014 09/03/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Procedural Limitations to Prevent Exceeding TS Limits and Safety Analysis Assumptions |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that applicable regulatory requirements in technical specification (TS) 3.7.1.1 and design basis inputs
Region: II | Harris | 16713 | 07/25/2014 09/03/2014 | 2014007-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Categorization of Valves in Potential Release Paths During Accidents |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50.55a, "Codes and Standards," for the licensee's failure to categorize valves that were subject to a specific maximum leakage amount while in the closed position as Category A, as required
Region: II | Harris | 16704 | 06/30/2014 07/25/2014 | 2014003-01 | NRC | FIN | Initiating Events | Green | Failure to Adequately Implement a Plant Modification |  | H.13 Consistent Process | TE?: N | 05000400 Harris 1 |  | 71111.18 | The inspectors identified a finding of very low safety significance (Green) when the licensee did not adequately implement the procedural requirements of ADM-NGGC-0106, "Configuration Management Program Implementation," during the installation of a tempor
Region: II | Harris | 16701 | 05/09/2014 06/23/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate All Targets Within the Zone of Influence of Ignition Sources |  |  | TE?: N | 05000400 Harris 1 |  | 71111.05XT | An NRC-identified non-cited violation of 10 CFR 50.48 (c) and National Fire Protection Association Standard (NFPA) 805 Section 2.4.3.2 was identified for the licensee's failure to address in the Fire Probabilistic Risk Assessment (Fire PRA) the risk contr
Region: II | Harris | 16698 | 03/31/2014 04/28/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately perform the new fuel oil surveillance requirement |  | H.1 Resources | TE?: N | 05000400 Harris 1 |  | 71111.22 | Green. The inspectors identified a Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1.a, Procedures and Programs, for the licensee's failure to have an adequate surveillance test to implement the requirements of SR 4.8.1.1.2.c, as requi
Region: II | Harris | 16699 | 03/31/2014 04/28/2014 | 2014002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to prevent recurrence of a significant condition adverse to quality |  | P.3 Resolution | TE?: N | 05000400 Harris 1 |  | 71152 | Green. A self-revealing Green finding was identified for the failure to implement an adequate corrective action to prevent recurrence (CAPR) for a Significant Condition Adverse to Quality (SCAQ) as required by licensee procedure CAP-NGGC-0205, Condition E
Region: II | Harris | 16700 | 03/31/2014 04/28/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to comply with Technical Specification 3.11.5.2 |  | H.8 Procedure Adherence | TE?: N | 05000400 Harris 1 |  | 71152 | Green. The inspectors identified a Green NCV of TS 3.11.2.5, Explosive Gas Mixture, for the failure to implement the actions of the limiting condition for operation (LCO). Specifically, during shutdown plant operations in November 2013, the licensee ident
Region: II | Harris | 16695 | 12/31/2013 02/04/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain environmental qualification for electric equipment |  | P.3(a) Self-Assessment | TE?: N | 05000400 Harris 1 |  | 71111.18 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.49 for the failure to adequately implement the environmental qualification (EQ) program for electric equipment important to safety. Specifically, between September 2013 and November
Region: II | Harris | 16697 | 12/31/2013 02/04/2014 | 2013005-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate transformer preventive maintenance procedure |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000400 Harris 1 |  | 71152 | A self-revealing Green finding was identified for the licensee's failure to adequately establish and implement procedure NGG-PMB-XFM-02, Equipment Reliability Template for Dry-Type Transformers, and implementing procedure PM-E0015, 480 V and 6.9 kV Transf
Region: II | Harris | 16692 | 09/30/2013 11/04/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to compensate for a blocked open fire door |  | H.3(a) Work Planning | TE?: N | 05000400 Harris 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of the Shearon Harris Nuclear Power Plant Operating License NPF-63 condition 2.F, Fire Protection Program, and 10 CFR 50.48(c), National Fire Protection Association (NFPA) Standard 805, for faili
Region: II | Harris | 16688 | 06/30/2013 08/01/2013 | 2013003-01 | NRC | FIN | Initiating Events | Green | Power Transient due to a Main Feedwater Pump Oil Leak |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71111.04Q | A self-revealing Green finding (FIN) was identified for the licensee's failure to adequately implement their procedure CAP-NGGC-0205, Condition Evaluation and Corrective Action Process, for two oil leaks from the "B" MFP which occurred on February 14, 201
Region: II | Harris | 16678 | 04/30/2013 04/30/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | "Inadequate Corrective Actions Involving the Incorrect Determinations of Operability." |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000400 Harris 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action was identified for the licensee's failure to take corrective actions related to incorrect operability determinations which resulted in violation of TS 3.8.1.1 (Electr
Region: II | Harris | 16679 | 04/30/2013 04/30/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | "Failure to Implement Design Control Measures for the EDG Starting and Control Air System." |  |  | TE?: N | 05000400 Harris 1 |  | 71111.17T | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," involving two examples. In one example, the licensee did not translate instrument uncertainties associated with the EDG low-pressure alarm and press
Region: II | Harris | 16686 | 04/30/2013 04/30/2013 | 2013002-05 | NRC | FIN | Initiating Events | Green | "Reactor Power Transient due to Inadvertent Isolation of the "4B" Feedwater Heater." |  | P.2(b) Implementing Operating Experience | TE?: N | 05000400 Harris 1 |  | 71153 | A self-revealing Green finding (FIN) was identified for the licensee's failure to establish and implement an adequate operating procedure (OP-136, Feedwater Heaters, Vents and Drains, Revision 41) to restore the "4B" feedwater heater (FWH) alternate level
Region: II | Harris | 16675 | 10/31/2012 11/01/2012 | 2012009-01 | NRC | NCV | Mitigating Systems | Green | Technical Specification Inoperability of MSIVs Due to Failure to Conduct Diagnostic Testing |  |  | TE?: N | 05000400 Harris 1 |  | NONE | -Green. The inspectors identified a non-cited violation of Technical Specification (TS) 3.7.1.5, Main Steam Line Isolation Valves, due to one or more MSIVs being inoperable for a time greater than the allowed outage time and a plant shutdown was not compl
Region: II | Harris | 16668 | 09/30/2012 10/24/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Perform Containment Visual Inspection when Containment Integrity is Required |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71111.18 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, when the licensee failed to adequately correct a previously identified issue associated with the performance of OST-1081, "Containment Visual Inspection
Region: II | Harris | 16674 | 09/30/2012 10/24/2012 | 2012004-02 | Self - Revealed | NCV | Mitigating Systems | Green | "B" Startup Transformer Lockout due to Loss of Oil Filled Cable Pressure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000400 Harris 1 |  | 71152 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, Procedures, was identified for the licensee's failure to develop an adequate procedure for maintenance on an oil filled cable. Specifically, the licensee failed to provide adequate instruct
Region: II | Harris | 15258 | 06/30/2012 07/26/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance Results in Inoperability of the "A" Emergency Service Water System |  |  | TE?: N | 05000400 Harris 1 |  | 71111.15 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, Procedures, was identified for the licensee's failure to implement an adequate preventive maintenance procedure to identify a condition which led to the inoperability of the "A" Emergency S
Region: II | Harris | 15259 | 06/30/2012 07/26/2012 | 2012003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Fuel Handling Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000400 Harris 1 |  | 71111.2 | A self-revealing Green NCV of TS 6.8.1, Procedures, was identified for the licensee's failure to follow procedure, FHP-014, Fuel and Insert Shuffle Sequence, during core offload resulting in inadvertently placing a spent fuel assembly in the wrong locatio
Region: II | Harris | 16666 | 06/30/2012 07/26/2012 | 2012003-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Use Appropriate Radioactive Sources to Calibrate Effluent Monitors. |  |  | TE?: N | 05000400 Harris 1 |  | 71124.05 | The inspectors identified two examples of a Green Non-Cited Violation (NCV) of TS 6.8.1, Procedures, for the licensee's failure to implement an adequate Quality Assurance (QA) program for effluent monitoring. Specifically, the secondary calibration (trans
Region: II | Harris | 15256 | 06/30/2012 07/16/2012 | 2012007-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Properly Install the Electrical Power Feed Cables for the EOF |  |  | TE?: N | 05000400 Harris 1 |  | 71152 | Green: The inspectors identified a Green Non-Cited Violation (NCV) of 10 CFR 50.54(q) for the licensee's failure to properly install the electrical power feed cables for the EOF in accordance with the national electrical code (NEC) as required by the Harr
Region: II | Harris | 15252 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correct the Reactor Auxiliary Building Emergency Exhaust System Dampers Failure to Close. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000400 Harris 1 |  | 71152 | The inspectors identified a Green Non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to correct a condition adverse to quality affecting the Reactor Auxiliary Building Emergency Exhaust System (RABEES). Spec
Region: II | Harris | 15248 | 12/08/2011 12/08/2011 | 2011011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure AOP-036.04 for Fire Area 1-A-BAL-C Post-Fire Safe Shutdown |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000400 Harris 1 |  | 71111.05XT | -Green. The team identified a non-cited violation of Harris Nuclear Plant Technical Specification 6.8.1.a. for inadequate guidance in fire response abnormal operating procedure AOP-036.04. Specifically, the procedure could not have been performed as writt
Region: II | Harris | 15246 | 09/30/2011 10/27/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Inadvertent Actuation of Turbine Driven Auxiliary Feedwater Pump Caused by Inadequate Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000400 Harris 1 |  | 71111.19 | A self-revealing Green NCV of Technical Specifications (TS) 6.8.1, Procedures, was identified for the licensee's failure to develop an adequate post maintenance test (PMT) procedure for the replacement of a defective 6.9kV undervoltage relay (UVTXSB/1732)
Region: II | Harris | 15247 | 09/30/2011 10/27/2011 | 2011004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Periodically Calibrate Radiation Monitors |  |  | TE?: N | 05000400 Harris 1 |  | 71124.05 | The inspectors identified a Green Non-cited Violation (NCV) of 10 CFR 20.1501 for the failure to periodically calibrate radiation monitoring equipment. Specifically, in 2004 the licensee eliminated periodic calibrations for 64 radiation monitors used to e
Region: II | Harris | 15249 | 07/29/2011 09/08/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action to Preclude Repetition of a Significant Condition Adverse to Quality Associated with the Quality Control Organization's Acceptance of Electrical Terminati |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71152B | Green: An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to take adequate corrective action to preclude repetition of a significant condition adverse to qualit
Region: II | Harris | 15232 | 06/30/2011 07/27/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Identifying Accumulated Gas in ECCS Systems |  | P.2(b) Implementing Operating Experience | TE?: N | 05000400 Harris 1 |  | NONE | -Green. The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish adequate instructions to identify accumulated gas in Emergenc
Region: II | Harris | 15234 | 06/30/2011 08/09/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Degraded Voltage Time Delay Settings - Two Examples |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV with two examples of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly control degraded voltage time delay setpoints. The licensee is evaluating changing the TS and field li
Region: II | Harris | 15235 | 06/30/2011 08/09/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Environmental Qualification on Steam Generator Power Operated Relief Valves |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR 50.49 for the licensee's failure to maintain its Environmental Qualification (EQ) program requirements on the Steam Generator Power Operated Relief Valves (S/G PORVs). While no immediate operability issues were id
Region: II | Harris | 15236 | 06/30/2011 08/09/2011 | 2011008-04 | NRC | NCV | Mitigating Systems | Green | Non-conservative Calculations for Motor Control Center Control Circuit Voltage |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to perform adequate calculations for Motor Control Center (MCC) control circuit voltage. Immediate actions included testing th
Region: II | Harris | 15237 | 06/30/2011 08/09/2011 | 2011008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Control Design Limits for ESCW Flow Balancing |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to control design limits for Essential Services Chilled Water System (ESCW) flow balancing. Immediate corrective actions included f
Region: II | Harris | 15241 | 06/30/2011 08/09/2011 | 2011008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Extend the Design Life for Molded-Case Circuit Breakers |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to maintain the qualification bases for safety-related molded case circuit breakers (MCCBs). Immediate corrective actions included review of t
Region: II | Harris | 15242 | 06/30/2011 08/09/2011 | 2011008-07 | NRC | NCV | Mitigating Systems | Green | Failure to Test Safety-Related Molded Case Circuit Breakers |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," involving the licensee's failure to include 79 safetyrelated MCCBs in the circuit breaker test program. Immediate corrective actions included review of breaker pe
Region: II | Harris | 15243 | 06/30/2011 08/09/2011 | 2011008-08 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Voltage for Safety Related Components |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to establish measures to ensure safety related components had adequate voltage. The licensee entered this issue into the CAP as NCR
Region: II | Harris | 15244 | 06/30/2011 08/09/2011 | 2011008-09 | NRC | FIN | Initiating Events | Green | Inadequate Corrective Action Inadvertent Loss of Thermal Barrier HX Flow |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC indentified a Green finding for licensee's failure to take adequate corrective action for the inadvertent closing of MOV 1CC-252 (Reactor Coolant Pump (RCP) Thermal Barrier Return Flow Isolation Valve) following the start of the standby Component
Region: II | Harris | 15245 | 06/30/2011 08/09/2011 | 2011008-10 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Preventative Maintenance Procedure for Safety-Related Tornado Dampers |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The NRC identified a Green, NCV of TS 6.8.1 for the failure to implement an adequate preventative maintenance procedure to ensure reliable operation of the plant's safety-related tornado dampers. Immediate corrective actions included procedure changes, te
Region: II | Harris | 15221 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Implement Procedural Guidance to Maintain the FHBEES Boundary |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000400 Harris 1 |  | 71111.04Q | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1, Procedures, for the licensee's failure to properly implement procedural guidance to maintain the Fuel Handling Building Emergency Exhaust System (FHBEES) boundary. Specifically,
Region: II | Harris | 15222 | 12/31/2010 01/28/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Emergency Safeguards Sequencer Actuation and Safety Injection Signal (SIS) while the Plant was in Mode 6. |  | H.4(a) Human Error Prevention | TE?: N | 05000400 Harris 1 |  | 71111.12 | A self-revealing Green NCV of Technical Specifications (TS) 6.8.1, Procedures, was identified for the licensee's failure to follow procedure MST-I0073, Train "B" 18 Month Manual Reactor Trip, Solid State Protection System Actuation Logic & Master Relay Te
Region: II | Harris | 15223 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with the Limiting Conditions for Operation, While the Refueling Water Storage Tank was Aligned to the Non-seismically Qualified Fuel Pool Purification System. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000400 Harris 1 |  | 71111.18 | The inspectors identified a Green NCV of TS 3.1.2.6, Borated Water Sources, for the failure to comply with the limiting conditions for operation, while the Refueling Water Storage Tank (RWST) was aligned to the non-seismic Fuel Pool Purification system (F
Region: II | Harris | 15224 | 12/31/2010 01/28/2011 | 2010005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Test Procedure Results in Deenergization of the "B" Safety Bus and Loss of Decay Heat Removal |  | H.3(b) Work Activity Coordination | TE?: N | 05000400 Harris 1 |  | 71111.19 | A self-revealing Green NCV of TS 6.8.1, Procedures, was identified for the licensee's failure to develop an adequate procedure for the post maintenance test of the recently replaced main generator lockout relay (MGLR). Specifically, the licensee failed to
Region: II | Harris | 15225 | 12/31/2010 01/28/2011 | 2010005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure to Properly Align the MOC Switch Contacts Associated with Breaker 1A-6 Results in Actuation of the "B" MDAFW Pump. |  | H.4(a) Human Error Prevention | TE?: N | 05000400 Harris 1 |  | 71111.19 | A self-revealing Green NCV of TS 6.8.1, Procedures, was identified for the licensee's failure to correctly implement Section D.2.10 of Engineering Change (EC) #74866R1 when aligning the Mechanism Operated Cell (MOC) switch for the "A" Main Feed Water Pump
Region: II | Harris | 15230 | 12/31/2010 01/28/2011 | 2010005-06 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance to Properly Lift/Land Leads |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000400 Harris 1 |  | 71111.22 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, Procedures, was identified for the licensee's failure to establish and implement procedural requirements that would ensure the Program "C" relay wiring configuration in the "A" Sequencer r
Region: II | Harris | 15215 | 06/30/2010 07/22/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure to Install the Load Block 5 Auxiliary Relay |  | H.4(a) Human Error Prevention | TE?: N | 05000400 Harris 1 |  | 71111.19 | Green. A self-revealing Green NCV of TS 6.8.1, Procedures, was identified for the licensee's failure to follow procedure PIC-E069, Sequencer Electomechanical Timing Relays; D.C. Pick-Up, D.C. Drop-Out, A.C. Pick-Up, and A.C. Drop-Out. Specifically, the li
Region: II | Harris | 15216 | 06/30/2010 07/22/2010 | 2010003-02 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip due to Failing to Properly Assemble an Oil Filter in the Hydrogen Seal Oil System |  | H.3(a) Work Planning | TE?: N | 05000400 Harris 1 |  | 71153 | Green. A self-revealing Green finding was identified for the licensee's failure to follow Work Control Management procedure WCM-006, Graded Approach to Planning and Scheduling, which has requirements that would have ensured the proper rebuild of the oil f
Region: II | Harris | 15209 | 03/31/2010 04/30/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Evaluate Operating Experience and Identify Potential Steam Voiding as a Condition Adverse to Quality |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000400 Harris 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, when the licensee failed to promptly evaluate operating experience (OE) received October 22, 2008 and identify potential steam voiding in the residual h
Region: II | Harris | 15210 | 03/31/2010 04/30/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | "A" ESW Pump Power Supply Cables Submerged in Water |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000400 Harris 1 |  | 71111.06 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that the licensee failed to maintain the "A" ESW pump power cables in an environment for which they were designed. Specifically, the cables were subme
Region: II | Harris | 15199 | 12/31/2009 01/26/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Install Spot Type Smoke Detectors |  |  | TE?: N | 05000400 Harris 1 |  | NONE | The inspectors identified a Green NCV of the Shearon Harris Nuclear Power Plant Operating License condition 2.F, Fire Protection Program, for failing to correctly install spot type smoke detectors between four and twelve inches down from the ceiling to th
Region: II | Harris | 15196 | 10/02/2009 10/30/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Preclude Repetition of a Significant Condition Adverse to Quality for Both Containment Spray Additive System Eductors Being Outside of the Technical Specification Flow Band |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify the cause and take corrective actions to preclude repetition of a significant condition adverse to quality
Region: II | Harris | 15197 | 10/02/2009 10/30/2009 | 2009006-02 | NRC | NCV | Barrier Integrity | Green | Failure to Correct a Condition Adverse to Quality Involving a Main Steam Isolation Valve Degrading Trend Before Valve Failure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000400 Harris 1 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality in a timely manner. Specifically, between May 27, 1997 and September 29, 2007
Region: II | Harris | 15185 | 09/30/2009 10/30/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Quality Assurance Training Program |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000400 Harris 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the licensee's failure to maintain an adequate training program for personnel performing activities affecting quality as necessary to assure tha
Region: II | Harris | 15181 | 06/30/2009 07/30/2009 | 2009003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Procedures to Control and Adjust the Manipulator Crane Gear Limit Setpoints |  | H.4(b) Procedural Compliance | TE?: N | 05000400 Harris 1 |  | 71152 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, Procedures, was identified when the licensee failed to follow Attachment 4, Manipulator Crane and Auxiliary Hoist Checkout, of Fuel Handling Procedure 20 (FHP-020), Refueling Operations, re
Region: II | Harris | 15177 | 12/31/2008 01/29/2009 | 2008005-01 | NRC | NCV | Public Radiation Safety | Green | Failure to monitor effluent releases from SFP filter backwash |  |  | TE?: N | 05000400 Harris 1 |  | NONE | The inspectors identified a non-cited (NCV) of 10 CFR 20.1302 (a) for failure to make adequate surveys of radioactive materials in effluents released to unrestricted areas. The licensee altered the configuration of the vent stack effluent radiation monito
Region: II | Harris | 15171 | 11/07/2008 12/19/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Sprinkler System in Cable Spreading Room A Does Not Meet Licensee's Fire Protection Program Requirements |  |  | TE?: N | 05000400 Harris 1 |  | 71111.05T | The team identified a non-cited violation of Shearon Harris Unit 1 operating license condition 2.F, for the licensee's failure to install the sprinkler system in Cable Spreading Room A (CSRA) in accordance with the approved fire protection program (FPP).
Region: II | Harris | 15170 | 09/30/2008 10/30/2008 | 2008004-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Control Over the Station's Very High Radiation Areas |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000400 Harris 1 |  | 7112101 | A self-revealing Green NCV was identified for the failure to maintain control of access to the station's very high radiation areas (VHRA), as required by 10 CFR 20.1602. The inspectors determined that the licensee failed to maintain sufficient controls of
Region: II | Harris | 15168 | 06/30/2008 07/28/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Categorize Maintenance Rule Functional Failures |  |  | TE?: N | 05000400 Harris 1 |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65 (a)(2) for the licensee's failure to categorize two failures of the condenser vacuum pump effluent radiation monitor (REM-3534) as maintenance rule functional failures and accordingly,
Region: II | Harris | 15178 | 05/29/2008 07/10/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Incorrect test acceptance criteria for Emergency Service Water (ESW) pump discharge check valves 1SW-9 and 10 during test procedure OST-1214/1215. |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for incorrect test acceptance criteria for Emergency Service Water (ESW) pump discharge check valves 1SW-9 and 10 during test procedure OST-1214/1215, ESW System O
Region: II | Harris | 15179 | 05/29/2008 07/10/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to translate critical design attributes into drawings and the as-built condition of the plant. |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to translate critical design attributes into drawings and the as-built condition of the plant. As a result, the fuel and air supplies to the emer
Region: II | Harris | 15156 | 12/31/2007 01/29/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | B Essential Services Chiller inoperable greater than TS allowed outage time |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000400 Harris 1 |  | 71111.12 | A Green self-revealing non-cited violation (NCV) of Technical Specification (TS) 3.7.13 was identified when the B essential services chilled water (ESCW) chiller tripped 2 minutes after it was started on November 5, 2007. The chiller tripped on low refrig
Region: II | Harris | 15157 | 12/31/2007 01/29/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate clearance for SW-271 |  | H.3(a) Work Planning | TE?: N | 05000400 Harris 1 |  | 71111.2 | A Green self-revealing NCV of TS 6.8.1., Programs and Procedures, was identified for an inadequate clearance order associated with engineering change 62848 on circuit 33 of power panel DP 1B-SB. As a result of the inadequate clearance, the discharge valve
Region: II | Harris | 15158 | 12/31/2007 01/29/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Loss of Annunciation System Due to Operator Error During Surveillance Testing |  | H.3(b) Work Activity Coordination | TE?: N | 05000400 Harris 1 |  | 71111.2 | A Green self-revealing non-cited violation (NCV) was identified for the failure to properly implement operating procedures in accordance with TS 6.8.1. Operator error in procedure implementation of procedure OST-1858, "Remote Shutdown System Operability -
Region: II | Harris | 15165 | 12/31/2007 01/29/2008 | 2007005-04 | NRC | NCV | Barrier Integrity | Green | Failure to correct cause of SW-233 local leak rate failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000400 Harris 1 |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B,Criterion XVI, "Corrective Actions" when licensee personnel failed to promptly correct a condition adverse to quality. Specifically, six local leak rate test (LLRT) failures occurred between 1
Region: II | Harris | 15150 | 09/30/2007 10/29/2007 | 2007004-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to maintain an acceptable program for periodic CCW Process Radiation Monitor calibrations in accordance with 10 CFR 20.1101 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | NONE | An NRC-identified non-cited violation (NCV) of 10 CFR 20.1101 was identified for failure to maintain an acceptable program for process radiation monitor calibrations in accordance with 10 CFR 20.1501(b). Specifically, the licensee failed to maintain a pro
Region: II | Harris | 15151 | 09/30/2007 10/29/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Operator Error During Swapping of Emergency Service Water (ESW) Suctions |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000400 Harris 1 |  | 71153 | A self-revealing non-cited violation (NCV) was identified for the failure to properly implement operating procedures in accordance with Technical Specifications (TS) 6.8.1. Operator error in procedure implementation led to the A-SA emergency service water
Region: II | Harris | 15148 | 06/30/2007 07/27/2007 | 2007003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correct low refrigerant level in the A essential services chiller. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000400 Harris 1 |  | 71111.12 | A self-revealing non-cited violation (NCV) of 10CFR50, Appendix B, Criterion XVI, "Corrective Action" was identified for failure to promptly correct a condition adverse to quality. The licensee failed to correct a low refrigerant level in the A essential
Region: II | Harris | 15139 | 11/03/2006 12/06/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control to Assure UFSAR Requirement to Detect and Isolate an RHR leak of 50 GPM in 30 minutes |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for inadequate design control measures to assure the capability to identify and isolate a residual heat removal (RHR) system leak of 50 gpm in 30 minutes as
Region: II | Harris | 15140 | 11/03/2006 12/06/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for RCS Standpipe Low Level Setpoint |  |  | TE?: N | 05000400 Harris 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control for a non-conservative setpoint related to the low Reactor Coolant System (RCS) Standpipe level for mid-loop operations. Specifically, the licensee failed to
Region: II | Harris | 15132 | 06/30/2006 07/28/2006 | 2006003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure During Service Water Control Valve Preventive Maintenance |  |  | TE?: N | 05000400 Harris 1 |  | 71111.15 | A Green self-revealing NCV of Technical Specification (TS) 6.8.1 was identified for the failure to follow procedures while performing maintenance on a service water valve which supports the train "A" essential services chilled water (ESCW) system chiller.
Region: II | Harris | 15137 | 06/30/2006 07/28/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Procedures Such That a Required Torque Was Not Provided for a Threaded Fastener on an ESCW System Chiller |  |  | TE?: N | 05000400 Harris 1 |  | 71111.15 | A self-revealing NCV was identified for the failure to maintain adequate procedures for the performance of maintenance on the ESCW system chillers. Specifically, procedures lacked sufficient details to perform maintenance on the chiller's pre-rotational v
Region: II | Harris | 124786 | 05/10/2019 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation |  |  | TE?: N | 05000400 Harris 1 |  | 71152
Region: II | Hatch | 125366 | 06/30/2019 08/07/2019 | 2019002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 Inadvertant Electrical Bus De-Energization and Equipment Damage Due to the New 2C Startup Transformer (SUT) Being Wired Out of Phase |  | H.5 - Work Management | TE?: N | 05000366 Hatch 2 | Design Control | 71111.19 | The inspectors documented a Green, self-revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to ensure that activities affecting quality shall be described by docu
Region: II | Hatch | 124491 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Brief Worker of Radiation Dose Rate Levels Prior to Entering a High Radiation Area |  | H.5 - Work Management | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 | Human Performance | 71124.01 | A self-revealing, Green, Non-Cited Violation (NCV) of Technical Specifications 5.7.1.b was identified when a worker entered a high radiation area (HRA) near the N2NG nozzle piping on the 156 foot elevation of the Unit 2 (U2) drywell without receiving an a
Region: II | Hatch | 124679 | 03/31/2019 05/10/2019 | 2019001-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to apply engineering controls in accordance with plant procedures to minimize potential concentrations of radioactive material in air. |  | H.5 - Work Management | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 | Human Performance | 71124.03 | NRC Identified a Green NCV of 10CFR 20.1701, “Use of process or other engineering controls,” for the licensee’s failure to use a High Efficiency Particulate Air Filter (HEPA) unit as prescribed by plant procedures.
Region: II | Hatch | 25892 | 12/31/2018 02/12/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Safety Relief Valves’ As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria |  | NPP | TE?: N | 05000321 Hatch 1 |  | 71153 | The inspectors documented a Green, self-revealing, non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, “Design Control” for the licensee’s failure to evaluate for installation differences b
Region: II | Hatch | 24717 | 09/30/2018 11/08/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperability of 2A EDG Due to Inadequate Acceptance Criteria for Determining Cleaning Requirements of Emergency Diesel Generator Day Tanks |  | H.1 - Resources | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.22 | Description: On May 29, 2018, during the performance of the 2A EDG 24-month operability surveillance, 34SV-R43-001-2, the licensee discovered a high differential pressure across the fuel oil duplex filter. Operations shifted duplex filters due to low fuel
Region: II | Hatch | 23499 | 05/04/2018 05/04/2018 | 2018001-01 | NRC | NCV | Public Radiation Safety | Green | Failure to comply with Type B shipping container Certificate of Compliance (CoC) requirements |  | NPP | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71124.08 | A Green NRC Identified NCV of 10 CFR 71.17, which addresses general licenses for NRC-approved packages, was identified for failure to comply with the package procedures relating to the use and maintenance of the packaging (seal leak test failures not corr
Region: II | Hatch | 23206 | 12/31/2017 02/06/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Continuous Fire Watch or Compensatory Measures Not Established per FHA |  | H.9 - Training | TE?: N | 05000366 Hatch 2 |  | 71111.15 | Green. An NRC-identified non-cited violation (NCV) of Unit 2 License condition 2.C.(3)(a) Fire Protection was identified when on October 17, 2017, the licensee failed to establish a continuous fire watch or alternative compensatory measures required b
Region: II | Hatch | 23207 | 12/31/2017 02/06/2018 | 2017004-02 | NRC | NCV | Barrier Integrity | Green | Lack of Requirement for Engineering Evaluation of Scaffolding Near Safety Related Piping |  | NPP | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | Green. An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified when the licensee failed to ensure engineering evaluations were performed when scaffolding was constructed within 2 inch
Region: II | Hatch | 23227 | 12/31/2017 01/19/2018 | 2017009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions to Preclude Repetition of Reactor Scrams Due to IRM Spiking |  | H.14 - Conservative Bias | TE?: N | 05000321 Hatch 1 |  | 71152B | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee’s failure to establish measures to assure that corrective action was taken to preclude repetition of a significan
Region: II | Hatch | 22350 | 09/30/2017 11/14/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Installation of Non-Conforming RPS Equipment |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.18 | Green. An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, “Design Control” was identified for failure to translate regulatory requirements and the design basis of the scram discharge volume (SDV) thermal probes into the S
Region: II | Hatch | 17836 | 06/30/2017 08/03/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Hardened grease prevents 1RHRSW pump breaker operation |  |  | TE?: N | 05000321 Hatch 1 |  | 71111.12 | Green. A self-revealing, Green, non-cited violation (NCV) of Hatch Unit 1 Technical Specification 5.4 "Procedures" was identified when procedures to rejuvenate grease in the '1C' residual heat removal service water (RHRSW) Pump breaker were not implemente
Region: II | Hatch | 17835 | 03/31/2017 05/04/2017 | 2017001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Abnormal Condition on 2C EDG Cross Drive Assembly |  | H.1 Resources | TE?: N | 05000366 Hatch 2 |  | 71153 | Green. A self-revealing non-cited violation (NCV) of Hatch Unit 2 Technical Specification 5.4.1 was identified when technicians performing maintenance on the 2C emergency diesel generator observed pitting on the lower crank component gears and did not ini
Region: II | Hatch | 17833 | 12/31/2016 01/31/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Establish Icing Controls on CAD Subsystem |  | P.1 Identification | TE?: N | 05000321 Hatch 1 |  | 71111.15 | An NRC-identified NCV of Hatch Unit 1 Technical Specification 5.4, "Procedures," was identified when procedures did not include inspection criteria for ice buildup of the Unit 1 nitrogen storage tank piping. The licensee entered the condition into their c
Region: II | Hatch | 17831 | 09/30/2016 11/01/2016 | 2016003-01 | Self - Revealed | FIN | Initiating Events | Green | Unit Downpower Caused by RFP Vent Line Failure |  | P.3 Resolution | TE?: N | 05000321 Hatch 1 |  | 71111.12 | A self-revealing finding was identified when the licensee failed to install a reactor feed pump (RFP) vent line weld in accordance with plant procedures resulting in a failure that required an unplanned Unit 1 power reduction greater than 20%. Failure
Region: II | Hatch | 17832 | 09/30/2016 11/01/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Work Hours are Within Work Hour Limits |  | H.13 Consistent Process | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | An NRC-identified non-cited violation (NCV) of 10 CFR Part 26, "Fitness for Duty Programs," was identified when the licensee failed to ensure that personnel subject to work hour controls did not exceed 72 hours in a work week. The licensee entered this co
Region: II | Hatch | 17827 | 06/30/2016 08/12/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | , Failure to Implement Maintenance Procedure for Control Room Air Conditioning System |  | H.1 Resources | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.12 | A self-revealing Green NCV of Hatch Unit 1 and Unit 2 Technical Specification 5.4, "Procedures," was identified when the 'B' main control room air conditioning condenser tripped on high discharge pressure due to an improperly adjusted water regulating val
Region: II | Hatch | 17829 | 06/30/2016 08/11/2016 | 2016010-02 | NRC | NCV | Initiating Events | Green | Failure to Identify N2E Nozzle Weld Through-Wall Flaw |  | H.11 Challenge the Unknown | TE?: N | 05000321 Hatch 1 |  | 71111.08G | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to promptly identify a condition adverse to quality regarding a through-wall flaw in the safe end-to-nozzle weld of the reactor
Region: II | Hatch | 17693 | 06/24/2016 08/01/2016 |  | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Qualify Modifications to Class 1E 4160V Buses |  | H.9 Training | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.17T | The inspectors identified a non-cited violation of Title 10 Code of Federal Regulations (CFR) Part 50 Appendix B, Criterion III, "Design Control," for the failure to verify adequate design and qualification of Class 1E buses in accordance with Institute f
Region: II | Hatch | 17703 | 06/24/2016 08/01/2016 |  | NRC | NCV | Mitigating Systems | Green | Failure to identify a condition adverse to quality for Masterpact 600V breakers |  | P.2 Evaluation | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.17T | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for failing to identify the applicability of US NRC Part 21 Report 2016-20-01 to the 1B emergency diesel generator's (EDG's) motor control center
Region: II | Hatch | 17779 | 06/24/2016 08/01/2016 |  | NRC | NCV | Mitigating Systems | Green | Failure to Control Qualification of Purchased 1E Components in Accordance to IEEE 323-1974 |  | H.2 Field Presence | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.17T | The inspectors identified two examples of a non-cited violation of 10 CFR 50 Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," for failing to assure that vendors met the quality standards specified in procurement documen
Region: II | Hatch | 17830 | 04/22/2016 06/03/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide reasonable assurance that Appendix R time critical operator actions (TCOAs) can be completed in a timely manner |  | P.2 Evaluation | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.05T | The NRC identified a Green non-cited violation (NCV) violation of Hatch Technical Specifications 5.4.1.d, "Procedures," for Units 1 and 2, for not ensuring manual action feasibility for actions in fire area (FA) 0024. Specifically, the licensee failed to
Region: II | Hatch | 17818 | 10/23/2015 12/07/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Circuit Breaker As-Found Testing |  |  | TE?: N | 05000366 Hatch 2 |  | 7111121 | The NRC identified a Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion XI "Test Control," for the failure to perform circuit breaker as-found electromechanical testing prior to inspecting, cleaning, and lubricating the mechanical components.
Region: II | Hatch | 17819 | 10/23/2015 12/07/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Nonconformances with Regulatory Guide 1.9-1971 |  | P.2 Evaluation | TE?: N | 05000366 Hatch 2 |  | 7111121 | The NRC identified a Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct non-conformances with the acceptance limits established for the emergency diesel generator (EDG) test require
Region: II | Hatch | 17823 | 10/23/2015 12/07/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Assure that Class 1E Components were Qualified for Design Temperatures |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The NRC identified a Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," for the licensee's failure to ensure that adequate environmental test requirements were satisfied before relyi
Region: II | Hatch | 17824 | 10/23/2015 12/07/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Design Basis Timing Margins for Safety Related Motor Operated Valves |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Green: The NRC identified a Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate if transients in control power voltage could affect the design basis margins for the timing of safety
Region: II | Hatch | 17825 | 10/23/2015 12/07/2015 | 2015007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Classify RCIC Sub-components as Safety-Related |  |  | TE?: N | 05000366 Hatch 2 |  | 7111121 | The NRC identified a Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to classify components in accordance with Regulatory Guide 1.26 as specified by the Unit 2 Updated Final Safety Analysis Report, Secti
Region: II | Hatch | 17816 | 09/30/2015 11/02/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Surveillance on Fire Barriers and Penetration Seals |  | H.2 Field Presence | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71153 | The NRC identified a non-cited violation (NCV) of Hatch Operating License Conditions (OLCs) 2.C.(3) and 2.C.(3)(a), for Units 1 and 2 respectively, for the licensee's failure to perform fire barrier penetration seal inspections in accordance with the r
Region: II | Hatch | 17817 | 09/30/2015 11/02/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | "1A" PSW Pump High Vibration Failure |  |  | TE?: N | 05000321 Hatch 1 |  | 71153 | A self-revealing, NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures, Instructions, and Drawings," was identified when the licensee failed to provide instructions to ensure alignment of the "1A" plant service water (PSW) pump column in the true vertic
Region: II | Hatch | 17810 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain HELB Penetrations |  | H.5 Work Management | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.15 | A Green NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for failure to maintain reactor building residual heat removal (RHR) diagonal room penetrations in the designed configuration. The v
Region: II | Hatch | 17807 | 03/31/2015 05/04/2015 | 2015001-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to perform adequate surveys of air samples for alpha activity |  | H.1 Resources | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71124.01 | An NRC-Identified non-cited violation (NCV) of 10 CFR 20.1501(a) was identified for failure to perform an adequate survey. Air samples obtained in the reactor cavity and on the refuel floor during a contamination event indicating greater than 0.3 beta-gam
Region: II | Hatch | 17808 | 03/31/2015 05/04/2015 | 2015001-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to perform complete analysis of air samples |  | H.8 Procedure Adherence | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71124.01 | An NRC-Identified non-cited violation (NCV) of TS 5.4.1 was identified for the failure of the licensee to perform complete quantitative analysis of air samples using approved counting equipment as required by the licensee's procedures. NMP-HP-301, Step 5.
Region: II | Hatch | 17809 | 03/31/2015 05/04/2015 | 2015001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Embedded Conduit prior to Core Drill Operations |  | H.5 Work Management | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Procedures, Instructions, and Drawings," was identified for failure to identify existing embedded conduit in the vicinity of prescribed core drills location. The violation
Region: II | Hatch | 17802 | 12/31/2014 01/26/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate fire penetration 1T43-H528J |  |  | TE?: N | 05000321 Hatch 1 |  | 71111.05Q | The NRC identified a Green Non-Cited Violation (NCV) of Unit 1 License Condition 2.C.(3) Fire Protection when a fire penetration that deviated from three-hour rating requirements was not evaluated in accordance with Unit 1 Fire Hazards Analysis (FHA) Appe
Region: II | Hatch | 17765 | 09/30/2014 11/12/2014 | 2014004-01 | Self - Revealed | FIN | Initiating Events | Green | Unit Downpower Caused by Relief Valve Failure |  | H.9 Training | TE?: N | 05000321 Hatch 1 |  | 71111.12 | A self-revealing finding was identified when the opening of the 8th stage feedwater heater relief valves due to improper set point adjustment necessitated a Unit 1 downpower. Failure to verify the 8th stage feedwater heater shell side relief valve set
Region: II | Hatch | 17800 | 09/30/2014 11/12/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Surveillance Procedure Resulted in Isolation of All Fire Water to the Station |  | H.1 Resources | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | The NRC identified a NCV of Technical Specification 5.4, "Procedures," for the licensee's failure to properly implement a valve lineup in a surveillance procedure for the fire protection system. The licensee inadvertently isolated all fire suppression wat
Region: II | Hatch | 17801 | 09/30/2014 11/12/2014 | 2014004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify Malfunction of HPCI Exhaust Drain Pot Level Instrumentation |  | H.12 Avoid Complacency | TE?: N | 05000321 Hatch 1 |  | 71153 | A self-revealing NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified on May 1, 2014 when a control room annunciator and subsequent investigation of the high pressure coolant
Region: II | Hatch | 17794 | 06/30/2014 07/31/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Prove Operability Following the Failure of the Secondary Containment Surveillance Test |  | H.9 Training | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.15 | Green. The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Procedures, Instructions, and Drawings," for the licensee's failure to prove operability following a failure of a surveillance test as required by Hatch p
Region: II | Hatch | 17785 | 03/31/2014 04/18/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Install Seismic Restraints of the Unit 2 LOCA LOSP Timer Cabinet Doors Following Inspection |  | H.1 Resources | TE?: N | 05000366 Hatch 2 |  | 71111.15 | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to prescribe in documented instructions, procedures, or drawings appropriate to the circumstances the in
Region: II | Hatch | 17792 | 03/31/2014 04/18/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Safety System MOVs in the GL 96-05 Periodic Verification Program |  | P.2 Evaluation | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | Green. The inspectors identified a Green NCV of 10 CFR 50.55a, "Codes and Standards," for the licensee's failure to establish a periodic verification program for the core spray, high pressure core injection, and reactor core injection cooling systems pump
Region: II | Hatch | 17793 | 03/31/2014 04/18/2014 | 2014002-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Operate the Unit 2 Master Feedwater Controller In Accordance With Procedures |  | H.12 Avoid Complacency | TE?: N | 05000366 Hatch 2 |  | 71153 | Green. A self-revealing Green non-cited violation (NCV) of Technical Specification 5.4, "Procedures," was identified when an automatic recirculation pump runback occurred after improper operations of the Unit 2 master feedwater controller "PF" push button
Region: II | Hatch | 17781 | 12/31/2013 01/27/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Scaffolding installed in safety related areas failed to meet procedureal requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.12 | The NRC inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to implement existing procedural guidance for the control of clearances between installed scaffolding and safe
Region: II | Hatch | 17782 | 12/31/2013 01/27/2014 | 2013005-02 | NRC | NCV | Initiating Events | Green | Failure to promptly identify source of leakage under Unit 1 reactor vessel |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000321 Hatch 1 |  | 71111.2 | NRC inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify the source of leakage under Unit 1 reactor vessel on February 26, 2013. On October 25, 2013
Region: II | Hatch | 17783 | 12/31/2013 01/27/2014 | 2013005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement an administrative procedure for equipment control when using personal danger tags |  | H.3(b) Work Activity Coordination | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | A self-revealing NCV of Hatch Unit 1 and Unit 2 Technical Specification 5.4., "Procedures," was identified on October 5, 2013, when the licensee failed to implement an administrative procedure for equipment control which caused the "A" main control room a
Region: II | Hatch | 17780 | 09/30/2013 10/31/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to take required actions for inoperable equipment in accordance with Hatch's fire hazards analysis, Appendix B |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71153 | The NRC identified a non-cited violation of Unit 1 License Condition 2.C.(3), "Fire Protection," and Unit 2 License Condition 2.C.(3)(a), "Fire Protection," which occurred on September 3, 2013, when the licensee failed to establish fire watches and compen
Region: II | Hatch | 17773 | 03/31/2013 05/02/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to perform appropriate post maintenance test on "2A" EDG |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000366 Hatch 2 |  | 71111.19 | Green. A self-revealing Green NCV of Hatch Unit 2 Technical Specification 5.4. "Procedures," was identified on March 9, 2013, when the licensee failed to perform post maintenance activities appropriate to the circumstances to verify "2A" emergency diesel
Region: II | Hatch | 17770 | 12/31/2012 01/28/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Low voltage safety-related cables subjected to water submersion |  |  | TE?: N | 05000366 Hatch 2 |  | 71111.06 | The NRC identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," on October 16, 2012, when the licensee failed to maintain safety-related cables in an environment for which they were designed. Specifically, sa
Region: II | Hatch | 17772 | 12/31/2012 01/28/2013 | 2012005-03 | Licensee - Identified | NCV | Emergency Preparedness | Green | Installation of a transformer for the TSC cooling coil and condensing unit control circuit not adequately designed to provide full system load. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | NONE | A self-revealing NCV of 10 CFR Part 50.54(q)(2), was identified when the licensee failed to maintain an adequate on-site Technical Support Center (TSC) to support emergency response. The violation existed from November 10 to December 22, 2011, when the TS
Region: II | Hatch | 17756 | 09/30/2012 10/30/2012 | 2012004-01 | NRC | NCV | Initiating Events | Green | Failure to follow transient combustible control requriements within the site's intake structure |  | H.4(b) Procedural Compliance | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.05A | An NRC identified Green non-cited violation (NCV) of Technical Specification 5.4, Procedures, was identified on August 14, 2012, for failure of the licensee to follow transient combustible control requirements within the site's intake structure. Specifica
Region: II | Hatch | 17757 | 09/30/2012 10/30/2012 | 2012004-02 | NRC | FIN | Mitigating Systems | Green | Licensed operator requalification annual operating test administration issues |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | NONE | An NRC-identified finding (FIN) was identified for the licensee's failure to adhere to licensed operator requalification examination standards during the administration of an annual operating test. Specifically, the licensee failed to adhere to the examin
Region: II | Hatch | 17758 | 09/30/2012 10/30/2012 | 2012004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to establish adequate preventative maintenance for the safety related main control room air conditioning units |  | P.2(b) Implementing Operating Experience | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.12 | A self revealing Green NCV (with two examples) of Hatch Unit 1 and Unit 2 TS 5.4, Procedures, was identified for failure to establish and perform preventive maintenance activities to replace the B main control room condensing unit overload in the MS2 moto
Region: II | Hatch | 17762 | 09/30/2012 10/30/2012 | 2012004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to follow clearance procedures for returning the A main control room air conditioning unit to service following maintenance |  | H.4(a) Human Error Prevention | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | A self-revealing Green NCV of Hatch Unit 1 and Unit 2 Technical Specification 5.4. Procedures, was identified on June 21, 2012, when the "C" main control room air conditioning unit tripped due to loss of power when the licensee operated an electrical brea
Region: II | Hatch | 17764 | 09/06/2012 10/10/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Account for Potential Pump Discharge Check Valve Back-leakage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify or check the adequacy of design of the plant service water system including the pump discharge check valves al
Region: II | Hatch | 17767 | 09/06/2012 10/10/2012 | 2012008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequacy of Intake Structure Ventilation Design |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that the licensee failed to verify or check the adequacy of the design of the intake structure ventilation support function for the plant servic
Region: II | Hatch | 17768 | 09/06/2012 10/10/2012 | 2012008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Appropriate Test Acceptance Criteria to Assure Satisfactory Steady State EDG Performance |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to incorporate adequate acceptance limits in surveillance test procedures used to verify acceptable steady state output vol
Region: II | Hatch | 17769 | 09/06/2012 10/10/2012 | 2012008-05 | NRC | FIN | Mitigating Systems | Green | Failure to Provide Appropriate Acceptance Criteria for EDG Air-Start System Check Valves |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Green. The team identified a finding for the licensee's failure to follow Regulatory Guide (RG) 1.155, "Station Blackout," guidance for testing and test control for the emergency diesel generator (EDG) air start system check valves. The testing deficiency
Region: II | Hatch | 17750 | 06/30/2012 07/30/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Removal of scaffolding built to allow implementation of Unit 1 manual operation of the containment hardened vent |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000321 Hatch 1 |  | 71111.05Q | The inspectors identified a non-cited violation (NCV) of Hatch Unit 1 Operating License condition 2.C. (4.c) for failure to maintain an adequate strategy to vent the primary containment through the installed hardened vent piping without power. The ability
Region: II | Hatch | 17751 | 06/30/2012 07/30/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Mispositioning and subsequent failure of Hatch Unit 1 reactor control rod blade |  |  | TE?: N | 05000321 Hatch 1 |  | 71152 | A self revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V. Instructions, Procedures, and Drawings, was identified for failure to accomplish 2004 control rod blade movements for the Unit 1 reactor in accordance with prescribed procedures.
Region: II | Hatch | 17752 | 06/30/2012 07/30/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate surveillance procedures for evaluating accumulated gas in the HPCI and RCIC systems |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | NONE | The inspectors identified a non-cited violation of Hatch Nuclear Plant Technical Specification 5.4, "Procedures," with five examples for the licensee's failure to establish, implement and maintain surveillance procedures for the high pressure coolant inje
Region: II | Hatch | 17743 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to assess and manage the increase in risk when removing residual heat removal and core spray from service |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000321 Hatch 1 |  | 71111.13 | Green. A self-revealing non-cited violation (NCV) of 10 CFR 50.65(a)(4) became apparent during the Unit 1 refueling outage when the residual heat removal shutdown cooling discharge valve, 1E11-F017B, failed to open electrically from the control room. The
Region: II | Hatch | 17740 | 12/31/2011 01/27/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Cables for Fire Safe Shutdown Not Protected In Accordance With 10 CFR 50 Appendix R Section III.G.2 |  |  | TE?: N | 05000321 Hatch 1 |  | 71153 | Green. The NRC identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix R, Section III.G.2, for the licensee's failure to protect one of the redundant trains of cables, located in the same fire area (FA), needed to achieve post-fire safe s
Region: II | Hatch | 17724 | 06/30/2011 08/03/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to promptly identify and take corrective actions to ensure Bussmann fuses identified by the Part 21 notification 2005-37 were removed from use in safety related applications. |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, was identified for failure to promptly identify and take corrective actions to ensure Bussmann fuses identified by the Part 21 notification 2005-37, were removed from use in
Region: II | Hatch | 17725 | 06/30/2011 08/03/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to consider potential adverse system interactions when developing procedure to open SRVs without power |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71153 | An NRC-identified NCV of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for failure to establish adequate procedures that address potential adverse system interactions when opening safety relief valves (SRV) with
Region: II | Hatch | 17728 | 06/30/2011 08/03/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Failure to address the anticipated environmental conditions when developing procedures to manually operate containment vent valves |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71153 | An NRC-identified NCV of 10 CFR 50, Appendix B, Criterion V. Instructions, Procedures, and Drawings, was identified for failure to establish adequate procedures that address the anticipated environmental conditions when operating containment vents without
Region: II | Hatch | 17719 | 03/31/2011 04/27/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inaccessbile fire hose station in the cable spreading room |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.05Q | An NRC-identified NCV of Hatch Unit 1 operating license condition 2.C.(3) and Hatch Unit 2 operating license condition 2.C.(3)(a), Fire Protection, was identified for failure to maintain fire hose station HS-C20 operable while equipment in the area was re
Region: II | Hatch | 17720 | 03/31/2011 04/27/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to control foreign material within a level 1 foreign material exclusion area |  | H.3(a) Work Planning | TE?: N | 05000321 Hatch 1 |  | 71111.19 | A self-revealing NCV of Technical Specification 5.4, Procedures, was identified for the licensee's failure on March 7, 2011, to implement foreign material exclusion procedures and prevent foreign material entering the service water system intake, a Level
Region: II | Hatch | 17723 | 03/31/2011 04/27/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Interaction of non-safety related power system with safety systems during bus transfers |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | NONE | An NRC indentified NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the failure to properly analyze electrical bus transfers that could adversely affect redundant safety buses. Specifically, the licensee failed to analyze th
Region: II | Hatch | 17730 | 02/24/2011 03/15/2011 | 2010009-03 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action for Installing Appendix R Emergency Lights |  | H.2(d) Facilities & Equipment | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.05T | Green. The team identified a non-cited violation of Hatch Unit 1 License Condition 2.C.3 and Unit 2 License Condition 2.C.3 (a) for the failure to take timely corrective actions to restore emergency lighting to be in compliance with 10 CFR Part 50, Append
Region: II | Hatch | 17716 | 09/30/2010 10/29/2010 | 2010004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correct a condition adverse to quality results in 1A emergency diesel generator fuel oil line failure |  | H.3(b) Work Activity Coordination | TE?: N | 05000321 Hatch 1 |  | 71152 | Green. A self-revealing NCV of 10 CFR 50 Appendix B Criterion XVI, Corrective Action, was identified for the licensee's failure to promptly identify and correct a diesel fuel oil leak on the 1A emergency diesel generator. The fuel oil leak was identified
Region: II | Hatch | 17717 | 09/30/2010 10/29/2010 | 2010004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to correct a condition adverse to quality with the IRM system results in reactor scram |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000321 Hatch 1 |  | 71153 | Green. A self-revealing NCV of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified for the failure to adequately correct a condition adverse to quality affecting the Intermediate Range Monitor (IRM) system. Consequently, a Unit 1 reacto
Region: II | Hatch | 17709 | 06/30/2010 07/30/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain safety related cables in a non-submerged environment |  | H.3(b) Work Activity Coordination | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.06 | -Green. The NRC identified a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure implement measures to assure that safety-related cables remained in an environment for which they were designed. Safety-related cables pur
Region: II | Hatch | 17710 | 06/30/2010 07/30/2010 | 2010003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to follow corrective action program procedure and prevent recurrence of severity level 2 root cause |  |  | TE?: N | 05000321 Hatch 1 |  | 71111.12 | -Green. A self-revealing NCV of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified for the licensee's failure to follow their corrective action program procedure, NMP-GM-002, Ver. 4.0, that required severity level 1 a
Region: II | Hatch | 17711 | 06/30/2010 07/30/2010 | 2010003-03 | NRC | NCV | Mitigating Systems | Green | Failure to follow procedure while in shutdown cooling to record corrected reactor water level |  | H.3(a) Work Planning | TE?: N | 05000366 Hatch 2 |  | 71111.2 | -Green. The NRC identified a NCV of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, for the licensee's failure to prescribe in procedure 34GO-OPS-015-2, Maintaining Cold Shutdown or Refueling Condition, appropriate documented in
Region: II | Hatch | 17706 | 03/31/2010 04/29/2010 | 2010002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to implement adequate configuration control on Unit 2 main generator stator water cooling temperature control instrument loop, 2N43-F100 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000366 Hatch 2 |  | 71153 | A self-revealing finding was identified for the licensee's failure to create, implement, and make available to maintenance personnel, quality processes or documents for configuration control. Specifically, the licensee failed to maintain the correct confi
Region: II | Hatch | 17688 | 07/31/2009 08/17/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Cause Determinations and Corrective Actions for Deficiencies in Containment Penetration Seals |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly correct deficiencies in containment penetration seals. The licensee initiated CR 2009105747 to evaluate corrective
Region: II | Hatch | 17689 | 07/31/2009 08/17/2009 | 2009006-02 | NRC | NCV | Barrier Integrity | Green | Failure to Correctly Establish Containment Isolation Valve Leakage Criteria for the Unit 2 Feedwater Check Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000366 Hatch 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to correctly establish containment isolation valve leakage criteria for Unit 2 feedwater check valves. The licensee initiated CR 2009104567 and
Region: II | Hatch | 17690 | 07/31/2009 08/17/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Establish Acceptance Criteria for the Standby Diesel Service Water Pump Section |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, Test Control, for failure to correctly establish acceptance criteria for the Standby Diesel Service Water (SDSW) System. The licensee performed a past operability determinat
Region: II | Hatch | 17691 | 07/31/2009 08/17/2009 | 2009006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Main Steam and Feedwater Line Pipe Whip Restraints |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.65(a)(1) for the licensee's failure to monitor the main steam line and feedwater line pipe whip restraints for Units 1 and 2. The licensee initiated CRs 2009105147 and 200910622 and plans to complete
Region: II | Hatch | 17692 | 07/31/2009 08/17/2009 | 2009006-05 | NRC | URI | Mitigating Systems | Green | Non-Interruptible Essential Instrument Air Header Check Valves for Units 1 and 2 |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Introduction: The team identified an Unresolved Item (URI) regarding non-interruptible essential instrument air header check valves for Units 1 and 2. The licensee had not performed periodic maintenance or testing that demonstrated the capability of the c
Region: II | Hatch | 17696 | 07/31/2009 08/17/2009 | 2009006-06 | NRC | URI | Mitigating Systems | Green | Reactor Building Equipment Drain Sump System for Units 1 and 2 |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | Introduction: The team identified an Unresolved Item (URI) regarding the licensee's failure to scope and monitor the Reactor Building Equipment Drain Sump System for Units 1 and 2 in the maintenance rule program. Description: The torus room and the re
Region: II | Hatch | 16882 | 06/30/2009 07/28/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fire Brigade Minimum Staffing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152 | Green. A Green NRC identified NCV of License Conditions 2.C.(3) for Unit-1 and 2.C.(3).(a) for Unit-2 was identified for failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed
Region: II | Hatch | 16878 | 03/31/2009 04/30/2009 | 2009002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Improper core drill location results in secondry containment inoperability |  | H.4(a) Human Error Prevention | TE?: N | 05000366 Hatch 2 |  | 71111.18 | A self-revealing NCV of 10 CFR Part 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified because workers did not properly follow the work instructions during a core drilling activity which resulted in a breach of secondary co
Region: II | Hatch | 16879 | 03/31/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Preconditioning of the turbine building plant service water isolation valves |  | P.2(b) Implementing Operating Experience | TE?: N | 05000366 Hatch 2 |  | 71111.22 | An NRC-identified NCV of 10 CFR Part 50 Appendix B, Criterion XI, Test Control was identified for preconditioning of the Turbine Building Plant Service Water (PSW) Isolation Valves. A maintenance work order stoked the valves several times prior to perform
Region: II | Hatch | 16880 | 03/31/2009 04/30/2009 | 2009002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to provide training to users of powered air-purifiying respirators |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7112103 | The inspectors identified a Green non-cited violation (NCV) of TS 5.4, Procedures, for failure to provide training to users of Powered Air-purifying Respirator (PAPR) type respiratory protection devices as required by procedure 10AC-MGR-026-0, Respiratory
Region: II | Hatch | 16874 | 09/19/2008 10/28/2008 | 2008007-01 | NRC | NCV | MISC | Green | Incomplete Mitigating Strategy Required by Facility Operating License (Section 4AO5.2 c) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 2515/171 | This B.5.b Pase 2 and 3 Mitigating Strategy Finding has been classified as OUO containing sensitive information classified under 2.390 - see inspection report for details.
Region: II | Hatch | 16868 | 03/30/2008 04/30/2008 | 2008002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Equipment Clearance Procedures Results in Control Room Ventilation Inoperability |  | H.4(a) Human Error Prevention | TE?: N | 05000366 Hatch 2 |  | 71111.13 | A self revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V was identified for the failure to recognize the impact of a clearance activity on the Main Control Room Environmental Control (MCREC) system. The licensee entered this violation int
Region: II | Hatch | 16871 | 03/07/2008 04/18/2008 | 2008006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Response to Water Contaminated Oil Results in HPCI Unavailability |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000366 Hatch 2 |  | 95001 | A Green NRC identified non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified when the licensee failed to thoroughly identify and correct water intrusion into the High Pressure Coolant Injection (HPCI) lubricating oi
Region: II | Hatch | 16867 | 12/31/2007 01/29/2008 | 2007005-01 | Self - Revealed | FIN | Initiating Events | Green | Improper Test Lead Construction Results in Plant Transient |  |  | TE?: N | 05000366 Hatch 2 |  | 71153 | A self-revealing finding was identified for the licensee's failure to follow proper work practices during construction of two test leads in accordance with skill of the craft training. The failure of the test leads resulted in an abrupt speed decrease in
Region: II | Hatch | 16864 | 09/30/2007 10/30/2007 | 2007004-01 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Instructions Results in Reactor Scram during Generator Recorder Calibration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000366 Hatch 2 |  | 71153 | A self-revealing non-cited violation (NCV) of 10CFR50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for inadequate work instructions provided to workers for the calibration of a main generator output recorder. The calibra
Region: II | Hatch | 16862 | 08/17/2007 09/14/2007 | 2007006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Update Parts Specifications Following a Design Modification |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152B | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion III was identified for failure to control the design aspects of a plant modification. The licensee failed to incorporate vendor parts and specifications for a modification to the Uni
Region: II | Hatch | 16863 | 08/17/2007 09/14/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required ASME Code, Section XI Testing |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71152B | An NRC-identified Green non-cited violation of 10 CFR 50.55a(g)(4) for the failure to perform periodic leakage testing of buried piping sections of the High Pressure Coolant Injection (HPCI) and Standby Diesel Service Water (SBDSW) systems as required by
Region: II | Hatch | 16860 | 03/31/2007 04/30/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Pre-conditioning of RHR/CS Room Cooler Valves |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71111.22 | An NRC-identified NCV of 10 CFR Part 50, APP B, Criterion XI, Test Control, was identified for pre-conditioning of the Residual Heat Removal (RHR)/Core Spray (CS) pump room cooler water supply valves. The surveillance test procedure sequence caused these
Region: II | Hatch | 16844 | 07/14/2006 08/24/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Use Adequate Test Instrumentation During Room Cooler Performance Tests. |  | H.2(d) Facilities & Equipment | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, for not assuring adequate test equipment or suitable environmental conditions were used for testing safety related room coolers. Specifical
Region: II | Hatch | 16845 | 07/14/2006 08/24/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Circuit Components with Motor Thermal Overload Devices Bypassed. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, relating to a design deficiency which has existed since initial plant operation. Specifically, the team identified that the licensee byp
Region: II | Hatch | 16846 | 07/14/2006 08/24/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | Alternate Boron Injection Supply Hose not suitable for pump suction application. |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR Part 50 Appendix B, Criterion III, Design Control, for improperly analyzing and allowing the use of a collapsible fire hose in the transfer of borated water from the standby liquid control
Region: II | Hatch | 16841 | 03/31/2006 04/27/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate that the Traveling Water Screen System Was Effectively Controlled per 10 CFR 50.65 (a)(2) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000321 Hatch 1 |  | 71111.12 | An NRC-identified Non-Cited Violation (NCV) of 10 CFR 50.65 (Maintenance Rule) was identified for failing to demonstrate that the performance of the Traveling Water Screens (TWS) was being effectively controlled through the performance of appropriate prev
Region: II | Hatch | 23498 | 05/04/2018 |  | Licensee - Identified | NCV |  | Green | Failure to control access to a Locked High Radiation Area |  |  | TE?: N | 05000321 Hatch 1 05000366 Hatch 2 |  | 71124.01 | A Green Licensee Identified Violation (LIV) of Hatch Nuclear Plant Technical Specification (TS), Section 5.7, High Radiation Area, for the licensee’s failure to properly control access to a Locked High Radiation Area (LHRA). TS 5.7.2 requires in part, tha
Region: II | Hatch | 125363 | 08/07/2019 |  |  | LIV |  | Green | Failure to perform a Fatigue Assessment |  |  | TE?: N | 05000366 Hatch 2 |  | 71152
Region: II | McGuire | 125211 | 06/30/2019 08/01/2019 | 2019002-01 | Self - Revealed | NCV | Initiating Events | Green | McGuire Loss of Inventory in Mode 5 |  | H.12 - Avoid Complacency | TE?: N | 05000369 McGuire 1 | Human Performance | 71111.2 | A self-revealed Green finding and associated NCV of TS 5.4.1, “Procedures,” was identified when the licensee failed to adequately implement the procedure requirements for installing a test gauge tubing for ECCS testing. Specifically, the licensee inst
Region: II | McGuire | 125212 | 06/30/2019 08/01/2019 | 2019002-02 | Self - Revealed | NCV | Initiating Events | Green | Unit 1 Over Temperature/Delta Temperature (OT/DT) Trip |  | H.11 - Challenge the Unknown | TE?: N | 05000369 McGuire 1 | Human Performance | 71153 | A self-revealed Green finding and associated NCV of TS 5.4.1 “Procedures,” was identified when the licensee failed to adequately implement procedure OP/1/A/6100/003, “Controlling Procedure for Unit Operation,” Enclosure 4.6, “Operation of Pressurizer Heat
Region: II | McGuire | 24362 | 07/27/2018 08/14/2018 | 2018012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Seismic Mounting Requirements for 125 VDC Vital Batteries into Installation and Replacement Procedure |  | H.6 - Design Margins | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71152B | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to translate the mounting requirements for seismic qualification contained in NLI t
Region: II | McGuire | 23530 | 03/31/2018 04/30/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Non-conservative change to core exit thermocouple acceptance criteria in PT/1/A/4600/003 D. |  | H.14 - Conservative Bias | TE?: N | 05000369 McGuire 1 |  | 71111.22 | The inspectors identified a Green NCV of Technical Specification (TS) 5.4, “Procedures” for an inadequate procedure change to PT/1/A/4600/003 D, “Monthly Surveillance Items.” Specifically, the licensee made a non-conservative change to the CET acceptance
Region: II | McGuire | 23531 | 03/31/2018 04/30/2018 | 2018001-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to adequately implement the SSPS test procedure resulted in a Unit 1 Reactor Trip. |  | H.12 - Avoid Complacency | TE?: N | 05000369 McGuire 1 |  | 71153 | A self-revealing Green NCV of TS 5.4 “Procedures,” was identified when the licensee failed to adequately implement procedure PT/0/A/4601/008 B, “SSPS Train B Periodic Test With NC System Pressure Greater Than 1955 PSIG,” resulting in a Unit 1 reactor trip
Region: II | McGuire | 25972 | 03/02/2018 04/12/2018 | 2018010-01 | NRC | FIN | Mitigating Systems | Green | Failure to Update Offsite Circuit Operability Limit for Single Busline Alignment. |  | H.6 - Design Margins | TE?: N | 05000369 McGuire 1 |  | 71111.21M | The inspectors identified a Green finding for the licensee's failure to update calculations as required by procedure AD-EG-ALL-1117, "Design Analyses and Calculations," Rev. 5. Specifically, the licensee reviewed calculation MCC-1381.05-00-0258, "U1, 6.9
Region: II | McGuire | 25973 | 03/02/2018 04/12/2018 | 2018010-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Update the FSAR With Pertinent Design Information |  | NPP | TE?: Y SL-NCVIV | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.21M | The inspectors identified a Green finding and associated Severity Level IV Non-cited Violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.71(e), for the licensee's failure to update the final safety analysis report (FSAR) to include
Region: II | McGuire | 36966 | 06/30/2017 07/24/2017 | 2017002-01 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate survey results in unposted high radiation area. |  | H.12 Avoid Complacency | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71124.01 | A self-revealing Green non-cited violation (NCV) of 10 CFR 20.1501(a)(2) was identified for the licensee's failure to conduct an adequate area radiation survey in Room 619 of the auxiliary building (waste gas decay tank (WGDT) room). Specifically, on Apri
Region: II | McGuire | 36965 | 03/31/2017 04/25/2017 | 2017001-01 | NRC | NCV | Initiating Events | Green | Failure to adequately control transient combustibles using a receptacle with a self-closing lid. |  | H.8 Procedure Adherence | TE?: N | 05000369 McGuire 1 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of the McGuire Unit 1 Renewed Facility Operating License Condition 2.C.4, "Fire Protection Program" (FPP), was identified for the licensee's failure to adequately implement fire protection procedures for a
Region: II | McGuire | 36964 | 02/10/2017 03/22/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to translate required gasket replacement requirements into limit switch maintenance manual. |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.21N | Green. The team identified a green non-cited violation (NCV) of Title10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate requirements necessary for maintaining the environmen
Region: II | McGuire | 36962 | 06/30/2016 07/22/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | Failure to perform general visual examinations of containment moisture barriers associated with containment liner leak chase test connections. |  | P.3 Resolution | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.08P | Green: An NRC-identified Green non-cited violation (NCV) of 10 CFR Part 50.55a, "Codes and Standards," was identified for the licensee's failure to perform general visual examinations of moisture barrier material in the reactor containment leak-chase chan
Region: II | McGuire | 36963 | 06/30/2016 07/22/2016 | 2016002-02 | NRC | NCV | Barrier Integrity | Green | Failure to ensure containment equipment hatch was properly closed during fuel movements. |  | H.8 Procedure Adherence | TE?: N | 05000369 McGuire 1 |  | 71111.2 | Green: An NRC-identified Green NCV of Technical Specification (TS) 5.4.1.d, "Procedures," was identified for the licensee's failure to adequately implement the commitments in Selective Licensee Commitment (SLC) 16.9.25, "Refueling Operations - Containment
Region: II | McGuire | 36961 | 03/31/2016 04/28/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | "Failure to Maintain Fire Extinguishers in Contaminated Radiation Control Zones in Accordance with the Fire Protection Program." |  | H.2 Field Presence | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | Green. An NRC-identified Green non-cited violation (NCV) of the McGuire Nuclear Station Unit 1 and Unit 2 Renewed Facility Operating License Condition 2.C.4, "Fire Protection Program (FPP)," was identified for failure to perform annual maintenance on fire
Region: II | McGuire | 36959 | 12/11/2015 01/19/2016 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Completely and Accurately Translate the Safe Shutdown Analysis to Procedures |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05T | Green. The NRC identified a Green non-cited violation (NCV) of McGuire Technical Specification 5.4.1.a, for Unit 1, for having an inadequate procedure to support safe shutdown for a fire in fire area (FA) 15/17. Specifically, the licensee's deterministic
Region: II | McGuire | 36958 | 09/30/2015 10/30/2015 | 2015003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Implement a Temporary Modification for a Leak Enclosure |  | H.13 Consistent Process | TE?: N | 05000370 McGuire 2 |  | 71152 | -Green: A self-revealing Green finding (FIN) was identified for failure to adequately implement the modification procedural requirements of engineering directives manual (EDM)-601, "Engineering Change Manual," for a temporary modification that installed a
Region: II | McGuire | 36957 | 06/30/2015 07/28/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Compensatory Actions for Obstructed Fire Sprinkler Spray Nozzle |  | H.8 Procedure Adherence | TE?: N | 05000370 McGuire 2 |  | 71111.05Q | Green: An NRC-identified Green NCV of Technical Specification (TS) 5.4.1.d, "Procedures," was identified for failure to evaluate and establish adequate compensatory measures for an impaired fire protection automatic water sprinkler system. Specifically, a
Region: II | McGuire | 36950 | 06/05/2015 07/23/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Protection System DC Molded Case Circuit Breaker Ratings |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | -Green: The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," consisting of two examples. In one example, the licensee failed to verify the adequacy of GE model TED molded case circuit breaker (MCC
Region: II | McGuire | 36951 | 06/05/2015 07/23/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Periodic Testing of Molded Case Circuit Breakers |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | -Green: The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," consisting of two examples. In one example, the licensee failed to scope some Class 1E molded case circuit breakers (MCCBs) into the Class
Region: II | McGuire | 36942 | 12/31/2014 02/03/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Control Transient Combustible Materials and Ignition Sources in Accordance with the Fire Protection Program |  | H.4 Teamwork | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | -Green: An NRC-identified Green NCV of the McGuire Unit 1 and Unit 2 Renewed Facility Operating License Condition 2.C.4, "Fire Protection Program (FPP)," was identified for the licensee's failure to adequately control fire ignition sources in the Unit 1 a
Region: II | McGuire | 36948 | 12/31/2014 02/03/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Containment Closeout Resulting in Loose Debris and Unanalyzed Materials Left in Containment |  | H.2 Field Presence | TE?: N | 05000369 McGuire 1 |  | 71111.2 | -Green: An NRC-identified Green NCV of Technical Specification 5.4.1.a, "Procedures," was identified for the failure to properly implement containment cleanliness and material control closeout procedures in accordance with procedure PT/1A/4600/003F, "Cont
Region: II | McGuire | 36939 | 06/26/2014 08/08/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Inadequately Sealed Safety Related Electrical Cabinet |  | H.8 Procedure Adherence | TE?: N | 05000369 McGuire 1 |  | 71152B | An NRC-identified NCV of 10 CFR Part 50 Appendix B, Criterion XVI, Corrective Action, was identified when the licensee failed to promptly identify a condition adverse to quality associated with the inadequate sealing for safety related cabinet 1FWPNRWLP (
Region: II | McGuire | 36934 | 03/31/2014 04/30/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately control transient combustible materials in accordance with the fire protection program |  | H.4 Teamwork | TE?: N | 05000370 McGuire 2 |  | 71111.05Q | An NRC-identified NCV of the McGuire Unit 1 and Unit 2 Renewed Facility Operating License Condition 2.C.4, Fire Protection Program (FPP), was identified for the licensee's failure to adequately control the storage of transient combustibles in the 2A resid
Region: II | McGuire | 36935 | 03/31/2014 04/30/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately control the use of self-extinguishing fire lids |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | An NRC-identified NCV of the McGuire Unit 1 and Unit 2 Renewed Facility Operating License Condition 2.C.4, FPP, was identified for the licensee's failure to adequately control the storage of transient combustibles in waste receptacles equipped with self-e
Region: II | McGuire | 36936 | 03/31/2014 04/30/2014 | 2014002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to implement adequate design control measures for rod control power supply replacement resulting in reactor trip |  |  | TE?: N | 05000369 McGuire 1 |  | 71153 | A self-revealing finding (FIN) was identified for the licensee's failure to implement adequate design control measures for the rod control power supply modification which resulted in the loss of 24VDC power in the 1AC rod control power cabinet. The in
Region: II | McGuire | 36933 | 12/31/2013 01/23/2014 | 2013005-01 | NRC | URI | Mitigating Systems | Green | Evaluation of gas void identified in Unit 2 ECCS piping |  |  | TE?: N | 05000370 McGuire 2 |  | 71111.22
Region: II | McGuire | 36928 | 06/30/2013 07/29/2013 | 2013003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to implement adequate venting instructions for condensate booster pump trip instrumentation resulting in reactor trip |  |  | TE?: N | 05000369 McGuire 1 |  | 71153 | A self-revealing finding was identified for the licensee's failure to implement adequate instructions for venting condensate booster pump (CBP) emergency low suction pressure trip instrumentation which resulted in air entrainment causing a non-conservativ
Region: II | McGuire | 36920 | 03/31/2013 04/24/2013 | 2013002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Revise Turbine Inlet Pressure Calibration Procedure |  | H.3(b) Work Activity Coordination | TE?: N | 05000370 McGuire 2 |  | 71153 | A self-revealing finding was identified for the licensee's failure to follow the requirements of the station modification program manual EDM 601 during implementation of a high pressure turbine replacement modification revision. This resulted in Anticipat
Region: II | McGuire | 36927 | 02/15/2013 03/27/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Modifications Result in Nonfunctional Fire Doors |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05T | An NRC identified Green non-cited violation of McGuire's Selected Licensing Commitment 16.9.5, Fire Rated Assemblies was identified for the licensee's inadequate implementation of modifications that results in nonfunctional fire doors. The Licensee has en
Region: II | McGuire | 36918 | 12/31/2012 01/25/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain complete and accurate pre-fire plans |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000370 McGuire 2 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of the Unit 2 Facility Operating License, Condition 2.C.4, Fire Protection Program, was identified for failure to maintain pre-fire plans in areas that contain safety-related equipment. The inspectors iden
Region: II | McGuire | 36916 | 09/30/2012 10/31/2012 | 2012004-01 | NRC | FIN | Mitigating Systems | Green | Failure to correctly implement technical specifications adversely affects requalification operating test quality |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.11Q | An NRC-identified finding was identified associated with the quality of the simulator scenarios developed by the licensee for the licensed operator requalification annual operating test. The licensee failed to follow the Technical Specification (TS) rules
Region: II | McGuire | 36909 | 08/31/2012 10/11/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform required extent of condition assessments for quick cause evaluations in accordance with McGuire's quality assurance program |  | H.4(b) Procedural Compliance | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | NONE | -Green. A finding of very low safety significance and associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified by inspectors for the licensee's failure to perform required extent of condi
Region: II | McGuire | 36900 | 06/30/2012 07/27/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement planned compensatory measures for impaired auxiliary building fire hose stations |  | H.3(a) Work Planning | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | An NRC-identified non-cited violation (NCV) of Technical Specification (TS) 5.4.1.d was identified for failure to implement adequate compensatory measures for multiple impaired manual fire hose stations (FHSs) in accordance with the approved fire protecti
Region: II | McGuire | 36907 | 06/18/2012 07/25/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Potential Blocking of TDCA Pump Lube Oil Cooler During Certain Fire Events |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | The NRC identified a NCV of License Condition 2.C.4 for failure to evaluate potential blockage of the Turbine Driven Auxiliary Feedwater (TDCA) pump lube oil cooler when pump suction is aligned to the circulating water (RC) system. Specifically, during ce
Region: II | McGuire | 36908 | 06/18/2012 07/25/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Tornado Missile Protection for EDG Exhaust Ventilation System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | The NRC identified a NCV of 10CFR50, Appendix B, Criterion III, "Design Control," for the failure to ensure adequate tornado missile protection for the emergency diesel generator (EDG) exhaust relief and backdraft dampers as required. Specifically, 12 inc
Region: II | McGuire | 36898 | 03/31/2012 04/26/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Operable Fire Assembly in Unit 2 Auxiliary Feedwater Pump Room |  | H.4(b) Procedural Compliance | TE?: N | 05000370 McGuire 2 |  | 71111.05Q | An NRC-identified Green non-cited violation (NCV) of Technical Specification (TS) 5.4.1.d was identified for failure to maintain an operable fire assembly resulting in an unsealed pipe penetration through a 3-hour rated fire barrier wall separating the
Region: II | McGuire | 36899 | 03/31/2012 04/26/2012 | 2012002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Enter Condition Adverse to Quality into the CAP |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000370 McGuire 2 |  | 71152 | A NRC-identified Green finding was identified for the failure to follow the site's corrective action program (CAP) procedure which required the initiation of a PIP for a degraded 2B emergency diesel generator (EDG) Bellofram seal. The degraded Bellofram
Region: II | McGuire | 36897 | 09/30/2011 10/28/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish adequate ND venting procedures |  | P.2(b) Implementing Operating Experience | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | NONE | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, for the failure to establish acceptance criteria to determine operability in surveillance procedures used to vent the decay heat removal (ND) sys
Region: II | McGuire | 36889 | 03/31/2011 05/06/2011 | 2011002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to eliminate fish in the SNSWP |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71153 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to correct a condition adverse to quality. The licensee had previously identified that the fish population in the Standby Nucl
Region: II | McGuire | 36881 | 10/22/2010 12/02/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with Emergency Diesel Generators Fuel Transfer System Niagara Flow Meters |  | H.3(a) Work Planning | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71152B | The NRC identified a Non-cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to correct a condition adverse to quality in that a single vulnerability failure of the fuel transfer (FD) system Niagara
Region: II | McGuire | 36880 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Initiating Events | Green | Failure to determine the cause and take corrective action to preclude repetition for control room area chilled water system |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71153 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to determine the cause of a significant condition adverse to quality involving both trains of Control Room Area Chilled Water
Region: II | McGuire | 36872 | 06/30/2010 07/26/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment Associated With 1EVIB Troubleshooting Activities |  | H.3(a) Work Planning | TE?: N | 05000369 McGuire 1 |  | 71111.13 | -Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(4) for an inadequate risk assessment prior to performing maintenance troubleshooting activities on the 120VAC Vital Instrument & Control (I&C) Power System. The troubleshooti
Region: II | McGuire | 36873 | 06/30/2010 07/26/2010 | 2010003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to barricade, conspicuously post, and adequately control access to a HRA |  | H.3(a) Work Planning | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71124.01 | -Green. A self-revealing NCV of TS 5.7.1 was identified for the failure of the licensee to barricade, conspicuously post, and adequately control access to a high radiation area (HRA). Specifically, on September 17, 2009, a crane flagman on a Radiation Wor
Region: II | McGuire | 36863 | 03/31/2010 04/28/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately implement the FIre Protection Program (FPP) for the Standby Shutdown System (SSS) |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.18 | The inspectors identified a Green NCV of the FPP required by 10 CFR 50.48 and License Condition 2.C.4 for failing to take adequate design control measures associated with the addition of the standby shutdown system (SSS) for both Units. Specifically, the
Region: II | McGuire | 36870 | 03/31/2010 04/28/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Failure to flow test nuclear service water "A" train standby nuclear service water pond (SNSWP) supply header at maximum design. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71153 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, was identified for the licensee's failure to flow test the Nuclear Service Water System (NSWS) "A" Train Standby Nuclear Service Water Pond (SNSWP) unit common supply header
Region: II | McGuire | 36858 | 12/21/2009 01/22/2010 | 2009501-01 | NRC | NCV | Emergency Preparedness | Green | Biennial exercise was not an adequate test |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71114.01 | The inspectors identified a Green NCV of 10 CFR50.47(b)(14) for failure to conduct a biennial exercise that was technically accurate and challenging, to the extent that it was not an adequate test of the plans, procedures, equipment, and implementation of
Region: II | McGuire | 36853 | 09/30/2009 10/29/2009 | 2009004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to properly calibrate area radiation monitors (Section 2OS3) |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7112103 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 20.1501(b) for the licensee's failure to ensure that area radiation monitors (ARMs) used for quantitative measurements were calibrated. The licensee failed to complete the detector sens
Region: II | McGuire | 36846 | 06/30/2009 07/30/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Design Control Measures For Fire Protection |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | Green: A non-cited violation of License Condition 2.C.4, Fire Protection Program (FPP), was identified for inadequate design control measures associated with the downgrading of a 3-hour rated fire barrier between the electrical penetration room and essent
Region: II | McGuire | 36847 | 06/30/2009 07/30/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Procedures Not Appropriate to the Circumstances for A Train RN Temporary Testing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.13 | Green: A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the failure to provide procedures appropriate to the circumstances. The temporary test procedure for flow te
Region: II | McGuire | 36851 | 06/30/2009 07/30/2009 | 2009003-04 | Self - Revealed | NCV | Barrier Integrity | Green | Untimely Corrective Actions for Containment Isolation Valve Inadequate Closing Margins |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71153 | Green: A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for untimely corrective action for containment isolation valves (CIVs) which could spuriously open during an event requiring contai
Region: II | McGuire | 36843 | 06/18/2009 07/27/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for RN System Flow Balancing |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | The team identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide adequate procedures for flow balanci
Region: II | McGuire | 36844 | 06/18/2009 07/27/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Basis Information Related to the Isolation Time for Safety Related MOVs into Instructions and Procedures |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | The team identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the applicable design bases were correctly translated into the in-service te
Region: II | McGuire | 36845 | 06/18/2009 07/27/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of the Design Adequacy of the Control Circuit Voltage for 600 VAC Safety Related Motors |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | The team identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for failure to establish measures to verify the design capability of the control circuit voltage for 600 VAC safety re
Region: II | McGuire | 36841 | 05/14/2009 06/25/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action for Appendix R Emergency Lighting Credited for Operator Action |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000370 McGuire 2 |  | 71111.05T | The inspectors identified a non-cited violation of McGuire Unit 2 Operating License Condition 2.C.4 for failure to implement and maintain their Fire Protection Program as described in design basis document MCS-1465.00-00-008, "Plant Design Basis Specifica
Region: II | McGuire | 36842 | 05/14/2009 06/25/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Pertinent Fire Brigade Information and Guidance Not Identified in Fire Fighting Strategies |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000370 McGuire 2 |  | 71111.05T | The inspectors identified a non-cited violation of Unit 2 Operating License Condition 2.C.4 and the Fire Protection Program as contained in design basis document MCS-1465.00-00-008, "Plant Design Basis Specification for Fire Protection." Specifically, the
Region: II | McGuire | 36835 | 03/31/2009 04/23/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with Abnormal Procedures for Loss of Nuclear Service Water |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.11Q | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the failure to promptly correct a condition adverse to quality associated with the sharing of the nuclear service water system between units in
Region: II | McGuire | 36832 | 12/31/2008 01/29/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | Failure to Perform an Adequate Risk Assessment for Switchyard Activities |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000370 McGuire 2 |  | 71111.13 | The inspectors identified a NCV of 10CFR50.65(a)(4) for failure to perform an adequate risk assessment for Unit 1 when the performance of switchyard activities affected both units, and were categorized as risk significant for Unit 2. This finding was docu
Region: II | McGuire | 36820 | 06/30/2008 07/24/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Main Feedwater Tempering Line Valves Into the Maintenance Rule Monitoring Program (Section 1R12) |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(b)(2)(i) for failure to scope the credited main feedwater tempering lines (one per steam generator) and associated valves into the Maintenance Rule monitoring program. This finding was mor
Region: II | McGuire | 36823 | 06/30/2008 07/24/2008 | 2008003-03 | NRC | NCV | Barrier Integrity | Green | Pre-conditioning of Unit 2 MSIVs Prior to Surveillance Testing (Section 1R22) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000370 McGuire 2 |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification (TS) 5.4.1.a for failure to establish an adequate procedure to test main steam isolation valves (MSIVs). Specifically, written test control procedures did not prevent and, therefor
Region: II | McGuire | 36810 | 03/31/2008 04/24/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish and Maintain Abnormal Procedures for Loss of Nuclear Service Water (Section 1R11) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.11Q | The inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a. for failure to adequately establish and maintain procedures required by Regulatory Guide 1.33, Appendix A, Section 5, Procedures for Abnormal Conditions. Specif
Region: II | McGuire | 36817 | 03/31/2008 04/24/2008 | 2008002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Foreign Material Exclusion Control Procedures (Section 1R13) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000370 McGuire 2 |  | 71111.13 | A self-revealing NCV of TS 5.4.1.a, for failure to adequately implement procedures required by Regulatory Guide 1.33, Appendix A, Section 9, Procedures for Performing Maintenance, was identified. Specifically, foreign material exclusion control procedures
Region: II | McGuire | 36818 | 03/31/2008 04/24/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Nuclear Service Water System Flow Analysis Deficiencies (Section 4OA5.2) |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | NONE | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to establish measures to verify the design capability of the RN pumps. Specifically, the licensee did not perform system hydraulic analyses or use other m
Region: II | McGuire | 36526 | 12/31/2007 01/31/2008 | 2007005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to take adequate corrective action for ensuring containment spray isolation valve thrust capacity. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000370 McGuire 2 |  | 71111.22 | The inspectors identified a self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, for inadequate corrective action associated with the prevention of exceeding the thrust capacities of containment spray (NS) isolation valves (due to differential pres
Region: II | McGuire | 36807 | 12/31/2007 01/31/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action for a Nonconformance Associated with ECCS Throttle Valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000369 McGuire 1 |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, for failure to take adequate corrective action for a nonconformance associated with potential clogging of the Unit 1 emergency core cooling system (ECCS) cold l
Region: II | McGuire | 36805 | 11/02/2007 12/07/2007 | 2007010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action For A Nonconformance Associated With ECCS Throttle Valves. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000370 McGuire 2 |  | NONE | The purpose of this letter is to provide you with the Nuclear Regulatory Commission's (NRC's) final significance determination for a finding at Duke Power Company's (Duke) McGuire Nuclear Station (MNS) involving the failure to take adequate corrective a
Region: II | McGuire | 36524 | 02/09/2007 03/08/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Appropriate Corrective Actions for Valve Positioners not Analyzed for Seismic Requirements |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71152B | The NRC identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee failed to take adequate corrective actions in response to a Green NCV issued for nonconformance with respect to the
Region: II | McGuire | 36517 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Initiating Events | Green | Failure to identify and evaluate multiple boric acid leaks. |  | H.4(b) Procedural Compliance | TE?: N | 05000370 McGuire 2 |  | 71111.08P | Green. The inspectors identified a non-cited violation (NCV) of 10CFR50, Appendix B, Criterion V, Instructions, Procedures and Drawings. Licensee activities affecting quality were not accomplished in accordance with site procedures, in that, the licensee
Region: II | McGuire | 36518 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | NCV | Barrier Integrity | Green | Failure to implement adequate design and test control for ice condenser lower inlet doors. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.22 | Green. The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, and Criterion XVI; Test Control, for the licensee's failure to have design documentation to support the ice condenser lower inlet d
Region: II | McGuire | 36522 | 12/31/2006 01/30/2007 | 2006005-04 | NRC | NCV | Public Radiation Safety | Green | Failure to conduct adequate QA activities to ensure waste shipments are characterized in accordance with 10 CFR 61.55. |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7112202 | Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 20 Appendix G, Section III.A.3 for failure to conduct adequate Quality Assurance (QA) activities to ensure compliance with the waste characterization requirements of 10 CFR 61.55. The
Region: II | McGuire | 36523 | 12/31/2006 01/30/2007 | 2006005-05 | NRC | NCV | Public Radiation Safety | Green | Failure to train HAZMAT employees. |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7112202 | An NCV of 10 CFR 71.5 and 49 CFR172.704(a) was identified for failure to provide required training to hazardous material (Hazmat) employees involved in the preparation and loading of packages containing radioactive material for public transport. Specifica
Region: II | McGuire | 36508 | 10/06/2006 10/30/2006 | 2006004-01 | NRC | NCV | Initiating Events | Green | Failure to monitor the off-site power system under 10 CFR 50.65 a(1). |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.12 | An NRC-identified NCV was identified for the licensee's failure to establish goals and monitor the performance of the offsite power system per 10 CFR 50.65a(1). The licensee reclassified the offsite power system (OSP) from a(1) status to a(2) status witho
Region: II | McGuire | 36496 | 05/19/2006 06/22/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Effect of EDG under-frequency not included in ECCS pump test acceptance criteria |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The licensee did not account for emergency diesel generator underfrequency in test acceptance criterion for ASME Section XI testing of the high hea
Region: II | McGuire | 36497 | 05/19/2006 06/22/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | Maximum differential pressure for containment sump isolation valves. |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The licensee did not evaluate the impact of leakage past the pressure isolation check valves during low head safety injection (ND) pump operation i
Region: II | McGuire | 36505 | 05/19/2006 06/22/2006 | 2006007-05 | NRC | NCV | Mitigating Systems | Green | Valve positioner not analyzed for seismic requirements |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The licensee did not evaluate potential failure of the non-safety related valve positioner in the safety related nuclear service water valves, and
Region: II | McGuire | 36506 | 05/19/2006 06/22/2006 | 2006007-06 | NRC | NCV | Mitigating Systems | Green | Effect of post-accident elevated temperatures not analyzed for nuclear service water piping inside containment |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 7111121 | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control. The licensee did not perform an analysis or use other means to demonstrate that the non-safety related nuclear service water system piping inside
Region: II | McGuire | 36493 | 03/31/2006 04/28/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action for Repetitive Fire Strategy Plan Deficiencies |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | 71111.05Q | A non-cited violation was identified for failing to take adequate corrective action to ensure accuracy of all fire strategy plans in response to two previous multiple example NCVs. Permanent combustible storage locations were identified in the auxiliary b
Region: II | McGuire | 36494 | 03/31/2006 04/28/2006 | 2006002-02 | NRC | NCV | Public Radiation Safety | Green | Review Licensee Assessments and Vendor Evaluations for Observed U1/U2 Unit Vent Volume Flow Rate Changes to Assure Representative Sampling |  |  | TE?: N | 05000369 McGuire 1 05000370 McGuire 2 |  | NONE | The inspectors identified a Green Non-Cited Violation (NCV) of 10 CFR 20.1302(a) for failure to ensure surveys of particulate radioactive materials in effluents released to unrestricted areas by the unit vents were adequate to demonstrate compliance with
Region: II | North Anna | 125101 | 06/07/2019 08/13/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Qualify Containment Components for Initial Acidic Chemical Environment |  | NPP | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 | Equipment Performance | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR 50.49(e)(3) when the licensee failed to qualify all 10 CFR 50.49 electrical equipment for the most severe chemical effects expected in containment.
Region: II | North Anna | 125175 | 06/07/2019 08/13/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Design for Aging and Accident Profile Testing |  | NPP | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 | Equipment Performance | 71111.21N | The inspectors identified three examples of a Green finding and associated Non-cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III when the licensee failed to verify compliance with environmental qualification (EQ) requirements in accordan
Region: II | North Anna | 25886 | 11/30/2018 12/19/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Describe Discovered Degraded Condition of Service Water Pump House Ventilation Equipment in accordance with Corrective Action Program |  | NPP | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.21M | The inspectors identified a Green finding and associated Non-Cited Violation (NCV) of Criterion V, “Instructions, Procedures, and Drawings,” in Appendix B of 10 Code of Federal Regulations (10 CFR), for the licensee’s failure to follow their corrective ac
Region: II | North Anna | 23989 | 03/31/2018 05/08/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assure Service Water Pump Sheds from Emergency Bus upon LOOP or SBO |  | H.12 - Avoid Complacency | TE?: N | 05000338 North Anna 1 |  | 71111.22 | A self-revealing Green NCV of TS 5.4.1.a, was identified for the licensee’s failure to have adequate written procedures for assuring proper configuration control in areas affected by maintenance or plant modifications. Specifically, the licensee failed to
Region: II | North Anna | 22360 | 04/21/2017 06/02/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Qualify MCCs in Cable Penetration areas in accordance with 10 CFR 50.49 |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.17T | The NRC identified a Green non-cited violation of 10 CFR 50.49(f) for failing to qualify structures, systems, and components (SSCs) (eight motor control centers) located in a radiation harsh environment in accordance with IEEE Std. 323-1974 Section 5, “Pr
Region: II | North Anna | 22361 | 04/21/2017 06/02/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Qualify EGS Quick Disconnects in Accordance With IEEE Std. 323-1974 |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.17T | The NRC identified a Green non-cited violation of 10 CFR 50.49(e)(5) for failing to base the qualified life of structures, systems, and components (SSCs) (i.e. Nordel Orings) on the known limits of extrapolation in accordance with IEEE 323 Sections 6.5.3,
Region: II | North Anna | 29025 | 03/31/2017 05/09/2017 | 2017001-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Design Control of 2-RC-P-1C Piping Supports |  | H.5 - Work Management | TE?: N | 05000339 North Anna 2 |  | 71153 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the failure to correctly translate applicable regulatory requirements and the design basis into specifications, drawings, procedures, and instructions
Region: II | North Anna | 29019 | 06/30/2016 07/27/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Translation of Design Calculations into Compensatory Measures when Removing Missile Barriers Could Result in EDGs and SBO Diesel Inoperable (Section 1R13) |  | H.14 Conservative Bias | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.13 | Green. The NRC identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the inadequate translation of design calculations into compensatory measures when removing missile barriers. The inadequate translation of design calculat
Region: II | North Anna | 29010 | 12/31/2015 01/29/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Foreign Material Exclusion Procedure (Section 1R12) |  | H.5 Work Management | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.12 | A self-revealing, Green NCV of TS 5.4.1.a, "Procedures," as required by Regulatory Guide 1.33, Revision 2, Appendix A, Section 9a, "Procedures for Performing Maintenance," was identified for inadequate implementation of licensee procedure MA-AA-102, Attac
Region: II | North Anna | 28989 | 11/06/2015 12/21/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance for Implementing Alternative Shutdown for a Fire in the Unit 2 Quench Spray Pump House |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of Technical Specification 5.4.1.a, for the licensee's failure to provide adequate procedural guidance for implementation of the alternative shutdown capability in the event of a fire in the q
Region: II | North Anna | 29009 | 11/06/2015 12/21/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that the Turbine-driven Auxiliary Feed Water Pump had the Capability to Provide Sufficient Flow Such that Residual Heat Removal Entry Conditions Could Be Achieved during Fire Event |  | H.4 Teamwork | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of North Anna Power Station, Units No.1 and No. 2, Renewed Facility Operating License, Conditions 2.D, "Fire Protection," for the licensee's failure to ensure that the turbinedriven auxiliary
Region: II | North Anna | 29017 | 09/30/2015 10/01/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Potential Water Hammer Impact Loading on AFW piping |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | The team identified a non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to control deviations from their piping design code of record for the auxiliary feed
Region: II | North Anna | 29024 | 09/30/2015 07/27/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Adequacy of Class 1E 120VAC Vital Bus Design (Section1R21) |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | NONE | -Green. The NRC identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of design for the protection devices at the 120VAC vital instrumentation buses. Specifically, the licensee'
Region: II | North Anna | 29007 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure To Maintain An Adequate Maintenance Procedure For The Turbine Driven Auxiliary Feedwater Pump |  | H.1 Resources | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A self-revealing NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to maintain an adequate maintenance procedure to set the governor valve on the Unit 1 Turbine Driven Auxiliary F
Region: II | North Anna | 29006 | 03/31/2015 05/07/2015 | 2015001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure To Follow Procedure For RWST Instruments |  | H.5 Work Management | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A self-revealing NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to follow work management procedures. Specifically, the licensee failed to follow the conduct of maintenance pro
Region: II | North Anna | 29003 | 09/30/2014 11/10/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Maintaining MCR/ESGR Air Handler |  | H.6 Design Margins | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A self-revealing NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for a failure to prescribe maintenance procedures affecting the quality of fan 1-HV-AC-7 appropriate to the circumstances. Specifically, th
Region: II | North Anna | 29000 | 06/30/2014 08/12/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain the Diesel Driven Fire Pump |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | A self-revealing NCV was identified for the licensee's failure to meet the requirements of NAPS Renewed Operating License Conditions 2.D, and the approved FPP for NAPS, Units 1 and 2. Specifically, the licensee failed to maintain the diesel driven fire pu
Region: II | North Anna | 29001 | 06/30/2014 08/12/2014 | 2014003-02 | Self - Revealed | FIN | Initiating Events | Green | Unit 2 Manual Reactor Trip After Loss of Main Feedwater Pump |  | H.4 Teamwork | TE?: N | 05000339 North Anna 2 |  | 71152 | A self-revealing finding was identified for failure to follow procedure after a feedwater transient that resulted in a Unit 2 manual trip. Specifically, the licensee failed to use diverse or alternate indications, such as motor amps, feedwater pump discha
Region: II | North Anna | 28998 | 03/31/2014 05/01/2014 | 2014002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to mark a foreign material exclusion closure devise results in non-funcionality of the alternate AC diesel |  | H.12 Avoid Complacency | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.19 | A self-revealing finding was identified for the licensee's failure to mark a foreign material exclusion (FME) closure device, as required by licensee procedure MA-AA-102, "Foreign Material Exclusion," Revision 14. This resulted in the non-functionality of
Region: II | North Anna | 28996 | 12/31/2013 02/10/2014 | 2013005-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Work Instructions for the Replacement of Protective Relays Causes a Unit 1 Reactor Trip Due to Loss of Station Service Bus Transformer After Start of 1C Condensate Pump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71152 | A Green, self-revealing finding was identified for failure to follow procedure for the replacement of protective relays that resulted in a Unit 1 trip. Specifically, the instructions in work order (WO) 59102618778 stated to "Have Control Ops install short
Region: II | North Anna | 28992 | 09/30/2013 10/30/2013 | 2013004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to provide vendor oversight results in a manual reactor trip |  |  | TE?: N | 05000339 North Anna 2 |  | 71152 | A Green self revealing finding was identified for the failure to properly provide oversight over supplemental (vendor) personnel during the replacement of the Unit 2 turbine and exciter rotors during the spring of 2010 in accordance with Dominion procedur
Region: II | North Anna | 28995 | 09/30/2013 10/30/2013 | 2013004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to establish and implement adequate preventative maintenance causes a reactor trip |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000339 North Anna 2 |  | 71152 | A Green self-revealing finding was identified for failure to establish and implement adequate preventative maintenance for the mechanism operated cell (MOC) switches. Specifically the licensee failed to recognize and recommend proper maintenance for these
Region: II | North Anna | 28990 | 03/31/2013 05/07/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Opposite Unit's Service Water Pumps Were Free of Fire Damage for a Postulated Fire in Either Unit's ESWGR |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | An NRC-identified non-cited violation was identified for the licensee's failure to meet the requirements of North Anna Power Station (NAPS) Renewed Operating License Conditions 2.D, and the approved Fire Protection Program for Units 1 and 2. Specifically,
Region: II | North Anna | 28991 | 03/28/2013 05/09/2013 | 2013007-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Vendor Recommendations Causes an Automatic Reactor Trip |  |  | TE?: N | 05000339 North Anna 2 |  | 71152B | A self-revealing finding was identified for failure to establish and implement appropriate periodic preventive maintenance for replacement frequency of the C4 capacitor on the Speed Error Amplifier card B (1A08D) in accordance with VPAP-803, Preventive Ma
Region: II | North Anna | 28987 | 12/14/2012 01/23/2013 | 2012012-02 | NRC | NCV | Mitigating Systems | Green | Emergency Lighting Not Installed as Required by 10 CFR 50 Appendix R Section III.J |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05T | An NRC identified non-cited violation of 10 CFR 50, Appendix R, Section III.J, and the North Anna Power Station (NAPS) approved Fire Protection Program, was identified for the licensee's failure to install fixed emergency lighting units (ELUs) in all area
Region: II | North Anna | 28983 | 09/30/2012 11/05/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Involving Inadequate Tornado MissileProtection for a Pipe Penetration in the SWP |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.01 | The inspectors identified a non-cited violation of 10CFR 50, Appendix B, Criterion XVI, "Corrective Action", for the failure to promptly identify and correct a condition adverse to quality associated with inadequate tornado missile protection for a vent l
Region: II | North Anna | 28984 | 09/30/2012 11/05/2012 | 2012004-02 | NRC | FIN | Emergency Preparedness | Green | Challenges to Personnel Accountability Following Declared Alert |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152 | The inspectors identified a self-revealing Green finding for the licensee's failure to follow posted manual personnel accountability instructions, which resulted in delays in completing the accounting process. Specifically, the licensee failed to perform
Region: II | North Anna | 27336 | 08/01/2012 09/25/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop an Adequate Procedure toTest the Quench Spray and Outside Recirculation Spray Pump Discharge Check Valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" for the licensee's failure to develop an adequate test procedure which demonstrated that the quench spray and outside recirculatio
Region: II | North Anna | 28976 | 08/01/2012 09/25/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure To Implement Design Control Measures For The Service Water Air System |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to implement design control measures involving two examples. In the first example, the licensee failed to translate the
Region: II | North Anna | 28977 | 08/01/2012 09/25/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of the SW Air System |  |  | TE?: N | 05000338 North Anna 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to test the Service Water (SW) air subsystem capability to perform its design bases function. Specifically, the licensee w
Region: II | North Anna | 28978 | 08/01/2012 09/25/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Measures for Thermal Overload Relays |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of thermal overload relay settings for motor operated valves and continuous duty motors. The lic
Region: II | North Anna | 28981 | 08/01/2012 09/25/2012 | 2012007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures and Procedure Compliance For Thermal Overload Relay Testing |  | H.4(b) Procedural Compliance | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving two examples. In the first example, the licensee failed to ensure that appropriate acceptance criteria was included i
Region: II | North Anna | 27334 | 06/30/2012 07/31/2012 | 2012003-01 | NRC | NCV | Barrier Integrity | Green | Failure to identify PWSCC in the Unit 1 B SG hot leg safe-end weld |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000338 North Anna 1 |  | 71111.08P | A self revealing non-cited violation (NCV) of the required augmented ISI examinations identified in 10 CFR 50.55a(g)(6)(ii)(F), Examination requirements for Class 1 piping and nozzle dissimilar metal butt welds, which implements ASME Code Case N-770-01, t
Region: II | North Anna | 27333 | 05/04/2012 05/10/2012 | 2012002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Provide Required Power for the Seismic Instrumentation Annunciators |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71153 | An NRC-identified, Green, finding (FIN) was identified by the inspectors for the licensee's failure to provide continuous standby power and sufficient power for a minimum 25 minutes of system operation for seismic instruments as required by a licensee sel
Region: II | North Anna | 27329 | 12/31/2011 02/13/2012 | 2011005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure to Ensure Proper Calibration of RHR Valve Control Circuit |  | H.4(a) Human Error Prevention | TE?: N | 05000339 North Anna 2 |  | 71111.22 | A self-revealing Green NCV of Technical Specification 5.4.1.a was identified for the licensee's failure to implement procedures as required by Regulatory Guide 1.33, Appendix A, Section 8, Procedures for Control of Measuring and Test equipment and for Sur
Region: II | North Anna | 27325 | 09/30/2011 11/09/2011 | 2011004-01 | NRC | FIN | Initiating Events | Green | Failure to Take Adequate Corrective Action to Preclude a Fire in the Units 1 and 2 Control Room Complex |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | A self-revealing finding was identified for the failure to take adequate corrective action for degradation of annunciator card resistors in accordance with the standards as established by the licensee's corrective action program procedure which resulted i
Region: II | North Anna | 27296 | 06/30/2011 07/28/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Fire Loads in a Safety-Related Area |  | H.4(b) Procedural Compliance | TE?: N | 05000338 North Anna 1 |  | 71111.05Q | The inspectors identified a non-cited violation of the North Anna Power Station, Unit 1 Renewed Facility Operating License, NPF-4, Condition 2.D, Fire Protection, which involved a failure to comply with transient fire load procedure requirements that resu
Region: II | North Anna | 27297 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fire Doors in Accordance with the Fire Protection Program |  | H.2(d) Facilities & Equipment | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | The inspectors identified a non-cited violation of the North Anna Power Station, Units 1 & 2 Renewed Facility Operating Licenses, NPF-4 & 7, Condition 2.D, Fire Protection, which involved a failure to comply with the requirements for maintaining the opera
Region: II | North Anna | 27302 | 06/30/2011 07/28/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications for Alignment of the Refueling Water Storage Tank to the Non-Seismic Refueling Purification System |  |  | TE?: N | 05000338 North Anna 1 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification (TS) 3.5.4, "Refueling Water Storage Tank (RWST)," for the failure to comply with the Limiting Conditions for Operation (LCO), while the Units 1 and 2 RWSTs were aligned to the non
Region: II | North Anna | 27303 | 06/30/2011 07/28/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Cause Evaluation of Scaffolding Affecting Unit 1 'A' Charging Pump |  | H.4(b) Procedural Compliance | TE?: N | 05000338 North Anna 1 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the failure to identify a condition adverse to quality involving noncompliance with a licensee procedure during an apparent cause evaluation (A
Region: II | North Anna | 27304 | 06/30/2011 07/28/2011 | 2011003-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Take Adequate Corrective Action to Preclude a Fire in the Units 1 and 2 Control Room Complex |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71153 | A self-revealing finding was identified for the failure to take adequate corrective action for degradation of annunciator card resistors in accordance with the standards as established by the licensee's corrective action program procedure which resulted i
Region: II | North Anna | 27309 | 06/30/2011 07/28/2011 | 2011003-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Qualification Testing of Fire Barrier Penetration Seals |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.18 | The inspectors identified a non-cited violation of North Anna Power Station, Units 1 & 2 Renewed Facility Operating Licenses, NPF-4 & 7, Condition 2.D, Fire Protection, for failure to maintain in effect all provisions of their NRC-approved fire protection
Region: II | North Anna | 27290 | 03/31/2011 05/02/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Installation of Unit 2 Low Head Safety Injection Piping and Related Supports |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.15 | A non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the NRC for the failure to accomplish the installation of Unit 2 low head safety injection (LHSI) piping and supports in accordance wit
Region: II | North Anna | 27291 | 03/31/2011 05/02/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Test Program Instructions for Safety-Related Instrument and Control Preventative Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.19 | A Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the NRC for failure to adequately prescribe the correct program instructions to ensure safety-related instrument and control (I
Region: II | North Anna | 27295 | 03/31/2011 05/02/2011 | 2011002-03 | NRC | NCV | Initiating Events | Green | Failure to Determine the Cause and Take Corrective Action to Preclude Repetition for Lightning Induced Reactor Trips |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000339 North Anna 2 |  | 71153 | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure to determine the cause of a significant condition adverse to quality (SCAQ) involving an automatic reactor trip
Region: II | North Anna | 27283 | 12/31/2010 01/28/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Fatigued Fuse Clips in Safety-Related Breakers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152 | A Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the NRC for failure to promptly identify and correct a condition adverse to quality regarding fatigued fuse clips associated with safety-related b
Region: II | North Anna | 27284 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Measures for Field Changes Affecting Station Battery Cables |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to ensure that design control measures for field changes impacting the support of station battery cables were commensurate with t
Region: II | North Anna | 27285 | 12/31/2010 01/28/2011 | 2010005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Correct Conditions Adverse to Quality for Valve Actuator Diaphragms |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000338 North Anna 1 |  | 71153 | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for two examples of the failure to promptly identify and correct a condition adverse to quality present in the actuator diaphragms of 1
Region: II | North Anna | 27289 | 12/31/2010 01/28/2011 | 2010005-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Maintain PM Procedures for Circuit Breakers Current with Industry Information and OE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71153 | A Green, self-revealing finding was identified for the failure to maintain a preventative maintenance (PM) procedure for circuit breakers current with industry information and operating experience (OE), as required by procedure, DNAP-2001, "Equipment Reli
Region: II | North Anna | 27260 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate procedurally controlled temporary modification for the emergency diesel generator starting air system |  |  | TE?: N | 05000338 North Anna 1 |  | 71111.18 | A non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure that design control measures for a field change performed on the Unit 1, '1J' emergency diesel generator (EDG) star
Region: II | North Anna | 27267 | 09/30/2010 10/29/2010 | 2010004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to conduct adequate review of calculation results in main turbine/reactor trip |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000339 North Anna 2 |  | NONE | A self-revealing finding was identified for the licensee's failure to conduct an adequate review of calculations for the operation of the Unit 2 main generator automatic voltage regulator (AVR), as required by licensee procedure CM-AA-CLC-301, "Engineerin
Region: II | North Anna | 27268 | 09/30/2010 10/29/2010 | 2010004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correctly translate turbine driven auxiliary feedwater pump lube oil subsystem vent design basis into specifications or drawings |  |  | TE?: N | 05000339 North Anna 2 |  | NONE | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the failure to correctly translate the design basis of the Unit 2 turbine driven auxiliary feedwater pump (TDAFWP) lube oil subsystem vent i
Region: II | North Anna | 27269 | 09/30/2010 10/29/2010 | 2010004-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate set point for balbance-of-plant bus undervoltage relay |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | NONE | A self-revealing finding was identified for the failure to establish an adequate set point for a balance-of-plant 4160 V bus undervoltage protection relay. The inadequate set point caused a reactor trip upon automatic start of a steam generator feedwater
Region: II | North Anna | 27273 | 09/30/2010 10/29/2010 | 2010004-06 | NRC | NCV | Initiating Events | Green | Failure to follow procedure to trip "A" reactor coolant pump on high bearing temperature |  | H.1(c) Communication of Decisions | TE?: N | 05000339 North Anna 2 |  | NONE | A non-cited violation of Technical Specifications 5.4.1a was identified by the inspectors for the failure to adequately implement procedural requirements which resulted in operation of the 'A' reactor coolant system (RCS) pump (RCP) beyond the motor high
Region: II | North Anna | 27251 | 06/30/2010 07/29/2010 | 2010003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Demonstrate Effective Control of a Pressurizer PORV 1-RC-PCV-1455C Performance in Accordance with the Maintenance Rule |  | H.4(a) Human Error Prevention | TE?: N | 05000338 North Anna 1 |  | 71111.12 | Green: A non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Plants," was identified by the inspectors for the failure to demonstrate that the performance of a Unit 1 pressurizer power operated rel
Region: II | North Anna | 27252 | 06/30/2010 07/29/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality For 2-RH-MOV-2700 Breaker |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000339 North Anna 2 |  | NONE | Green: A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to promptly identify and correct a condition adverse to quality for the breaker associated with 2-RH-MOV-2700, Loop 'A
Region: II | North Anna | 27240 | 03/31/2010 05/07/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Implementation Results in Inoperability of a Fire Suppression System |  | H.4(a) Human Error Prevention | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | A self-revealing, non-cited violation of Technical Specifications 5.4.1d was identified for the failure to adequately implement procedural requirements to reset a high pressure carbon dioxide (CO2) fire suppression system for the EDG pump room #1. The lic
Region: II | North Anna | 27246 | 03/31/2010 05/07/2010 | 2010002-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedures Results in Loss of Offsite Power to 1H and 2J Emergency Buses |  | H.4(a) Human Error Prevention | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71153 | A Green, self-revealing finding was identified for the licensee's failure to follow or adhere to licensee procedures for switchyard relay maintenance, human performance and management oversight, which resulted in the loss of the Technical Specifications (
Region: II | North Anna | 27247 | 03/31/2010 05/07/2010 | 2010002-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Establish a Procedure for Undervoltage Timers Results in Main Turbine/Reactor Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000339 North Anna 2 |  | 71153 | A Green, self-revealing finding was identified for the licensee's failure to establish an adequate procedure for calibration of under voltage timers which resulted in the failure of the Unit 2 'G' bus to fast transfer from 'C' reserve station service tran
Region: II | North Anna | 27248 | 03/31/2010 05/07/2010 | 2010002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Install LSHI/ORS Pump Discharge Piping in accordance with Prescribed Drawings |  |  | TE?: N | 05000338 North Anna 1 |  | 71153 | A non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the NRC for the failure to accomplish the installation of low head safety injection (LHSI) and outside recirculation spray (ORS) pump d
Region: II | North Anna | 27250 | 03/31/2010 05/07/2010 | 2010002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Adequate Post-Modification Test Program for Piping Supports |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71153 | A Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the NRC for the failure to establish an adequate postmodification test program for piping supports affected by piping design changes (modifications).
Region: II | North Anna | 27232 | 01/25/2010 03/11/2010 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Periodic TOL Testing on Unit 1 |  |  | TE?: N | 05000338 North Anna 1 |  | 7111121 | Green: The team identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to assure that thermal overload protection devices (TOLs) on safety-rel
Region: II | North Anna | 27233 | 01/25/2010 03/11/2010 | 2009007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure RSST 'A' LTC Controller Settings Were Correctly Implemented |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | Green: The inspectors identified a finding having very low safety significance (Green) involving the failure of the licensee to ensure that the control settings for the non-safety related reserve station service transformer (RSST) 'A' replacement load tap
Region: II | North Anna | 27239 | 01/25/2010 03/11/2010 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Adequacy of Control Voltage to the 4160 and 480 VAC Equipment |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 7111121 | Green: The team identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the adequacy of control voltage to the 4160 and 480 VAC equipment in support
Region: II | North Anna | 27231 | 12/31/2009 01/28/2010 | 2009005-05 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Results in Excess Letdown Heat Exchanger Leakage |  |  | TE?: N | 05000338 North Anna 1 |  | 71153 | A Green, self-revealing, non-cited violation of TS 5.4.1a was identified for the failure to adequately establish procedural requirements for component cooling (CC) water flow through the Unit 1 excess letdown heat exchanger (Hx) which resulted in a cracke
Region: II | North Anna | 27219 | 11/12/2009 12/24/2009 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Address the Potential for CO2 Over-pressurization within the Unit 2 Cable Vault & Tunnel |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of North Anna Nuclear Station Operating License Condition 2. (D), "Fire Protection," in that the licensee failed to adequately address the potential for carbon dioxide (CO2) over-pressurization w
Region: II | North Anna | 27220 | 11/12/2009 12/24/2009 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Powering Credited Components for Fire in Cable Vault & Tunnel. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of Technical Specification 5.4.1, Procedures, in that the Unit 1 post-fire safe shutdown (SSD) procedure 1-FCA-3, "Cable Vault and Tunnel Fire", Revision 20, was not consistent with the safe shut
Region: II | North Anna | 27221 | 11/12/2009 12/24/2009 | 2009008-04 | NRC | URI | Mitigating Systems | Green | Potential for CO2 Over-pressurization of Unit 2 Cable Vault & Tunnel |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.05T | Contrary to the above, the licensee failed to adequately address the potential for CO2 over-pressurization within the Unit 2 CV&T (FA 3-2) consistent with the original CO2 system design. The violation applied to Unit 2 only, and has existed since initial
Region: II | North Anna | 27207 | 10/15/2009 10/30/2009 | 2009004-03 | NRC | FIN | Mitigating Systems | Green | Degradation of a Flood Protection Feature |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.15 | A finding was identified by the NRC for the licensee's failure to maintain the functionality of an internal flood protection feature which was installed to reduce core damage frequency based on evaluations performed for the plant. The licensee entered thi
Region: II | North Anna | 27209 | 10/15/2009 10/30/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Preconditioning of the Low Head Safety Injection Motor Operated Valves |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000338 North Anna 1 |  | 71111.22 | A NRC-identified non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified for preconditioning of low head safety injection (LHSI) motor operated valves (MOVs). A preventative maintenance (PM) work order specified tha
Region: II | North Anna | 27210 | 10/15/2009 10/30/2009 | 2009004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Design and Install Oil Collection Devices for Reactor Coolant Pump Motor Stator Air Coolers |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152 | The inspectors identified a non-cited violation of the North Anna Power Plant Facility Renewed Operating Licensee NPF-4 & 7, Condition D, Fire Protection Program, which involved a failure to ensure an adequate design of the Units 1 and 2 reactor coolant p
Region: II | North Anna | 27211 | 10/15/2009 10/30/2009 | 2009004-07 | Self - Revealed | FIN | Initiating Events | Green | Failure to Determine Cause and Related Corrective Action Results in Loss of a Required Offsite Power Supply |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000339 North Anna 2 |  | 71152 | A self-revealing finding was identified for the licensee's failure to comply with the standards established in their corrective action program (CAP) to determine the correct cause and take corrective action to preclude repetition (CAPR) which resulted in
Region: II | North Anna | 27199 | 06/30/2009 07/27/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Repair or Rework Nonconforming Parts in Accordance with Documented Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000338 North Anna 1 |  | 71111.2 | A self-revealing, Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XV, Nonconforming Materials, Parts, or Components was identified for failure to repair or rework nonconforming parts in accordance with documented procedures which resulted i
Region: II | North Anna | 27204 | 06/30/2009 07/27/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Involving Inadequate Tornado Missle Protection for the EDG Day Tank Vents |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152 | A Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the NRC for failure to promptly identify and correct a condition adverse to quality associated with inadequate tornado missile protection for the
Region: II | North Anna | 27197 | 03/31/2009 04/29/2009 | 2009002-02 | NRC | NCV | Initiating Events | Green | Failure to Accomplish Procedures Renders Both Trains of High Head Safety Injection System Inoperable |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000339 North Anna 2 |  | 71153 | A Green NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the NRC for multiple examples of a failure to accomplish a procedure for activities affecting quality which simultaneously rendered both trains
Region: II | North Anna | 27193 | 12/31/2008 01/28/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Reactor Coolant Pump Motor Oil Collection System Installation and Design Problems |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05Q | The finding was more than minor because it impacted the mitigating systems cornerstone objective to ensure the availability, reliability, and capability of systems that respond to initiating events to prevent undesirable consequences, and the related attr
Region: II | North Anna | 27191 | 06/30/2008 08/25/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Establish Procedural Requirements for Air Start Check Valve Maintenance for the '1H' EDG |  |  | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A Green self-revealing non-cited violation of Technical Specification (TS) 5.4.1.a was identified for failure to adequately establish procedural requirements for repair of the Unit 1 '1H' emergency diesel generator (EDG) air start check valves. The licens
Region: II | North Anna | 27183 | 03/30/2008 04/30/2008 | 2008002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperability of 1H EDG Due to Failure to Adequately Establish Procedural Requirements for Protective Relay Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A self-revealing, non-cited violation of Technical Specification (TS) 5.4.1a was identified for a failure to adequately establish procedure requirements for protective relay testing which resulted in the inoperability of the '1H' emergency diesel generato
Region: II | North Anna | 27189 | 03/30/2008 04/30/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Involving Unit 2 Containment Sump Strainer Gaps |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000339 North Anna 2 |  | 71111.2 | A Green NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for inadequate design control measures to assure that the measurement technique used to verify the gaps between Unit 2 containment sump stra
Region: II | North Anna | 27190 | 03/30/2008 04/30/2008 | 2008002-05 | NRC | NCV | Mitigating Systems | Green | Spurious Turbine Driven Auxiliary Feedwater Pump Trip Due to Failure to Adequately Implement Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000339 North Anna 2 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.4.1a for a failure to adequately implement maintenance procedure requirements for the turbine driven auxiliary feedwater pump (TDAFWP) which, consequently, led to a spurious trip
Region: II | North Anna | 27181 | 01/30/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Install an Oil Collection System on a Reactor Coolant Pump Motor |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000339 North Anna 2 |  | 71111.05Q | The inspectors identified a non-cited violation of the North Anna Power Plant Facility Renewed Operating Licensee NPF-7, Condition D, Fire Protection Program, which involved a failure to adequately install a section of the oil collection system on the Uni
Region: II | North Anna | 27180 | 12/31/2007 01/31/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Procedure for Installation of Containment Sump Modification |  | H.4(b) Procedural Compliance | TE?: N | 05000338 North Anna 1 |  | 71111.2 | A Green, non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion V, was identified by the NRC for failure to adequately accomplish a procedure for installation of the Unit 1 containment sump strainer modification. On Oct
Region: II | North Anna | 27172 | 09/30/2007 10/30/2007 | 2007004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for SW System Inspection and Maintenance which Resulted in Reduced SW Flow to the Unit 2 RS Hx |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000339 North Anna 2 |  | 71111.07A | A Green non-cited, self-revealing violation (NCV) of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the failure to have an adequate procedure to ensure that the recirculation spray heat exchanger service wat
Region: II | North Anna | 27173 | 09/30/2007 10/30/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required ASME Code Section XI Leakage Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4) associated with failure to perform testing of buried, isolable piping for the charging, safety injection, recirculation spray, quench spray, auxiliary feedwater, and service water syst
Region: II | North Anna | 27171 | 08/31/2007 10/12/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Control and Storage of Safety-Related EDG Parts |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152B | A non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XIII, Handling, Storage and Shipping, was identified by the NRC. Specifically, the licensee failed to ensure adequate controls for the storage and preservation of safety-related material and
Region: II | North Anna | 27166 | 06/30/2007 07/31/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures Result in Failure of a Backflow Preventer for Internal Flood Protection |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000338 North Anna 1 |  | 71111.19 | Inadequate Procedures Result in Failure of a Backflow Preventer for Internal Flood Protection A Green, non-cited violation of Technical Specification 5.4.1.a was identified by the NRC for failure to establish adequate post maintenance test procedures f
Region: II | North Anna | 27167 | 06/30/2007 07/31/2007 | 2007003-02 | NRC | NCV | Initiating Events | Green | Failure to Secure the Unit 2 Safety Related Pressurizer Heater Cabinet Doors as Required by Procedure VPAP-0312 |  | H.4(b) Procedural Compliance | TE?: N | 05000339 North Anna 2 |  | NONE | Failure to Secure the Unit 2 Safety Related Pressurizer Heater Cabinet Doors as Required by Procedure VPAP-0312 A Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V was identified by the NRC for failure to properly accomplish a procedure
Region: II | North Anna | 27160 | 03/31/2007 04/26/2007 | 2007002-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Implementation of a Non-quality Procedure Results in Reactor Trips |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.12 | A self-revealing finding was identified for inadequate implementation of a non-quality procedure associated with the equipment reliability process. This led to a 'run-to-failure' classification for two different 7300 System cards which each resulted in a
Region: II | North Anna | 27165 | 03/31/2007 04/26/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulting in the Inoperability of 2J Emergency Diesel Generator |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.22 | A self-revealing non-cited violation of Technical Specification (TS) 5.4.1.a was identified for a failure to adequately implement a surveillance procedure which resulted in the inoperability of the 2J Emergency Diesel Generator (EDG). The licensee restore
Region: II | North Anna | 27155 | 12/31/2006 01/29/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Unsatisfactory Performance of a Fire Brigade Crew |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.05A | The inspectors identified a Green, non-cited violation of the Fire Protection Program because the licensee's assessment of a fire brigade drill was inadequate. Fire brigade performance was not accurately critiqued to identify deficiencies requiring correc
Region: II | North Anna | 27156 | 12/31/2006 01/29/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Failure of Control Room Chiller |  |  | TE?: N | 05000338 North Anna 1 |  | 71111.12 | A Green, self-revealing, non-cited violation of Technical Specification 5.4.1.a was identified for inadequate maintenance work which resulted in the failure of a control room chiller on October 12, 2006. The licensee initiated action to evaluate the probl
Region: II | North Anna | 27157 | 12/31/2006 01/29/2007 | 2006005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Corrective Action to Upgrade Breaker Operating Mechanism |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.22 | A Green, self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI was identified as a result of inadequate corrective action to upgrade the operating mechanism for a Unit 2 Quench Spray pump breaker. The licensee initiated corrective act
Region: II | North Anna | 27154 | 09/30/2006 10/30/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Tornado Missile Protection for the AFW System |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.01 | A non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III was identified by the NRC on July 10, 2006, for the failure to adequately protect auxiliary feedwater (AFW) components from tornado generated missiles. The licensee installed a modificati
Region: II | North Anna | 27152 | 06/30/2006 07/28/2006 | 2006003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Action Results in Failure of Control Room Chiller to Start |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.12 | A self-revealing non-cited violation of 10 CFR 50 Appendix B Criterion XVI was identified for inadequate corrective action which resulted in an inoperable control room chiller. On May 16, 2006, the chiller failed to start due to a faulty chilled water flo
Region: II | North Anna | 27153 | 06/30/2006 07/28/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Maintenance Procedure Impacting Pressurizer PORV Operability |  |  | TE?: N | 05000338 North Anna 1 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification (TS) 5.4.1a associated with the licensee's failure to correctly implement a maintenance procedure which resulted in a failure of a Unit 1 pressurizer power operated relief valve (P
Region: II | North Anna | 27147 | 06/30/2006 07/28/2006 | 2006003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Regarding High Cycle Fatigue Failure of the 2J EDG Lube Oil Filter Vent Line |  |  | TE?: N | 05000339 North Anna 2 |  | 71152 | A self-revealing non-cited violation of 10 CFR 50 Appendix B Criterion XVI was identified for the licensee's failure to properly identify and evaluate the extent of condition involving high cycle fatigue of components associated with Emergency Diesel Gene
Region: II | North Anna | 27146 | 03/31/2006 04/26/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to translate TS operable-operability definition regarding hazard barriers into instructions as required by 10 CFR 50 Appendix B Criterion III |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.13 | An NRC-identified non-cited violation of 10 CFR 50 Appendix B Criterion III was identified for failure to translate design requirements into procedures. Specifically, the licensee failed to properly translate the Technical Specification (TS) "Operable-Ope
Region: II | North Anna | 27149 | 03/31/2006 04/26/2006 | 2006002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Design Control Results in Safeguards Instrument Rack Room Flood Problem |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71111.06 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion III was identified for inadequate design control resulting in a flood potential for the Units 1 and 2 safeguards instrument rack rooms. On July 9, 2005, back flush of control room ch
Region: II | North Anna | 27150 | 02/10/2006 03/24/2006 | 2005008-01 | NRC | NCV | Mitigating Systems | Green | Carbon Dioxide System for Unit 2 Cable Vault and Tunnel Area Has Degraded Manual Mode |  |  | TE?: N | 05000339 North Anna 2 |  | 71111.05T | NRC inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.48, Fire Protection, for a degraded carbon dioxide suppression system in the Unit 2 cable vault and tunnel fire area. The system was degraded in that the manual mode of operation wou
Region: II | North Anna | 126184 | 12/16/2019 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation |  |  | TE?: N | 05000338 North Anna 1 05000339 North Anna 2 |  | 71152B
Region: II | Oconee | 125909 | 12/31/2019 02/13/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of Reactor Building Cooling Units |  | H.6 - Design Margins | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 | Human Performance | 71111.18 | Inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to verify the adequacy of design of the reactor building cooling units (RBCUs). Specifically, safety analysis engin
Region: II | Oconee | 125635 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Control of Heavy Load in Spent Fuel Pool |  | H.4 - Teamwork | TE?: N | 05000287 Oconee 3 | Procedure Quality | 71111.13 | Inspectors identified a Green finding and associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1, “Procedures,” when the licensee failed to properly pre-plan and control a heavy load lift in the Unit 3 spent fuel pool.
Region: II | Oconee | 125401 | 06/30/2019 08/14/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of Design of LPSW System for Auxiliary Building Flooding |  | NPP | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 | Design Control | 71111.06 | Inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to verify the adequacy of design of the LPSW system. Specifically, design review calculation OSC-8671, “Auxiliary Building Flood Des
Region: II | Oconee | 125400 | 06/30/2019 08/14/2019 | 2019002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor or Demonstrate Control of Performance Under the Maintenance Rule |  | H.1 - Resources | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 | Equipment Performance | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(a)(2) when the licensee failed to monitor the performance or demonstrate effective control of performance of the standby shutdown facility.
Region: II | Oconee | 125359 | 06/07/2019 07/19/2019 | 2019012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide a Water Flow Alarm for a Fixed Suppression System as required by NFPA 805 |  | NPP | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 | Protection Against External Factors | 71111.05XT | The NRC team identified a finding and associated non-cited violation (NCV) of very low significance (Green), for the licensee’s failure to provide a water flow alarm for a fixed suppression system, in accordance with NFPA 805, Sections 3.9.2 and 3.9.3.
Region: II | Oconee | 125512 | 05/03/2019 08/14/2019 | 2019010-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Reinstalling Reactor Coolant Makeup Pump Oil Suction Tubing |  | NPP | TE?: N | 05000269 Oconee 1 | Procedure Quality | 71152B | The inspectors identified an AV of TS 5.4.1, "Procedures," when the licensee failed to provide procedures, instructions, or drawings regarding reinstallation of the RCM pump suction tubing that were appropriate to the circumstances. The AV is pending an i
Region: II | Oconee | 38863 | 10/19/2018 02/13/2019 | 2018004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Administrative Procedures During Transient Conditions. |  | H.14 - Conservative Bias | TE?: N | 05000269 Oconee 1 |  | 71153 | A self-revealed Green finding and associated NCV was identified of Technical Specification (TS) 5.4.1, “Procedures” with two examples. The licensee failed to properly implement the variance process per AD-OP-ALL-1001, “Conduct of Abnormal Operations,” and
Region: II | Oconee | 25878 | 10/05/2018 11/16/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Use of Combined Qualification for Rotork Motor Operated Valve Actuator |  | NPP | TE?: N | 05000269 Oconee 1 |  | 71111.21N | The inspectors identified a Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) 50.49(e)(5), for the licensee's failure to appropriately include the effects of thermal aging in the qualification o
Region: II | Oconee | 25879 | 10/05/2018 11/16/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Impact to Required Design Functions for Viking Penetrations Following Changes to East Penetration Room Environmental Parameters |  | NPP | TE?: N | 05000269 Oconee 1 |  | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of Criterion III of Appendix B of Title 10 of the Code of Federal Regulations, Part 50, for the licensee's failure to establish measures for the selection and review for su
Region: II | Oconee | 24340 | 06/30/2018 07/27/2018 | 2018002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform ISI General Visual Examinations of Containment Moisture Barrier Associated with Containment Liner Leak Chase Test Connection Piping |  | P.5 - Operating Experience | TE?: N | 05000287 Oconee 3 |  | 71111.08P | The inspectors identified a Green NCV of 10 CFR Part 50.55a, “Codes and Standards,” involving the licensee’s failure to properly apply Subsection IWE, of ASME Section XI, for conducting general visual examinations of the leak chase test connection piping
Region: II | Oconee | 24119 | 05/04/2018 07/27/2018 | 2018002-02 | NRC | NCVIV | Public Radiation Safety | Green | Failure to Coordinate a No-later-than Arrival Time for the Shipment of a Category 2 Quantity of Radioactive Material |  |  | TE?: Y SL-IV-NCVIV | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71124.08 | The inspectors identified a Severity Level IV Non-cited Violation (NCV) of 10 CFR 37.75(b) when the licensee failed to coordinate a no-later-than arrival time for a Category 2 shipment of radioactive material. Specifically, the licensee failed to recogniz
Region: II | Oconee | 23959 | 03/27/2018 03/27/2018 | 2018013-01 | NRC | NCV | Initiating Events | Green | Failure to Translate Design and Licensing Basis Requirements and Verify Adequate Design | EA Case: EA-18-036 | NPP | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.21M | The NRC identified an apparent violation (AV) of Title 10 of the Code of Federal Regulations part 50, Appendix B, Criterion III, for the licensee's failure to adequately translate applicable regulatory requirements and design basis into specifications, pr
Region: II | Oconee | 23960 | 03/27/2018 03/27/2018 | 2018013-02 | NRC | NCV | Initiating Events | Green | Failure to Submit for License Review and Obtain a License Amendment for a Modification | EA Case: EA-18-036 | NPP | TE?: Y SL-IV-NCV | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.21M | The team identified an AV of Title 10 of the Code of Federal Regulations part 50.59(c)(2), "Changes, tests, and Experiments," for the failure to submit a plant modification for license review and obtain a license amendment for a change that resulted in mo
Region: II | Oconee | 23190 | 12/31/2017 01/30/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to identify sensitive equipment during modification results in loss of safety function. |  | H.5 - Work Management | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71153 | A self-revealing Green non-cited violation (NCV) of Oconee Nuclear Station Technical Specification (TS), Section 5.4, “Procedures,” was identified for the licensee’s failure to identify sensitive equipment in a work area that warranted implementation of c
Region: II | Oconee | 23191 | 12/31/2017 01/30/2018 | 2017004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to properly risk screen work within 2 feet of a single point vulnerability component. |  | H.5 - Work Management | TE?: N | 05000287 Oconee 3 |  | 71153 | A self-revealing Green NCV of Oconee Nuclear Station Technical Specification (TS), Section 5.4, “Procedures,” was identified for the licensee’s failure to identify and properly risk screen work within 2 feet of a single point vulnerability (SPV) component
Region: II | Oconee | 36616 | 03/31/2017 05/09/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to comply with 10 CFR 55.49. |  | H.1 Resources | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.11B | A green NRC-identified non-cited violation (NCV) of 10 CFR 55.49, "Integrity of Examinations and Tests," was identified because the licensee engaged in an activity that compromised the integrity of examinations. Specifically, the licensee failed to ensure
Region: II | Oconee | 36617 | 03/24/2017 05/04/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct a broken cable trench cover. |  | H.13 Consistent Process | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to assure that a condition adverse to quality associated with a damaged tren
Region: II | Oconee | 36611 | 12/31/2016 02/03/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Appropriate Evaluation of Motor Operated Valve Actuator Output Capability |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.15 | -Green. The NRC identified a non-cited violation (NCV) of Title 10 Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly determine the bounding degraded voltage to be assumed in the d
Region: II | Oconee | 36615 | 12/31/2016 02/03/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Inappropriate Voltage Band in Lee Combustion Turbine Unit Operating Procedure |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.15 | -Green. The NRC identified a NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to identify appropriate procedural updates that were needed to ensure the Lee combustion turbine (LCT) procedures
Region: II | Oconee | 36610 | 09/30/2016 11/09/2016 | 2016003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Translate Design Requirements to Prevent the Effects of Waterhammer |  | H.6 Design Margins | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.17T | Green. The NRC identified a finding for the licensee's failure to translate the limiting flow rate design requirement into station procedures used to start and operate the alternate reactor building cooling (RBC) system, in accordance with the Duke Energy
Region: II | Oconee | 36602 | 06/30/2016 08/04/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | Failure to perform ISI general visual examinations of containment moisture barrier. |  |  | TE?: N | 05000287 Oconee 3 |  | 71111.08P | Green: An NRC-identified Green NCV of 10 CFR Part 50.55a, "Codes and Standards," was identified for the licensee's failure to conduct 100 percent general visual examinations of the moisture barriers to the containment liner in accordance with Subsection I
Region: II | Oconee | 36603 | 06/30/2016 08/04/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to properly control transient combustible materials in the Oconee Main Control Rooms. |  | H.8 Procedure Adherence | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | Green: An NRC-identified Green non-cited violation (NCV) of Oconee Nuclear Station Units 1, 2, and 3 Renewed Facility Operating License Condition 3.D, "Fire Protection," was identified for the licensee's failure to adequately implement the requirements of
Region: II | Oconee | 36604 | 06/30/2016 08/04/2016 | 2016002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Degraded power cables result in inoperable startup transformer and loss of Unit 3 safety function. |  | P.2 Evaluation | TE?: N | 05000287 Oconee 3 |  | 71153 | A self-revealing Green violation of Oconee Technical Specification 5.4, "Procedures," was identified for the licensee's failure to establish written procedures. Station procedure IP/0/A/2400/002, "Substation Insulators, Lighting Arrestors, CCVT, Transform
Region: II | Oconee | 36601 | 03/18/2016 05/02/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Postulated Fire Affecting High Pressure Injection Pump Did Not Receive a VFDR Evaluation |  | H.13 Consistent Process | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05XT | Green. The NRC identified a Green NCV of 10 CFR 50.48(c) and National Fire Protection Association Standard (NFPA) 805, Section 2.4.2.4 for the licensee's failure to perform an adequate engineering analysis to determine the effects of fire on the ability t
Region: II | Oconee | 36589 | 12/31/2015 02/03/2016 | 2015004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Adequately Maintain Controlled Procedures in Emergency Response Facilities |  | H.7 Documentation | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71114.05 | -Green. The inspectors identified a Green NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50.47(b)(16), for the licensee's failure to maintain the effectiveness of its emergency plan by ensuring procedures for use by the emergency response
Region: II | Oconee | 36590 | 12/31/2015 02/03/2016 | 2015004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Accomplish Activities Affecting Quality in Accordance With Station Instructions and Procedures Which Resulted in a Valid AFIS Actuation |  | H.8 Procedure Adherence | TE?: N | 05000270 Oconee 2 |  | 71153 | - Green. A Green self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to accomplish activities affecting quality in accordance with instructions and p
Region: II | Oconee | 36583 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Design Inputs for PSW Testing and Engineering Evaluations |  | H.12 Avoid Complacency | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.17T | -Green. The NRC identified a finding for the licensee's failure to verify the adequacy of design inputs used in protected service water (PSW) testing and engineering evaluations to validate that the PSW system could perform its design function with respec
Region: II | Oconee | 36584 | 06/30/2015 08/05/2015 | 2015002-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Acceptance Criteria for PSW Pump Surveillance Testing |  | H.12 Avoid Complacency | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.17T | Green. The NRC identified a finding for the licensee's failure to ensure that appropriate acceptance criteria was used during testing to verify PSW primary pump functionality in accordance with the Duke Energy Carolinas Topical Report, Quality Assurance P
Region: II | Oconee | 36585 | 06/30/2015 08/05/2015 | 2015002-03 | NRC | FIN | Mitigating Systems | Green | Failure To Translate The Design Basis Into Procedures Used To Test The HPI Motor Coolers |  | H.4 Teamwork | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.17T | Green. The NRC identified a finding for the licensee's failure to translate the design requirements of the high pressure injection (HPI) pump motor coolers into the procedure used to verify adequate flow from PSW, in accordance with the Duke Energy Caroli
Region: II | Oconee | 36579 | 12/29/2014 02/03/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Keowee Hydro Unit 2 Inoperable for Longer Than Allowed TS Outage Time |  | P.3 Resolution | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71153 | -Green A self-revealing Green NCV of Oconee Nuclear Station Technical Specification (TS) 3.8.1, "AC Sources - Operating," was identified for Keowee Hydro Unit 2 being inoperable for longer than allowed TS outage time. The licensee modified Keowee Hydro Un
Region: II | Oconee | 36570 | 03/21/2014 06/27/2014 |  | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Under Voltage Relays at the Worst Case Minimum Drop Out Bus Voltage |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that at the worst-case voltage, protective devices and thermal overload relays for safety-related loads would n
Region: II | Oconee | 36571 | 03/21/2014 06/27/2014 |  | NRC | NCV | Mitigating Systems | Green | Failure to Correct Issues with DC System Voltage Calculations and 120Vac Motor Control Center (MCC) Control Circuit Calculations |  | P.3 Resolution | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | The team identified a Green non-cited violation (NCV), with two examples, of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct conditions adverse to quality. Specifically, the licensee (1) failed to correct v
Region: II | Oconee | 36567 | 12/31/2013 02/06/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to properly maintain a fire barrier penetration seal |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 |  | 71152 | An NRC-identified non-cited violation (NCV) of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 (NFPA 805), Section 3.11.4, was identified for the licensee's failure to comply with the fire barrier penetration sealing and inspection r
Region: II | Oconee | 36556 | 08/09/2013 09/23/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Modifications to fire doors did not receive engineering equivalency evaluations |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05T | Green. An NRC-identified Green non-cited violation (NCV) of Oconee Nuclear Station Units 1, 2, and 3 Renewed Facility Operating License Condition 3.D and NFPA 805 was identified for the licensee's modification of five fire doors from their tested configur
Region: II | Oconee | 36557 | 08/09/2013 09/23/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to identify ignition sources and target during initial fire scenario development |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000269 Oconee 1 |  | 71111.05T | An NRC-identified non-cited violation (NCV) of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 (NFPA 805), Section 2.4.3.2, was identified for the licensee's failure to address in their fire probabilistic safety analysis (also referr
Region: II | Oconee | 36564 | 08/09/2013 09/23/2013 | 2013007-03 | NRC | NCVIV | Mitigating Systems | Green | Fire protection program change did not meet Oconee license condition reuirements for NFPA 805 chapter three |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-IV-NCVIV | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05T | An NRC-identified Green finding and associated traditional enforcement Severity Level IV NCV of ONS Renewed Facility Operating License Condition 3.D for Units 1, 2, and 3 were identified for the licensee's failure to implement and maintain in effect all p
Region: II | Oconee | 36565 | 08/09/2013 09/23/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate unapproved combustibles in accordance with procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05T | An NRC-identified Green non-cited violation of Oconee Nuclear Station Units 1, 2, and 3 Renewed Facility Operating License Condition 3.D was identified for the licensee's failure to follow procedures for the control of transient combustible materials. The
Region: II | Oconee | 36553 | 03/31/2013 04/24/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Pressure Boundary in Unit-3 Control Battery Room |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000287 Oconee 3 |  | 71111.15 | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to take timely corrective actions for a condition adverse to quality. The licensee failed to take timely actions to
Region: II | Oconee | 36551 | 09/30/2012 10/31/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain accurate pre-fire plans |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05Q | An NRC-identified non-cited violation of the Oconee Units 1, 2, and 3 renewed facility operating licenses, condition 3.D. was identified for the licensee's failure to maintain accurate pre-fire plans in areas that contain safety related equipment. Discrep
Region: II | Oconee | 36542 | 06/30/2012 07/31/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform a calculation to determine site PMP ponding levels in a timely manner |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.01 | An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to implement corrective actions for a condition adverse to quality. The licensee did not develop a calculatio
Region: II | Oconee | 36550 | 06/30/2012 07/31/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to follow the engineering change process |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.01 | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified for the licensee's failure to follow EDM 601, Engineering Change Manual, during the design and construction of the Protected
Region: II | Oconee | 36538 | 03/31/2012 05/07/2012 | 2012002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Test Safety-Significant Medium Voltage Cables |  | P.2(b) Implementing Operating Experience | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.12 | An NRC-Identified finding was identified for the licensee's failure to develop an adequate procedure for performing cable degradation testing on medium voltage cables. Consequently, a degraded condition of one of the conductors from CT-5 to the standby bu
Region: II | Oconee | 36539 | 03/31/2012 05/07/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Installation of Safety-related Control Cables |  | H.3(a) Work Planning | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.17T | An NRC-Identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to develop adequate procedures governing the installation of safety related control cables
Region: II | Oconee | 36540 | 03/31/2012 05/07/2012 | 2012002-04 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure UFSAR described Flood Protection Measures In Place |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | An NRC-Identified finding was identified for the licensee's failure to ensure the Oconee UFSAR-described Auxiliary Building (AB) flood protection measures were maintained. Penetrations were not included in a surveillance program to verify below-grade pene
Region: II | Oconee | 36531 | 12/31/2011 01/13/2012 | 2011005-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Adequate Surveys to Identify Potential Radiological Hazards |  | H.3(b) Work Activity Coordination | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71124.01 | A Green self-revealing, non-cited violation (NCV) of 10 CFR 20.1501(a) was identified for failure to perform adequate surveys to verify radiological conditions within the Unit 3 Reactor Building (RB). This resulted in a worker unknowingly entering an area
Region: II | Oconee | 36532 | 12/16/2011 01/26/2012 | 2011008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Involving the Environmental Qualification of Limitorque Valve Actuators |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, requires in part, that measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, and non-conformances are promptly identified and corrected.
Region: II | Oconee | 36220 | 10/07/2011 10/04/2011 | 2011018-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Evaluation for the SSF |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | A NRC-identified NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified when the licensee failed to perform an adequate operability evaluation and failed to perform a 50.59 evaluation for a compensatory measure f
Region: II | Oconee | 36225 | 09/30/2011 10/28/2011 | 2011004-01 | NRC | NCV | Barrier Integrity | Green | Failure to promptly identify and correct an adverse condition affecing operability of letdown line containment isolation valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.15 | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to promptly identify and correct a condition adverse to quality. The licensee failed to identify and correct a degr
Region: II | Oconee | 36226 | 09/30/2011 10/28/2011 | 2011004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to verify adequate closure margin |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.18 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified when the licensee failed to follow their modification process. The licensee did not verify the valve actuator margin to be greater than the margin
Region: II | Oconee | 36227 | 09/30/2011 10/28/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to correctly process a UFSAR change |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.19 | An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified when the licensee failed to follow NSD 220, Updated Final Safety Analysis Report (UFSAR) Revision Process, and process
Region: II | Oconee | 36229 | 09/30/2011 11/14/2011 | 2011010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze the Pressurizer Safety valves and PORV and Downstream Piping at the correct Pressure |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to perform a pressurizer safety valve and pressurizer Power Operated Relief Valve (PORV) analysis that
Region: II | Oconee | 36230 | 09/30/2011 11/14/2011 | 2011010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations for Keowee Voltage Relays |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to perform adequate calculations to support the Keowee generator voltage trip setpoints provided in Tec
Region: II | Oconee | 36231 | 09/30/2011 11/14/2011 | 2011010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Calculations for MCC Control Circuits |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to perform adequate voltage calculations for safety-related Motor Control Center (MCC) 120VAC control c
Region: II | Oconee | 36236 | 09/30/2011 11/14/2011 | 2011010-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Control Circuit Voltage Calculations for 4160V breakers |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to perform adequate voltage calculations for safety-related 4160V circuit breaker 125VDC control circui
Region: II | Oconee | 36237 | 09/30/2011 11/14/2011 | 2011010-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Installation of SSF Submersible Pump |  | H.2(d) Facilities & Equipment | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings", for the licensee's failure to maintain complete and accurate procedures for installation of the Standby Shutdown F
Region: II | Oconee | 36238 | 09/30/2011 11/14/2011 | 2011010-06 | NRC | NCV | Mitigating Systems | Green | Failure to Account for the Full Range of Emergency Power AC Frequency When Evaluating the Performance of Safety-Related Components |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | Green. The team identified a Green non cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to account for the full range of emergency AC power frequencies allowed by the surveillance procedure w
Region: II | Oconee | 36224 | 09/20/2011 10/04/2011 | 2011018-01 | NRC | NCV | Mitigating Systems | Green | Installation of Non-Qualified SSF Pressurizer Heater Breakers Impacting Operability During Certain SSFCredited Events | EA Case: 2011226 | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to install Standby Shutdown Facility (SSF) pressurizer heater breakers that were qualified for expected environmental conditions
Region: II | Oconee | 36218 | 09/09/2011 09/07/2011 | 2011017-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain SSF Pressurizer Heater Breakers as Safety-Related Components |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 93812 | An NRC-identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to maintain the Standby Shutdown Facility (SSF) pressurizer heater breakers and associated electrical componen
Region: II | Oconee | 36209 | 06/30/2011 07/27/2011 | 2011003-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Design Verification of the NPBS-BWST/SSF Trench Foundation |  | H.3(a) Work Planning | TE?: N | 05000270 Oconee 2 |  | 71111.01 | A self-revealing finding was identified for the licensee's failure to implement the requirements of the modification program to ensure the natural phenomenon barrier system (NPBS) borated water storage tank (BWST)/standby shutdown facility (SSF) trench fo
Region: II | Oconee | 36207 | 05/19/2011 06/23/2011 | 2011016-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to take required compensatory actions for 1 and 2 RIA-40 condenser off-gas radiation monitor inoperability |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 |  | NONE | Green: An NRC-identified Non-Cited Violation (NCV) of Technical Specification 5.4.1.d, for failure to follow procedures NSD 513, "Primary to Secondary Leak Monitoring Program," and OP/0/A/1106/031, "Primary to Secondary Leak Rate Monitoring and Instrument
Region: II | Oconee | 36200 | 03/31/2011 05/13/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate risk management associated with the removal of the Unit 2 west penetration room girts |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000270 Oconee 2 |  | 71111.13 | An NRC-identified non-cited violation of 10 CFR 50.65(a)(4) was identified for the licensee's failure to effectively implement risk mitigation actions as defined in the Complex Activity Plan for the Unit 2 Cask Decon Tank Room and West Penetration Room (W
Region: II | Oconee | 36206 | 03/31/2011 05/13/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate post modification testing to ensure SSF DG functionality |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.18 | An NRC-identified [Green Non-cited] Violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to ensure that a modification installed on the Safe Shutdown Facility (SSF) Diesel Generator (DG) monitoring p
Region: II | Oconee | 36191 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately protect risk significant and safety-related systems, structures or components (SSCs) from cold weather conditions. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.01 | An NRC-identified non-cited violation (NCV) of TS 5.4.1.a was identified for the licensee's failure to implement procedures to ensure equipment associated with cold weather protection of risk significant and safety-related systems, structures or component
Region: II | Oconee | 36192 | 12/31/2010 01/28/2011 | 2010005-02 | NRC | FIN | Mitigating Systems | Green | Failure to prescribe procedures for inspecting the east penetration room floor seals |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.06 | An NRC-identified finding was identified for the licensee's failure to verify the operability of the East Penetration Room (EPR) expansion joint floor seals for all three units since 2006. Selected Licensee Commitment (SLC) Surveillance Requirement (SR) 1
Region: II | Oconee | 36193 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to install structural rebar as required by instructions and drawings. |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.18 | An NRC-identified non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to adhere to drawings and instructions during the installation of rebar in QA-1 structures
Region: II | Oconee | 36197 | 12/17/2010 01/31/2011 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Failure to properly evaluate potentially degraded conditions for potential impact on operability or functionality. |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | -Green. An NRC-identified Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to evaluate degraded or nonconforming conditions and perform operability determin
Region: II | Oconee | 36198 | 12/17/2010 01/31/2011 | 2010009-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately monitor performance of the standby shutdown facility HVAC system as required by 10 CFR 50.65 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | -Green. An NRC-identified non-cited violation of 10 CFR 50.65(a)(2), was identified for failure to demonstrate that Standby Shutdown Facility (SSF) Ventilation system performance was being effectively controlled through the preventive maintenance (PM) pro
Region: II | Oconee | 36187 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to install fiber reinforced polymer on Unit 1 auxiliary building wall as required by procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000269 Oconee 1 |  | 71111.18 | An NRC-identified Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings, was identified for the licensee's failure to install Fiber Reinforced Polymer (FRP) on the Unit 1 Auxiliary Building wall in accordan
Region: II | Oconee | 36189 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | EQ components not installed in the as-qualified configuration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | A NRC-identified non-cited violation was identified for the licensee's failure to comply with 10 CFR 50.49(f) in that Rosemount transmitters, Limitorque valve actuators, and electrical penetration assemblies (EPAs), each an item of electric equipment impo
Region: II | Oconee | 36190 | 09/30/2010 10/29/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Unqualified electrical penetration assemblies |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | An NRC-identified non-cited violation of 10 CFR 50.49(l) was identified when the licensee did not follow the requirements for replacing components within EPAs when existing components qualified under the Division of Operating Reactors, Guidelines for Eval
Region: II | Oconee | 36178 | 06/30/2010 07/27/2010 | 2010003-01 | NRC | NCV | Initiating Events | Green | Inadequate Risk Management Associated With the Unit 2 Electrical Generator Rotor Lifts |  | H.3(a) Work Planning | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 |  | 71111.13 | Green. An NRC-identified Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified for the licensee's failure to adequately develop and effectively implement risk mitigation actions associated with lifting the Unit 2 main generator rotor. The l
Region: II | Oconee | 36185 | 06/30/2010 07/27/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Install Structural Rebar as Required by Instructions and Drawings |  | H.4(b) Procedural Compliance | TE?: N | 05000287 Oconee 3 |  | 71111.17T | Green. An NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified. The licensee failed to adhere to drawings and instructions during the installation of rebar in the Unit
Region: II | Oconee | 36186 | 06/30/2010 07/27/2010 | 2010003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Conduct an Adequate Area Radiation Survey of a Room in the Radwaste Facility |  | H.3(b) Work Activity Coordination | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71124.01 | Green. A self-revealing non-cited violation (NCV) of 10 CFR 20.1501(a) was identified for the licensee's failure to conduct an adequate area radiation survey to evaluate the magnitude and extent of radiation levels for an area located in the Radwaste Faci
Region: II | Oconee | 36168 | 03/31/2010 05/14/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Fire Brigade Performance Weaknesses |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.05A | A Green NRC-identified NCV of Condition 3.D of Facility Operating Licenses DPR-38 (Unit 1), DPR-47 (Unit 2) and DPR-55 (Unit 3) was identified for the licensee's failure to identify, critique, and develop corrective actions for fire brigade performance we
Region: II | Oconee | 36163 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Risk Management Actions Associated With Modification Work Activities on the BWSTs for all Three Oconee Units |  | H.3(b) Work Activity Coordination | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.13 | An NRC-identified Green NCV of 10 CFR 50.65(a)(4) was identified for the licensee's failure to effectively implement the risk mitigation actions contained in the approved complex activity plans associated with modifications on all three Borated Water Stor
Region: II | Oconee | 36165 | 12/31/2009 01/28/2010 | 2009005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Establish and Implement an Adequate Procedure for Performing Core Alignment Verification |  | P.2(b) Implementing Operating Experience | TE?: N | 05000269 Oconee 1 |  | 71111.2 | A self-revealing Green NCV of Technical Specification (TS) 5.4.1 was identified for failure to maintain procedure PT/0/A/0775/015, "Core Alignment Verification," which resulted in damage to three Unit 1 fuel assemblies. The inspectors determined that
Region: II | Oconee | 36166 | 12/31/2009 01/28/2010 | 2009005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply with Radiological Postings and the Requirements for Entering a Posted High Radiation Area |  | H.4(a) Human Error Prevention | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7112101 | A self-revealing Green NCV of Technical Specification 5.4.1, Procedures, was identified for the failure to read and comply with all radiological postings and, prior to entering a high radiation area, attend a documented radiation protection briefing, know
Region: II | Oconee | 36167 | 12/31/2009 01/28/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | Inappropriate Removal of Workers Associated With Modification Work Activities on the BWST's from Work Hour Controls |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | NONE | An NRC-identified Green NCV of 10 CFR 26.205 was identified when the licensee excluded individuals working on BWST modifications from work hour controls. This violation has been entered into the licensee's corrective action program as PIP O-09-6989. Th
Region: II | Oconee | 36159 | 10/15/2009 10/29/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate assessment and management of risk during SSF ASW inoperability (Section 1R13) |  | H.3(a) Work Planning | TE?: N | 05000270 Oconee 2 |  | 71111.13 | An NRC-identified non-cited violation of 10 CFR 50.65(a)(4) was identified for the licensee's failure to provide adequate guidance to perform an appropriate risk assessment associated with the repair of a through-wall leak on the Unit 2 Standby Shutdown F
Region: II | Oconee | 36160 | 10/15/2009 10/29/2009 | 2009004-02 | Self - Revealed | FIN | Initiating Events | Green | Unit 3 trip due to generator phase differential lockout (Section 4OA3) |  | H.4(a) Human Error Prevention | TE?: N | 05000287 Oconee 3 |  | 71153 | A self-revealing finding was identified when Unit 3 experienced a reactor trip from 42 percent power as a result of a main generator lockout. The generator lockout was caused by an incorrect tap setting on a phase differential relay (HU-4). The failure
Region: II | Oconee | 36157 | 08/28/2009 09/24/2009 | 2009006-01 | NRC | NCV | Initiating Events | Green | Failure to Provide Margin Between the LPI Relief Valve Set Point and the Peak Discharge Pressure of the LPI System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000287 Oconee 3 |  | 71152B | A self-revealing, non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion III, Design Control, was identified for failure to provide sufficient margin between the peak discharge pressure of the low pressure injection (LPI) system and the relief valve
Region: II | Oconee | 36156 | 06/30/2009 07/28/2009 | 2009003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Implement Procedures for Draining the Reactor Coolant System |  | H.4(b) Procedural Compliance | TE?: N | 05000287 Oconee 3 |  | 71111.2 | Green. A self-revealing non-cited violation (NCV) of Technical Specification 5.4.1 was identified for the failure to adequately implement the procedural requirements for draining the RCS to 100 inches in the pressurizer, resulting in draining approximatel
Region: II | Oconee | 36146 | 06/30/2008 07/25/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Required Pressure Tests Not Performed (Section 1R08.1) |  | H.3(b) Work Activity Coordination | TE?: N | 05000269 Oconee 1 |  | 71111.08P | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.55a(g)(4) for the failure to perform periodic leakage testing of Class 1 portions of low pressure injection system during the third inspection interval of the Unit 1 Inservice Inspec
Region: II | Oconee | 36148 | 06/11/2008 08/01/2008 | 2008008-01 | NRC | NCV | Initiating Events | Green | Failure to Comply with Procedure OMP 1-18 by Overriding Abnormal Procedure Requirements Beyond the Point of Placing the Plant in a Safe/Stable Condition (Section 4OA5.2b.(1)) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000269 Oconee 1 |  | 93812 | The team identified a non-cited violation of Technical Specification 5.4.1 for failure to properly implement procedure OMP 1-18, Implementation Standard During Abnormal and Emergency Events, which allows actions to be taken outside of procedures during ab
Region: II | Oconee | 36150 | 06/11/2008 08/01/2008 | 2008008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Comply With Procedure SOMP 04-02 and Fully Implement or Formally Change the Requirements of AP/1/A/1700/016 (Section 4OA5.2b.(3)) |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000269 Oconee 1 |  | 93812 | The team identified a non-cited violation of Technical Specification 5.4.1 for failure to properly implement procedure SOMP 04-02, Procedure Use and Adherence, during Unit 1 cooldown and depressurization activities. Specifically, the licensee made the dec
Region: II | Oconee | 36149 | 06/11/2008 08/01/2008 | 2008008-03 | NRC | NCV | Initiating Events | Green | Failure to Enter AP/1/A/1700/026 for a Loss of RCS Inventory from a Seal Leak Which Developed on the 1A2 RCP (Section 4OA5.2b.(2)) |  | H.4(b) Procedural Compliance | TE?: N | 05000269 Oconee 1 |  | 93812 | The team identified a non-cited violation of Technical Specification 5.4.1 for failure to fully comply with procedure SOMP 04-02, Procedure Use and Adherence, during Unit 1 cooldown and depressurization activities. Specifically, AP/1/A/1700/016, Abnormal
Region: II | Oconee | 36151 | 06/11/2008 08/01/2008 | 2008008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Procedure OMP 2-01 When Monitoring Plant Parameters (Section 4OA5.2b.(4)) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000269 Oconee 1 |  | 93812 | The team identified a non-cited violation of Technical Specification 5.4.1 for failure to comply with procedure OMP 2-01, Duties and Responsibilities of On-Shift Operations Personnel, on two occasions during Unit 1 cooldown and depressurization activities
Region: II | Oconee | 36136 | 03/31/2008 04/30/2008 | 2008002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Installation of SSF DG Field Flash Relay Cover (Section 1R19) |  | H.4(a) Human Error Prevention | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.19 | A self-revealing finding (FIN) was identified for failure to implement self-checking during Standby Shutdown Facility (SSF) diesel generator (DG) field flash relay cover reinstallation, resulting in a failure of the relay during post maintenance testing a
Region: II | Oconee | 36140 | 03/31/2008 04/30/2008 | 2008002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement the Procedure to Stroke RBS Valves (Section 1R22) |  | H.3(b) Work Activity Coordination | TE?: N | 05000287 Oconee 3 |  | 71111.22 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1 was identified for failure to adequately implement the procedure to stroke reactor building spray (RBS) valves, which resulted in a loss of Reactor Coolant System (RCS) inven
Region: II | Oconee | 36141 | 03/31/2008 04/30/2008 | 2008002-03 | Self - Revealed | NCV | Initiating Events | Green | Dilution of the RCS While Lining Up for SFP Makeup (Section 4OA3) |  | H.4(b) Procedural Compliance | TE?: N | 05000287 Oconee 3 |  | 71153 | A self-revealing NCV of TS 5.4.1 was identified for the failure to properly implement the procedural requirements of OP/3/A/1104/006C, Spent Fuel Pool (SFP) Makeup, which led to an over dilution of the Unit 3 RCS. The failure to properly implement the
Region: II | Oconee | 36142 | 03/14/2008 04/21/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control in the Translation of Design Basis Information into Procedure for Draining and Nitrogen Purging the RCS (Section 1R21.2.2) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | The inspectors identified a finding of very low safety significance involving a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee failed to verify the applicability of design basis information,
Region: II | Oconee | 36143 | 03/14/2008 04/21/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Local Manual Operating Capability for EFW Flow Control Valves (Section 1R21.2.6) |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | The inspectors identified a finding of very low safety significance involving a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee failed to establish measures to verify the design capability for local manual handwh
Region: II | Oconee | 36134 | 12/31/2007 01/31/2008 | 2007005-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Loss of Unit 3 SFP Cooling Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000287 Oconee 3 |  | 71111.2 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1 was identified for failure to establish and implement an adequate procedure for loss of the Unit 3 spent fuel pool (SFP) cooling and/or level. More specifically, Abnormal Pro
Region: II | Oconee | 36135 | 12/31/2007 01/31/2008 | 2007005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Establish Adequate Procedures for Containment Closure Following a Loss of Decay Heat Removal Event |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000287 Oconee 3 |  | 71111.2 | The inspectors identified an NCV of TS 5.4.1 for the failure to establish and implement adequate procedures for containment closure following a potential loss of decay heat removal (LDHR) event. More specifically, existing procedures did not adequately ad
Region: II | Oconee | 36132 | 09/30/2007 10/30/2007 | 2007004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Promptly Identify A Condition Adverse To Quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.19 | A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for failure to take timely corrective action to repair the Standby Shutdown Facility (SSF) air conditioning compressor #2. As a result, t
Region: II | Oconee | 36133 | 09/30/2007 10/30/2007 | 2007004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure To Implement LTOP Controls |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000269 Oconee 1 |  | 71153 | A self-revealing NCV of Technical Specification (TS) 3.4.12, Low Temperature Overpressure Protection (LTOP), was identified for failure to take the appropriate actions when administrative controls specified by TS 3.4.12 were required and not available. Th
Region: II | Oconee | 36129 | 07/27/2007 10/03/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action Resulting in the Inoperability of Unit 1 Reactor Coolant Makeup Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 |  | 71152B | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI was identified by the NRC for failure to take adequate corrective action to prevent unexpected inoperability of the Unit 1 standby shutdown facility (SSF) reactor coolant makeup (RCMU) system d
Region: II | Oconee | 36128 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Meet the Minimum Licensed Operator Staffing Requirements as required by 10 CFR 50.54(m)(2)(i) |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.11B | The inspectors identified an non-cited violation (NCV) of 10 CFR 50.54 Conditions of a license, for failing to meet the minimum licensed operator staffing requirements as stated in 10 CFR 50.54(m)(2)(i). Between March 2003 and February 2007, seven Senior
Region: II | Oconee | 36126 | 06/30/2007 07/30/2007 | 2007003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure Tagout Compatibility with Plant Conditions |  | H.3(b) Work Activity Coordination | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.12 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1 was identified for failure to ensure a high pressure service water (HPSW) system tagout was compatible with overall plant conditions, in that the elevated water storage tank
Region: II | Oconee | 36127 | 06/30/2007 07/30/2007 | 2007003-03 | NRC | NCV | Public Radiation Safety | Green | Failure to conduct adequate QA activities to ensure waste shipments are characterized in accordance with 10 CFR 61.55 |  | P.3(a) Self-Assessment | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7112202 | The inspectors identified a NCV of 10 CFR 20 Appendix G, Section III.A.3 for failure to conduct adequate Quality Assurance activities to ensure compliance with the waste characterization requirements of 10 CFR 61.55. Specifically, the licensee failed to p
Region: II | Oconee | 36125 | 03/31/2007 04/27/2007 | 2007002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow the Installation Procedure for the MDEFW Pump 1A Thrust End Bearing |  |  | TE?: N | 05000269 Oconee 1 |  | 71111.12 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1 was identified for failure to adequately implement the procedure requirements for thrust end bearing installation on motor driven emergency feedwater (MDEFW) Pump 1A, resulti
Region: II | Oconee | 36111 | 06/30/2006 07/28/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Examinations of Letdown Filter Supports. |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71111.08P | The inspectors identified a finding involving a non-cited violation of 10 CFR Part 50.55a(g)(4)ii for failure to perform a visual (VT-3) examination of the letdown filter housing supports as required by Section XI of the ASME Code. The examinations were p
Region: II | Oconee | 36112 | 06/30/2006 07/28/2006 | 2006003-05 | NRC | NCV | Public Radiation Safety | Green | Failure to calibrate 1RIA-37 Approriately For The Radiation Measured. |  |  | TE?: N | 05000269 Oconee 1 |  | 7112201 | The inspectors identified a non-cited violation of 10 CFR 20.1501 (b) for failure to ensure that equipment used for effluent monitoring was calibrated for the radiation measured. Specifically, during a 2005 annual calibration of the Unit 1 Gaseous Waste D
Region: II | Oconee | 36113 | 06/30/2006 07/28/2006 | 2006003-06 | Self - Revealed | NCV | Initiating Events | Green | Loss of Unit 3 Offsite Power During Mode 6. |  |  | TE?: N | 05000287 Oconee 3 |  | 71153 | self-revealing non-cited violation of Technical Specification (TS) 5.4.1 was identified for failure to adequately implement the procedure requirements for protected train equipment, resulting in the lockout of CT3 transformer and subsequent loss of Unit 3
Region: II | Oconee | 36114 | 06/30/2006 07/28/2006 | 2006003-07 | NRC | NCV | Mitigating Systems | Green | Failure To Maintain Containment Electrical Penetration Enclosures. |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI for failure to identify a condition adverse to quality in that East and West Penetration Room containment electrical penetration enclosures had not been maintained, suc
Region: II | Oconee | 36108 | 06/30/2006 06/29/2006 | 2006014-01 | NRC | NCV | Mitigating Systems | Green | Failure to promptly correct long-standing east penetration room blowout panel-related deficiencies that preclued flood mitigation in the auxiliary buidling. | EA Case: 2006070 |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 71152 | NCV of 10 CFR Part 50, Appendix B, Criteria XVI, Corrective Action, for failure to promptly identify and correct a significant condition adverse to quality. Specifically, as a result of inappropriate east penetration room blowout panel modifications (iden
Region: II | Oconee | 36102 | 03/17/2006 04/28/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative EOP Procedure Setpoint for Operator Action to accomplish BWST to RBES swap over on Low BWST Level |  |  | TE?: N | 05000269 Oconee 1 05000270 Oconee 2 05000287 Oconee 3 |  | 7111121 | The team identified a Green, non-cited violation (NCV) of Technical Specification 5.4.1.b for a non-conservative operator action setpoint in the Emergency Operating Procedures. Specifically, the 6 foot level setpoint for operator action to complete the
Region: II | Oconee | 36094 | 02/15/2006 02/21/2006 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Long-Standing Discrepancy Between the Unit 3 Control Room and its Tornado Licensing Basis Specified in the Updated Final Safety Analysis Report | EA Case: 2005228 |  | TE?: N | 05000287 Oconee 3 |  | 71152 | NCV for failure to promptly identify and correct a long-standing discrepancy between the Unit 3 control room and its tornado licensing basis specified in the Updated Final Safety Analysis Report: (1) a failure to take adequate corrective actions to bring
Region: II | Robinson | 125560 | 09/19/2019 09/19/2019 | 2019012-01 | NRC | AV | Initiating Events | Green | Failure to Perform Hourly Fire Watches | EA Case: EA-19-025 | H.8 - Procedure Adherence | TE?: N | 05000261 Robinson 2 | Protection Against External Factors | 71111.05Q | The inspectors identified an apparent violation of 10 CFR § 50.48, Fire Protection, and an associated reactor oversight process Green finding for the failure to conduct hourly fire watches in accordance with procedure AD-EG-ALL-1522, Duties of a Fire Watc
Region: II | Robinson | 124598 | 03/31/2019 05/14/2019 | 2019001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Furnish Evidence of Activity Affecting Quality |  | NPP | TE?: N | 05000261 Robinson 2 | Design Control | 71111.21N | The NRC identified a Green finding and associated non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVII, "Quality Assurance Records," for the failure to furnish evidence of an activity affecting quality ass
Region: II | Robinson | 38856 | 12/31/2018 02/07/2019 | 2018004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure for Movement of Fuel Assemblies in the Spent Fuel Pool |  | H.1 - Resources | TE?: N | 05000261 Robinson 2 |  | 71111.2 | A self-revealing Green NCV of Technical Specifications 5.4.1, “Procedures,” was identified for the licensee’s failure to incorporate (1) specific procedural steps describing the function of the SFP Bridge crane hoist overload trip in FHP-003, “Fuel Assemb
Region: II | Robinson | 22611 | 10/20/2017 12/04/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Determine Qualified Life |  | H.7 - Documentation | TE?: N | 05000261 Robinson 2 |  | 71111.21N | The NRC identified a non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to establish a qualified life for the motors covered b
Region: II | Robinson | 22612 | 10/20/2017 12/04/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required O-ring Replacement to Maintain Qualification |  | NPP | TE?: N | 05000261 Robinson 2 |  | 71111.21N | The NRC identified a non-cited violation of 10 CFR Part 50.49, “Environmental qualification of electric equipment important to safety for nuclear power plants,” for the licensee’s failure to correctly identify the maintenance required to maintain the cor
Region: II | Robinson | 22613 | 10/20/2017 12/04/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Determine Most Severe Containment Spray pH |  | NPP | TE?: N | 05000261 Robinson 2 |  | 71111.21N | The NRC identified a non-cited violation of 10 CFR Part 50.49, “Environmental qualification of electric equipment important to safety for nuclear power plants,” for the licensee’s failure to correctly determine the most severe composition of chemicals fo
Region: II | Robinson | 32735 | 03/31/2017 05/05/2017 | 2017001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform General Visual Examinations of Containment Moisture Barriers Associated with Containment Liner Leak-Chase Test Connections |  | P.3 - Resolution | TE?: N | 05000261 Robinson 2 |  | 71111.2 | An NRC-identified Green non-cited violation (NCV) of 10 CFR Part 50.55a, "Codes and Standards," was identified for the failure to perform general visual examinations of moisture barriers in the containment leak-chase channel test connections in accordance
Region: II | Robinson | 32704 | 09/30/2016 11/04/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Scope Tainter Gate Flood Protection Features in Maintenance Rule Resulting in Degraded Performance |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.12 | A self-revealing Green NCV of 10 CFR 50.65(b)(2)(ii) was identified for the failure to scope the external flood protection function of the Robinson Lake Dam spillway (Tainter) gates in the maintenance rule (MR) monitoring program. The failure to include t
Region: II | Robinson | 32719 | 09/30/2016 11/04/2016 | 2016003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Main Turbine Trip Maintenance Resulting in Turbine/Reactor Trip |  | H.5 Work Management | TE?: N | 05000261 Robinson 2 |  | 71111.13 | A self-revealing Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified for the failure to adequately assess and manage the increase in risk associated with online maintenance activities involving the removal of the cover to the main turbine
Region: II | Robinson | 32721 | 08/19/2016 10/03/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Keep EOP FRP-H.1 in Conformance with Plant Specific Guidelines |  | H.4 Teamwork | TE?: N | 05000261 Robinson 2 |  | 7111121 | The NRC identified a non-cited violation of Technical Specification 5.4.1 for the licensee's failure to maintain emergency operating procedure (EOP) FRP-H.1, "Response to Loss of Secondary Heat Sink," in accordance with their commitment to implement EOPs
Region: II | Robinson | 32727 | 08/19/2016 10/03/2016 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Appropriate Maintenance or Testing for the Dedicated Shutdown Transformer |  | P.2 Evaluation | TE?: N | 05000261 Robinson 2 |  | 7111121 | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations (10 CFR) Part 50.63, "Loss of all alternating current power," for the licensee's failure to meet their commitment to the guidance in NRC RG 1.155, "Station Blackout." Specifi
Region: II | Robinson | 32728 | 08/19/2016 10/03/2016 | 2016008-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Comply with TS Requirements for Containment High Range Radiation Monitors |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The NRC identified a non-cited violation of Technical Specification (TS) 3.3.3, "Post Accident Monitoring (PAM) Instrumentation," for the licensee's failure to maintain the operability of the containment radiation monitors (high range) (CHRRMs). In respon
Region: II | Robinson | 32729 | 08/19/2016 10/03/2016 | 2016008-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Follow Operability Determination Process |  | P.5 Operating Experience | TE?: N | 05000261 Robinson 2 |  | 7111121 | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow their operability determination procedure. Specifically,
Region: II | Robinson | 32688 | 03/31/2016 05/13/2016 | 2016001-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Establish and Implement Procedure During Tornado Watch/Warning |  | H.5 Work Management | TE?: N | 05000261 Robinson 2 |  | 71111.01 | The inspectors identified a Green non-cited violation (NCV) of technical specification (TS) 5.4.1.a for the licensee's failure to adequately establish and implement procedure OMM-021, Operation During Adverse Weather Conditions. Specifically, the licensee
Region: II | Robinson | 32689 | 03/31/2016 05/13/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Safety-Related Auxiliary Building Ventilation Fans into the Maintenance Rule |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(b)(1), for the licensee's failure to include safety-related structures, systems and components (SSCs) within the scope of the maintenance rule (MR) program. Specifically, the licensee failed to include
Region: II | Robinson | 32690 | 03/31/2016 05/13/2016 | 2016001-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure for a Light Indication Replacement |  | H.12 Avoid Complacency | TE?: N | 05000261 Robinson 2 |  | 71111.13 | The inspectors identified a Green NCV of TS 5.4.1.a, for the licensee's failure to adequately implement procedure OMM-001-11, Logkeeping, while performing maintenance. Specifically, the licensee replaced a local light indication for a containment instrume
Region: II | Robinson | 32693 | 03/31/2016 05/13/2016 | 2016001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Control Deviations of from Design Specifications for the Service Water System |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.22 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to assure that appropriate quality standards are specified and included in design documents and that deviations from such st
Region: II | Robinson | 32694 | 03/31/2016 05/13/2016 | 2016001-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Maintain Emergency Operating Procedures EOP-ECA-0.0 and EOP-E-0 |  | H.12 Avoid Complacency | TE?: N | 05000261 Robinson 2 |  | 71111.11Q | The NRC identified a Green NCV of TS 5.4.1.a for the licensee's failure to adequately maintain procedures EOP ECA-0.0, Loss of All AC Power, and EOP-E-0, Reactor Trip or Safety Injection, as recommended in RG 1.33, Revision 2, Appendix A, February 1978. R
Region: II | Robinson | 32684 | 06/30/2015 07/16/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Engineering Change Procedure for Modification of RPS |  | H.4 Teamwork | TE?: N | 05000261 Robinson 2 |  | 71111.18 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified when the licensee failed to follow EGR-NGGC-0005, Engineering Change, during a modification of the RPS. This resulted in having i
Region: II | Robinson | 32674 | 12/31/2014 01/28/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Protect Diesel Driven Equipment from Effects of Extreme Cold Temperatures |  | P.2 Evaluation | TE?: N | 05000261 Robinson 2 |  | 71111.01 | The inspectors identified a Green non-cited violation (NCV) of Technical Specification (TS) 5.4.1, for failure to establish procedural guidance to protect diesel driven equipment important to safety from the effects of extreme cold temperatures. Specifica
Region: II | Robinson | 32672 | 06/30/2014 07/21/2014 | 2014003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Identify and Correct Degraded Wire Labels in the Reactor Protection Relay Cabinets |  | P.1 Identification | TE?: N | 05000261 Robinson 2 |  | 71153 | A self-revealing Green non-cited violation (NCV) was identified for the licensee's failure to promptly identify and correct degraded wire labels in the reactor protection cabinets, which were a condition adverse to quality, as required by 10 CFR Part 50,
Region: II | Robinson | 32667 | 05/09/2014 06/10/2014 | 2014008-01 | NRC | NCV | Initiating Events | Green | Failure to Take Adequate Corrective Action to Preclude Repetition of a Significant Condition Adverse to Quality Associated with the Steam Generator Tube Leak |  |  | TE?: N | 05000261 Robinson 2 |  | 71152B | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to take adequate corrective action to prevent repetition of a significant condition adverse to quality regarding steam generator tube
Region: II | Robinson | 32656 | 03/31/2014 04/29/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately critique fire brigade drills |  | H.13 Consistent Process | TE?: N | 05000261 Robinson 2 |  | 71111.05Q | Green. A Green NRC-Identified non-cited violation (NCV) of Facility Operating License DPR-23, Condition 3.E, Fire Protection Program, was identified for the licensee's failure to identify, critique, and develop corrective actions for fire brigade performa
Region: II | Robinson | 32657 | 03/31/2014 04/29/2014 | 2014002-02 | Self - Revealed | FIN | Initiating Events | Green | Steam generator tube leak resulting from foreign material |  | H.11 Challenge the Unknown | TE?: N | 05000261 Robinson 2 |  | 71111.08P | Green. A self-revealing Green FIN was identified for the licensee's failure to thoroughly inspect and remove foreign material from feedwater piping after initial breach of the pipe, as required by licensee procedure MNT-NGGC-0007, Foreign Material Exclusi
Region: II | Robinson | 32664 | 03/31/2014 04/29/2014 | 2014002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate preventive maintenance on 4 KV breaker 52/7 results in an automatic reactor trip |  | P.3 Resolution | TE?: N | 05000261 Robinson 2 |  | 71111.12 | Green. A self-revealing Green finding (FIN) was identified for the licensee's failure to perform adequate preventive maintenance (PM) in accordance with, licensee procedure ADM-NGGC-107, Equipment Reliability Process, for 4 KV Breaker 52/7, Unit Auxiliary
Region: II | Robinson | 32665 | 03/31/2014 04/29/2014 | 2014002-04 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate design control measures for diesel fuel oil cloud point |  | H.6 Design Margins | TE?: N | 05000261 Robinson 2 |  | 71111.15 | Green. The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, because the licensee failed to provide adequate design control measures to ensure appropriate specifications were translated into procedures for die
Region: II | Robinson | 32650 | 12/31/2013 01/31/2014 | 2013005-01 | NRC | NCV | Initiating Events | Green | Inadequate Preparation for Cold Weather Conditions |  | H.3(a) Work Planning | TE?: N | 05000261 Robinson 2 |  | 71111.01 | The inspectors identified a Green non-cited violation (NCV) of Technical Specification 5.4.1 for the licensee's failure to implement freeze protection requirements specified in station procedures. Specifically the inspectors found that the required tempor
Region: II | Robinson | 32651 | 12/31/2013 01/31/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Transient Materials Not Removed from Containment Prior to Reactor Startup |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000261 Robinson 2 |  | 71111.2 | The inspectors identified a Green non-cited violation of Technical Specification (TS) 5.4.1 for the failure to properly implement procedure PLP-006, Containment Vessel Inspection Closeout, prior to startup following RFO 28. The improper closeout resulted
Region: II | Robinson | 32655 | 12/31/2013 01/31/2014 | 2013005-03 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Entry Into a HRA |  | H.4(a) Human Error Prevention | TE?: N | 05000261 Robinson 2 |  | 71124.01 | A self-revealing, Green, non-cited violation (NCV) of TS 5.7.1, "High Radiation Area," was identified for an unauthorized entry into a High Radiation Area (HRA). Specifically, two workers entered the residual heat removal pump room without knowledge of cu
Region: II | Robinson | 32649 | 09/30/2013 10/30/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Lack of preventive maintenance results in "B" EDG recirculation damper failure |  | P.2(b) Implementing Operating Experience | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(2) for the licensee's failure to demonstrate that the performance of the "B" Emergency Diesel Generator (EDG) ventilation recirculation damper was effectively controlled throug
Region: II | Robinson | 32646 | 06/30/2013 07/31/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope in all CVCS Instruments used in EOPs in the Maintenance Rule Program |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(b)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because the licensee failed to scope in all the Chemical Volume and Control (CVCS) instruments used in pla
Region: II | Robinson | 32634 | 05/17/2013 06/28/2013 | 2013007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Account for Containment Temperature Measurement Uncertainty |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to account for instrument uncertainty on the containment bulk temperature instrumentation which was used to verify techni
Region: II | Robinson | 32635 | 05/17/2013 06/28/2013 | 2013007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate SBO Coping Equipment for Environmental Conditions |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green finding for the licensee's failure to follow NRC Regulatory Guide 1.155, "Station Blackout," guidance (to which they are committed in the Updated Final Safety Analysis Report) for evaluating equipment needed to cope with a stat
Region: II | Robinson | 32642 | 05/17/2013 06/28/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Have Adequate Analyses Supporting the Degraded Voltage Relay Setpoints |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to have adequate analyses that supported safety-related load operation during a design basis accident while supplied by o
Region: II | Robinson | 32643 | 05/17/2013 06/28/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Have Adequate Analyses For the E1 Bus Fast Transfer |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of the plant design during fast bus transfers. Specifically, the licensee failed to have an adequa
Region: II | Robinson | 32644 | 05/17/2013 06/28/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Have Appropriate Procedure to Verify Degraded Voltage Relay Circuit Status |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to prescribe an adequate procedure that verified DGVR circuit operability following degraded voltag
Region: II | Robinson | 32631 | 12/31/2012 02/06/2013 | 2012005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Effectively Implement Gas Intrusion Program (GL 2008-01) |  | H.4(b) Procedural Compliance | TE?: N | 05000261 Robinson 2 |  | NONE | Green. The inspectors identified a Finding for the licensee's failure to perform the 18-month pre-refueling outage (RO) ultrasonic testing (UT) examinations on 47 potential gas accumulation locations required by plant operating manual PLP-085, "Emergency
Region: II | Robinson | 32627 | 11/30/2012 12/20/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fire Load Limits in Fire Area A |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000261 Robinson 2 |  | 71111.05T | Green. The inspectors identified a Green Non-Cited Violation (NCV) of Robinson's License Condition 3. E, "Fire Protection Program", for increasing the amounts of in-situ combustibles in several fire zones within fire area "A" above required limits in NR
Region: II | Robinson | 32628 | 11/30/2012 12/20/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Deficiencies in the Emergency Lighting System Preventive Maintenance Program |  | P.1(b) Trend Performance CAP | TE?: N | 05000261 Robinson 2 |  | 71111.05T | Green. The inspectors identified a Green NCV of 10 CFR Part 50.65, Maintenance Rule, for the licensee's failure to identify and correct deficiencies in the emergency lighting system (ELS) preventive maintenance program. The licensee entered the issues i
Region: II | Robinson | 32626 | 09/30/2012 10/30/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include the Fuel Oil Supply to the TSC/EOF/Security Diesel in the Maintenance Rule |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(b)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because the licensee failed to include all aspects of the Fuel Oil System in the mai
Region: II | Robinson | 32618 | 06/30/2012 07/30/2012 | 2012003-02 | Self - Revealed | FIN | Initiating Events | Green | Lack of preventive maintenance on feedwater control switch results in an automatic reactor trip |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71111.12 | A self-revealing Green finding was identified when the licensee failed to establish adequate preventative maintenance for equipment associated with the feedwater control systems. Specifically, the licensee's inappropriate classification of the feedwater f
Region: II | Robinson | 32619 | 06/30/2012 07/30/2012 | 2012003-03 | NRC | FIN | Mitigating Systems | Green | Inoperability of the refueling water storage tank not recognized as a safety system functional failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71151 | The inspectors identified a Green finding for the licensee's failure to identify and document Safety System Functional Failures (SSFF) in accordance with REG-NGGC-0009, NRC Performance Indicators and Monthly Operating Report Data. The licensee did not rec
Region: II | Robinson | 32620 | 06/30/2012 07/30/2012 | 2012003-04 | NRC | NCVIV | Mitigating Systems | Green | Inaccurate safety system functional failure performance indicator submittal |  |  | TE?: Y SL-IV-NCVIV | 05000261 Robinson 2 |  | 71151 | The inspectors identified a Severity Level (SL) IV NCV of 10 CFR 50.9(a), "Completeness and Accuracy of Information," when the licensee inaccurately reported Safety System Functional Failure (SSFF) performance indicator data beginning with the 4th quarter
Region: II | Robinson | 32611 | 05/25/2012 07/05/2012 | 2012007-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action to Preclude Repetition of a Significant Condition Adverse to Quality Associated with the Refueling Water Storage Tank Purification |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000261 Robinson 2 |  | 71152B | Green: A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to take adequate corrective actions to prevent recurrence (CAPR) in response to a significant condition adverse to qual
Region: II | Robinson | 32612 | 05/25/2012 07/05/2012 | 2012007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Trending Requirements Set Forth in Plant Procedures |  | P.1(b) Trend Performance CAP | TE?: N | 05000261 Robinson 2 |  | 71152B | Green: An NRC identified finding was identified for the licensee's failure to implement trending requirements set forth in CAP-NGGC-0206, "Performance Assessment and Trending" and EGR-NGGC-0010, "System Component Trending Program and System Notebooks." Co
Region: II | Robinson | 32597 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Technical Specification Action Requirements Regarding 'B' Battery Inoperability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000261 Robinson 2 |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification (TS) 3.8.4, DC Electrical Sources, when the licensee failed to comply with the action time following discovery of reasonable information to determine that Surveillance Requirement (SR) 3.8.4
Region: II | Robinson | 32603 | 03/31/2012 04/30/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Change resulted in Interference and Inoperability of Containment Water Level Indication |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's installation of a plant modification that adversely affected the operability of nearby safety related equipment. Specifically, the licensee
Region: II | Robinson | 32604 | 03/31/2012 04/30/2012 | 2012002-03 | NRC | FIN | Barrier Integrity | Green | Low Temperature Overpressure System Rendered Inoperable For Operational Convenience |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.2 | The inspectors identified a Green finding for failure to follow the TS bases associated with Improved Technical Specification (ITS) 3.0.2 Limiting Condition for Operability (LCO) Applicability. Specifically, the licensee rendered the Low Temperature Overp
Region: II | Robinson | 32591 | 09/30/2011 11/14/2011 | 2011004-01 | NRC | NCV | Initiating Events | Green | Water Intrusion into Safety-Related Buildings due to Inadequate Design of Site Storm Water Runoff Drainage System |  | P.1(b) Trend Performance CAP | TE?: N | 05000261 Robinson 2 |  | 71111.01 | A self-revealing apparent violation (AV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the licensee's failure to consider how the aggregate changes to the site's topography could impact the site's ability to drain storm wat
Region: II | Robinson | 32596 | 09/30/2011 11/14/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Prompt Corrective Actions to Establish Guidance to Monitor and Operate Service Water Strainers Following LOOP |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71111.15 | Green. The inspectors identified a Green NCV of Technical Specification (TS) 5.4.1, Administrative Controls, Procedures, for failure to establish procedural guidance to monitor Service Water System (SWS) parameters and operate the SWS strainers following
Region: II | Robinson | 32583 | 06/30/2011 07/27/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Seismic Analysis for Installation of Safety Related Cable Trays and Conduit |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.15 | -Green. The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to perform an adequate seismic analysis during the plant modification of the 125VDC Battery Chargers.
Region: II | Robinson | 32584 | 06/30/2011 07/27/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Refueling Water Storage Tank Inoperable While On Purification |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000261 Robinson 2 |  | 71111.15 | Green. The inspectors identified a NCV of Technical Specification (TS) 3.5.4 Refueling Water Storage Tank (RWST), which required the RWST to be operable in modes 1 through 4. The licensee failed to comply with the TS Action Statements when the RWST was re
Region: II | Robinson | 32574 | 03/31/2011 04/27/2011 | 2011002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Two of Six Operating Crew Failures on the Simulator Operational Evaluation Portion of the 2011 Annual Requalification Operating Test |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000261 Robinson 2 |  | 71111.11B | Green: A self-revealing Green finding associated with operating crew performance on the simulator during facility-administered requalification examination was identified. Two of the six crews evaluated failed to pass their simulator examinations. As immed
Region: II | Robinson | 32573 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | FIN | Initiating Events | Green | Failure to Perform 5-year Vendor Manual Specified Reactor Coolant Pump Motor Inspections |  |  | TE?: N | 05000261 Robinson 2 |  | 71152 | The inspectors identified a Green finding for failure to perform vendor recommended inspections of the reactor coolant pump (RCP) motors. Visual inspections of the RCP stator assemblies were not performed at five year intervals in accordance with the vend
Region: II | Robinson | 31533 | 12/31/2010 12/10/2010 | 2010012-01 | Self - Revealed | NCV | Mitigating Systems | Green | Procedure violation for overriding feedwater isolation safety function in Mode 3 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000261 Robinson 2 |  | NONE | A self-revealing Green NCV of Technical Specification (TS) 5.4.1, Procedures, was identified when the licensee bypassed the feedwater isolation safety function, in Mode 3, a condition prohibited by TS and an action contrary to procedural requirements. On
Region: II | Robinson | 31534 | 12/31/2010 12/10/2010 | 2010012-02 | NRC | FIN | Mitigating Systems | Green | Operator transient response adversely affected by uncorrected, known plant deficiency |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000261 Robinson 2 |  | NONE | The inspectors identified a Green finding for failure to correct a known equipment deficiency which adversely affected the operators' ability to respond to reactor trip transients. Contrary to the licensee's corrective action program, as described in proc
Region: II | Robinson | 31537 | 11/15/2010 12/23/2010 | 2010011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Proper In-service Testing Acceptance Criteria to Prevent Reverse Rotation of the SDAFW Pump |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to ensure the in-service testing (IST) of the discharge check valve of the Auxiliary Feedwater (AFW) steam driven pump applied an accep
Region: II | Robinson | 31538 | 11/15/2010 12/23/2010 | 2010011-02 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure that the Full Range of Emergency Diesel Generator Frequency is Accounted for in the Safety Analyses |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to account for the high range of Emergency Diesel Generator (EDG) frequency allowed by technical specifications (TS) in the safety a
Region: II | Robinson | 32566 | 11/15/2010 12/23/2010 | 2010011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Capability of the Fuel Oil Storage Tank and the Service Water Pumps to Fulfill Their Safety Functions Under All Conditions |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to have calculations supporting the design bases of safety related components, specifically for the EDG fuel oil storage tank with respect to t
Region: II | Robinson | 32567 | 11/15/2010 12/23/2010 | 2010011-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate EDG Starting Air System Design Requirements into TS |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly translate the design basis of the EDG air start system into specifications. Specifically, the licensee did not properly translate
Region: II | Robinson | 32568 | 11/15/2010 12/23/2010 | 2010011-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Criteria to Prevent Spurious Actuation of Amptector Trip Devices |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," in that the licensee failed to verify the adequacy of the design for Amptector trip devices installed on safety related 480V circuit breakers. The licensee reviewed
Region: II | Robinson | 32569 | 11/15/2010 12/23/2010 | 2010011-06 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Vendor Recommendations Into Procedures for 480V Circuit Breakers |  | P.2(b) Implementing Operating Experience | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures, Instructions and Drawings," for failure to follow procedure EGR-NGGC-006, Vendor Manuals, which requires performance of reviews to determine technical accuracy and potenti
Region: II | Robinson | 32570 | 11/15/2010 12/23/2010 | 2010011-07 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Adequate Post Maintenance Test of Residual Heat Removal Valve Interlock Function |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a finding having very low safety significance (Green) involving the failure to perform a post maintenance test to verify functionality of valve position permissive interlocks associated with the reactor coolant system (RCS) hot leg loo
Region: II | Robinson | 31512 | 09/30/2010 11/12/2010 | 2010004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to have adequate work and post maintenance testing insturctions for the volume control tank comparator module |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71111.19 | A self revealing Green finding was identified for a failure to have adequate work orders to properly configure and post maintenance test the volume control tank (VCT) level comparator module. The licensee's procedure ADM-NGGC-0104, Work Implementation and
Region: II | Robinson | 31518 | 09/30/2010 11/12/2010 | 2010004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to design and implement a simulator model that demonstrated reference plant response |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.11Q | A self-revealing Green NCV of 10 CFR 55.46(c), "Simulation Facilities", was identified for a plant referenced simulator used for administration of operating tests not correctly modeling the reference plant. A loss of electrical power that resulted in a lo
Region: II | Robinson | 31519 | 09/30/2010 11/12/2010 | 2010004-03 | NRC | FIN | Initiating Events | Green | Deficiencies in non safety-related cable installation result in fire and rector trip |  |  | TE?: N | 05000261 Robinson 2 |  | NONE | A self-revealing Green finding was identified for the licensee's failure to adequately follow guidance in a design change package for the installation of non safety-related 4kV cables. This resulted in cables with design features inappropriate for the app
Region: II | Robinson | 31532 | 09/30/2010 11/12/2010 | 2010004-04 | NRC | NCV | Initiating Events | Green | Failure to establish an adequate PATH-1 emergency operating procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71153 | The inspectors identified an apparent violation (AV) of Technical Specifications (TS) 5.4.1, "Procedures", for the licensee's failure to establish and maintain an adequate emergency procedure that ensured reactor coolant pump (RCP) seal cooling was mainta
Region: II | Robinson | 31509 | 08/26/2010 10/08/2010 | 2010006-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Correct a Control Power Fuse Defect in 4kV Breaker 52/24 |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000261 Robinson 2 |  | 71152B | A self-revealing finding of very low safety significance was identified for the licensee's failure to follow the site's CAP procedure, CAP-NGGC-0200, "Corrective Action Program," Revision 26; in that a degraded control power condition for the non-vital 4k
Region: II | Robinson | 31508 | 06/30/2010 07/28/2010 | 2010003-01 | NRC | NCV | Initiating Events | Green | Failure to determine the cause of and take corrective actions to preclude repetition of an identified programmatic deficiency in foreign-material-exclusion controls. |  |  | TE?: N | 05000261 Robinson 2 |  | 71152 | Green. The inspectors identified a violation of 10 CFR 50, Appendix B, Criterion XVI, for the licensee's failure in 2004 to determine the cause of a programmatic deficiency in foreign-material-exclusion (FME) controls, which resulted in steam generator tu
Region: II | Robinson | 31502 | 03/31/2010 04/30/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inaccurate Drawings Result In Loss of RWST Level Indication Due to Freezing |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.15 | A self-revealing non-cited violation of Technical Specification 5.4.1, Procedures, was identified in that the licensee used inaccurate drawings to hang clearances on freeze protection circuits which resulted in the Refueling Water Storage Tank (RWST) leve
Region: II | Robinson | 31503 | 03/31/2010 04/30/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | "A" Emergency Diesel Generator Fuel Oil Transfer Pump Power Supply Cable Subjected to Continuous Submersion in Water Design Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71111.06 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, in that the licensee failed to maintain a safety-related cable in an environment for which it was designed. Specifically, the "A" Emergency Diesel (EDG) Fuel Oil
Region: II | Robinson | 31494 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | FIN | Mitigating Systems | Green | Failure To Identify Oil Leakage On A Operating Charging Pump |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.15 | The inspectors identified a Green finding for the licensee's failure to identify an oil leak on the "A" charging pump. This failure was determined to be a performance deficiency with respect to licensee procedure OMM-001-11, "Logkeeping," which requires o
Region: II | Robinson | 31488 | 06/30/2009 07/29/2009 | 2009003-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to properly restore service water to the evaporative air coolers resulting in emergency diesel generator inoperability |  | H.4(a) Human Error Prevention | TE?: N | 05000261 Robinson 2 |  | 71111.15 | A self-revealing finding was identified for the licensee's failure to follow procedures while restoring auxiliary building evaporative air coolers to service. Although a violation of regulatory requirements was not identified, this failure was a performan
Region: II | Robinson | 31489 | 06/30/2009 07/29/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Failure to follow procedures while performing maintenance on an emergency diesel generator. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000261 Robinson 2 |  | 71111.15 | The inspectors identified a green non-cited violation of Technical Specification (TS) 5.4.1, Administrative Controls (Procedures) associated with two events in which maintenance technicians performed maintenance on the A emergency diesel generator (EDG) w
Region: II | Robinson | 31493 | 06/30/2009 07/29/2009 | 2009003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to address environmental conditions associated with freeze-protection temperature sensors |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71152 | A green self-revealing finding was identified for the licensee's failure to identify the environmental conditions that temperature sensors in certain freeze-protection circuits could experience after routine installation of cold-weather enclosures during
Region: II | Robinson | 31480 | 03/31/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to meet the required actions of TS 3.8.1 for condition B |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71111.15 | Green. The inspectors identified a Green non-cited violation of Technical Specification 3.8.1, for the licensee's failure to meet the required actions of TS 3.8.1 for one inoperable emergency diesel generator (EDG), which are, in part, that within 24 hour
Region: II | Robinson | 31487 | 03/31/2009 04/30/2009 | 2009002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate procedures produced conditions which caused a reactor trip |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000261 Robinson 2 |  | 71153 | Green. A self-revealing finding was documented for the licensee's failure to provide adequate procedures for maintenance and installation of the main generator and exciter. As a result, work activities using those procedures produced conditions which led
Region: II | Robinson | 31478 | 09/30/2008 10/24/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately assess risk when assuming availability prior to performing post maintenance testing. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) for the failure on August 14 to adequately assess plant risk as Yellow after post-maintenance valve lineups failed to restore service water cooling to the B emergency diesel
Region: II | Robinson | 31479 | 09/30/2008 10/24/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to maintain emergency diesel generator service water valve configuration control |  | H.3(b) Work Activity Coordination | TE?: N | 05000261 Robinson 2 |  | 71111.19 | The inspectors identified a Green NCV of Technical Specification 5.4.1 for the failure on August 11 to maintain configuration control of the service water system for the B emergency diesel generator (EDG) when a service-water isolation valve to the EDG wa
Region: II | Robinson | 31476 | 06/30/2008 07/21/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to manage the increase in plant risk by failing to implement risk-management actions prior to performing switchyard maintenance activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000261 Robinson 2 |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) for the failure to protect the Emergency Diesel Generators (EDGs) and Auxiliary Feedwater (AFW) pumps during maintenance activities involving the operation of bucket trucks
Region: II | Robinson | 31477 | 06/30/2008 07/21/2008 | 2008003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to barricade and conspicuously post a High Radiation Area during refueling outage 24 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71152 | The inspectors identified a Green non-cited violation of Technical Specification (TS) 5.7.1 for the failure to barricade and conspicuously post a High Radiation Area (HRA) during refueling outage 24. The finding is more-than-minor because the area radi
Region: II | Robinson | 31475 | 03/31/2008 04/29/2008 | 2008002-02 | NRC | NCV | MISC | Green | Failure of the licensee to assess the increased risk resulting from removing a boric acid injection path from service |  | H.3(a) Work Planning | TE?: N | 05000261 Robinson 2 |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(4) for the failure of the licensee to perform a risk assessment on March 10, 2008, before establishing maintenance boundaries which removed a boric acid injection flow path from serv
Region: II | Robinson | 31473 | 12/31/2007 01/25/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Determine the Cause of a Failure of the Steam-Driven Auxiliary Feedwater Pump to Start |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI for the licensee's failure in 2005 to determine the cause of a failure of the steam-driven auxiliary feedwater pump to start, thereby allowing a subsequent similar fai
Region: II | Robinson | 31471 | 08/17/2007 09/21/2007 | 2007006-01 | NRC | FIN | Mitigating Systems | Green | Failure to install Thermal Overload (TOL) protection on the 'D' deep well pump |  |  | TE?: N | 05000261 Robinson 2 |  | 7111121 | The team identified a finding having very low safety significance (Green) involving the failure of the licensee to meet a self imposed standard. The licensee committed in modification package EC 59037, "Install 'D' Deep Well Pump," to meet or exceed the r
Region: II | Robinson | 31470 | 03/31/2007 04/20/2007 | 2007002-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide Adequate Respiratory Protection Equipment for Emergency Response |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000261 Robinson 2 |  | NONE | An NRC-identified non-cited violation of 10 CFR 50.47(b)(10) was identified for the failure to provide adequate respiratory protection equipment for emergency response, compromising the protective actions developed for the plume exposure pathway for emerg
Region: II | Robinson | 31466 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent a Repetitive Failure of a Safety-Related Pump's Motor Controller |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, for failure to identify the cause and take corrective action to prevent recurrence for a significant condition adverse to quality, in that the lic
Region: II | Robinson | 31460 | 06/30/2006 07/28/2006 | 2006003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Meet Technical Specification Requirements for Radiation Protection Manager Qualification |  |  | TE?: N | 05000261 Robinson 2 |  | 7112101 | The inspectors identified a non-cited violation (NCV) of Technical Specifications (TS) 5.3.1 for failure to ensure the Manager of Radiation Control function met the minimum qualification requirements specified in ANSI/ANS 3.1-1981, American National Stand
Region: II | Robinson | 31459 | 03/31/2006 04/30/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Performance of Safety-Related Breaker Effectively Controlled |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2) for failure to demonstrate that the performance of a safety-related breaker was being effectively controlled through the performance of appropriate preventive maintenance, in that repet
Region: II | Robinson | 124604 | 05/14/2019 |  |  | LIV |  | Green | Inadequate Surveillance for Control Room Envelope |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.22
Region: II | Robinson | 126017 | 11/14/2019 |  |  | LIV |  | Green | Failure to Maintain Adequate Environment for Class 1E Electrical Cables |  |  | TE?: N | 05000261 Robinson 2 |  | 71111.06
Region: II | Saint Lucie | 126167 | 12/31/2019 02/13/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Failure to meet the Transient Combustible Requirements Specified by NFPA 805 |  | NPP | TE?: N | 05000389 Saint Lucie 2 | Protection Against External Factors | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.48(c), “National Fire Protection Standard NFPA 805,” requirements. Specifically, the licensee failed to comply with transient combustible control requirements in an ordinary fire zo
Region: II | Saint Lucie | 126336 | 12/31/2019 02/13/2020 | 2019004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to properly follow licensee procedure ENG-QI-1.0 “Quality Instruction Nuclear Engineering Design Control,” during a modification of reactor coolant pump (RCP) motor component cooling water (CCW) piping. |  | NPP | TE?: N | 05000335 Saint Lucie 1 | Design Control | 71153 | A self-revealed green finding was identified when the licensee failed to properly follow licensee procedure ENG-QI-1.0 “Quality Instruction Nuclear Engineering Design Control,” during a modification of RCP motor CCW piping during the 2010 1A1 RCP refurbis
Region: II | Saint Lucie | 125895 | 09/30/2019 11/14/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to accurately translate the static head loss to calculate the maximum allowable biological fouling of the ultimate heat sink culverts |  | NONE | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 | Protection Against External Factors | 71111.07T | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III was identified for the licensee's failure to accurately translate the static head loss, associated with the design basis water level of Big Mud Creek, to the calculations that establ
Region: II | Saint Lucie | 124461 | 04/04/2019 04/22/2019 | 2019010-01 | NRC | NCV | Initiating Events | Green | Failure to Consider Valve Stability During Modification to Pressurizer Safety Valves |  | NPP | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 | Design Control | 71111.21M | The inspectors identified a Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to include appropriate limitations on
Region: II | Saint Lucie | 124450 | 03/31/2019 05/09/2019 | 2019001-01 | NRC | NCV | Initiating Events | Green | Failure to Meet the Transient Combustible Requirements Specified by NFPA 805 |  | P.3 - Resolution | TE?: N | 05000335 Saint Lucie 1 | Protection Against External Factors | 71111.05Q | The NRC identified a Green non-cited violation (NCV) of 10 CFR 50.48(c), “National Fire Protection Standard NFPA 805,” requirements. Specifically, the licensee failed to comply with transient combustible control requirements in a high risk fire zone as r
Region: II | Saint Lucie | 24700 | 08/17/2018 11/08/2018 | 2018003-01 | NRC | NCV | Initiating Events | Green | Failure to meet the Transient Combustible Requirements Specified by NFPA 805 |  | H.5 - Work Management | TE?: N | 05000389 Saint Lucie 2 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.48(c), “National Fire Protection Standard NFPA 805,” requirements. Specifically, the licensee failed to comply with transient combustible control requirements in high risk fire zones
Region: II | Saint Lucie | 23521 | 03/31/2018 05/01/2018 | 2018001-01 | Self - Revealed | FIN | Mitigating Systems | Green | Improper Evaluation of LCV-9005 position setpoints Leads to AFAS |  | NPP | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealed Green finding was identified when the licensee failed to properly evaluate a discrepancy between ‘A’ and ‘B’ feedwater bypass level control valve positions, as required by licensee procedures PI-AA-205, “Condition Evaluation and Corrective
Region: II | Saint Lucie | 22625 | 12/31/2017 01/29/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Reactor System Trip Process for Inoperable Channel Results in Operation in a Condition Prohibited by Technical Specifications |  | H.1 - Resources | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | A Green, self-revealing NCV of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures and Drawings,” was identified for the licensee’s failure to have an adequate procedure for reducing the trip setpoint of th
Region: II | Saint Lucie | 22626 | 12/31/2017 01/29/2018 | 2017004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Surveillance Maintenance Procedure Resulting in a Condition Prohibited by Technical Specifications |  | H.12 - Avoid Complacency | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A Green, self-revealing, NCV of TS 6.8.1 was identified for the licensee’s failure to adequately implement a maintenance procedure during a monthly flow channel check for the 2C Auxiliary Feedwater (AFW) pump. Specifically, the licensee failed to implemen
Region: II | Saint Lucie | 23163 | 12/31/2017 01/29/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality |  | NPP | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | The NRC-identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Actions, failure to identify and correct a condition adverse to quality. The licensee failed to identify that their procedures lacked actions to
Region: II | Saint Lucie | 21632 | 09/30/2017 10/24/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Adequacy of Unit 2 Engineered Safeguards 4.16 kV Bus UV Protection Design |  | NPP | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified for the licensee’s failure to verify the adequacy of the design of Unit 2, engineered safeguards 4.16 kV bus under voltage prot
Region: II | Saint Lucie | 14944 | 03/31/2017 05/09/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Adding an Incorrect Lubrication Oil to the 1B CS Motor Inboard Bearing |  | H.12 Avoid Complacency | TE?: N | 05000335 Saint Lucie 1 |  | 71111.15 | Green: An NRC-identified Green, non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures and Programs," was identified for the licensee's failure to establish, implement, and maintain written procedures covering activities referenced i
Region: II | Saint Lucie | 14942 | 09/30/2016 11/10/2016 | 2016003-01 | NRC | NCV | Barrier Integrity | Green | Reactor Coolant System Leakage Technical Specification Violation |  | H.14 Conservative Bias | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | Green: An NRC-identified Green non-cited violation (NCV) of Unit 1 Technical Specification 3.4.6.2 "Reactor Coolant System Leakage" was identified. Specifically, the licensee failed to enter TS 3.4.6.2 Action 'c" for reactor coolant system pressure isolat
Region: II | Saint Lucie | 14938 | 06/24/2016 08/08/2016 | 2016011-03 | NRC | NCV | Initiating Events | Green | Failure to Meet the Combustible Control Requirements Specified By NFPA 805 Section 3.3.1.2(1) |  | H.5 Work Management | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.05XT | Green. Inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50.48(c), "National Fire Protection Association Standard NFPA 805," for the licensee's failure to comply with the combustible control requirements for work platforms that were locat
Region: II | Saint Lucie | 14928 | 04/29/2016 06/09/2016 | 2016010-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Comply with TS requirements for Containment High-Range Radiation Monitors (CHRRM) |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.21N | Green: The inspectors identified a green non-cited violation of Technical Specification (TS) 3.3.3.1 for failing to take the required TS actions after identifying a condition adverse to quality that affected the operability of the containment high range
Region: II | Saint Lucie | 14929 | 04/29/2016 06/09/2016 | 2016010-02 | NRC | NCV | Mitigating Systems | Green | Green: The inspectors identified a green non-cited violation of Technical Specification (TS) 3.3.3.1 for failing to take the required TS actions after identifying a condition adverse to quality that |  | H.6 Design Margins | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.21N | Green: The inspectors identified three examples of a green non-cited violation of Title 10 Code of Federal Regulations (CFR) Part 50.49.e.(5) "aging" for the licensee's failure to assure conformance with the qualification procedures and methods specifie
Region: II | Saint Lucie | 14935 | 04/29/2016 06/09/2016 | 2016010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Define, Justify, and Document Activation |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.21N | Green: The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify, justify, and document an activation energy used to determine the thermal lifespan of safety rela
Region: II | Saint Lucie | 14899 | 03/31/2016 05/03/2016 | 2016001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area |  | H.8 Procedure Adherence | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71124.07 | A self-revealing, Green non-cited violation (NCV) of Technical Specifications (TS) 6.12.1.b occurred when a worker entered a high radiation area (HRA) without being made knowledgeable of dose rates in the area prior to entry. Specifically, on 11/09/2015,
Region: II | Saint Lucie | 14900 | 03/31/2016 05/03/2016 | 2016001-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Detailed Work Instructions Resulted in a Unit Transient (Section 4OA2.2) |  | H.11 Challenge the Unknown | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | Green. A self-revealing finding was identified for the licensee's failure to provide adequate work instructions for the circulating water system 1B1 traveling water screen drive motor replacement. Specifically, the inadequate work instructions resulted in
Region: II | Saint Lucie | 14911 | 03/31/2016 05/03/2016 | 2016001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Prevent Failure of the 2C ICW Pump Motor (Section 4OA2.3) |  | P.2 Evaluation | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | Green. A self-revealing, NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to implement corrective actions to prevent failure of the 2C intake cooling water (ICW) pump. The failure was a resul
Region: II | Saint Lucie | 14912 | 03/04/2016 04/11/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Elevated Temperature Effects on MOV Actuator Output Capability |  | P.2 Evaluation | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111121 | Green: The NRC identified a non-cited violation of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to consider the impact of elevated ambient temperatures on motor operated valv
Region: II | Saint Lucie | 14913 | 03/04/2016 04/11/2016 | 2016008-02 | NRC | NCVIV | MISC | Green | Failure to Update UFSAR to Reflect Station Blackout Coping Time Basis |  |  | TE?: Y SL-IV-NCVIV | 05000335 Saint Lucie 1 |  | 7111121 | SL-IV: The NRC identified a non-cited violation of 10 CFR 50.71, "Maintenance of Records, Making of Reports," for the licensee's failure to update the Updated Final Safety Analysis Report (UFSAR) to reflect the offsite power design characteristic group
Region: II | Saint Lucie | 14919 | 03/04/2016 04/11/2016 | 2016008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of 125VDC MCCBs |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 7111121 | Green: The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to perform testing for safety-related 125 volts direct current (VDC) molded case circuit breakers (MCCBs) to detect
Region: II | Saint Lucie | 14920 | 03/04/2016 04/11/2016 | 2016008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Degraded Condition of Unit 1 Electrical Equipment Room Supply Fan Gravity Dampers |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71111.21M | Green: The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify a condition adverse to quality, which prevented the Unit 1 electrical equipment room (EER) supply f
Region: II | Saint Lucie | 14921 | 03/04/2016 04/11/2016 | 2016008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Design of Unit 1 Electrical Equipment Room Ventilation System |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 7111121 | Green: The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of the Unit 1 electrical equipment room (EER) ventilation system design when performing a d
Region: II | Saint Lucie | 14922 | 03/04/2016 04/11/2016 | 2016008-06 | NRC | FIN | Mitigating Systems | Green | Failure to Provide a Missile-Protected Intertie |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71111.21M | Green: The NRC identified a finding for the licensee's failure to properly provide a completely missile-protected intertie from the Unit 1 diesel oil transfer pumps to the Unit 2 diesel oil storage tanks. The licensee entered the issue into the correcti
Region: II | Saint Lucie | 14894 | 12/31/2015 02/05/2016 | 2015004-01 | NRC | FIN | Mitigating Systems | Green | NRC Biennial Written Examinations Did Not Meet Qualitative Standards |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.11B | An NRC-identified finding related to 10 CFR 55.59, "Requalification," was identified based on a determination that greater than 20 percent of the 2014 biennial written exam question sampled for review were flawed. The finding did not involve a violation o
Region: II | Saint Lucie | 14893 | 12/31/2015 02/05/2016 | 2015004-02 | NRC | FIN | Mitigating Systems | Green | Non-willful Compromise of a Remedial Examination Required by 10 CFR 55.59 Affected the Equitable and Consistent Administration of the Exam |  | H.8 Procedure Adherence | TE?: Y SL-IV-FIN | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.11B | An NRC-identified severity level IV (SLIV) NCV of 10 CFR 55.49, "Integrity of examinations and tests" was identified based on a determination that a non-willful compromise of a remedial examination required by 10 CFR 55.59 affected the equitable and consi
Region: II | Saint Lucie | 14880 | 12/31/2015 02/05/2016 | 2015004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Prevent Fouling of the CCW HXs (Section 4OA2.3) |  | P.3 Resolution | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | Green: An NRC-identified NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to implement corrective actions to prevent fouling of the 2B component cooling water (CCW) heat exchanger (HX) that r
Region: II | Saint Lucie | 14881 | 12/31/2015 02/05/2016 | 2015004-04 | NRC | NCV | Mitigating Systems | Green | Procedural Non-compliances Relating to Installed Scaffold Located Near Safety-related SSCs (Section 4OA2.4) |  | P.3 Resolution | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | A Green NRC-identified NCV of TS 6.8.1, "Procedures and Programs," was identified for the licensee's failure to properly implement written procedures covering activities referenced in NRC Regulatory Guide 1.33, Revision 2, dated February 1978. Specificall
Region: II | Saint Lucie | 14895 | 12/31/2015 02/05/2016 | 2015004-05 | NRC | NCV | Initiating Events | Green | Failure to Verify the Adequacy of the Unit 1 and Unit 2 Steam Generator Tube-to-Tubesheet Welds Design |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | An NRC-identified, Non-cited Violation of 10 CFR Appendix B, Criterion III, "Design Control," was identified for the failure to verify the adequacy of the Unit 1 and Unit 2 replacement steam generators (RSGs) design with respect to the requirements in the
Region: II | Saint Lucie | 14874 | 09/30/2015 11/05/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Unsecured Utility Cart With An Unrestrained Operating Pedestal Fan Near Safety-related ECCS Equipment (Section 1R15) |  | H.9 Training | TE?: N | 05000335 Saint Lucie 1 |  | 71111.15 | NRC-identified, NCV of Technical Specification (TS) 6.8.1, Procedures and Programs, was identified for the licensee's failure to implement written procedures covering activities referenced in NRC Regulatory Guide 1.33, Revision 2, dated February 1978. Spe
Region: II | Saint Lucie | 14875 | 08/09/2015 11/05/2015 | 2015003-04 | NRC | NCV | Initiating Events | Green | Failure to Follow Reactor Protection System Surveillance Procedure Resulting in Reactor Plant Trip (Section 4OA3.3) |  | H.12 Avoid Complacency | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | A Green, self-revealing, NCV of TS 6.8.1 was identified for the licensee's failure to adequately implement surveillance procedures during reactor protection system (RPS) testing. Specifically, the licensee failed to implement as-written operations surveil
Region: II | Saint Lucie | 14857 | 06/30/2015 08/04/2015 | 2015002-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Assess Potential Gaseous Effluents Released from Containment Equipment Hatch Openings during a Loss of Negative Pressure |  | P.5 Operating Experience | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | NONE | The inspectors identified a Green non-cited violation of Technical Specification 6.8.1 for the failure to implement procedures for the monitoring, evaluating, and reporting of gaseous effluents in accordance with the methodology in the Off-Site Dose Calcu
Region: II | Saint Lucie | 14861 | 06/30/2015 08/04/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification 3.0.3 |  | P.2 Evaluation | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | The NRC identified a non-cited violation of Technical Specification (TS) 3.0.3 for the licensee's failure to take the required actions to shut down the plant in a timely manner. The licensee's failure to perform an adequate operability evaluation in accor
Region: II | Saint Lucie | 14854 | 03/30/2015 05/06/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessments on the Emergency Core Cooling System |  | H.9 Training | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(4), for the licensee's failure to conduct adequate risk assessments prior to pe
Region: II | Saint Lucie | 14843 | 03/06/2015 04/17/2015 | 2015007-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Submit a License Amendment Request for Unit 1 RPS |  | H.3 Change Management | TE?: Y SL-IV-NCVIV | 05000335 Saint Lucie 1 |  | 71111.17T | Severity Level IV. An NRC-identified severity level IV (SL IV) non-cited violation (NCV) of 10 CFR 50.59(c)(2)(ii) and an associated finding of very low safety significance (Green) was identified for the licensee's failure to obtain a license amendmen
Region: II | Saint Lucie | 14844 | 03/06/2015 04/17/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Procedural Limitations to Prevent Exceeding Non-LOCA Event Analysis Assumptions for Steam Generator Blowdown Flow Rate |  | H.6 Design Margins | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.17T | Green. An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to assure that design basis assumptions for steam generator blowdown (SGBD) flow rate were translated
Region: II | Saint Lucie | 14855 | 01/16/2015 05/06/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Procedural Non Compliances Relating to Temporarily Installed Ladders Located Near Safety-related SSCs |  | P.1 Identification | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | The NRC identified a Green, non-cited violation of Technical Specification (TS) 6.8.1, Procedures and Programs, for the licensee's failure to establish, implement, and maintain written procedures covering activities referenced in NRC Regulatory Guide 1.
Region: II | Saint Lucie | 14838 | 12/31/2014 01/30/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Work Instructions During Installation of Unit 2 Vent Valve V3811 |  | H.8 Procedure Adherence | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," resulted from the licensee's failure to implement work order instructions to install Unit 2 safety-related vent valve V3811 in acc
Region: II | Saint Lucie | 14835 | 09/30/2014 10/20/2014 | 2014004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Foreign Material Exclusion Requirements in Reactor Vessel Maintenance Procedures |  | H.1 Resources | TE?: N | 05000389 Saint Lucie 2 |  | NONE | A self-revealing non-cited violation (NCV) of Unit 2 Technical Specification 6.8.1.a was identified for the licensee's failure to follow the requirements in reactor vessel maintenance procedures, to exclude foreign material from the reactor coolant system
Region: II | Saint Lucie | 14831 | 09/30/2014 10/20/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Reasonable Maintenance Effectiveness Demonstration for the ECCS Floor Drain Valve System |  | P.4 Trending | TE?: N | 05000335 Saint Lucie 1 |  | 71111.12 | An NRC-identified non-cited violation (NCV) of 10 CFR 50.65(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," resulted from the licensee's failure to establish a technically justifiable and reasonable maintenan
Region: II | Saint Lucie | 14820 | 06/30/2014 07/25/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow the nuclear design control procedure for auxiliary feedwater valves |  | H.14 Conservative Bias | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | . A self-revealing, non-cited violation (NCV) of Technical Specification (TS) 6.8.1, was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33, Revision 2,
Region: II | Saint Lucie | 14821 | 06/30/2014 07/25/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Failure to design the emergency diesel generators to operate under worst case environmental conditions |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | An NRC-identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified. The licensee's failure to translate design control measures to ensure operation of Unit 2 emergency diesel generators (EDGs) under wo
Region: II | Saint Lucie | 14814 | 03/31/2014 05/01/2014 | 2014002-01 | NRC | NCV | Occupational Radiation Safety | Green | Noncompliance with Barricading and Posting Requirements |  | H.2 Field Presence | TE?: N | 05000389 Saint Lucie 2 |  | 71124.01 | A Green self-revealing non-cited violation (NCV) of 10 CFR 20.1501(a) and Technical Specification (TS) 6.12.1 was identified for failure to perform radiological surveys to ensure that the potential radiological hazards and extent of radiation levels were
Region: II | Saint Lucie | 14813 | 03/31/2014 05/01/2014 | 2014002-03 | NRC | FIN | Initiating Events | Green | Failure to Provide Detailed Work Instructions Resulted in Degraded Debris Filter System Performance and resulted in a Manual Reactor Trip |  | H.7 Documentation | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing Green finding was identified for the licensee's failure to provide adequate work instructions. The maintenance work instructions for a debris filter system (DFS) backwash valve motor operator did not contain adequate details to ensure the
Region: II | Saint Lucie | 14807 | 02/07/2014 03/21/2014 | 2014007-01 | NRC | NCV | Initiating Events | Green | Inadequate Corrective Actions to Address Water Intrusion in the HCV-09-2A Relay Box |  | P.2 Evaluation | TE?: N | 05000389 Saint Lucie 2 |  | 71152B | A self-revealing, green Non-Cited Violation (NCV) of 10 CFR Part 50 Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to correct an identified condition adverse to quality associated with the water intrusion into the
Region: II | Saint Lucie | 14808 | 02/07/2014 03/21/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Seismic Restraining Procedures on Ladders Located Near Safety-Related Equipment |  | P.3 Resolution | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152B | A green NRC identified non-cited violation (NCV) of Technical Specification 6.8.1, Procedures and Programs, was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory
Region: II | Saint Lucie | 14809 | 02/07/2014 03/21/2014 | 2014007-03 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Refueling Operations Procedure Resulting in a Fuel Mishandling Event |  | H.4 Teamwork | TE?: N | 05000389 Saint Lucie 2 |  | 71152B | A green self-revealing, Non-Cited Violation (NCV) of Technical Specification (TS) 6.8.1, Procedures and Programs, was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regul
Region: II | Saint Lucie | 14801 | 12/31/2013 01/31/2014 | 2013005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Use Only NIOSH Certified Respiratory Protection Equipment |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71124.03 | A self-revealing Green non-cited violation (NCV) of 10 CFR Part 20.1703(a) was identified for the use of respiratory protection equipment that had not been certified as safe by the National Institute for Occupational Safety and Health (NIOSH). The license
Region: II | Saint Lucie | 14802 | 12/31/2013 01/31/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Implement Appropriate Corrective Actions for AFW System Corrosion |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee failed to identify localized corrosion on the discharge piping for the 1C auxiliary feedwater pump that
Region: II | Saint Lucie | 14795 | 10/09/2013 10/30/2013 | 2013008-01 | NRC | FIN | Mitigating Systems | Green | Failure to Meet Training Program Standards on Job Performance Measures for the Annual Licensed Operator Requalification Operating Examination |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.11B | The inspectors identified a finding associated with the licensee's failure to meet training program standards in the development of job performance measures (JPMs) for the licensed operator requalification annual operating tests. The inspectors identified
Region: II | Saint Lucie | 14797 | 09/30/2013 10/29/2013 | 2013004-02 | Self - Revealed | FIN | Initiating Events | Green | Partial loss of offsite power due to non-segregated bus failure |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71153 | A self-revealing finding was identified for the licensee's failure to establish adequate preventive maintenance (PM) activities for both units' startup transformers (SUTs) 6.9kV non-segregated bus runs in accordance with site PM program requirements. As a
Region: II | Saint Lucie | 14800 | 09/30/2013 10/29/2013 | 2013004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency diesel generator inoperable for a period greater than the allowed outage time |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing non-cited violation of Technical Specification (TS) 3.8.1.1.b was identified due to the licensee operating with an inoperable emergency diesel generator (EDG) for longer than the allowed outage time (AOT) of 14 days without taking the req
Region: II | Saint Lucie | 14791 | 06/30/2013 07/30/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor SSCs under 10 CFR 50.65(a)(1) |  | P.1(b) Trend Performance CAP | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.12 | The inspectors identified a Green non-cited violation associated with the licensee's failure to follow the requirements of 10 CFR 50.65(a)(2), Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants. Corrective actions include
Region: II | Saint Lucie | 14792 | 06/30/2013 07/30/2013 | 2013003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate MSIV Modification Installation and Test |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control was identified for the licensee's failure to specify adequate modification installation and testing criteria to ensure the Unit 1 modified main steam i
Region: II | Saint Lucie | 14790 | 05/13/2013 06/25/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Feasibility of All OMAs Used as Compensatory Measures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.05T | A Green NRC-identified non-cited violation of St. Lucie Unit 1 and Unit 2 operating license conditions 3.E was identified for the licensee's failure to comply with the requirements of the St. Lucie Fire Protection Program for verifying the feasibility of
Region: II | Saint Lucie | 12790 | 03/31/2013 04/25/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality for Alignment of the Safety-Related Refueling Water Tank to a Non-Seismic Spent Fuel Pool Purification system |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | A Green NRC identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for the failure to promptly identify and correct a condition adverse to quality (CAQ) involving alignment of the safety-related refueling
Region: II | Saint Lucie | 12789 | 03/31/2013 04/25/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Reactor Auxiliary Building Penetrations were Adequately Flood Protected |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71153 | A Green NRC identified non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to ensure that all below grade Unit 1 and 2 reactor auxiliary building penetrations were adequately sealed as req
Region: II | Saint Lucie | 12784 | 12/31/2012 01/30/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to follow seismic restraining procedures on ladders located near safety-related equipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71151 | An NRC identified non-cited violation (NCV) of Technical Specification 6.8.1, was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33, Revision 2, dated
Region: II | Saint Lucie | 12785 | 12/31/2012 01/30/2013 | 2012005-02 | Self - Revealed | NCV | Initiating Events | Green | Missing relay cover results in inadvertent emergency diesel generator actuation |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71151 | A self-revealing, non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion XVI Corrective Action was identified for failure to promptly identify and correct a missing cover on a safety-related undervoltage relay. The licensee's failure to identify the
Region: II | Saint Lucie | 12786 | 12/18/2012 02/01/2013 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Severe Weather Mitigation |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111121 | The team identified a non-cited violation of Technical Specification 6.8, "Procedures and Programs," for an inadequate technical specification required procedure to combat a loss of feedwater or feedwater system failure. Abnormal operating procedure 1-AOP
Region: II | Saint Lucie | 12782 | 10/12/2012 11/16/2012 | 2012009-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Implement Design Changes Procedure |  | H.3(a) Work Planning | TE?: N | 05000335 Saint Lucie 1 05000335 Saint Lucie 1 |  | 95002 | A self-revealing finding with two examples was identified for the licensee's failure to adequately implement their design change process for post-modification testing (PMT). In the first example, the PMT procedure was not adequate for post-modification te
Region: II | Saint Lucie | 12778 | 09/30/2012 10/30/2012 | 2012004-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to ship radioactive material in accordance with DOT regulations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71124.08 | A self-revealing, Green non-cited violation (NCV) of 10 CFR 71.5 was identified for the licensee's failure to ship radioactive material in accordance with Department of Transportation (DOT) requirements as specified in 49 CFR Parts 171-180. Specifically,
Region: II | Saint Lucie | 12779 | 09/30/2012 10/30/2012 | 2012004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to implement procedure EN-AA-205, Design Change Packages |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A self-revealing, non-cited violation (NCV) of Technical Specification (TS) 6.8.1, was identified which requires written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33, Revision 2, dated
Region: II | Saint Lucie | 12744 | 06/30/2012 07/30/2012 | 2012003-01 | NRC | NCV | Barrier Integrity | Green | Failure to perform examinations of reactor pressure vessel supports |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000335 Saint Lucie 1 |  | NONE | A Green, NRC identified, non-cited violation (NCV) of Code of Federal Regulation (CFR) 10 CFR Part 50.55a, Codes and Standards, involving the licensee's failure to include the reactor pressure vessel supports in the scope of the licensee's inservice inspe
Region: II | Saint Lucie | 12745 | 06/30/2012 07/30/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to follow the design control procedure when removing Unit 1 EDG electrical cabinet seismic bolting |  | H.4(b) Procedural Compliance | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A Green, NRC identified, non-cited violation (NCV) of Technical Specification (TS) 6.8.1, was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33, Revisi
Region: II | Saint Lucie | 12746 | 04/20/2012 06/01/2012 | 2012007-01 | NRC | FIN | Initiating Events | Green | Failure to perform preventive maintenance on the 1B condensate pump discharge check valve |  | H.3(b) Work Activity Coordination | TE?: N | 05000335 Saint Lucie 1 |  | NONE | An NRC identified finding was identified for the licensee's failure to perform a preventive maintenance (PM) activity within its prescribed frequency on the 1B condensate pump discharge check valve. Consequently, the valve failed after a reactor trip and
Region: II | Saint Lucie | 12750 | 04/20/2012 06/01/2012 | 2012007-02 | NRC | NCV | Initiating Events | Green | Failure to correct a LPSI pump design deficiency |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000389 Saint Lucie 2 |  | NONE | An NRC-identified Green NCV of 10 CFR Part 50 Appendix B, Criterion XVI, Corrective Actions was identified for the licensee's failure to correct an identified condition adverse to quality associated with Low Pressure Safety Injection (LPSI) pump casing di
Region: II | Saint Lucie | 12751 | 04/20/2012 06/01/2012 | 2012007-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to implement timely corrective actions resulted in a plant trip |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | NONE | A self-revealing finding was identified for the licensee's failure to implement timely corrective actions. Specifically, after the overheating and failure of a Circulating Water Pump (CWP) motor resulted in an unplanned reactor down power, the licensee fa
Region: II | Saint Lucie | 12768 | 04/20/2012 06/01/2012 | 2012007-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement vendor technical manual recommendations to inspect EDG immersion heaters |  | H.3(b) Work Activity Coordination | TE?: N | 05000335 Saint Lucie 1 |  | NONE | A self revealing potentially greater than Green AV of Technical Specification 6.8.1.a was identified for failure to establish adequate maintenance procedures associated with the emergency diesel generator (EDG) system. Specifically, station personnel fail
Region: II | Saint Lucie | 12769 | 04/20/2012 06/01/2012 | 2012007-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Vendor Described Preventive Maintenance on the Circulating Water Pump Motors |  |  | TE?: N | 05000335 Saint Lucie 1 |  | NONE | A self-revealing finding was identified for the licensee's failure to implement vendor recommended preventive maintenance requirements to monitor and trend motor stator temperatures using the installed resistance temperature detector (RTDs) for the 1A2 Ci
Region: II | Saint Lucie | 12743 | 03/31/2012 04/26/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Reactor Protection System Surveillance Procedure Resulting in Reactor Plant Trip |  | H.4(b) Procedural Compliance | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | Green. A Green, self-revealing, non-cited violation (NCV) of Technical Specification (TS) 6.8.1 was identified which requires that written procedures be established, implemented, and maintained covering activities referenced in NRC Regulatory Guide 1.33,
Region: II | Saint Lucie | 12740 | 12/31/2011 01/30/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Procedure for Evaluation of Past Operability |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a NCV of Technical Specification (TS) 6.8.1 and Regulatory Guide (RG) 1.33 for the licensee failing to implement a written procedure for operability determinations. Safety related procedure EN-AA-203-1001, "Operability Determinat
Region: II | Saint Lucie | 12737 | 06/30/2011 07/28/2011 | 2011003-01 | NRC | FIN | Initiating Events | Green | Failure to Comply with Design Drawing Results in Main Steam Vent Line Failure and Subsequent Transient |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing finding of very low safety significance was identified following a rapid downpower and manual reactor trip of Unit 2 on May 16, 2011. Specifically, the licensee failed to comply with an approved design drawing during installation fabricat
Region: II | Saint Lucie | 12733 | 03/31/2011 04/29/2011 | 2011002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to perform adequate surveys to identify potential radiological hazards during valve repair in the 1B WGDT room ( |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71124.04 | A self-revealing non-cited violation (NCV) of 10 CFR Part 20.1501(a) was identified for failure to perform adequate surveys to verify radiological conditions within the Unit 1 "B" Waste Gas Decay Tank (WGDT) room prior to allowing workers to enter the are
Region: II | Saint Lucie | 12734 | 03/31/2011 04/29/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures and Guidelines to ensure RAB Doors are Completely Dogged Closed |  | H.4(a) Human Error Prevention | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | A NRC identified NCV of Technical Specification (TS) 6.8.1, which requires that written procedures be established, implemented, and maintained covering the activities in NRC Regulatory Guide 1.33, "Quality Assurance Program Requirements (Operation)," Appe
Region: II | Saint Lucie | 12730 | 12/31/2010 01/27/2011 | 2010005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality that Resulted in the 1C-AFW Pump Being Out ofService for Greater Than Its Allowed Outage Time |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A self-revealing Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to promptly identify and correct a condition adverse to quality (CAQ) that resulted in the 1C Auxili
Region: II | Saint Lucie | 12731 | 12/31/2010 01/27/2011 | 2010005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Take Timely and Effective Corrective Actions for ECCS Fan Damper Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee failing to take timely and effective corrective actions for Emergency Core Cooling System (ECCS) area exhaust fan damper louver failures resu
Region: II | Saint Lucie | 12724 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Identify and Correct a condition Adverse to Quality |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000389 Saint Lucie 2 |  | 71111.04Q | An NRC-identified NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for failure of the licensee to promptly identify and correct a condition adverse to quality (CAQ) associated with the Unit 2 reactor water tank isolation valve MV-07-1B
Region: II | Saint Lucie | 12725 | 09/30/2010 10/29/2010 | 2010004-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Installation ofPZ Safety Valves |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified regarding the licensee's failure to provide adequate guidance in a safety-related maintenance procedure to ensure pressurizer safety va
Region: II | Saint Lucie | 12726 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Restoration of Non-Essential CCW Flow Following SIAS |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71153 | An NRC-identified NCV of very low safety significance involving Technical Specification 6.8.1, for failure of the licensee to provide adequate procedures for restoration of non-essential component cooling water (CCW) following a Safety Injection Actuation
Region: II | Saint Lucie | 12727 | 09/30/2010 11/03/2010 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately monitor performance of the 2B EDG and 1C AFW pump as required by 10 CFR 50.65 |  | H.4(b) Procedural Compliance | TE?: N | 05000335 Saint Lucie 1 |  | 95002 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(2) for failure to demonstrate that the performance of the 2B Emergency Diesel Generator (EDG) and 1C Auxiliary Feedwater Pump (AFW) systems was effectively controlled by preventative main
Region: II | Saint Lucie | 12715 | 06/30/2010 07/28/2010 | 2010003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Operations Procedure Results in Loss of 1B 125 v DC Bus |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A self-revealing NCV of Technical Specification 6.8.1 was identified for an inadequate operating procedure which resulted in the loss of the 1B Direct Current (DC) vital electrical bus and unplanned entry into Technical Specification Action 3.9.8.2.a. for
Region: II | Saint Lucie | 12716 | 06/30/2010 07/28/2010 | 2010003-02 | Self - Revealed | NCV | Initiating Events | Green | Untimely Corrective Actions to Resolve Seat Leakage of Containment Spray Valves 2-MV-07-3/4 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure of the licensee to take timely and effective corrective actions to prevent seat leakage past containment spray isolation valves 2-MV-07-3 and 2-MV-07-4
Region: II | Saint Lucie | 12717 | 06/30/2010 07/28/2010 | 2010003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Take Timely and Effective Corrective Actions to Prevent RCS Pressure Boundary Leakage through the RCP Seal Lines |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified when a reactor coolant pump (RCP) seal line weld failure resulted in RCS pressure boundary leakage in July 2009. Specifically, the licensee failed to prevent t
Region: II | Saint Lucie | 12704 | 03/31/2010 04/28/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for 2A1 EDG Immersion Heaters |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000389 Saint Lucie 2 |  | 71111.15 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct a condition adverse to quality for degraded wiring in the 2A1 EDG immersion heater power circu
Region: II | Saint Lucie | 12708 | 03/31/2010 04/28/2010 | 2010002-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Main Steam Isolation Valve Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when safety related surveillance test procedure 2-OSP-08.01, "Main Steam Isolation Valves Periodic Test," was i
Region: II | Saint Lucie | 12709 | 03/19/2010 04/19/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to promptly correct a condition adverse to quality associated with degraded intake cooling water pump discharge check valves. |  | H.3(b) Work Activity Coordination | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71152B | The NRC identified a Green Non-cited Violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly correct a condition adverse to quality that being degraded check valves on the intake cooling water system af
Region: II | Saint Lucie | 12702 | 12/31/2009 01/20/2010 | 2009005-01 | NRC | NCV | Initiating Events | Green | Inadequate Safety-Related Maintenance Procedure to Properly Align the 2B2 Reactor Coolant Pump/Motor Shaft Coupling Assemblies |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | An inspector identified non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33 was identified for an inadequate safety-related maintenance procedure. Specifically, the inspectors identified that during reassembly of Reactor Coola
Region: II | Saint Lucie | 12686 | 12/03/2009 01/19/2010 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Meet the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1 Requirements for the Overpressure Protection for the CCW Surge Tank . |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to translate the design basis as specified in the license application into specifications, drawings, procedures, and instructions. The licensee
Region: II | Saint Lucie | 12688 | 12/03/2009 01/19/2010 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Safety-Related 125V DC System Design Basis Information Consistent with the Plant Configuration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 7111121 | The inspectors identified a finding involving a violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to maintain the safety-related 125V DC system design basis information consistent with the plant configuration. S
Region: II | Saint Lucie | 12675 | 09/30/2009 10/30/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Timely and Effective Corrective Actions to Prevent Recurrence of EDG Day Tank Level Switch Failures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A self-revealing Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified for failure of the licensee to take timely and effective corrective actions to prevent recurrence of Unit 1 emergency diesel generator (E
Region: II | Saint Lucie | 12671 | 06/30/2009 07/29/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment When Performing Weekly Pump Venting |  | H.3(a) Work Planning | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.13 | The inspectors identified NCV of 10 CFR 50.65 (a)(4) when the licensee did not perform an adequate risk assessment which resulted in an underestimation of the associated risk while performing weekly Emergency Core Cooling System (ECCS) pump venting. On Ap
Region: II | Saint Lucie | 12673 | 06/30/2009 07/29/2009 | 2009003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure When Placing Shutdown Cooling In-service |  | H.4(a) Human Error Prevention | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing NCV of Technical Specification (TS) 6.8.1.a and Regulatory Guide (RG) 1.33 was identified for the licensee failing to implement a written procedure for general plant operations. The normal operating procedure 2-NOP-03.05, "Shutdown Coolin
Region: II | Saint Lucie | 12674 | 06/30/2009 07/29/2009 | 2009003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Have a Fully Qualified and Active Licensed Operator at the Control Boards During Reactivity Manipulations |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing Non-Cited Violation (NCV) of 10 CFR 50.54(i), Conditions of Licenses, for failure to have a fully qualified and active licensed operator at the control boards during reactivity manipulations. On June 7, 2008, the Shift Manager (SM) of rec
Region: II | Saint Lucie | 12670 | 04/30/2009 06/10/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality |  | H.3(b) Work Activity Coordination | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.05T | The team identified two examples of a non-cited violation of St. Lucie's Unit 1 and Unit 2 Operating License Conditions 3.E for the licensee's failure to promptly correct conditions adverse to quality. The first example involved failure to take prompt cor
Region: II | Saint Lucie | 12663 | 03/31/2009 04/30/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Required TS Surveillance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 71111.22 | The inspectors identified a Green noncited violation of Technical Specifications 3.8.1, "AC Sources," for failure to perform a required monthly surveillance test in its entirety. Specifically, the inspectors identified that St. Lucie has not performed Uni
Region: II | Saint Lucie | 12664 | 03/31/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely and Effective Corrective Actions for EDG Day Tank Level Switch Failure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | The inspectors identified a Non Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure of the licensee to take timely and effective corrective actions to prevent recurrence of Unit 1 emergency diesel generator (EDG)
Region: II | Saint Lucie | 12668 | 03/31/2009 04/30/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Post Maintenance Test on the 1A-EDG Fuel Oil Day Tank Low Level Switch |  | H.3(b) Work Activity Coordination | TE?: N | 05000335 Saint Lucie 1 |  | 71111.19 | The inspectors identified a NCV of TS 6.8.1.a and Regulatory Guide (RG) 1.33, for the licensee failing to specify and ensure an appropriate post maintenance test (PMT) was performed as required by administrative procedure ADM-78.01, "Post Maintenance Test
Region: II | Saint Lucie | 12669 | 03/31/2009 04/30/2009 | 2009002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Adequate Process Controls during Maintenance Activities Resulted in a Manual Reactor |  | H.3(a) Work Planning | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing finding was identified for failure to implement adequate process controls to minimize risk during maintenance on the Unit 2, 5B feedwater heater high level limit switch resulting in a manual reactor trip on June 4, 2008. No violations of
Region: II | Saint Lucie | 12660 | 12/31/2008 01/30/2009 | 2008005-01 | Self - Revealed | NCV | Initiating Events | Green | Unit 1 Loss of Shutdown Cooling |  | H.4(a) Human Error Prevention | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | A self-revealing Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when a reactor operator (RO) failed to comply with a system surveillance procedure while restoring the 1A Low P
Region: II | Saint Lucie | 12652 | 09/30/2008 10/30/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct an Open and Degraded Missile Shield Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000389 Saint Lucie 2 |  | 71111.05Q | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify and correct the west side entrance door of the 2B diesel fuel oil storage tank (DFOST) building that was unable to
Region: II | Saint Lucie | 12653 | 09/30/2008 10/30/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Ten Minutes Station Blackout Requirement |  |  | TE?: N | 05000335 Saint Lucie 1 |  | NONE | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.63 for the licensee's non-compliance with the station blackout rule since 1993. The licensee failed to demonstrate that electrical power for Unit 1 could be provided within ten minutes of
Region: II | Saint Lucie | 12654 | 09/30/2008 10/30/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Station Blackout Cross-tie Cable |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | NONE | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(1) for the licensee's failure to monitor the SBO cross-tie cable for Units 1 and 2 against license established goals. The cable has not been tested or energized since 1993. The
Region: II | Saint Lucie | 12648 | 06/30/2008 07/17/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedure Fails to Limit the likelihood of Heavy Load Drop Accident in Containment |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71111.2 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion V, AInstructions, Procedures, and Drawings,@ for the licensee failing to have in place adequate heavy load handling procedures that would control and limit the likelihood of a heavy load
Region: II | Saint Lucie | 12641 | 03/31/2008 04/30/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Failure to Take Timely and Effective Corrective Actions to Prevent RCS Pressure Boundary Leakage through the RCP Seal Lines |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to take timely and effective corrective actions to prevent recurrence of Reactor Coolant System (RCS) pressure boundary leakage t
Region: II | Saint Lucie | 12642 | 03/31/2008 04/30/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Distribute EOP Revisions to the Required Location for Usage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion VI, Document Control, for inadequate document control that resulted in copies of several revised emergency operating procedures (EOPs) not being distributed to the d
Region: II | Saint Lucie | 12639 | 12/31/2007 02/01/2008 | 2007005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to follow procedures for the 2B Purification Ion Exchange system resin change-out activities |  | H.4(b) Procedural Compliance | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7112101 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.8.1(a) for failure to follow procedural guidance established for radioactive resin replacement activities was identified. Specifically, on November 13, 2007, Operations personnel
Region: II | Saint Lucie | 12640 | 12/31/2007 02/01/2008 | 2007005-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Implement Appropriate DOT Type A Package Closure Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7112202 | The inspectors identified a Green NRC-identified NCV of 10 CFR 71.5 for failure to implement package design specifications for the proper closure of Type A shipping packages as required by Department of Transportation (DOT) regulations. Specifically, for
Region: II | Saint Lucie | 12633 | 09/28/2007 11/05/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Verification of ICW Operability |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111121 | The team identified a violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for an inadequate procedure used to verify operability of the Intake Cooling Water (ICW) system when high ocean temperatures occur. The find
Region: II | Saint Lucie | 12634 | 09/28/2007 11/05/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Use the Most Limiting Design Inputs in Engineering Analyses - Several Examples |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111121 | The team identified a violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to use the most limiting design inputs in engineering analyses. Several examples were identified. The finding was more than minor because if uncorrect
Region: II | Saint Lucie | 12635 | 09/28/2007 11/05/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action Associated with Degraded Performance of the CCW Heat Exchanger Temperature Control Valve (2-TCV 14-4A) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111121 | The team identified a violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for inadequate corrective actions associated with the degraded performance of the Component Cooling Water (CCW) heat exchanger temperature control valve (2-TCV-14-
Region: II | Saint Lucie | 12629 | 06/30/2007 07/19/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions for Ensuring Proper Oil Levels in Safety-Related Pump Motors |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000335 Saint Lucie 1 |  | 71152 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take timely and effective corrective actions to prevent recurrence of continued NRC-identified low oil levels in emergency core cooling syste
Region: II | Saint Lucie | 12619 | 03/31/2007 04/26/2007 | 2007002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedure for Post Maintenance Testing of a Containment Isolation Valve |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71111.19 | The inspectors identified a Non-Cited Violation (NCV) of Technical Specification (TS) 6.8.1.a, which requires that written procedures be implemented covering the activities in applicable procedures recommended by Regulatory Guide 1.33, including procedure
Region: II | Saint Lucie | 12620 | 03/31/2007 04/26/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | Failure to Take Adequate Corrective Actions for Establishing Current Transformer Inspections |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take timely and effective corrective actions to prevent recurrence of a known condition whereby the epoxy-anhydride coa
Region: II | Saint Lucie | 12621 | 03/31/2007 04/26/2007 | 2007002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Atmospheric Dump Valve Maintenance Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000335 Saint Lucie 1 |  | 71153 | A self-revealing finding was identified following an event when Unit 1 inadvertently entered Operational Mode 3 (Hot Standby) due to a failure of the 1A air operated atmospheric dump valve (HCV-08-2A) actuator diaphragm and subsequent plant heat up. It wa
Region: II | Saint Lucie | 12622 | 03/31/2007 04/26/2007 | 2007002-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Unit 2 Number 1 Throttle Valve Maintenance Procedure |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing finding was identified for improper torquing of cap screws used to attach a blind flange to an auxiliary servo actuator associated with the turbine digital electro-hydraulic (DEH) control system which caused a premature failure of an O-ri
Region: II | Saint Lucie | 12615 | 12/31/2006 01/25/2007 | 2006005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Survey Unit 1 Control Room Outside Intake Air |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 7112103 | . A self-revealing non-cited violation (NCV) of 10 CFR 20.1501(a) was identified for failure to conduct radiation surveys of the Unit 1 (U1) control room ventilation outside intake air. From March 31, 2006 to October 28, 2006, the 'B' U1 Control Room Outs
Region: II | Saint Lucie | 12616 | 12/31/2006 01/25/2007 | 2006005-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Calculate Accurate Airborne Effluent Doses to Members of the Public |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7112201 | The inspectors identified a NCV of 10 CFR 20.1302(b) for failure to perform accurate calculations of airborne effluent releases to demonstrate that the maximally exposed individual did not exceed the annual dose limit. Specifically, during the period of M
Region: II | Saint Lucie | 12617 | 12/31/2006 01/25/2007 | 2006005-03 | NRC | FIN | Initiating Events | Green | Failure to Correct a Known Deficiency Associated With a Turbine Building Salt Water Cooling System Configuration Issue |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | A self-revealing finding was identified for failure to correct a known deficiency associated with a turbine building cooling water system piping connection with a history of leakage and leak repairs. Specifically, previous pipe repairs replaced aluminum b
Region: II | Saint Lucie | 12614 | 10/20/2006 12/04/2006 | 2006010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Test the Sound Powered Phones in Accordance With Surveillance Procedures |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71111.05T | The team identified a non-cited violation of Unit 1 Operating License Condition 3.E for failure to perform tests on the sound powered phone system credited for post-fire safe shutdown in accordance with the approved Unit 1 fire protection program (FPP). T
Region: II | Saint Lucie | 12610 | 09/30/2006 10/26/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Erection of Temporary Ladders and Structures On Or Around Safety Related Equipment |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 7111117A | A Non-Cited Violation was identified for failing to implement administrative procedure ADM-27.11, Scaffold Control, on issues related to the erection of ladders and scaffold structures around safety related equipment. Specifically, over a short period of
Region: II | Saint Lucie | 12611 | 09/30/2006 10/26/2006 | 2006004-02 | Self - Revealed | FIN | Initiating Events | Green | Personnel Error Caused Partial Loss of Feedwater and Manual Reactor Trip |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71153 | A self-revealing finding was identified for failure of the licensee to use human performance tools as outlined in their Nuclear Administrative Procedure (NAP) 403, Conduct of Maintenance. Specifically, maintenance personnel did not perform adequate self c
Region: II | Saint Lucie | 12604 | 03/31/2006 04/27/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Reset the 1C AFW Pump Mechanical Over Speed Trip Linkage |  |  | TE?: N | 05000335 Saint Lucie 1 |  | 71111.15 | A Green self-revealing NCV was identified for the licensee failing to comply with 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." As a result of an inadequate procedure, a turbine driven auxiliary feed water (AFW) pump w
Region: II | Saint Lucie | 12606 | 03/31/2006 04/27/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Unit 1 and 2 Containment Building ECCS Sump Design Control |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71111.15 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure of the licensee to evaluate the potential consequences of unfiltered debris migrating from the reactor cavity sump to the Emergency Core Cooling S
Region: II | Saint Lucie | 12607 | 03/31/2006 04/27/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Actions for EDG Air Start Motor Failures |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take timely and effective corrective actions to prevent recurrence of Emergency Diesel Generator (EDG) air start motor failures. On Jan
Region: II | Saint Lucie | 125561 | 09/09/2019 |  | Licensee - Identified | LIV |  | Green | GREEN LIV for Failure to Ensure the Capability to Detect CDA Compromise at All Times |  |  | TE?: N | 05000335 Saint Lucie 1 05000389 Saint Lucie 2 |  | 71130.10P
Region: II | Saint Lucie | 125719 | 11/14/2019 |  |  | LIV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000389 Saint Lucie 2 |  | 71152
Region: II | Sequoyah | 126388 | 12/31/2019 02/11/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of ERCW Flow to CCS Train 2A After Implementing Temporary Modification |  | H.14 - Conservative Bias | TE?: N | 05000328 Sequoyah 2 | Design Control | 71153 | A self-revealed Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified when the licensee failed to verify adequate essential raw cooling water (ERCW) system flow to train 2A co
Region: II | Sequoyah | 126547 | 12/31/2019 02/11/2020 | 2019004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Obstruction in Steam Generator Pressure Channel Sense Line Results in ESFAS Channel Inoperability |  | P.3 - Resolution | TE?: N | 05000327 Sequoyah 1 | Equipment Performance | 71153 | A self-revealed Green finding and associated non-cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified when the licensee failed to ensure the pressure instrumentation sense line for a steam generator pres
Region: II | Sequoyah | 125507 | 09/30/2019 10/28/2019 | 2019003-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Follow Procedures |  | H.1 - Resources | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 | Plant Facilities/Equipment and Instrumentation | 71124.06 | A self-revealed Green finding and associated non-cited violation of Technical Specification 5.5 was identified when the licensee failed to follow a plant procedure to estimate flow rates when the Unit 1 (U1) and Unit 2 (U2) Shield Building Ventilation Flo
Region: II | Sequoyah | 125109 | 06/30/2019 07/25/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Obstruction in Steam Generator Pressure Channel Sense Line Results in Engineered Safeguard Feature Actuation System (ESFAS) Channel Inoperability |  | H.5 - Work Management | TE?: N | 05000327 Sequoyah 1 | Equipment Performance | 71111.15 | The inspectors identified a green, non-cited violation of 10 CFR 50 Appendix B criterion XVI when the licensee failed to ensure the pressure instrumentation sense line for a steam generator pressure protection channel transmitter was not obstructed. Speci
Region: II | Sequoyah | 124563 | 03/31/2019 05/10/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Significant Degradation Mechanisms in ASCO Solenoid Operated Valves |  | NPP | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 | Equipment Performance | 71111.21N | The NRC identified a Green finding and associated non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) 50.49(e)(5), for the licensee’s failure to account for all significant degradation mechanisms for ASCO solenoid valve FSV-032-80.
Region: II | Sequoyah | 124591 | 03/31/2019 05/10/2019 | 2019001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Heat Rise in Foxboro/Weed Instruments |  | NPP | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21N | The NRC identified a Green finding and associated non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) 50.49(e)(5), for the licensee’s failure to account for the heat rise of specific components within the Foxboro/Weed instrument FT-063
Region: II | Sequoyah | 124506 | 03/15/2019 04/25/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate AC Power System Calculations Conform to Design Bases |  | NPP | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 | Design Control | 71111.21M | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, Design Control, for the licensee's failure to verify or check the adequacy of design of
Region: II | Sequoyah | 25967 | 12/31/2018 01/31/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate PMT results in condition prohibited by Tech Specs |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153
Region: II | Sequoyah | 23956 | 03/31/2018 05/07/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Essential Raw Cooling Water Pumps Inoperable due to Frozen Motor Bearing Cooling Lines |  | NPP | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | A self-revealing Green NCV of Technical Specification 5.4.1, “Procedures,” was identified when Sequoyah/TVA did not establish, implement and maintain applicable procedures recommended in Regulatory Guide 1.33, Appendix A, Section 9, “Procedures for Pe
Region: II | Sequoyah | 23957 | 03/31/2018 05/07/2018 | 2018001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Calibration of Reactor Trip Instrumentation Results in a Condition Prohibited by Technical Specifications |  | H.9 - Training | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | A self-revealing Green finding and associated NCV of Sequoyah Unit 1 Technical Specification 5.4, “Procedures,” was identified on June 25, 2016, when the licensee did not implement procedures to calibrate Delta-T/Tavg Channel IV with the correct test equi
Region: II | Sequoyah | 23219 | 12/11/2017 01/24/2018 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Unjustified Qualified Life for Target Rock Power-Operated Relief Valves (PORVs) |  | NPP | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21N | The team identified a Green NCV of Title 10 Code of Federal Regulations 50.49(e)(5) “Aging” when the licensee failed to replace, refurbish, or demonstrate additional life for components that exceeded their qualified life. The licensee failed to justify ch
Region: II | Sequoyah | 23220 | 12/11/2017 01/24/2018 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Qualification for Unit One Reactor Lower |  | NPP | TE?: N | 05000327 Sequoyah 1 |  | 71111.21N | The team identified a Green NCV of Title 10 Code of Federal Regulations 50.49(f) “Electrical Equipment Qualification” when the licensee failed to perform an adequate similarity analysis for the environmental qualification of their Reliance 75 horsepower r
Region: II | Sequoyah | 22367 | 03/31/2017 05/03/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Barrier Penetration |  | P.1 - Identification | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The NRC identified a non-cited violation of the facility's operating license for the failure to identify a nonfunctional fire barrier penetration and enter it into the corrective action program (CAP) when the initial damage to the fire barrier occurred. T
Region: II | Sequoyah | 12008 | 12/19/2016 02/14/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Degrader Fire Barrier Penetrations |  | P.1 Identification | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The NRC identified a non-cited violation (NCV) of the facility's operating license for the licensee's failure to ensure that all fire barrier penetrations in fire zones boundaries protecting safety related areas are functional at all times. Specifically,
Region: II | Sequoyah | 12005 | 09/30/2016 10/28/2016 | 2016003-01 | NRC | NCV | Barrier Integrity | Green | Hydrogen Mitigation System Inoperable Longer than Allowed by Technical Specifications | EA Case: 2016003 | H.12 Avoid Complacency | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | A self-revealing Green NCV of TS 3.6.8 was noted for the licensee's failure to restore an inoperable train of HMS to service within the required completion time 7 days. In addition, the licensee failed to be in Mode 3 within the following 6 hours followin
Region: II | Sequoyah | 12006 | 09/30/2016 10/28/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Isolation of Fire Suppression System to a Significant Portion of the Plant Site | EA Case: 2016003 | H.8 Procedure Adherence | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | A self-revealing Green NCV of the facility's operating license was identified for the licensee's failure ensure the fire suppression system was operable and capable of suppressing fires. Specifically, the licensee inadvertently disabled the High Pressure
Region: II | Sequoyah | 11906 | 07/15/2016 08/31/2016 | 2016008-01 | NRC | NCV | Initiating Events | Green | Failure to Maintain Design Control of MSIV Controls |  |  | TE?: N | 05000327 Sequoyah 1 |  | NONE | A self-revealing Green non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, "Design Control", was identified for the licensee's failure to maintain design control of MSIV 1-FCV-1-22 controls. Specif
Region: II | Sequoyah | 12007 | 06/30/2016 08/12/2016 | 2016002-01 | Self - Revealed | AV | Mitigating Systems | Green | Isolation of Fire Suppression System to a Significant Portion of the Plant Site. |  | H.8 Procedure Adherence | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.04Q | A self-revealing apparent violation (AV) of the facility's operating license was identified for the licensee's failure ensure the fire suppression system was operable and capable of suppressing fires. Specifically, the licensee inadvertently disabled th
Region: II | Sequoyah | 11995 | 06/17/2016 07/28/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Design Change Process when Modifying the Safety-Related Fire Dampers |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to use the design change process to make modifications to the E
Region: II | Sequoyah | 11996 | 06/17/2016 07/28/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Install Safety-Related Components that are Designed to Withstand the Effects of a Design Basis Tornado |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to install emergency diesel generator components that could withstand the effects of a design basis tornado as req
Region: II | Sequoyah | 12001 | 06/17/2016 07/28/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Monitoring of the 480V Shutdown Transformers |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to have documented procedures in place to ensure effective monitoring of the 480V Shutdown Tr
Region: II | Sequoyah | 12002 | 06/17/2016 07/28/2016 | 2016007-04 | NRC | FIN | Barrier Integrity | Green | Failure to Energize Hydrogen Igniters during Extended Station Blackout |  | P.5 Operating Experience | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.21M | The NRC identified a finding (FIN) for the licensee's failure to meet their docketed commitment to revise the back-up generators to include supplying one train of containment hydrogen igniters per unit in response to Generic Safety Issue 189, "Suscepti
Region: II | Sequoyah | 11993 | 03/31/2016 05/11/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Application of Flame Retardant on Cable Room Penetrations |  | H.8 Procedure Adherence | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The NRC identified a non-cited violation (NCV) of Unit 1 and 2 Technical Specification 5.4.1 for the licensee's failure to adequately implement fire protection procedures. Specifically, the inspectors identified several cables located within a cable tray
Region: II | Sequoyah | 11994 | 03/31/2016 05/11/2016 | 2016001-02 | NRC | NCV | Initiating Events | Green | Inadvertent Safety Injection Due to Inadequate Main Steam Procedure |  | P.5 Operating Experience | TE?: N | 05000327 Sequoyah 1 |  | 71153 | A self-revealing NCV of Units 1 & 2 Technical Specification, 5.4.1 was documented for the licensee's failure to implement an adequate procedure associate with the startup of the main steam system. Specifically, the licensee caused an inadvertent safety in
Region: II | Sequoyah | 11988 | 12/31/2015 02/12/2016 | 2015004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Recognize and Submit for Approval a Reduction in Effectiveness of the Emergency Plan |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71114.04 | The inspectors identified a Severity Level IV NCV of Title 10 of the Code of Federal Regulations, Part 50.54(q), for changes to the licensee's radiological emergency plan, effective December 18, 2014, that reduced the effectiveness of the plan and therefo
Region: II | Sequoyah | 11971 | 10/01/2015 11/09/2015 | 2015003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Work Risk Activity and Oversight of Supplemental Personnel Procedures |  | H.13 Consistent Process | TE?: N | 05000327 Sequoyah 1 |  | 71152 | A self-revealing Green NCV of TS 6.8.1.a, "Administrative Controls of Procedures and Programs," was identified for the licensee's failure to implement procedures related to quality during the surveillance capsule relocation activity. Specifically, procedu
Region: II | Sequoyah | 11964 | 09/19/2015 11/09/2015 | 2015003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Clearance Causes damage to 'A' train Solid State Protection System |  | H.1 Resources | TE?: N | 05000327 Sequoyah 1 |  | 71111.13 | A self-revealing Green NCV of Unit 1 Technical Specification (TS) 6.8.1.a was identified for the licensee's failure to adequately establish a clearance boundary during plant maintenance. Specifically, the licensee caused damage to a safetyrelated componen
Region: II | Sequoyah | 11972 | 07/31/2015 09/14/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain control of and update safety related design out documents (electrical calculations) |  | P.3 Resolution | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.17T | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the licensee's failure to control safety related calculations that reviewed equipment essential to the function of Class 1E elect
Region: II | Sequoyah | 11974 | 07/31/2015 09/14/2015 | 2015007-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to request a licensee amendment prior to removing interlocks from shared onsite emergency and shutdown AC electric systems |  |  | TE?: Y SL-IV-NCVIV | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.17T | The inspectors identified a SLIV violation of 10CFR 50.59.c.(2).ii, "Changes, tests and experiments," for the licensee's failure to obtain a license amendment prior to implementing a change to the onsite emergency and shutdown AC electric systems supplyin
Region: II | Sequoyah | 11979 | 07/31/2015 09/14/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct inadequate procurement evaluation processes |  | H.3 Change Management | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.17T | The inspectors identified three examples of a Green non-cited (NCV) of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action, for the licensee's failure to identify and correct a conditions adverse to quality that were associated with processes for eval
Region: II | Sequoyah | 11980 | 07/31/2015 09/14/2015 | 2015007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Qualification Criteria Associated with Class 1E Electrical Component Static Performance Characteristics |  | H.3 Change Management | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.17T | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of defined shelf life and design life characteristics of Class 1E electrical equi
Region: II | Sequoyah | 11962 | 06/30/2015 08/11/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Follow Foreign Material Control Procedures (Section 1R15) |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71111.15 | A self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the licensee's failure to follow a foreign material exclusion procedure and precluded foreign material from entering the safety-re
Region: II | Sequoyah | 11961 | 03/31/2015 04/30/2015 | 2015001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Results in an Inadvertent Sprinkler Deluge in the Cable Spreading Room |  | H.12 Avoid Complacency | TE?: N | 05000327 Sequoyah 1 |  | 71111.05Q | Green. A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 6.8.1.f, "Fire Protection Program Implementation," was identified for the licensee's failure to follow a fire protection procedure. Specifically, the licensee failed t
Region: II | Sequoyah | 11955 | 09/30/2014 10/30/2014 | 2014004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Perform Adequate Maintenance on Containment Vacuum Relief Valve (Section 1R12) |  | H.1 Resources | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.12 | A Self-revealing Green Non-Cited Violation (NCV) of Technical Specification (TS) 6.8.1.a. was identified for the licensee's failure to adequately implement a maintenance procedure associated with a vacuum relief containment isolation valve. Specifically,
Region: II | Sequoyah | 11953 | 06/30/2014 08/01/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform visual examination of the Unit 1 and Unit 2 CRDM seismic plate supports |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.08P | An NRC-identified Green non-cited violation (NCV) of 10 CFR 50.55a(g)(4), "Inservice Inspection Requirements" was identified for the licensee's failure to perform visual examinations of the control rod drive mechanism (CRDM), American Society of Mechanica
Region: II | Sequoyah | 11954 | 06/30/2014 08/01/2014 | 2014003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to comply with entry requirements to a HRA |  | H.12 Avoid Complacency | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71124.01 | The inspectors identified a Green, self-revealing, NCV of Technical Specification (TS) 6.12.1, "High Radiation Area", for two examples where workers made entries into High Radiation Areas (HRA) on May 16, 2014, without meeting the entry requirements speci
Region: II | Sequoyah | 11973 | 04/02/2014 09/14/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to meet Design Basis Requirements to have Interlocks between Shared systems |  | H.14 Conservative Bias | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.17T | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion III, "Design Control," for the licensee's failure to ensure that plant licensing and design basis for shared Class 1E electrical systems were controlled and main
Region: II | Sequoyah | 11943 | 03/31/2014 04/29/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate clearance causes control air system transient |  | H.5 Work Management | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | A self-revealing non-cited violation of Units 1 and 2 Technical Specification 6.8.1.a, Administrative Controls (Procedures), was documented for the licensee's failure to establish an adequate clearance in preparation for maintenance activities on the B st
Region: II | Sequoyah | 11944 | 03/05/2014 04/15/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Improper orientation of fire dampers in auxiliary building |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | An NRC-identified Green non-cited violation of Sequoyah Operating License Conditions 2.C.(16) and 2.C.(13) for Units 1 and 2 respectively, was identified for the licensee's failure to ensure that fire dampers were functional, as required by the approved f
Region: II | Sequoyah | 11945 | 03/05/2014 04/15/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Auxiliary control instrument room 2A sprinklers not in compliance with NFPA 13-1975 |  | P.2 Evaluation | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | An NRC-identified Green non-cited violation of Sequoyah Operating License Conditions 2.C.(16) and 2.C.(13), for Units 1 and 2 respectively, was identified for the licensee's failure to properly install an automatic pre-action fire sprinkler system in Auxi
Region: II | Sequoyah | 11946 | 03/05/2014 04/15/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Design control requirements not met during safety-related circuit breaker replacemetns |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | An NRC-identified Green non-cited violation (with two examples) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to assure that design documents were controlled and appropriate quality standards for d
Region: II | Sequoyah | 11947 | 03/05/2014 04/15/2014 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Failure to maintain necessary materials and procedures for cold shutdown repairs |  | H.4 Teamwork | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | An NRC-identified Green non-cited violation of Sequoyah Operating License Conditions 2.C.(16) and 2.C.(13), for Units 1 and 2 respectively, was identified for the licensee's failure to maintain necessary materials and procedures for cold shutdown repairs,
Region: II | Sequoyah | 11948 | 03/05/2014 04/15/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to perform the required reviews when adding fire watches to the fire protection program |  | P.2 Evaluation | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | An NRC-identified Green non-cited violation of Sequoyah Operating License Conditions 2.C.(16) and 2.C.(13), for Units 1 and 2 respectively, was identified for the licensee's failure to perform the required reviews when adding fire watches to the fire prot
Region: II | Sequoyah | 11936 | 12/31/2013 02/07/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Unit 1 Train "A" RHR Containment Suction Valve Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000327 Sequoyah 1 |  | 71153 | Timely corrective actions were not taken to correct a dual position indication (open and closed loghts both illuminated) on the Unit 1 'A' train residual heat removal containment sump suction control valve. The finding was determined to be more than minor
Region: II | Sequoyah | 11935 | 11/22/2013 12/11/2013 | 2013014-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Translate Design Basis into Procedure Acceptance Criteria Time to Perform Operator Action. |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate design basis requirements into emergency sub-procedure, ES-1.3, "Transfer to Residual Heat Removal Conta
Region: II | Sequoyah | 11916 | 09/30/2013 11/12/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to correct a condition adverse to quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000328 Sequoyah 2 |  | 71111.05Q | The NRC identified a Green non-cited violation (NCV) of 10CFR50 appendix B, Criterion XVI, for the licensee's failure to correct a condition adverse to quality (CAQ) per NPG-SPP-22.302, "Corrective Action Program Screening and Oversight". Specifically, in
Region: II | Sequoyah | 11917 | 08/09/2013 09/23/2013 | 2013007-01 | NRC | NCV | Initiating Events | Green | Failure to Evaluate a Potential Condition Adverse to Quality Prior to Mode Change |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow a test control procedure to evaluate indications of excessive check valve leakage prior to chan
Region: II | Sequoyah | 11918 | 08/09/2013 09/23/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Impact for Full Range of EDG Frequency |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the entire range of allowable emergency diesel generator (EDG) frequencies into design basis documents. The failur
Region: II | Sequoyah | 11922 | 08/09/2013 09/23/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Translate the Design and Licensing Basis for the 125 VDC System Into Design Calculations |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly translate the design and licensing bases for the 125 VDC system into design calculations. The licensee inappropriat
Region: II | Sequoyah | 11923 | 08/09/2013 09/23/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Basis for AFW MOV Motor Brake Alternate Voltage Criteria |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to check the adequacy of the design of the steam generator feedwater isolation valve motor brakes. Specifically, the licensee
Region: II | Sequoyah | 11924 | 08/09/2013 09/23/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Document Deficiencies Discovered During Receipt Inspections in the Corrective Action program |  | H.4(b) Procedural Compliance | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of TS 6.8.1, Procedures and Programs, the licensee's failure to properly implement maintenance procedures for performing receipt inspection of new 480V circuit breakers. Specifically, the licensee's failure to ev
Region: II | Sequoyah | 11932 | 08/09/2013 09/23/2013 | 2013007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Perform 50.59 Screens for Scaffolds and Clearances |  | H.4(b) Procedural Compliance | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of TS 6.8.1, Procedures and Programs, for the licensee's failure to implement procedures for equipment and maintenance control. The licensee's failure to perform 10 CFR 50.59 reviews of temporary plant changes (e.
Region: II | Sequoyah | 11933 | 08/09/2013 09/23/2013 | 2013007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for 2010 Degraded Voltage Issue |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct deficiencies in electrical calculations for the safety-related AC electrical distribution
Region: II | Sequoyah | 11904 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate abnormal operating procedure for internal flood mitigation strategy |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71152 | The inspectors identified a Green NCV of Technical Specification (TS) 6.8.1,"Procedures and Programs," for the licensee's failure to establish an adequate procedure associated with Abnormal Operating Procedure (AOP) M.08, "Internal Flooding." Specifically
Region: II | Sequoyah | 11907 | 03/31/2013 05/09/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to promptly identify and correct conditions adverse to quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with three examples of the licensee's failure to promptly identify and correct conditions adverse to quality. Specifically, the licensee fa
Region: II | Sequoyah | 11908 | 03/31/2013 05/09/2013 | 2013002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure of ground fault relay leads to loss of RCP and reactor trip |  | H.3(b) Work Activity Coordination | TE?: N | 05000328 Sequoyah 2 |  | 71153 | A self-revealing Green NCV of Unit 2 Technical Specification (TS) 6.8.1, "Procedures & Programs," was noted for the licensee's failure to provide adequate procedures for maintenance and surveillance activities involving the RCP circuit breaker ground faul
Region: II | Sequoyah | 11889 | 12/31/2012 02/13/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement freeze protection program requirements |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.01 | A NRC-identified Green non-cited violation (NCV) of Unit 1 and 2 Technical Specification 6.8.1.a for the licensee's failure to follow station procedures to adequately implement freeze protection requirements. Specifically, inspectors found a number of req
Region: II | Sequoyah | 11890 | 12/31/2012 02/13/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to implement fire protection impairment requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The inspectors identified a Green noncited violation of Units 1 & 2 Technical Specification 6.8.1.f for the licensee's failure to implement procedures required for fire protection program implementation. The inspectors found multiple examples of where fir
Region: II | Sequoyah | 11891 | 12/31/2012 02/13/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | Failure to establish adequate procedures for fire protection impairment requirements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The inspectors identified a Green noncited violation of Units 1 & 2 Technical Specification 6.8.1.f for the licensee's failure to establish adequate procedures required for fire protection program implementation. Specifically, NPG-SPP-18.4.6, Control of F
Region: II | Sequoyah | 11894 | 12/31/2012 02/13/2013 | 2012005-04 | NRC | NCV | Barrier Integrity | Green | Failure to perform ISI general visual examinations of containment moisture barrier associated with containment liner leak chase test connection threaded pipe plugs |  | P.2(b) Implementing Operating Experience | TE?: N | 05000328 Sequoyah 2 |  | 71111.08P | The inspectors identified a Green NCV of 10 CFR Part 50.55a, "Codes and Standards," involving the licensee's failure to properly apply Subsection IWE of ASME Section XI for conducting general visual examinations of the metal-to-metal pipe plugs installed
Region: II | Sequoyah | 11895 | 12/31/2012 02/13/2013 | 2012005-05 | NRC | VIO | Mitigating Systems | Green | Failure to adequately evaluate and qualify molded case circuit breakers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71152 | The inspectors identified a violation with several examples of 10 CFR 50, Appendix B, Criterion III, "Design Control," for failure to implement design control measures that review for suitability of application of materials, parts, and equipment that are
Region: II | Sequoyah | 11885 | 06/30/2012 08/01/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Fire Drill | EA Case: 2012003 | P.3(a) Self-Assessment | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05A | The inspectors identified a noncited violation of Units 1 & 2 Technical Specification 6.8.1.f for the licensee's failure to implement procedures required for fire protection program implementation. Specifically, the licensee failed to evaluate six minimum
Region: II | Sequoyah | 11886 | 06/30/2012 08/01/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Turbine Throttle Valve Reactor Trip Function Degraded | EA Case: 2012003 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 |  | 71152 | The inspectors identified a Green NCV of Unit 1 TS 6.8, "Procedures & Programs," for the licensee's failure to provide adequate procedures for maintenance and surveillance activities involving the main turbine throttle valves and the associated solid stat
Region: II | Sequoyah | 11390 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Procedures forTornado Watch/Warning | EA Case: 2012002 | H.4(b) Procedural Compliance | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.01 | The inspectors identified a noncited violation of Units 1 & 2 Technical Specification of 6.8.1.a for the licensee's failure to adequately implement procedure AOP-N.02, "Tornado Watch/Warning," Revision 28. On March 2, 2012, the licensee entered AOP-N.0
Region: II | Sequoyah | 11391 | 03/31/2012 04/30/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Fire Drill Training Requirements | EA Case: 2012002 | H.2(b) Personnel Training & Qualifications | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | The inspectors identified a noncited violation of facility operating license DPR-77 condition 2.C.(16) and facility operating license DPR-79 condition 2.C.(13) for failure to implement and maintain in effect all provisions of the approved fire protecti
Region: II | Sequoyah | 11404 | 03/31/2012 04/30/2012 | 2012002-03 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Corrective Action Program Procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | The inspectors identified a finding for the licensee's failure to meet the requirements of corrective action program procedure NPG-SPP-03.1.7, PER Actions, Revision 2. Specifically, the licensee failed to ensure that the corrective action plan and asso
Region: II | Sequoyah | 11878 | 03/31/2012 04/30/2012 | 2012002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Turbine Driven Auxiliary Feedwater Pump Inoperable Due to Overspeed Trip | EA Case: 2012002 | H.3(a) Work Planning | TE?: N | 05000327 Sequoyah 1 |  | NONE | A self-revealing NCV of Unit 1 TS 6.8, "Procedures & Programs," was identified for the licensee's failure to provide adequate procedures for a maintenance activity involving the required inspection of an Essential Raw Cooling Water (ERCW) pipe leak in
Region: II | Sequoyah | 11879 | 03/31/2012 04/30/2012 | 2012002-06 | NRC | NCV | Mitigating Systems | Green | Change to Fire Protection Program Which Adversely Affected Safe Shutdown Without Prior NRC Approval | EA Case: 2012002 |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | The inspectors identified a non-cited violation of Sequoyah operating license conditions 2.C. (16) and 2.C. (13) for Units 1 and 2 respectively, for a change made to the Sequoyah fire protection program which was determined to adversely affect safe shu
Region: II | Sequoyah | 11880 | 03/11/2012 03/29/2012 | 2012007-01 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip due to Improper Preferred Inverter Maintenance |  | H.3(b) Work Activity Coordination | TE?: N | 05000327 Sequoyah 1 |  | 95001 | A self-revealing finding was identified for the licensee's failure to properly implement work procedures during the performance of a preventive maintenance (PM) activity associated with the Unit 1 Preferred Inverter. The improper performance of selected
Region: II | Sequoyah | 11874 | 12/31/2011 01/30/2012 | 2011005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Loss of Power Diesel Generator Start Instrumentation Surveillance Testing | EA Case: 2011005 | H.4(a) Human Error Prevention | TE?: N | 05000328 Sequoyah 2 |  | 71111.22 | A self-revealing non-cited violation of Unit 2 Technical Specification (TS) 6.8.1.a was identified for the licensee's failure to follow station procedures during the performance of a surveillance testing activity. While performing degraded voltage/load sh
Region: II | Sequoyah | 11421 | 12/31/2011 01/30/2012 | 2011005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Thermal Power Less Than Licensed Limit |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000327 Sequoyah 1 |  | 71152 | The inspectors identified a non-cited violation of Unit 1 Operating License DPR-77 Condition 2. (C).1 "Maximum Power Level" for the licensee's failure to take prudent action to ensure that the licensed power limit was not exceeded during a pre-planned ev
Region: II | Sequoyah | 11422 | 12/31/2011 01/30/2012 | 2011005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Nuclear Instrumentation System Channel Calibration Error |  | H.4(a) Human Error Prevention | TE?: N | 05000328 Sequoyah 2 |  | 71153 | A self-revealing non-cited violation of Unit 2 TS 3.0.3 was identified for the licensee's failure to place the unit in Mode 3 within seven hours when a Limiting Condition for Operation (LCO) was not met in Modes 1 and 2. The requirements of LCO 3.3.1, "Re
Region: II | Sequoyah | 11430 | 06/30/2011 07/29/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform instrumentation surveillance testing within required frequency |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.22 | The inspectors identified a non-cited violation of Units 1 and 2 TS Surveillance Requirement (SR) 4.0.2 for the licensee's failure to perform SRs specified in Units 1 and 2 TS 3/4.3.1, "Reactor Trip System Instrumentation," and 3/4.3.2, "Engineered Safety
Region: II | Sequoyah | 11432 | 06/13/2011 07/08/2011 | 2011006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Compensatory Actions for Blocked Sprinklers |  | H.4(b) Procedural Compliance | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05T | The inspectors identified a non-cited violation of Sequoyah Operating License Conditions 2.C.(16) and 2.C.(13) for Units 1 and 2, respectively, for failure to establish compensatory measures for an obstructed sprinkler system. Specifically, scaffolding in
Region: II | Sequoyah | 11433 | 06/13/2011 07/08/2011 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Sprinkler System in Room 690.0-A1 of the Auxiliary Building has NFPA Code Deviation |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05T | The inspectors identified a non-cited violation of Operating License Conditions 2.C.(16) and 2.C.(13), for Units 1 and 2 respectively, for failure to install the automatic suppression system (sprinkler system) in the auxiliary building corridor 690 foot e
Region: II | Sequoyah | 11420 | 03/31/2011 05/12/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately qualify molded-case circuit breakers to safety-related application through commercial grade dedication. |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to assure that appropriate quality standards were specified and included in design documents and that deviations from such
Region: II | Sequoyah | 11423 | 03/31/2011 05/12/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Loss of 480-V motor control center due to inadequate breaker replacement maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 |  | 71111.15 | A self-revealing non-cited violation of Unit 1 TS 6.8, "Procedures & Programs," was identified for the licensee's failure to provide adequate procedures for maintenance involving the replacement of a safety-related 480V breaker. This resulted in the norma
Region: II | Sequoyah | 11424 | 03/31/2011 05/12/2011 | 2011002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate maintenance procedures result in inoperable feedwater regulating valve. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 |  | 71152 | A self-revealing non-cited violation of 10 CFR 50 Appendix B Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to provide adequate procedures for maintenance on the Unit 1 loop 3 feedwater regulating valve (FRV). The ap
Region: II | Sequoyah | 11425 | 03/31/2011 05/12/2011 | 2011002-04 | Self - Revealed | FIN | Initiating Events | Green | Reactor trip due to unpluged steam dump load reject controller |  | H.3(a) Work Planning | TE?: N | 05000327 Sequoyah 1 |  | 71153 | A self-revealing finding was identified for the licensee's failure to perform adequate post-maintenance testing, as specified by procedures SPP-8.3, Post-Modification Testing, revision 10, and NPG-SPP-06.3, Pre-/Post-Maintenance Testing, revision 0, in co
Region: II | Sequoyah | 11411 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | NCV | Initiating Events | Green | Failure to collect reactor coolant pump oil leakage |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | -Green. The inspectors identified a Green non-cited violation of 10 CFR 50 Appendix R, Section III.O, "Oil collection system for reactor coolant pump," for the licensee's failure to ensure the capability of the reactor coolant pump (RCP) oil collection sy
Region: II | Sequoyah | 11418 | 12/31/2010 01/28/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to implement Technical Specification requirements to vent ECCS piping |  | H.3(b) Work Activity Coordination | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | -Green. The inspectors identified a Green non-cited violation of Technical Specification 6.8.1(c), "Procedures and Programs," for the failure to establish surveillance test procedures to verify that ECCS piping systems were full of water by venting access
Region: II | Sequoyah | 11419 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to use worst case 6900 VAC bus voltage in design calculations |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | -Green. The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to assure that applicable regulatory requirements and the design basis for structures, systems, and component
Region: II | Sequoyah | 11403 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate inspection of raw water side of containment spray heat exchangers |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.07A | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B Criterion V, "Instructions, Procedures, and Drawings," for the failure to provide adequate documented instructions for inspection of the containment spray heat exchangers. Preventive
Region: II | Sequoyah | 11409 | 09/30/2010 10/29/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative design calculation for RHR suction temperature limit |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | The inspectors identified a Green non-cited violation of 10 CFR 50 Appendix B Criterion III, "Design Control," for the failure to provide design control measures for verifying the adequacy of the design calculation used to establish the maximum RHR operat
Region: II | Sequoyah | 11410 | 09/30/2010 10/29/2010 | 2010004-03 | NRC | NCV | Barrier Integrity | Green | Failure to maintain thermal power less than licensed limit |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000328 Sequoyah 2 |  | NONE | The inspectors identified a Green non-cited violation of Unit 2 TS 6.8, "Procedures and Programs," for the failure to take prompt action to maintain reactor thermal power less than the licensed power limit of 3455 megawatts thermal (MWt) in response to a
Region: II | Sequoyah | 11400 | 04/16/2010 05/24/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Violation of 10 CFR 50, Appendix B, Criterion V for Failure to Follow Procedure for Vendor Contact Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for the failure to properly maintain the vendor contact program for safety-related components. The team identified 37 exam
Region: II | Sequoyah | 11394 | 03/31/2010 04/29/2010 | 2010002-01 | Self - Revealed | FIN | Initiating Events | Green | Reactor trip due to inadequate configuratin control |  | H.4(a) Human Error Prevention | TE?: N | 05000328 Sequoyah 2 |  | 71153 | A self-revealing finding was identified for two examples of the licensee's failure to follow station procedures. The licensee failed to follow work order instructions to ensure two valves associated with the main feedwater pump turbine seal steam supply s
Region: II | Sequoyah | 11392 | 12/31/2009 01/29/2010 | 2009005-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Evaluate Mission Dose for Manual Operator Actions Required by Plant Procedures |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.2 | The inspectors identified a non-cited violation (NCV) of Units 1 and 2 Technical Specification 6.8, "Procedures & Programs," for the licensee's failure to follow procedures involving the review and approval of revisions to a plant abnormal operating proce
Region: II | Sequoyah | 11393 | 12/31/2009 01/29/2010 | 2009005-02 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip due to Inadequate Transformer Bus Duct Maintenance Procedure |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | A self-revealing finding was identified for an inadequate maintenance procedure which was used to perform a periodic maintenance activity to clean and inspect the bus duct associated with the 'D' common station service transformer (CSST). This resulted in
Region: II | Sequoyah | 11387 | 09/30/2009 10/30/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow emergency diesel generator operating procedure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | A self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to follow plant procedures for performing independent verifications of procedural steps. Eme
Region: II | Sequoyah | 11388 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | FIN | Initiating Events | Green | Feedwater regulating valve failure due to inadequate maintenance procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 |  | 71153 | A self-revealing finding was identified for an inadequate maintenance procedure which was used to perform a rebuild of the Unit 1, Loop 1, main feedwater regulating valve (FRV) actuator. The failure to specify an applicable torque requirement associated w
Region: II | Sequoyah | 11389 | 09/30/2009 10/30/2009 | 2009004-03 | NRC | NCV | Initiating Events | Green | Failure to perform a 10 CFR 50.59 evaluation for abnormal operating procedure M.09, "loss of charging". |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | NONE | The inspectors identified a Severity Level IV NCV of 10 CFR 50.59 for the licensee's failure to perform a 10 CFR 50.59 evaluation for a new station Abnormal Operating Procedure (AOP) - M.09, "Loss of Charging," Rev. 0, that included a preplanned, procedur
Region: II | Sequoyah | 11386 | 07/31/2009 08/28/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Correct a Condition Adverse to Quality Associated with Out-of-Train Maintenance Controls |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71152B | Green. The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly correct a condition adverse to quality by failing to implement corrective actions to address deficient
Region: II | Sequoyah | 11384 | 06/30/2009 07/23/2009 | 2009003-02 | NRC | NCV | Initiating Events | Green | Reactor trip due to inadequate plant operating procedures |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | On April 28, 2009, with Unit 1 operating at approximately 27 percent RTP during startup from a refueling outage, a moisture separator reheater (MSR) shell side relief valve lifted. Operators responded by reducing power to approximately 18 percent RTP in a
Region: II | Sequoyah | 11358 | 01/07/2009 05/01/2009 | 2009002-01 | NRC | NCV | Initiating Events | Green | Pressurizer Pressure Transient due to Inadequate Maintenance Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000328 Sequoyah 2 |  | 71111.19 | Green. A Green self-revealing non-cited violation of Unit 2 Technical Specification 6.8.1 was identified for the licensee's failure to have an adequate procedure to ensure replacement of the pressurizer pressure master controller would not adversely impac
Region: II | Sequoyah | 11348 | 06/30/2008 08/06/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Gland Seal Steam Header Isolation Valves Not Scoped In Maintenance Rule |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.12 | The inspectors identified a Green, non-cited violation of 10 CFR 50.65(b)(2)(i) for the licensee's failure to include the gland seal steam supply and supply bypass isolation valves in the scope of their maintenance rule program. These valves are used in t
Region: II | Sequoyah | 11349 | 06/30/2008 08/06/2008 | 2008003-02 | NRC | URI | Mitigating Systems | Green | Procedure 0-MA-REM-000-001.0, Extended Station Blackout, Does Not Close Hydrogen Igniter Breakers |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 2515/174
Region: II | Sequoyah | 11352 | 06/27/2008 08/11/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Fire Detectors in 480 V Shutdown Board Room 2B2 Not Installed According to NFPA Code |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71111.05T | A Green non-cited violatin of Unit 2 License Condition 13, Fire Protection, was identified since fire detectors in the Unit 2 480 Volt shutdown board room 2B2 were not installed according to the applicable National Fire Protection Association code. Spe
Region: II | Sequoyah | 11354 | 06/27/2008 08/11/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Sprinklers too far below Ceiling in Cable Spreading Room |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05T | A green non-cited violation of Unit 1 License Condition 16 and Unit 2 License Condition 13, Fire Protection, was identified for failure to install the automatic suppression system (sprinkler system) in the cable spreading room according to the applicabl
Region: II | Sequoyah | 11345 | 03/31/2008 04/30/2008 | 2008002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Tagging Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | Green. A self-revealing NCV was identified for an inadequate tagging procedure that resulted in a failure to properly isolate a fire hydrant before maintenance. Because of the failure, the hydrant was forced off the associated fire protection system heade
Region: II | Sequoyah | 11347 | 03/31/2008 04/30/2008 | 2008002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Calibration Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000327 Sequoyah 1 |  | 71111.22 | Green. A self-revealing NCV was identified for failure to properly follow procedure when calibrating Loop 3 Steam Pressure Channel 1 on Unit 1. Because of failure to follow procedure, automatic steam generator level control rapidly reduced feedwater flow
Region: II | Sequoyah | 11343 | 12/31/2007 01/30/2008 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Effectively Implement Foreign Material Control Requirements in the RCS |  |  | TE?: N | 05000327 Sequoyah 1 |  | 71111.2 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, for failure to implement licensee Procedure SPP-6.5, Foreign Material Control. During a review of the core verification video following refueling and reactor vessel hea
Region: II | Sequoyah | 11359 | 12/14/2007 05/01/2009 | 2009002-02 | NRC | FIN | Barrier Integrity | Green | Procedure 0-MA-REM-000-001.0, Extended Station Blackout, Did Not Close Hydrogen Igniter Breakers |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71152 | Green. An NRC inspector identified a Green finding for the licensee's failure to implement a docketed commitment made to the NRC. Specifically, the licensee did not adequately revise procedures in accordance with a self-imposed standard to provide backup
Region: II | Sequoyah | 11332 | 09/30/2007 10/26/2007 | 2007004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure when Adjusting EDG Intake Fire Damper |  | H.4(b) Procedural Compliance | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.12 | Green. A self-revealing non-cited violation of Technical Specification 6.8.1a was identified for failure to follow procedures when performing maintenance on the intake fire damper for Emergency Diesel Generator 2A. Because of this failure, the damper inad
Region: II | Sequoyah | 11333 | 09/10/2007 10/11/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure To Use Appropriate Assumptions in Design Calculations |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a violation of 10 CFR 50, Appendix B, Criterion III, Design Control, associated with TVA's use of non-conservative design input values in design calculations. TVA's failure to use appropriate inputs in design calculations resulted in a
Region: II | Sequoyah | 11340 | 09/10/2007 10/11/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | No Procedure for Inspection/Replacement of DG Local Electrical Panel Filters |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a violation of Technical Specification 6.8.1 associated with Tennessee Valley Authority's (TVA) failure to develop a procedure that would provide periodic inspection and replacement of the emergency diesel generator room electrical pan
Region: II | Sequoyah | 11341 | 09/10/2007 10/11/2007 | 2007006-03 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Reduced Inventory/Mid-loop Operation. |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a violation of TS 6.8.1 for failure to establish an adequate procedure for reactor coolant system reduced inventory/mid-loop operations. Specifically, procedure 0-GO-13, Reactor Coolant System (RCS) Drain and Fill Operations, Rev. 57,
Region: II | Sequoyah | 11342 | 09/10/2007 10/11/2007 | 2007006-04 | NRC | NCV | Initiating Events | Green | Inadequate Abnormal Operating Procedure for RHR System Malfunctions During Mode 4 Conditions. |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 7111121 | The team identified a violation of Technical Specification 6.8.1 for failure to establish an adequate abnormal operating procedure for the Residual Heat Removal System (RHR) system malfunctions during shutdown conditions. Procedure AOP-R.03, RHR System Ma
Region: II | Sequoyah | 11321 | 03/31/2007 04/26/2007 | 2007002-02 | NRC | FIN | Initiating Events | Green | Failure to Properly Follow Procedure When Modifying Feedwater Regulating Valves |  | H.4(a) Human Error Prevention | TE?: N | 05000328 Sequoyah 2 |  | 71153 | A Green self-revealing finding was identified for failure to properly follow installation procedures when implementing a modification to the Unit 2 feedwater regulating valves. Inadequate clearance between the air tubing and fixed structures resulted in t
Region: II | Sequoyah | 11318 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Certify Qualifications and Status of Licensed Operators Were Current and Valid |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.11B | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 55.53, "Conditions of Licenses" for failure to certify the qualifications and status of licensed operators were current and valid prior to their resumption of license duties. Specific
Region: II | Sequoyah | 11319 | 12/31/2006 01/30/2007 | 2006005-02 | Self - Revealed | URI | Mitigating Systems | Green | Appendix R Manual Isolation Valve Failure to Close Within the Required Time |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71111.19
Region: II | Sequoyah | 11322 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate 20-foot Separation Zones for Fire Protection in Unit 1 480V Board Room 1B |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | The inspectors identified a Green non-cited violation of Unit 1 License Condition 16, Fire Protection, and Unit 2 License Condition 13, Fire Protection, for failure to protect certain equipment that was required for safe shutdown from fire damage. The lic
Region: II | Sequoyah | 11323 | 12/31/2006 01/30/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | Unprotected Power Cables to Vital Inverters in the Unit 1 480V Board Room 1B |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153 | The inspectors identified a Green non-cited violation of Unit 1 License Condition 16, Fire Protection, and Unit 2 License Condition 13, Fire Protection, for failure to protect certain electrical cables for safe shutdown equipment from fire damage. The pow
Region: II | Sequoyah | 11328 | 12/31/2006 01/30/2007 | 2006005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Lighting for Time-Critical Local Manual Actions for Post-Fire Safe Shutdown |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71153 | The inspectors identified a Green non-cited violation of Unit 2 License Condition 13, Fire Protection, for failure to maintain adequate lighting in the Unit 2 main steam valve vault room to support time-critical operator actions required for post-fire saf
Region: II | Sequoyah | 11308 | 06/30/2006 07/27/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Secure Crane Wall Doors in Mode 3 |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 6.8.1 for failure to follow procedure when entering containment at the beginning of the Unit 2 Cycle 13 outage. The doors between the raceway and the lower part of the polar crane
Region: II | Sequoyah | 11309 | 06/30/2006 07/27/2006 | 2006003-02 | Self - Revealed | FIN | Initiating Events | Green | Loose Isolated Phase Bus Duct Gasket Actuated Main Generator Neutral Overvoltage Relay Causing Reactor Trip |  |  | TE?: N | 05000328 Sequoyah 2 |  | 71153 | A self-revealing finding was identified for failure to implement effective preventive maintenance procedures to identify and correct a loose isolated phase bus duct gasket before its attachment degraded to the point of allowing the gasket to contact the b
Region: II | Sequoyah | 11306 | 03/31/2006 04/14/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Blocked Sprinkler Head Without Compensatory Actions |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.05Q | The inspectors identified a non-cited violation of Sequoyah Operating Licenses DPR-077, Section 2.C.(16) and DPR-079, Section 2.C.(13) for failure to establish adequate compensatory actions for obstructed fire sprinklers in the cable spreading room. Due t
Region: II | Sequoyah | 11307 | 03/31/2006 04/14/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Implement Compensatory Measures Necessary for Air in the ERCW Discharge |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 6.8.1 for failure to fully implement the compensatory measures needed to ensure the operability of the motor driven auxiliary feedwater pumps when using the essential raw cooling w
Region: II | Sequoyah | 124669 | 05/10/2019 |  |  | LIV |  | Green | Failure to Implement Required Compensatory Measure for ABSCE Boundary Breach Renders Both Trains of ABGTS Inoperable |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71153
Region: II | Sequoyah | 126524 | 02/11/2020 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation |  |  | TE?: N | 05000327 Sequoyah 1 05000328 Sequoyah 2 |  | 71114.05
Region: II | Summer | 125016 | 05/23/2019 06/27/2019 | 2019011-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Corrective Action Program Procedure |  | P.3 - Resolution | TE?: N | 05000395 Summer |  | 71152B | An NRC-identified Green finding was identified for the licensee’s failure to follow their corrective action process for condition report CR-12-02287. Specifically, the licensee failed to properly recognize this issue as a condition affecting regulatory co
Region: II | Summer | 124589 | 03/31/2019 05/14/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Evaluate Internal Heat Rise in ASCO Solenoid Valves |  | NPP | TE?: N | 05000395 Summer | Equipment Performance | 71111.21N | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR 50.49(e)(5) for the licensee's failure to appropriately consider heat rise and applicable accelerated aging criteria in the qualification of ASCO valve IPV02020-2
Region: II | Summer | 124772 | 03/31/2019 05/14/2019 | 2019001-02 | NRC | NCV | Barrier Integrity | Green | Failure to take Technical Specification (TS) actions for inoperable Reactor Building Cooling Unit (RBCU) Condensate Flow Monitor (TS 3.4.6.1) and submit Licensee Event Report (LER)(10 CFR 50.73(a)) |  | P.3 - Resolution | TE?: Y SL-IV-NCV | 05000395 Summer | RCS Equipment and Barrier Performance | 71152 | The inspectors identified a Green finding with an associated enforcement problem involving a non-cited violation (NCV) of TS 3.4.6.1, “Reactor Coolant System Leakage Detection Systems,” for a failure to take TS actions for inoperable RBCU Condensate Flow
Region: II | Summer | 38858 | 12/31/2018 02/13/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Leading to ‘A’ EDG Fire Event |  | P.3 - Resolution | TE?: N | 05000395 Summer |  | 71111.13 | A self-revealing, Green NCV of Technical Specification 6.8, “Procedures and Programs,” was identified for the failure to ensure procedures for performing maintenance on the ‘A’ EDG were adequately established which led to a leak in the ‘A’ EDG exhaust man
Region: II | Summer | 23514 | 04/04/2018 04/02/2018 | 2018010-01 | NRC | NCV | Barrier Integrity | Green | Failure to Justify Activation Energy for Valcor SOV (XVX06050A) |  | NPP | TE?: N | 05000395 Summer |  | 71111.21N | The NRC identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR 50.49 (e)(5) when the licensee failed to justify the basis for the activation energy used for Valcor solenoid operated valve (SOV) XVX06050A in accordance with Regulato
Region: II | Summer | 23515 | 04/04/2018 04/02/2018 | 2018010-02 | NRC | NCV | Barrier Integrity | Green | Failure to Verify the Seismic Qualification of Valcor Solenoid Operated Valve XVX06050A |  | NPP | TE?: N | 05000395 Summer |  | 71111.21N | The NRC identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to verify the adequacy of design for the seismic qualification of valve XVX06050A in acco
Region: II | Summer | 23516 | 04/04/2018 04/02/2018 | 2018010-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Radiation Harsh Environmental Qualification of Reactor Building Spray Pump A |  | NPP | TE?: N | 05000395 Summer |  | 71111.21N | The NRC identified a Green finding and associated NCV of 10 CFR 50.49 (e)(4) when the licensee failed to verify that RB spray pump A could perform its function under the radiation conditions expected during an accident in accordance with Section 2.1(3)(a
Region: II | Summer | 23994 | 03/31/2018 05/10/2018 | 2018001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Perform an Adequate Risk Assessment With Consequent Reactor Trip |  | H.5 - Work Management | TE?: N | 05000395 Summer |  | 71153 | A self-revealed, Green NCV was identified for the licensee’s failure to adequately assess risk in accordance with 10 CFR 50.65(a)(4), “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” involving repairs to a non-safety
Region: II | Summer | 23180 | 12/31/2017 02/13/2018 | 2017004-01 | NRC | FIN | Mitigating Systems | Green | Failure to Accomplish Station Procedures for Severe Weather |  | H.1 - Resources | TE?: N | 05000395 Summer |  | 71111.01 | A Green finding (FIN) was identified by the NRC for the failure of the licensee to accomplish operations administrative procedure, OAP-109.1, “Guidelines for Severe Weather,” Rev. 4H, for adequate control of sandbags used for ground level plant building a
Region: II | Summer | 23183 | 12/31/2017 02/13/2018 | 2017004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of an Emergency Feedwater Auto Start Actuation Signal |  | P.2 - Evaluation | TE?: N | 05000395 Summer |  | 71153 | A self-revealing, Green, non-cited violation (NCV) of technical specification (TS) 3.3.2 was identified involving the failure of the ‘C’ main feedwater pump to trip and resultant loss of an emergency feedwater auto start actuation signal. The licensee ent
Region: II | Summer | 22313 | 10/20/2017 11/30/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Design for the EFW system when Supplied by SW |  | NPP | TE?: N | 05000395 Summer |  | 71111.21M | Green: The NRC identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to verify the emergency feedwater (EFW) pumps would be capable of
Region: II | Summer | 22314 | 10/20/2017 11/30/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Testing Program for Inverter XIT5904 and Time Delay Relay in the EFW/SW Crosstie Valve Actuation Circuitry |  | NPP | TE?: N | 05000395 Summer |  | 71111.21M | Green: The NRC identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” involving two examples. Specifically, the licensee (1) failed to establish a testing program to assure the adequacy of the shutdown setpoint of the safety-relat
Region: II | Summer | 22315 | 10/20/2017 11/30/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a CAQ for Power Shield Catalog #609903-T501N |  | NPP | TE?: N | 05000395 Summer |  | 71111.21M | Green: The NRC identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Actions,” for the licensee’s failure to identify that a deviation in equipment qualification of power shield relays in 480V switchgear XSW-1DB1 was a condition ad
Region: II | Summer | 22336 | 09/30/2017 11/01/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Inspection of Fire Barriers |  | H.1 - Resources | TE?: N | 05000395 Summer |  | 71111.05Q | The inspectors identified a Green, NCV of Operating License Condition 2.C.(18), “Fire Protection Program,” for failure to adequately establish a surveillance procedure for fire penetration inspections. The licensee entered the problem into their correctiv
Region: II | Summer | 22276 | 09/30/2017 11/01/2017 | 2017003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess the Risk for an Activity with Consequent Loss of Core Cooling (Section 1R13) |  | H.5 - Work Management | TE?: N | 05000395 Summer |  | 71111.13 | The inspectors identified a Green, NCV of 10 CFR 50.65(a)(4), “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” involving the licensee’s failure to perform an adequate risk assessment for an activity involving restora
Region: II | Summer | 125903 | 06/30/2017 10/25/2019 | 2017002-01 |  | NOV | Mitigating Systems | Green | Closure of Previous NRC-identified SL-IV Cited Violation |  | NONE | TE?: N | 05000395 Summer |  | 71111.05XT | The inspectors identified a Green finding with a cited violation of Operating Licensee Condition 2.C.(18) for failure to ensure that conditions adverse to fire protection as noted in a previous NRC-identified Green NCV, 05000395/2013003-03, "Failure to Ad
Region: II | Summer | 17080 | 12/31/2016 02/08/2017 | 2016004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Accomplish Procedure for Foreign Material Exclusion Control Involving Failure of a Safety-Related Breaker |  | H.5 Work Management | TE?: N | 05000395 Summer |  | 71153 | Green. The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to accomplish safety-related (SR) station administrative procedure, SAP-0363, "Forei
Region: II | Summer | 17079 | 10/27/2016 02/08/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality for 'B' Emergency Diesel Generator Exhaust Manifold Weld Indications |  | P.3 Resolution | TE?: N | 05000395 Summer |  | 71111.15 | Green. A self-revealing, Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to promptly identify and correct a condition adverse to quality (CAQ) involving welded joint indications in the 'B' emergency d
Region: II | Summer | 17067 | 10/21/2016 12/05/2016 | 2016010-02 | NRC | NCV | Mitigating Systems | Green | Failure to identify unsealed cabinet Specified by NFPA 805 Section 3.3.1.2(1) (Section 1RO5.15) |  | H.2 Field Presence | TE?: N | 05000395 Summer |  | NONE | Green. The NRC identified a Green, non-cited violation (NCV) of the 10 CFR 50.54(hh)(2) requirements. Specifically, the team identified aspects of the implementation strategy that were inconsistent to support the stated commitments. The licensee's fail
Region: II | Summer | 17068 | 10/21/2016 12/05/2016 | 2016010-03 | NRC | NCV | Mitigating Systems | Green | Failure to ensure credited equipment to support the 50 54hh requirements were adequate (Section 1RO5.16) |  |  | TE?: N | 05000395 Summer |  | NONE | Green. The NRC identified a Green, non-cited violation (NCV) for the failure to include potentially high-risk fire scenarios in the current fire protection program. In this instance, the team identified unsealed electrical cabinets credited as being sea
Region: II | Summer | 17071 | 10/21/2016 12/05/2016 | 2016010-05 | NRC | NCV | Mitigating Systems | Green | Failure to meet corrective action requirements consistent with NFPA 805 Section 2.6.3) (Section 4OA2) |  | P.3 Resolution | TE?: N | 05000395 Summer |  | NONE | Green. The NRC identified a Green non-cited violation (NCV) of the V.C Summer Nuclear Station, Unit 1, Renewed Facility Operating License (FOL) Condition 2.C.18 requiring the licensee to implement and maintain in effect all provisions of the approved FP
Region: II | Summer | 17066 | 10/14/2016 11/22/2016 |  | NRC | NCV | MISC | Green | Failure to Correct a Condition Adverse to Quality Associated with a Previously Issued NCV (Section 4OA1.C.2) |  | P.3 Resolution | TE?: N | 05000395 Summer |  | 71152B | Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct a condition adverse to quality associated with a previously issued NCV, 05000395/2012004-02, Inadequate I
Region: II | Summer | 17078 | 10/12/2016 02/08/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedures for Corrective Actions to Address Conditions Adverse to Fire Protection |  | H.1 Resources | TE?: N | 05000395 Summer |  | 71111.05Q | Green. The inspectors identified a Green, non-cited violation (NCV) of the V.C. Summer Nuclear Station Operating License, Condition 2.C (18), "Fire Protection Program," for the failure to establish procedures requiring corrective action for conditions, in
Region: II | Summer | 17060 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Meet HRA Entry Requirements (Two Examples) |  | H.12 Avoid Complacency | TE?: N | 05000395 Summer |  | 71124.01 | Green. The inspectors identified two examples of a Green, self-revealing, non-cited violation (NCV) of Technical Specification (TS) 6.12.1, "High Radiation Area." TS 6.12.1 requires that entries into high radiation areas (HRAs) be controlled with issuance
Region: II | Summer | 17061 | 09/30/2016 11/08/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Prescribe Work Instructions for a Temporary Repair on a Safety-Related Component |  | H.1 Resources | TE?: N | 05000395 Summer |  | 71152 | Green. The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to prescribe instructions for a temporary repair of the safety-related 'C' component
Region: II | Summer | 17058 | 04/29/2016 07/27/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage Risk of Maintenance Activities Following Risk Model Updates (Section 1R13) |  | H.5 Work Management | TE?: N | 05000395 Summer |  | 71111.13 | Green. The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," involving the licensee's failure to develop and implement specific risk mana
Region: II | Summer | 16466 | 03/31/2016 05/11/2016 | 2016001-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Implement Adequate Administrative Controls Following a Departure from NFPA 80-1973 and Provide NRC Staff Complete and Accurate Information |  | P.3 Resolution | TE?: Y SL-IV-NCVIV | 05000395 Summer |  | 71111.05Q | The inspectors identified a Severity Level IV, non-cited violation (NCV) of 10 CFR 50.9(a), "Completeness and accuracy of information," and an associated Green non-cited violation of V.C. Summer, Operating License Condition 2.C.(18) for a NFPA 80-1973 cod
Region: II | Summer | 16462 | 12/31/2015 01/29/2016 | 2015004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Accomplish Procedure for Diagnostic Testing Resulting in Valve Failures (Section 4OA2.2) |  | P.2 Evaluation | TE?: N | 05000395 Summer |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, which requires in part that activities affecting quality shall be accomplished in accordance with procedures. Specifically, the
Region: II | Summer | 16465 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk Associated with Emergent Work |  | H.5 Work Management | TE?: N | 05000395 Summer |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(4) which requires in part that the licensee assess and manage the increase in risk that may result from proposed maintenance activities. Specifically, the licensee failed to assess and ma
Region: II | Summer | 16460 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fire Door/Steam Propagation Barrier in Accordance With the Fire Protection Program Procedure |  | H.1 Resources | TE?: N | 05000395 Summer |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specifications (TS) 6.8.1.f, Fire Protection Program (FPP) procedures, which involved a failure to comply with the requirements of FPP-025, "Fire Containment," Revision (Rev.) 4H, for maintainin
Region: II | Summer | 16445 | 11/07/2014 12/22/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures for Scaffolding and Special Orders for 10CFR50.59 Screenings/Evaluations |  | H.8 Procedure Adherence | TE?: N | 05000395 Summer |  | 7111121 | The team identified a Green non-cited violation of technical specification (TS) 6.8.1, Procedures and Programs, for the licensee's failure to follow procedure requirements to perform 10CFR50.59 screenings/evaluations on scaffolding and special orders fo
Region: II | Summer | 16452 | 11/07/2014 12/22/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Failure to Follow Corrective Action Program Procedures |  | P.1 Identification | TE?: N | 05000395 Summer |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow station procedures to perform operability/functionality evaluations for condition
Region: II | Summer | 16453 | 11/07/2014 12/22/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Instrument Uncertainties Result in Non-Conservative Values In EOP-2.2 & ARP-001-XCP-612; RWST Swapover |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a Green non-cited violation NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to consider instrument uncertainties when determining refueling water storage tank (RWST) setpoints and assoc
Region: II | Summer | 16454 | 11/07/2014 12/22/2014 | 2014007-04 | NRC | NCV | Barrier Integrity | Green | Failure to Account for Containment Temperature Measurement Uncertainty |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to account for instrument uncertainty on the containment bulk average temperature instrumentation used in calculat
Region: II | Summer | 16443 | 08/22/2014 10/03/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Degraded Emergency Feedwater System Piping Supports |  | H.1 Resources | TE?: N | 05000395 Summer |  | 71152B | An NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to identify and correct conditions adverse to quality. Specifically, inspectors determined the licensee failed to identify three d
Region: II | Summer | 16434 | 06/30/2014 08/13/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Accomplish Procedure to Determine Cause and Correct Failures of Reactor Building Spray System Relief Valve |  | P.2 Evaluation | TE?: N | 05000395 Summer |  | 71152 | An NRC-identified NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to accomplish a general test procedure, GTP-302, requirement to determine the cause and correct the conditions
Region: II | Summer | 16442 | 06/30/2014 08/13/2014 | 2014003-02 | NRC | FIN | Mitigating Systems | Green | Failure to Develop Adequate Post Modification Testing for the Alternate Seal Injection System |  | H.11 Challenge the Unknown | TE?: N | 05000395 Summer |  | 71152 | An NRC-identified FIN was identified for the failure of the licensee to accomplish station procedures for development, review, and performance of adequate post modification testing of the alternate seal injection (ASI) system. The problem is in the licens
Region: II | Summer | 16432 | 03/31/2014 05/01/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Declare the 'A' Safety Injection Pump Inoperable and Enter TS 3.5.2 Action a (Section 1R12) |  |  | TE?: N | 05000395 Summer |  | 71111.15 | The NRC identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to enter TS 3.5.2, Action a, due to inoperability of the 'A' charging/safety injection (SI) pump during periods when
Region: II | Summer | 16433 | 03/31/2014 05/01/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality for an Inboard Bearing Oil Leak on the 'A' CCW Pump |  | P.3 Resolution | TE?: N | 05000395 Summer |  | 71152 | The NRC identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality (CAQ) involving an inboard bearing oil leak on the 'A' component cooling wate
Region: II | Summer | 16428 | 12/31/2013 02/10/2014 | 2013005-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure for Control of containment Penetrations |  |  | TE?: N | 05000395 Summer |  | NONE | An NRC-identified Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings,"was identified for the licensee's failure to prescribe an adequate procedure for control of temporary containment penetration devic
Region: II | Summer | 16426 | 11/22/2013 01/02/2014 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Design the Safety-related Chiller Modification to Appropriate Quality Standards |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000395 Summer |  | 71111.17T | Green: The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to review the application of design processes prescribed for the heating, ventilation, and air conditioning (HVAC) syste
Region: II | Summer | 16427 | 11/22/2013 01/02/2014 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent a Water Hammer Event in the RBCU SW Discharge Piping |  |  | TE?: N | 05000395 Summer |  | 71111.17T | Green: The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of design to prevent water hammer on the reactor building cooling unit (RBCU) service water
Region: II | Summer | 16418 | 11/01/2013 11/01/2013 | 2013010-01 | NRC | FIN | Mitigating Systems | Green | Failure to Meet Training Program Standards on Job Performance Measures for the Annual Licensed Operator Requalification Operating Examination (Section 1R11.1) |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000395 Summer |  | 71111.11B
Region: II | Summer | 16419 | 11/01/2013 11/01/2013 | 2013010-02 | NRC | FIN | Mitigating Systems | Green | Failure to Meet Training Program Standards for the Biennial Licensed Operator Requalification Written Examination (Section 1R11.2) |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000395 Summer |  | 71111.11B
Region: II | Summer | 16420 | 11/01/2013 11/01/2013 | 2013010-03 | NRC | FIN | Mitigating Systems | Green | Failure to Meet Training Program Standards for Administration of the Annual Licensed Operator Requalification Operating Examination (Section 1R11.3) |  | H.4(b) Procedural Compliance | TE?: N | 05000395 Summer |  | 71111.11B
Region: II | Summer | 16415 | 09/30/2013 11/12/2013 | 2013004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to evaluate readiological conditions |  | H.3(a) Work Planning | TE?: N | 05000395 Summer |  | 71124.01 | A Green, self-revealing, NCV was identified for the failure to perform radiological surveys required by 10 CFR 20.1501(a) to ensure the potential radiological hazards and extent of radiation levels were understood and controlled before disassembling press
Region: II | Summer | 16416 | 09/30/2013 11/12/2013 | 2013004-02 | NRC | FIN | Mitigating Systems | Green | Failure to develop adequate corrective action for a condition adverse to quality involving the loss of the alternate AC transformer |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000395 Summer |  | 71152 | The inspectors identified a Green finding of licensee procedure, SAP-999, "Corrective Action," Revision 11 for the failure to develop corrective actions for a Level 3 condition report (CR) which described a condition adverse to quality (CAQ) associated wi
Region: II | Summer | 16417 | 09/30/2013 11/12/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Failure to adequately evaluate new fire hoses for post-loss coolant accident conditions. |  | H.2(d) Facilities & Equipment | TE?: N | 05000395 Summer |  | 71111.05Q | The NRC inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately accomplish engineering services procedure, ES-0419, "Equal To/Better Than (ETBT) Evaluation Process," R
Region: II | Summer | 16405 | 06/30/2013 08/06/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Past Operability Evaluation of the Service Water Outlet Header to 'B' Component Cooling Water Cross-Connect Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to accomplish a past operability evaluation for the 'B' component cooling water (CCW) train as required b
Region: II | Summer | 16406 | 06/30/2013 08/06/2013 | 2013003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Design, Install and Maintain Oil Collection Devices for Reactor Coolant Pump Motors |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71111.05Q | The inspectors identified three examples of a non-cited violation of the Virgil C. Summer Nuclear Station, Unit No. 1, Renewed Facility Operating Licensee No. NPF-12, Condition 2.C(18), Fire Protection System, associated with 10 CFR 50, Appendix R, Sectio
Region: II | Summer | 16407 | 06/30/2013 08/06/2013 | 2013003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage the Risk Impact of Time to Core Boil With Reactor Vessel Upper Internals Installed and Cavity Level is Greater Than Reactor Vessel Flange |  | H.3(a) Work Planning | TE?: N | 05000395 Summer |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(4) which requires in part that the licensee assess and manage the increase in risk that may result from proposed maintenance activities. Specifically, the licensee failed to assess and ma
Region: II | Summer | 16404 | 03/31/2013 05/06/2013 | 2013002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Examinations of Reactor Pressure Vessel Supports |  | P.2(b) Implementing Operating Experience | TE?: N | 05000395 Summer |  | NONE | The inspectors identified a non-cited violation (NCV) of Code of Federal Regulation (CFR) 10 CFR Part 50.55a, "Codes and Standards," involving the licensee's failure to include the reactor pressure vessel supports in the scope of the V. C. Summer Inservic
Region: II | Summer | 16402 | 12/31/2012 02/07/2013 | 2012005-06 | NRC | NCV | Public Radiation Safety | Green | Resin Shipment in Steel High Iintegrity Container Noncompliance with 10 CFR 61.56(b)(2) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71124.08 | A self-revealing NCV of 10 CFR 61.56(b)(2) was identified because the licensee transported a cask shipment for disposal at the Energy Solutions Disposal Facility, Barnwell, South Carolina, which contained liquid above regulatory limits for final form for
Region: II | Summer | 16403 | 12/31/2012 02/07/2013 | 2012005-07 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality for Alignment of the Safety-Related Refueling Water Storage Tank to a Non-Seismic Spent Fuel Purification system |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | NONE | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the failure to promptly identify and correct a condition adverse to quality (CAQ) involving alignment of the safety-related refueling
Region: II | Summer | 16391 | 10/31/2012 12/14/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures and Procedure Compliance For Preventative Maintenance Deferrals |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71152B | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to ensure that the procedure for performing Preventative Maintenance (PM) deferrals included provisio
Region: II | Summer | 16388 | 09/30/2012 11/07/2012 | 2012004-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Update the UFSAR for a Modification to the Sodium Hydroxide System |  |  | TE?: Y SL-IV-NCVIV | 05000395 Summer |  | 71152 | A Green, severity level (SL) IV, non-cited violation was identified by the NRC for the failure of the licensee to update the updated final safety analysis report (UFSAR) for a modification to the sodium hydroxide (NaOH) portion of the reactor building spr
Region: II | Summer | 16390 | 09/30/2012 11/07/2012 | 2012004-02 | NRC | NCVIV | Mitigating Systems | Green | Inadequate Installation of Unit 1 Service Water Piping and Related Pipe Support |  |  | TE?: Y SL-IV-NCVIV | 05000395 Summer |  | 71153 | A non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the NRC for the failure to accomplish the installation of Unit 1 service water (SW) piping and supports in accordance with prescribed d
Region: II | Summer | 16386 | 07/03/2012 07/31/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Duties of the Shift Engineer During Off-Normal Fire Events |  |  | TE?: N | 05000395 Summer |  | 71111.05T | An NRC identified non-cited violation of V.C. Summer Technical Specification 6.8.1.e., Procedures and Programs - Emergency Plan, was identified related to the emergency plan procedural duties of the Shift Engineer (SE)/Shift Technical Advisor (STA) dur
Region: II | Summer | 16387 | 07/03/2012 07/31/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Missing Cold Shutdown Repair Equipment |  | H.2(d) Facilities & Equipment | TE?: N | 05000395 Summer |  | 71111.05T | An NRC identified non-cited violation of License Condition 2.C (18), "Fire Protection System," was identified for the licensee's failure to provide readily available equipment to support the implementation of cold shutdown fire emergency procedures (FE
Region: II | Summer | 16367 | 04/01/2012 05/11/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Combustibles Adjacent to a Safety-Related Motor Control Center |  | H.3(a) Work Planning | TE?: N | 05000395 Summer |  | 71111.05Q | The inspectors identified a non-cited violation of V.C. Summer Nuclear Station Technical Specification 6.8.1 for a failure to implement the requirements of their fire protection procedures for control of transient combustibles associated with a work activ
Region: II | Summer | 16368 | 04/01/2012 05/11/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Inspect Service Water Pump Motor Lube Oil Heat Exchangers |  |  | TE?: N | 05000395 Summer |  | 71111.07A | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately prescribe a procedure to inspect the service water (SW) pump motor lube oil heat exchangers
Region: II | Summer | 16369 | 04/01/2012 05/11/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze a Moderate Energy Fluid System for Leakage Cracks |  |  | TE?: N | 05000395 Summer |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to analyze a moderate energy fluid system for leakage cracks resulting in flooding and/or spray as described in the licensee's
Region: II | Summer | 16373 | 04/01/2012 05/11/2012 | 2012002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Conditions Adverse to Quality for Lightning Induced Trips of Safety-Related Chillers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | 71152 | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for two examples of the failure to promptly identify and correct a condition adverse to quality (CAQ) involving safety-related chiller tri
Region: II | Summer | 16376 | 04/01/2012 05/11/2012 | 2012002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Fire Protection Program Requirements for Procurement and Use of Approved Fire Hose |  | H.4(b) Procedural Compliance | TE?: N | 05000395 Summer |  | 71153 | The NRC identified an apparent violation of V.C. Summer Nuclear Station's Renewed Operating License NPF-12, 2.C(18), "Fire Protection System," with two examples for the failure to comply with Fire Protection Program (FPP) requirements in which the license
Region: II | Summer | 16363 | 09/30/2011 10/27/2011 | 2011004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement a Procedure for Manipulation of the C' Main Steam Isolation Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000395 Summer |  | 71153 | A self-revealing, non-cited violation was identified for the failure to comply with Technical Specification 6.8.1 to adequately implement a main steam operating procedure during manipulation of the 'C' main steam isolation valve (MSIV) resulting in excess
Region: II | Summer | 16336 | 06/30/2011 08/04/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess and Manage Risk of Switchyard Maintenance Activities During Lowered RCS Inventory Conditions (Section 1R13) |  | H.3(a) Work Planning | TE?: N | 05000395 Summer |  | 71111.13 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure to perform an adequate risk assessment and implement approved high r
Region: II | Summer | 16337 | 06/30/2011 08/04/2011 | 2011003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform ISI General Visual Examinations of Containment Moisture Barrier Associated with Containment Liner Leak Chase Test Connection Threaded Pipe Plugs |  |  | TE?: N | 05000395 Summer |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50.55a, "Codes and Standards," involving the licensee's failure to properly apply Subsection IWE of ASME Section XI for conducting general visual examinations of the metal-to-metal pipe plugs installed
Region: II | Summer | 16343 | 04/15/2011 05/05/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Procedures to Provide Starting Air to EDGs During a SBO Event |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50.63, "Loss of all Alternating Current Power," for failure to ensure Regulatory Guide 1.155, "Station Blackout," (SBO) requirements were implemented. Specifically, the licensee failed to develop p
Region: II | Summer | 16347 | 04/15/2011 05/05/2011 | 2011006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate the Design Basis into Procedures for Low EDG Air Pressure and Low Thermal Barrier Heat Exchanger Flow |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control" involving two examples. In one example, the licensee did not properly translate the instrument uncertainties associated with the EDG low pressure ala
Region: II | Summer | 16348 | 04/15/2011 05/05/2011 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Calculate Motor Actuator Output Torque and Control Circuit Voltages for MOVs |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to use conservative motor control center (MCC) voltage inputs or methodologies when calculating motor actuator outpu
Region: II | Summer | 16349 | 04/15/2011 05/05/2011 | 2011006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of the Suction Lift for the Fuel Oil Transfer Pumps |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to establish design control measures to verify or check the adequacy of design inputs used to determine the required suct
Region: II | Summer | 16355 | 04/15/2011 05/05/2011 | 2011006-05 | NRC | NCV | Mitigating Systems | Green | Failure to Develop a Procedure to Ensure an Emergency Diesel Generator Alarm Device was Calibrated or Tested |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a NCV of Technical Specification 6.8, "Procedures and Programs", for the licensee's failure to develop a procedure to ensure an EDG alarm device was properly calibrated or tested. Specifically, the component validating the "full" sta
Region: II | Summer | 16356 | 04/15/2011 05/05/2011 | 2011006-06 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Test Emergency Feedwater Pump Discharge Check Valves |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control" for the licensee's failure to establish a test program that demonstrated the operability of EFW pump discharge check valves. The test procedure was
Region: II | Summer | 16357 | 04/15/2011 05/05/2011 | 2011006-07 | NRC | NCV | Mitigating Systems | Green | Failure to Use the Most Limiting Design Inputs in an Electrical Calculation |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to use the most limiting design inputs in an electrical calculation associated with determining settings for the degr
Region: II | Summer | 16361 | 04/15/2011 05/05/2011 | 2011006-08 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Timely Corrective Actions to Address Design Bases Requirements for SGTR Event |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action", for the licensee's failure to implement prompt corrective actions to ensure that SG primary to secondary break flow could be terminated within th
Region: II | Summer | 16362 | 04/15/2011 05/05/2011 | 2011006-09 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Account for the In-rush Current of the 7.2 kV Breaker Spring Charging Motors in a Safety-related Battery Voltage Drop Calculation |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to adequately account for the in-rush current of the 7.2 kV breaker spring charging motors in a safety-related calcul
Region: II | Summer | 16327 | 12/31/2010 01/27/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct condition adverse to quality involving inadequate EDG engine driven pump preventive maintenance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | NONE | -Green. The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a condition adverse to quality following the February 10, 2010, failure of the '
Region: II | Summer | 16320 | 10/22/2010 11/23/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to maintain safety related cables in a nonsubmerged environment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | 71152B | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a condition adverse to quality. The licensee failed to recognize that low voltage safety related cables leadin
Region: II | Summer | 16319 | 06/30/2010 07/27/2010 | 2010003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Station Tagout Procedure for Controlling Safety and Non-safety Related Grounding Equipment Results in Loss of All Balance of Plant Power and Switchgear Fires |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71153 | A Green self-revealing non-cited violation (NCV) of TS 6.8.1.a was identified for the failure to establish adequate procedural tagging controls of safety and non-safety related electrical ground protection equipment which contributed to the main power tra
Region: II | Summer | 16308 | 12/31/2009 01/29/2010 | 2009005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Results in Inadvertent Loss of Spent Fuel Pool Inventory |  | H.4(b) Procedural Compliance | TE?: N | 05000395 Summer |  | 71111.2 | A Green self-revealing non-cited violation (NCV) was identified for the failure to comply with TS 6.8.1. As a result of the failure to follow a procedure, approximately 8000 gallons of water was inadvertently transferred from the SFP to the refueling cavi
Region: II | Summer | 16309 | 12/31/2009 01/29/2010 | 2009005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedure and Correct Previously Identified Deficiencies with the Operator Workaround Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000395 Summer |  | 71152 | A Green NRC-identified finding was identified for the failure to adequately implement a procedure and correct previously identified deficiencies with the licensee's operator workaround program. This resulted in operator workarounds and challenges not full
Region: II | Summer | 16301 | 03/31/2009 04/29/2009 | 2009002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Effectively Monitor the Performance of the Control Room Normal and Emergency Air Handling System per the Maintenance Rule |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000395 Summer |  | 71111.12 | The inspectors identified an NCV of 10 CFR 50.65 (Maintenance Rule) with two examples for failing to demonstrate that the performance of the control room normal and emergency air handling (control room ventilation) system was being effectively controlled
Region: II | Summer | 16297 | 12/10/2008 01/07/2009 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Motor Starting Analysis |  |  | TE?: N | 05000395 Summer |  | 7111121 | Green. The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee failed to verify the adequacy of the degraded voltage relay voltage setpoints by performing motor starting analyses based on volta
Region: II | Summer | 16298 | 12/10/2008 01/07/2009 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | EDG Exceeded Technical Specification Allowable Outage Time |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000395 Summer |  | 7111121 | This finding is more than minor because exceeding a Technical Specification Limiting Condition of Operation affects the Mitigating Systems Cornerstone objective of ensuring the availability, reliability, and operability of the EDGs to perform their intend
Region: II | Summer | 16299 | 12/10/2008 01/07/2009 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Analyzing the Impact of Updated Vendor Technical Manual |  | P.2(b) Implementing Operating Experience | TE?: N | 05000395 Summer |  | 7111121 | This finding is more than minor because it affects the Mitigating Systems Cornerstone objective to ensure the reliability, availability, and capability of systems that respond to initiating events and is associated with the attribute of procedure quality,
Region: II | Summer | 16300 | 12/10/2008 01/07/2009 | 2008007-04 | NRC | FIN | Mitigating Systems | Green | Failure to Maintain a Vendor Interface Program |  |  | TE?: N | 05000395 Summer |  | 7111121 | This finding is more than minor because it affects the Mitigating Systems Cornerstone objective to ensure the reliability, availability, and capability of systems that respond to initiating events and is associated with the attribute of equipment performa
Region: II | Summer | 16294 | 09/30/2008 10/30/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform ECG Tests During the Biennial Medical Exam for Licensed Operators |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000395 Summer |  | 71111.11B | On August 11, 2008, while reviewing licensed operator medical records, the inspectors identified two operators who had not received an ECG test as part of their biennial medical exam. The inspectors then reviewed additional licensed operator medical recor
Region: II | Summer | 16295 | 09/30/2008 10/30/2008 | 2008004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain the Control Room Pressure Boundary Operable and Complete the Required TS Actions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71111.15 | A Green non-cited violation of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.6, "Control Room Normal and Emergency Air Handling System," was identified by the inspectors for failure to maintain the control room boundary intact an
Region: II | Summer | 16292 | 06/30/2008 07/29/2008 | 2008003-01 | NRC | FIN | Initiating Events | Green | Untimely Corrective Actions To Resolve Feedwater Regulating Valve Malfunction Resulted In Reactor Trip |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000395 Summer |  | 71152 | A Green self-revealing finding was identified for the failure to implement effective and timely corrective actions to prevent failure of a main feedwater regulating valve IFV000498 that resulted in a reactor trip. This valve failed due to previously ident
Region: II | Summer | 16293 | 06/27/2008 07/23/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | B.5.b Phase 2 and 3 Mitigating Strategy |  | H.2(d) Facilities & Equipment | TE?: N | 05000395 Summer |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: II | Summer | 16285 | 12/31/2007 01/24/2008 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | Failure to implement TS required administrative controls when opening containment isolation valves 8767-DN and 8768-DN |  | H.3(a) Work Planning | TE?: N | 05000395 Summer |  | 71111.13 | Green. A Green non-cited violation (NCV) of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.4, "Containment Isolation Valves", was identified by the inspectors for the failure to implement required administrative controls when ope
Region: II | Summer | 16286 | 12/31/2007 01/24/2008 | 2007005-02 | NRC | NCV | Initiating Events | Green | Failure to maintain two required reactor coolant system leak detection systems operable and complete the required TS actions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000395 Summer |  | 71111.22 | Green. A Green non-cited violation (NCV) of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.6.1, "Leak Detection Systems", was identified by the inspectors for failure to maintain two required reactor coolant system (RCS) leak det
Region: II | Summer | 16284 | 09/30/2007 10/30/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Dedicated Manual Operator Risk Management Actions During EDG Surveillance Testing |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000395 Summer |  | 71111.22 | A Green non-cited violation (NCV) of 10 CFR 50.65(a)(4) was identified by the inspectors for the licensee's failure to manage the increase in plant risk during the conduct of "A" emergency diesel generator (EDG) routine surveillance testing. Specifically,
Region: II | Summer | 16280 | 03/31/2007 04/30/2007 | 2007002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Results in Repetitive Spurious Tripping of EDG Room Ventilation Fan Molded Case Circuit Breakers |  |  | TE?: N | 05000395 Summer |  | 71111.15 | A Green self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for inadequate corrective actions which resulted in repetition of a significant condition adverse to quality involving the spurious tri
Region: II | Summer | 16281 | 03/31/2007 04/30/2007 | 2007002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Shutdown of Required Containment Radiation Monitor During Reactor Building Purge System Operation Results in Violation of TS 3.3.2 |  |  | TE?: N | 05000395 Summer |  | 71153 | A Green self-revealing non-cited violation of Technical Specification 3.3.2 was identified for failure to maintain two containment radiation monitors operable and capable of automatically isolating reactor building purging operations in the event of high
Region: II | Summer | 16274 | 12/31/2006 01/25/2007 | 2006005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Surveillance Procedure Resulting in Inoperability of "B" ECCS Accumulator |  |  | TE?: N | 05000395 Summer |  | 71111.22 | A green self-revealing non-cited violation of Technical Specification 6.8.1.c was identified for failure to follow surveillance testing procedure resulting in the inadvertent partial draining of the "B" emergency core cooling system (ECCS) accumulator. Th
Region: II | Summer | 16275 | 12/31/2006 01/25/2007 | 2006005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure for Maintaining Steam Generator Water Level Results in Turbine Trip During Power Escalation |  |  | TE?: N | 05000395 Summer |  | 71153 | A green self-revealing non-cited violation of Technical Specification 6.8.1.a was identified for operator failure to follow procedure for maintaining steam generator water level while transitioning from the emergency feedwater system to the main feedwater
Region: II | Summer | 16271 | 09/30/2006 10/30/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Associated with a Previous Violation Involving Failure to Implement Procedures for a Loss of Control Room Annunciator Event |  |  | TE?: N | 05000395 Summer |  | 71153 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions for a previously identified NCV. The corrective actions taken were not adequ
Region: II | Summer | 16272 | 09/30/2006 10/30/2006 | 2006004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Fire Protection Surveillance Procedure to Prevent Inadvertent Fire Damper Closures and High Temperatures in the Relay Room |  |  | TE?: N | 05000395 Summer |  | 71111.22 | A Green self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.8.1.f was identified for failure to follow a fire protection surveillance testing procedure resulting in a TS Limiting Condition for Operation (LCO) entry due to exceeding
Region: II | Summer | 16258 | 06/30/2006 07/27/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate and Timely Corrective Actions to Preclude Repetitive Spurious Tripping of Safety Related Molded Case Circuit Breakers |  |  | TE?: N | 05000395 Summer |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B Criterion XVI was identified for the licensee's failure to take adequate and timely corrective actions to preclude repetition of a significant condition adverse to quality. Specifical
Region: II | Summer | 16261 | 06/23/2006 07/27/2006 | 2006008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify the SBLOCA Most Limiting Condition for Verification of RHR MOV Operability |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee's corrective action to address an industry operating experience issue applicable to their station was inadequate in that
Region: II | Summer | 16262 | 06/23/2006 07/27/2006 | 2006008-02 | NRC | NCV | Mitigating Systems | Green | Deficient Extent of Condition Review for EDG B Lube Oil TCV Malfunction |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee's corrective action to evaluate an extent of condition on emergency diesel generator (EDG) A following identification of
Region: II | Summer | 16263 | 06/23/2006 07/27/2006 | 2006008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for EDG Intercooler Performance Testing |  |  | TE?: N | 05000395 Summer |  | 7111121 | The team identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, the licensee used non-conservative acceptance criteria for the emergency diesel generator (EDG) intercooler performance test, PTP-213.00
Region: II | Summer | 16067 | 03/31/2006 04/28/2006 | 2006007-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Use Adequate Maintenance Procedures to Inspect and Repair Main Steam Isolation Valves |  |  | TE?: N | 05000395 Summer |  | 71152B | A self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for failure to establish, implement, and maintain adequate maintenance procedures to ensure that the Main Steam Isolat
Region: II | Summer | 125347 | 08/12/2019 |  |  | LIV |  | Green | Licensee Identified Violation |  |  | TE?: N | 05000395 Summer |  | 71111.15
Region: II | Summer | 125868 | 11/07/2019 |  |  | LIV |  | Green | Licensee Identified Non-Cited Violation, of 10 CFR 50.54(q)(2) and 50.47(b)(4) |  |  | TE?: N | 05000395 Summer |  | 71114.04
Region: II | Surry | 126374 | 12/31/2019 02/12/2020 | 2019004-01 | NRC | FIN | Initiating Events | Green | Failure to Identify Nonfunctional Backflow Preventers During Operator Rounds |  | H.9 - Training | TE?: N | 05000280 Surry 1 05000281 Surry 2 | Protection Against External Factors | 71111.06 | An NRC-identified Green Finding was identified for the licensee’s failure to adequately inspect backflow preventers as required by procedure 0-LOG-AUX-001R, “Auxiliary Building Logs.” Specifically, the licensee failed to identify deficiencies with the dev
Region: II | Surry | 126364 | 12/31/2019 02/12/2020 | 2019004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Align ‘B’ Emergency Service Water Pump to Angle Drive to Diesel Engine Train in accordance with As Built Design Specification |  | H.14 - Conservative Bias | TE?: N | 05000280 Surry 1 05000281 Surry 2 | Procedure Quality | 71153 | A self-revealing Green non-cited violation of 10 CFR 50 Appendix B, Criterion III, “Design Control,” was identified for the licensee’s failure to adequately translate alignment design requirements of the ‘B’ train Emergency Service Water (ESW) pump and en
Region: II | Surry | 124944 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Enter Turbine Building Degradation in the Corrective Action Program |  | H.13 - Consistent Process | TE?: N | 05000280 Surry 1 05000281 Surry 2 | Protection Against External Factors | 71153 | A self-revealed Green finding was identified when the licensee failed to document, evaluate and implement adequate corrective actions in accordance with PI-AA-200, Corrective Action Program (CAP), upon discovery of the degraded turbine building (TB) roof.
Region: II | Surry | 124324 | 12/31/2018 02/12/2019 |  | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Plant Risk During Testing of an Instrument Air Compressor |  | P.2 - Evaluation | TE?: N | 05000280 Surry 1 | Configuration Control | 71111.13 | An NRC-identified Green NCV of 10 CFR Part 10 CFR 50.65, “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” section a(4), for the licensee's failure to assess and manage the increase in risk for routine surveillance te
Region: II | Surry | 124326 | 12/31/2018 02/12/2019 |  | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Maintain Reactor Coolant System Pressure during Solid Plant Operation |  | H.12 - Avoid Complacency | TE?: N | 05000280 Surry 1 | Human Performance | 71153 | A self-revealed Green finding of OP-AA-100, “Conduct of Operations,” was identified for the licensee’s failure to adequately implement operator fundamentals. Specifically, operators did not appropriately execute clear communication, peer checks, and super
Region: II | Surry | 24648 | 09/30/2018 10/26/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control a Modification of the Containment Spray System |  | H.3 - Change Management | TE?: N | 05000280 Surry 1 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified for the licensee’s failure to control the modification for installation of a drain line on the Unit 1 “A” CS pump bearing housing. This resulted in th
Region: II | Surry | 24124 | 06/30/2018 07/23/2018 | 2018002-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Preventative Maintenance Procedure Results in Additional Failures of Emergency Bus Undervoltage and Degraded Voltage Relays |  | P.3 - Resolution | TE?: N | 05000281 Surry 2 |  | 71152 | An NRC-identified Green NCV of Surry Technical Specification (TS) 6.4.D was identified for the failure to follow procedure ER-AA-102, “Preventative Maintenance Program,” which resulted in the Unit 2 “H” emergency bus degraded voltage (DV) relay failure on
Region: II | Surry | 23533 | 03/13/2018 04/23/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement the 10 CFR, Part 50, Appendix R, III.G.3 requirements consistent with fire protection license condition 3I. |  | NPP | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The NRC identified a Green finding and associated non-cited violation (NCV) of the requirements consistent with license condition 3.I, Surry Units 1 and Unit 2. Specifically, the licensee failed to adequately protect fiberglass pipe that is susceptible
Region: II | Surry | 23185 | 12/31/2017 02/01/2018 | 2017004-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Instructions for Corrective Maintenance on Unit 1 “C” Hot Leg Sample Valve |  | NPP | TE?: N | 05000280 Surry 1 |  | 71111.12 | A self-revealing, non-cited violation (NCV) of Surry Technical Specification (TS) 6.4.A.7 was identified for the failure to have detailed written procedures with appropriate instructions in design change packages (DCPs) 78-001, 80-007, and 84-369 when rep
Region: II | Surry | 23186 | 12/31/2017 02/01/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Non-Functional Flood Control Barrier |  | P.2 - Evaluation | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.15 | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI was identified for the licensee’s failure to identify a condition adverse to quality related to the material condition of the machinery equipment room (MER) 5 flood dike. Specificall
Region: II | Surry | 21687 | 09/01/2017 09/22/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Design Maximum Ambient Temperature Effect on Main Steam Valve House |  | NPP | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.21M | Green: The NRC identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee’s failure to correctly evaluate the heat-up of the Main Steam Valve House (MSVH), which contains the auxiliary feedwater pumps as wel
Region: II | Surry | 29296 | 06/30/2017 08/02/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Have Work Instructions Impacting MER 5 Flood Barrier |  | H.4 Teamwork | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.06 | An NRC-identified, NCV of Surry Technical Specification (TS) 6.4.A.7 was identified because the mechanical equipment room (MER) 5 flood dike was not installed in accordance with the manufacturer's installation procedures after it was removed for maintenan
Region: II | Surry | 29294 | 03/31/2017 05/03/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Requalification Examination Integrity (Section 1R11.1) |  | H.12 Avoid Complacency | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.11B | Green. An NRC-identified NCV of 10 CFR 55.49, "Integrity of examinations and tests," was identified for the licensee's failure to adhere to the requirements of TR-AA-730, Licensed Operator Biennial and Annual Operating Requalification Exam Process, Revisi
Region: II | Surry | 29293 | 02/17/2017 03/15/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to verify or check the adequacy of a design change in the Recirculation Spray Service Water Valve Pits. (Section 4OA2.1) |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152B | Green: The inspectors identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify or check the adequacy of the design of bulkheads in the recirculation spray service water mot
Region: II | Surry | 29289 | 12/31/2016 02/01/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Change of Surveillance Frequency Caused the Charging Service Water Header to Become Biologically Fouled (Section 1R12) |  | H.14 Conservative Bias | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.12 | Green. A self-revealing NCV of 10 CFR 50, Appendix B, Criterion XVI was identified because the surveillance procedure frequency used to flush the service water (SW) piping in Machinery Equipment Room (MER)-3 and MER-4 was changed from two weeks to four we
Region: II | Surry | 21683 | 12/31/2016 02/01/2017 | 2016004-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Change Post Maintenance Testing Causes Water Intrusion into Station Service Transformer and a Reactor Trip (4OA3) |  | P.5 - Operating Experience | TE?: N | 05000281 Surry 2 |  | 71153 | Green. A self-revealing finding was identified because the test requirements section of the station service transformer (SST) design change (DC) was not comprehensive in that it did not test that the isolated phase bus ducting terminal boxes were construc
Region: II | Surry | 29288 | 09/30/2016 10/26/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Non-Functioning Service Water Seismic Support Causes Service Water Pipe Crack |  | P.2 Evaluation | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.12 | Green. A self-revealing, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI was identified because the licensee failed to promptly identify a condition adverse to quality associated with the material condition of the "B" Emergency Service W
Region: II | Surry | 29280 | 03/31/2016 04/27/2016 | 2016001-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a 10 CFR 50.59 Evaluation for Blocking Ventilation to Main Steam Valve Houses |  | H.8 Procedure Adherence | TE?: Y SL-IV-NCVIV | 05000280 Surry 1 05000281 Surry 2 |  | 71111.01 | An NRC-identified finding of very low safety significance and an associated Severity Level IV NCV of 10 CFR 50.59, "Changes, Tests, and Experiments," was identified when the licensee failed to perform and maintain a written evaluation to demonstrate that
Region: II | Surry | 29269 | 12/31/2015 02/02/2016 | 2015004-01 | Self - Revealed | NCV | Initiating Events | Green | Insufficient Gasket Crush on Pressurizer Spray Valve Body to Bonner Joint |  | H.13 Consistent Process | TE?: N | 05000281 Surry 2 |  | 71111.12 | A self-revealing, Green non-cited violation (NCV) of Surry Technical Specification (TS) 6.4.A.7 was identified because 2-RC-PCV-2455A, the Unit 2 "A" pressurizer (PZR) spray valve, developed a body to bonnet mechanical joint leak as a result of the failur
Region: II | Surry | 29270 | 12/31/2015 02/02/2016 | 2015004-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Testing Procedue Causes and Emergency Bus to Deenergize |  | H.7 Documentation | TE?: N | 05000281 Surry 2 |  | 71111.12 | A self-revealing, Green NCV of Surry TS 6.4.A.7 was identified because the Unit 2 "H" emergency bus was lost during performance of 2-PT-2.33A, "Emergency Bus Undervoltage and Degraded Protection Test "H" Train," on September 16, 2015. An inadequate proced
Region: II | Surry | 29271 | 12/31/2015 02/02/2016 | 2015004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Charging Pump Service Water Pump Failure Due to Inadequate Preventative Maintenance |  | H.5 Work Management | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152 | A self-revealing Green NCV of Surry TS 6.4.D was identified because the preventative maintenance cleaning of the six inch service water (SW) piping upstream of the SW rotating strainers was deferred with insufficient technical justification. Specifically,
Region: II | Surry | 29272 | 12/31/2015 02/02/2016 | 2015004-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Causes Main Turbine and Reactor Trip |  | H.7 Documentation | TE?: N | 05000281 Surry 2 |  | 71153 | A self-revealing Green NCV of Surry TS 6.4.A.7 was identified because Unit 2 tripped during performance of 2-OP-TM-001, "Turbine - Generator Startup to 20% - 25% Turbine Power," on July 21, 2015. An inadequate procedure allowed the main turbine (MT) gover
Region: II | Surry | 29277 | 09/30/2015 11/12/2015 |  | NRC | FIN | Mitigating Systems | Green | Charging Pump Cubicle Floor Drain Backflow Preventer Failures during Unit 1 Safeguards Building Flooding |  | H.7 Documentation | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.12 | A self-revealing, Green finding was identified because the instructions section of the procedure used to test floor drain back flow preventers (BFPs) did not include the instructions necessary to successfully fulfill the purpose of the procedure. A lack o
Region: II | Surry | 29278 | 09/30/2015 11/12/2015 |  | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure during Maintenance Results in Service Water Header Inoperability |  | H.5 Work Management | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | A self-revealing, Green NCV of Technical Specifications (TS) 6.4.D was identified for failure to follow procedure WM-AA-101, "Work Order Planning," Revision 1. Specifically, the licensee inappropriately revised a work order which resulted in the actuator
Region: II | Surry | 29279 | 09/30/2015 11/12/2015 |  | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of Class 1E 125VDC Branch Circuit Breaker Design |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify or check the adequacy of design of the Class 1E 125 volt direct current (VDC) molded case circuit breakers
Region: II | Surry | 29258 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Barrier Integrity | Green | Failure to conduct a detailed visual examination of the concrete-liner interface for the Unit 1 containment |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.08P | An NRC-identified NCV of 10 CFR 50.55a, "Codes and Standards," was identified for the licensee's failure to conduct a detailed visual examination of the concrete-liner interface for the Unit 1 containment, per the American Society of Mechanical Engineers
Region: II | Surry | 29263 | 06/30/2015 08/06/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | "A" MDAFW Pump Motor Outboard Bearing Damaged |  | H.11 Challenge the Unknown | TE?: N | 05000280 Surry 1 |  | 71111.12 | A self-revealing NCV of Surry Technical Specification (TS) 6.4.D was identified because the Unit 1 "A" motor driven auxiliary feedwater (MDAFW) pump motor outboard bearing thermocouple was improperly installed while installing a new motor on the MDAFW pum
Region: II | Surry | 29251 | 05/29/2015 07/06/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure a Functional Alternate Shutdown System Alignment during Appendix R Fire EventsEvents |  |  | TE?: N | 05000280 Surry 1 |  | 71111.05T | The inspectors identified a Green non-cited violation (NCV) of Surry's Operating License, Condition 3.I, Fire Protection, for the licensee's failure to ensure a functional alternate safe shutdown flow path during an Appendix R fire. The licensee entere
Region: II | Surry | 29252 | 05/29/2015 07/06/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement In-service Testing and Inservice Inspections for Charging Cross-tie Components. |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The inspectors identified a Green NCV of 10 CFR 50.55(a) for the licensee's failure to implement in-service testing (IST) and in-service inspections (ISI) for charging cross-tie components. The licensee entered this issue into their corrective action p
Region: II | Surry | 29257 | 05/29/2015 07/06/2015 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Multiple Design Deficiencies in the Fire Protection Program |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The inspectors identified a Green NCV of Surry's Operating License, Condition 3.I, Fire Protection, for design control deficiencies in the fire protection program. The licensee entered this issue into their corrective action program as condition report
Region: II | Surry | 29250 | 03/31/2015 05/07/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Charging Service Water Pipe Leak |  | P.2 Evaluation | TE?: N | 05000281 Surry 2 |  | 71111.12 | An NRC-identified, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified because the licensee failed to promptly identify a condition adverse to quality associated with the material condition of the Unit 2
Region: II | Surry | 29247 | 12/31/2014 02/02/2015 | 2014005-01 | NRC | NCV | Initiating Events | Green | Unit 2 Trip Due to Loose RPS Wire Connection |  | H.7 Documentation | TE?: N | 05000281 Surry 2 |  | 71153 | An NRC-identified, non-cited violation (NCV) of Surry Technical Specification (TS) 6.4, Unit Operating Procedures and Programs, Section A.7 was identified because Surry procedure 0-ECM-1801-01, "Westinghouse Type BF - BFD - or NBFD65NR Relay Replacement"
Region: II | Surry | 29244 | 09/26/2014 11/10/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Preventative Maintenance on Class 1E Molded Case Circuit Breakers |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a Green non-cited violation of Technical Specification 6.4.A.7, "Unit Operating Procedures and Programs," for the licensee's failure to implement written procedures to perform periodic tests for the Class 1E 125 volt direct current
Region: II | Surry | 29245 | 09/26/2014 11/10/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Range of Conditions that Effect Canal Level Probes |  | H.6 Design Margins | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly evaluate and quantify the system response times and accuracies over the range of conditions under whic
Region: II | Surry | 29241 | 06/30/2014 07/30/2014 | 2014003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Amount of Packing in Pressurizer Spray Valve |  |  | TE?: N | 05000281 Surry 2 |  | 71111.22 | A self-revealing NCV of Surry Technical Specification (TS) 6.4.A.7 was identified because 2-RC-PCV-2455A, the Unit 2 "A" pressurizer (PZR) spray valve's packing gland was repacked with the incorrect number of packing rings in May, 2008. When the Unit 2 "A
Region: II | Surry | 29240 | 03/31/2014 05/01/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Recirculation Spray Heat Exchanger Inlet Isolation Valve MOV Thermal Overload Not Properly Reset (Section 1R15) |  | H.7 Documentation | TE?: N | 05000280 Surry 1 |  | 71111.15 | A self-revealing NCV of Surry Technical Specification (TS) 6.4.A.7 was identified because 1-SW-MOV-103D, the "B" and "C" recirculation spray heat exchanger (RSHX) inlet isolation valve, motor thermal overload was improperly reset after planned maintenance
Region: II | Surry | 29236 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Missile Protect Beyond Design Bases FLEX Modification to LHSI Piping |  | H.3(b) Work Activity Coordination | TE?: N | 05000280 Surry 1 |  | 71111.18 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the licensee's failure to adequately protect safety-related low head safety injection system (LHSI) piping from a tornado missile. Specifically, the
Region: II | Surry | 29239 | 12/31/2013 02/10/2014 | 2013005-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Maintain Control of Licensed Radioactive Material that was not in Storage |  | H.4(b) Procedural Compliance | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71124.08 | A self-revealing non-cited violation of 10 CFR 20.1802, "Control of Material not in Storage", was identified for the licensee's failure to maintain control and constant surveillance of licensed radioactive material in a controlled or unrestricted area (He
Region: II | Surry | 29232 | 03/31/2013 04/30/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inoperability of One Train of Charging Pump Service Water |  | H.4(a) Human Error Prevention | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | A self-revealing NCV of Technical Specification 6.4.D was identified for the failure to follow procedure 2-MOP-SW-001, "Charging Pumps Service Water Pumps Removal from and/or Return to Service," Revision 3 . Specifically, the licensee incorrectly implemen
Region: II | Surry | 29231 | 12/31/2012 01/30/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Submerged Cables Identified in Safety-Related Manhole |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.06 | The inspectors identified a Green noncited violation of Technical Specification 6.4.A.7, which requires appropriate corrective maintenance procedures which would have an effect on the safety of the reactor. Specifically, Dominion procedure 0-MCM-1207-01,
Region: II | Surry | 29229 | 09/30/2012 11/02/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure for "1B" Charging Pump |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000280 Surry 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to implement operability procedure, OP-AA-102, "Operability Determinations." Specific
Region: II | Surry | 29227 | 03/31/2012 05/10/2012 | 2012002-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain a Standard Emergency Action Level Scheme for Earthquakes |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152 | The inspectors identified a self-revealing non-cited violation (NCV) of 10 CFR 50.54(q) for the failure to maintain in effect, an emergency plan which meets the requirements of 10 CFR 50.47(b)(4). Specifically, a standard emergency classification and acti
Region: II | Surry | 29220 | 01/12/2012 02/22/2012 | 2011011-01 | NRC | NCV | Initiating Events | Green | Failure to Provide Appropriate Procedural Guidance for Component Cooling Water Flow to the Thermal Barrier Heat Exchangers |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a non-cited violation of Technical Specification 6.4.A.3, "Unit Operating Procedures and Programs," for the licensee's failure to provide appropriate procedural guidance to assure the operator's ability to detect and correct a componen
Region: II | Surry | 29221 | 01/12/2012 02/22/2012 | 2011011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Control Measures to Verify the Adequacy of TOLs at Degraded Voltage Conditions |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to use the most conservative motor currents in the analysis to determine the adequacy of thermal overloads (TOLs) at degra
Region: II | Surry | 29222 | 01/12/2012 02/22/2012 | 2011011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Instructions in the Operations Surveillance Procedure for the Charging Pump Service Water System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a non-cited violation of Technical Specification 6.4.A.7, "Unit Operating Procedures and Programs", for the licensee's failure to provide adequate instructions in the surveillance procedure for the charging pump service water system. T
Region: II | Surry | 29225 | 01/12/2012 02/22/2012 | 2011011-04 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor or Perform Effective Preventive Maintenance on the AAC Diesel Ventilation Supply Dampers and Exhaust Fans Louvers |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to perform condition monitoring or otherwise implement an effective preventive ma
Region: II | Surry | 29226 | 01/12/2012 02/22/2012 | 2011011-05 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Control Measures to Verify the Adequacy of Inputs Into the RS NPSHa Analysis |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's use of a non-conservative net positive suction head required (NPSHr) value in the analysis that determined the adequacy of the net
Region: II | Surry | 29217 | 12/31/2011 02/13/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Address Rainwater Intrusion into the Unit 1 RPS Relay Room |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000280 Surry 1 |  | 71153 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee failing to correct a condition adverse to quality. Specifically, the licensee failed to correct a known degraded building
Region: II | Surry | 29215 | 09/30/2011 11/01/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Scaffolding Procedure Requirements |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.04Q | The inspectors identified a NCV of Technical Specifications (TS) 6.4.D for failing to follow the requirements of procedure MA-AA-105, "Scaffolding." Specifically, the licensee did not adequately implement scaffold evaluation, screening, and risk requireme
Region: II | Surry | 29216 | 09/30/2011 11/01/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Instrument Uncertainty and Establish Calibration Controls for Rotameters Used to Vent Gas from ECCS Systems |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | NONE | An NRC-identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XI, "Test Control," (with two examples) was identified for the failure to establish measures to apply rotameter instrument measurement error and appropriate instrument calibra
Region: II | Surry | 29212 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | NCV | Emergency Preparedness | Green | Failure to classify and declare a Notification of Unusual Event |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000281 Surry 2 |  | 71153 | A Green non-cited violation was identified by the inspectors for the licensee's failure to classify and declare a Notification of Unusual Event when conditions warranted as required by 10 CFR 50.54(q) and 10 CFR 50.47(b)(4). The inspectors reviewed IMC
Region: II | Surry | 29211 | 06/30/2011 07/28/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Qualification Testing of Fire Barrier Penetration Seals |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | NONE | A Green non-cited violation of Surry Units 1 and 2 Operating License Condition 3.I, "Fire Protection," was identified by the inspectors for failure to have adequate qualification testing results, as directed by Appendix A to Branch Technical Position APCS
Region: II | Surry | 29206 | 03/31/2011 05/05/2011 | 2011002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Determine the Correct Cause and Prevent Recurrence for a Significant Event |  | P.2(b) Implementing Operating Experience | TE?: N | 05000281 Surry 2 |  | 71152 | A Green, self-revealing finding was identified for the licensee's failure to comply with the standards established in their corrective action program (CAP) to determine the correct cause and take corrective action to prevent recurrence (CAPR) for a signif
Region: II | Surry | 29209 | 03/31/2011 05/05/2011 | 2011002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Multiple Conditions Adverse to Fire Protection |  | H.3(a) Work Planning | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | A Green, self-revealing non-cited violation of Condition 3.I to the Surry Unit 1 and Unit 2 Updated Facility Operating Licenses, DPR-32 and DPR-37, was identified for the licensee's failure to take corrective action for degraded conditions adverse to the
Region: II | Surry | 29196 | 12/31/2010 01/31/2011 | 2010005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Results in Inadvertent Actuation of Safety Injection |  | H.4(a) Human Error Prevention | TE?: N | 05000280 Surry 1 |  | 71111.22 | A self-revealing Green NCV of TS 6.4, Unit Operating Procedures and Programs, was identified for the failure to follow procedure 1-OPT-ZZ-001, ESF Actuation with Undervoltage and Degraded Voltage 1H Bus. Specifically, on October 26, 2010, a test lead was
Region: II | Surry | 29197 | 12/31/2010 01/31/2011 | 2010005-03 | NRC | NCV | Barrier Integrity | Green | Heavy Load Lift of the 1B RCP Motor Over Exposed Reactor Fuel |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000280 Surry 1 |  | 71111.2 | An NRC-identified Green NCV of Technical Specification (TS) 6.4, Unit Operating Procedures and Programs, was identified. Personnel failed to follow the defined heavy load shipping path inside containment as specified in procedure, GMP-001, Heavy Load Rigg
Region: II | Surry | 29204 | 08/16/2010 09/10/2010 | 2010006-01 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct Degraded Unit 1 Nuclear Instrument RC Filters |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000280 Surry 1 |  | 93812 | An NRC identified non-cited violation of 10 CFR 50, Appendix B, Criteria XVI, Corrective Action, was identified for the licensee's failure to identify and correct degraded RC filters associated with Unit 1 Nuclear Instrument (NI) cabinets for N-42 and N-4
Region: II | Surry | 17264 | 06/30/2010 07/28/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate that the Reliability of Systems or Components were effectively controlled per 10 CFR 50.65 (a)(2) |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.12 | The NRC identified a Green Non-Cited Violation of 10CFR50.65 a(2) for the licensee's failure to demonstrate that the reliability of High Safety Significant (HSS) systems and Low Safety Significant (LSS) systems in stand-by was being effectively controlled
Region: II | Surry | 29194 | 06/30/2010 07/28/2010 | 2010003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Rigging Practices Result in Damage to Safety Related Equipment |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000280 Surry 1 |  | 71111.13 | A self-revealing Green Finding was identified for failure to adequately rig a 300 pound motor in the auxiliary building in accordance with the manufacturer's recommendations on May 11, 2010. As a result, the motor slipped from its rigging and dropped appr
Region: II | Surry | 17263 | 03/31/2010 04/30/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify a non-conservative error in the quarterly TS surveillance for the Unit 1 A battery |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.19 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action" for failure to identify that a non-conservative error had been introduced into the Unit 1 A main station battery quarterly technical specification surveilla
Region: II | Surry | 17256 | 12/31/2009 01/28/2010 | 2009005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inoperability of MCR isolation Damper 1-VS-MOD-103D due to failure to promptly identify and correct internal hydraulic leakage |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.12 | A self-revealing Green NCV of 10 CFR 50 Appendix B, Criterion XVI, was identified for the failure to correct a condition adverse to quality which led to main control room isolation damper 1-VS-MOD-103D being inoperable for approximately 19 hours on Septem
Region: II | Surry | 17257 | 12/31/2009 01/28/2010 | 2009005-02 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to perform an adequate operability determination for main control room isolation damper 1-VS-MOD-103D |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.15 | A self-revealing Green Finding was identified for the incorrect operability determination of main control room isolation damper 1-VS-MOD-103D. The damper, declared operable and left in-service following loss of power to its hydraulic pump on September 21,
Region: II | Surry | 17255 | 10/02/2009 10/30/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Demonstrate Effective Preventive Maintenance of Safety Injection Check Valves nor Set Goals and Monitor under 10CFR50.65(a)(1) |  |  | TE?: N | 05000280 Surry 1 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Plants," for failure to demonstrate effective preventive maintenance of Unit 1 low head safety injection
Region: II | Surry | 17237 | 09/30/2009 10/29/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Compensatory Measures for the Impairment of Fire Detection Systems |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05Q | The inspectors identified a Green NCV of the Surry operating license, section 3.1 "Fire Protection," for an inadequate procedure that resulted in compensatory continuous fire watches in MERs #3 and #4 being inadequate (CR342078). Correctie action, revisin
Region: II | Surry | 17238 | 09/30/2009 10/29/2009 | 2009004-02 | NRC | FIN | Mitigating Systems | Green | Failure to Provide an Adequate Basis for Operability of ESW Pump !-SW-P-1B. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.15 | The inspectors identified a Green finding for the incorrect operability determination for emergency service water pump 1-SW-P-1B on August 1, 2009,after vibrations had increased 391% in the vertical plane (CR 343396). A violation of regulatory requirement
Region: II | Surry | 17239 | 09/30/2009 10/29/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Tornado Protection for Engine Driven Emergency Service Water Pumps 1-SW-P-1A/B/C |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.18 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control". The design change for the emergency service water pumps (DC-SU-08-0001) was not adequate to protect the diesel-driven emergency service water pumps from damag
Region: II | Surry | 17240 | 09/30/2009 10/29/2009 | 2009004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions Lead to Packing Failure of ESW Pump 1-SW-P-1B. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.19 | A self-revealing Green NCV of Technical Specification 6.4, "Unit Operating Procedures and Programs," was identified for the failure to provide adequate work instructions for maintenance on 1-SW-P-1B, a safety-related component, which led to failure of the
Region: II | Surry | 17247 | 09/30/2009 10/29/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Ground on Safety Bus 1H |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000280 Surry 1 |  | NONE | A green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for failure to promptly identify and correct a condition adverse to quality related to a ground on emergency safety bus 1H. This resulted in the deg
Region: II | Surry | 17248 | 09/30/2009 10/29/2009 | 2009004-06 | NRC | NCV | Mitigating Systems | Green | Ineffective Action for ELU Performance Deficiencies |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152 | The inspectors identified a Green NCV of Surry Operating Licenses, Section 3.1 "Fire Protection," for failure to promptly identify and correct a condition adverse to fire protection in regard to Appendix R emergency lighting unit performance failures due
Region: II | Surry | 17249 | 09/30/2009 10/29/2009 | 2009004-07 | NRC | NCV | Mitigating Systems | Green | Failure to Remove Blocking Device From Piping Supports |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000280 Surry 1 |  | 71152 | The inspectors identified a Green NCV of Technical Specification 6.4, "Unit Operating Procedures," associated with blocking devices not being removed from piping supports following maintenance due to procedure issues related to procedure adequacy and adhe
Region: II | Surry | 17227 | 06/30/2009 07/28/2009 | 2009003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Installation of a Design Change |  | H.3(a) Work Planning | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.18 | A self-revealing Green non-cited violation of TS 6.4 "Unit Operating Procedures and Programs" was identified for the failure to provide adequate work instructions for installation of design change SU-08-0001, for engine-driven emergency service water pump
Region: II | Surry | 17230 | 06/26/2009 08/05/2009 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Maintenance for Backup Battery for the Halon 1301 System in ESGRs |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The team identified a performance deficiency and Green NCV for failing to implement a maintenance program for the backup batteries for the Halon 1301 system for the emergency switchgear rooms to ensure on a continuing basis that 24-hour backup power was a
Region: II | Surry | 17223 | 12/31/2008 01/30/2009 | 2008005-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Work Instructions Result in Actuation of Unit 1 Safety Injection Train B. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000280 Surry 1 |  | 71153 | A Green self-revealing non-cited violation (NCV) of Technical Specification 6.4.A.7 was identified for failure to provide adequate work instructions for corrective maintenance on the safety injection (SI) system. The inadequate work instructions led to an
Region: II | Surry | 17224 | 12/31/2008 01/30/2009 | 2008005-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Review of Vendor Information Led to Unit 1 Manual Reactor Trip. |  | H.4(a) Human Error Prevention | TE?: N | 05000280 Surry 1 |  | 71153 | A Green self-revealing Finding was identified for failure to perform an adequate review of the vendor's recommended balance moves for the Unit 1 main turbine. As a result, an improper balance move was made to the Unit 1 main turbine during the April force
Region: II | Surry | 17225 | 09/30/2008 11/12/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for the EDG Ambient Air Temperature Limit. |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.01 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion III, "Design Control," for a change in the EDG ambient air temperature operating limits, from 100¦F to 120¦F, that was made without an adequate design analysis.
Region: II | Surry | 17214 | 03/30/2008 04/23/2008 | 2008002-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of thermal barrier cooling due to a failure to follow procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000281 Surry 2 |  | 71111.22 | A self-revealing finding of very low safety significance that constituted a non-cited violation (NCV) of Technical Specification 6.4.D was identified. Licensee personnel failed to follow procedure 2-IPM-CC-F-207A and caused cooling water flow to the therm
Region: II | Surry | 17215 | 03/30/2008 04/23/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Start-up Procedure which Resulted in Leaving Loose Fibrous Insulation in Containment |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000280 Surry 1 |  | 71111.2 | An NRC-identified, non-cited violation (NCV) of very low safety significance was identified for the failure to follow start-up procedure 1-GOP-1.7, revision 2, "Unit Startup, RCS Heat Up from Ambient to HSD", which resulted in leaving loose fibrous insula
Region: II | Surry | 17216 | 02/29/2008 04/08/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate and Use Limiting Case 4160 VAC Bus Frequency and Voltage in Design Calculations |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The inspectors identified two examples of a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to evaluate variations of emergency diesel generator (EDG) output frequency in electrical design loading calculation
Region: II | Surry | 17221 | 02/29/2008 04/08/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Use Appropriate Acceptance Criteria for Testing Battery Voltage at the One Minute Mark |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for incorrect acceptance criteria in test procedure 1-EPT-0106-01, Main Station Battery 1A Service Test. This finding was entered into the licensee's corrective ac
Region: II | Surry | 17222 | 02/29/2008 04/08/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Use Limiting Case High dP In 2-FW-MOV-260A Design Calculations |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000281 Surry 2 |  | 7111121 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to evaluate the most limiting differential pressure (dP) for opening valve 2-FW-MOV-260A, auxiliary feedwater (AFW) cross-tie motor-
Region: II | Surry | 17210 | 12/31/2007 01/31/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Temporary Fire Suppression Capacity Not Equivalent to Unit 1 Containment Fire Hose Stations |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000280 Surry 1 |  | 71111.05Q | A Green NRC-identified non-cited violation of paragraph (a)(1) of 10 CFR 50.48, "Fire Protection," was identified for failure to maintain the fire suppression capability for the Unit 1 containment building as specified by the approved fire protection plan
Region: II | Surry | 17209 | 12/31/2007 01/31/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Failure to meet ASME Section XI requirements for replacement of safety injection valve 2-SI-82 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000281 Surry 2 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR 50.55a(g)(4) for failure to meet requirements of ASME Section XI for the replacement of safety injection valve 2-SI-82 performed during the last Unit 2 refueling outage. The licensee failed t
Region: II | Surry | 17207 | 12/31/2007 01/31/2008 | 2007005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency Service Water Pump 1-SW-P-1B Inoperable Due to an Inadequate Maintenance Instruction for Reassembly of the ESW strainer |  | H.4(a) Human Error Prevention | TE?: N | 05000280 Surry 1 |  | 71111.19 | A Green self-revealing non-cited violation of Technical Specification 6.4, "Unit Operating Procedures and Programs," was identified for failure to have an adequate maintenance procedure for the emergency service water (ESW) pump strainer. This resulted in
Region: II | Surry | 17208 | 12/31/2007 01/31/2008 | 2007005-04 | NRC | URI | Mitigating Systems | Green | Fibrous Material left in Unit 1 Containment |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000280 Surry 1 |  | 71111.2 | On 11/28/07, during Unit 1 Containment Close-out, inspectors identified loose bat insulation in a 15' X 5' penetration in the 'C' Loop Room. When the inspectors notified the licensee, they removed two 55 gallon bags of fibrous insulation which were approx
Region: II | Surry | 17213 | 12/31/2007 01/31/2008 | 2007005-05 | NRC | NCV | Mitigating Systems | Green | Carbon Dioxide Suppression System Degraded in Two Fire Areas in Unit 1 and Three Fire Areas in Unit 2 |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | NONE | The NRC identified a Green NCV of Unit 1 and Unit 2 Operating License Condition 3.I because the installed carbon dioxide (CO2) fire suppression systems could not be shown to deliver the design basis gas concentration. This finding applied to the Unit 1 an
Region: II | Surry | 17205 | 10/12/2007 11/26/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Catqagorize a Maintenance Preventable Functional Failure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000280 Surry 1 |  | 71152B | The inspectors identified an NCV of 10 CFR 50.65 (a)(2) after Surry Power Station failed to categorize the failure of the Unit 2 Charging Pump Component Cooling System as a maintenance preventable functional failure and accordingly, failed to monitor the
Region: II | Surry | 17206 | 10/12/2007 11/26/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Procedures Related to the Operation of the Auxiliary Feedwater System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71152B | NRC identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to revise procedure ECA 0.0, Loss of all AC Power, as corrective action for a condition identified by the licensee that could cause a
Region: II | Surry | 17203 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Suitability of Application of Equipment Essential to Safety-Related Functions |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111117B | The NRC identified a non-cited violation (NCV) for the failure to ensure the suitability of application of equipment essential to the safety-related functions of structures, systems, and components (SSCs) through their commercial dedication process as req
Region: II | Surry | 17204 | 06/30/2007 07/30/2007 | 2007003-02 | NRC | NCV | Initiating Events | Green | Failure to Perform an adequte Risk Assessment for Unit 2 Cross-Under Relief Valve Event |  | H.3(a) Work Planning | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(4), which requires that the licensee assess and manage the increase in risk that may result from the proposed maintenance activities. Specifically, in assessing the increase in risk of pl
Region: II | Surry | 17198 | 03/31/2007 04/30/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include the Pressurizer Power Operated Relief Valve in the On-line Risk Assessment Prior to Other Maintenance Activities |  |  | TE?: N | 05000281 Surry 2 |  | 71111.13 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for failure to assess the increase in risk that results from proposed maintenance
Region: II | Surry | 17199 | 03/31/2007 04/30/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures During Maintenance Resulting in a Stuck Control Rod |  |  | TE?: N | 05000280 Surry 1 |  | 71152 | A self-revealing, non-cited violation of Technical Specification 6.4.D, "Unit Operating Procedures and Programs", was identified for failure to follow procedure. Specifically, foreign material was left inside a Unit 1 control rod guide tube which prevente
Region: II | Surry | 17200 | 03/31/2007 04/30/2007 | 2007002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedural Instructions Results in Inoperable Charging Pump Component Cooling Water System |  |  | TE?: N | 05000281 Surry 2 |  | 71153 | A self-revealing non-cited violation of Technical Specification 6.4.A, "Unit Operating Procedures and Programs," was identified for failure to have adequate written procedures for normal startup of systems and components involving nuclear safety. Specific
Region: II | Surry | 17201 | 03/31/2007 04/30/2007 | 2007002-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Perform an Adequate Extent of Condition Review for Unit 1 June 29, 2006, Turbine Building Damage Event |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | A Green self-revealing finding was identified for not performing an adequate extent of condition review in accordance with the licensee's established procedures. The potential consequences of having siding torn from the Turbine Building if Unit 2 experien
Region: II | Surry | 17202 | 03/31/2007 04/30/2007 | 2007002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Breaker Control Circuit Design Deficiency Results in Failure to Supply Emergency Bus 1J |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71153 | A self-revealing, non-cited violation of 10 CFR 50.63 was identified regarding a breaker control circuit design deficiency which prevented the licensee from supplying the 1J emergency bus on Unit 1 from the alternate AC diesel generator. The problem occur
Region: II | Surry | 17189 | 10/27/2006 12/01/2006 | 2006011-04 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to Activate ERDS Within One Hour of an Alert Declaration |  | H.3(a) Work Planning | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 93812 | A green self-revealing non-cited violation of 10 CFR 50.72(a)(4) was identified. During the October 7, 2006, partial loss of offsite power event, the licensee failed to activate the Emergency Response Data System (ERDS) within one hour of an Alert declara
Region: II | Surry | 17183 | 06/30/2006 08/11/2006 | 2006009-01 | NRC | URI | Mitigating Systems | Green | Carbon Dioxide Suppression System Degraded in Two Fire Areas at Unit 1 and Three Fire Areas at Unit 2 |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T
Region: II | Surry | 17184 | 06/30/2006 08/11/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Removal of Damper Motor Operators From CO2 System in Normal Switchgear Rooms |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The team identified a non-cited violation of Operating License Condition 3.I for removing the automatic feature of ventilation dampers which degraded the fixed gaseous suppression system in the normal switchgear room at both units by allowing carbon dioxi
Region: II | Surry | 17185 | 06/30/2006 08/11/2006 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Post-Fire Safe Shutdown During a Fire in Mechanical Equipment Room 3 |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 6.4.E for failure to provide an adequate post-fire safe shutdown procedure. Procedure 0-FCA-7.00, Rev. 10, failed to ensure that a source of water would be aligned to the suction of the
Region: II | Surry | 17179 | 02/10/2006 03/09/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative ECA Procedure Setpoint for Operator Action to Secure LHSI and HHSI Pumps on Low RWST Level |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 7111121 | The team identified a Green, non-cited violation (NCV) of Technical Specification 6.4.A.3, Unit Operating Procedures and Programs, for a non-conservative emergency contingency action (ECA) procedure setpoint regarding low Refueling Water Storage Tank (RWS
Region: II | Surry | 124438 | 03/14/2019 |  |  | LIV |  | Green | Failure to implement and maintain adequate program for vulnerability assessments. |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71130.10P
Region: II | Surry | 125049 | 08/05/2019 |  |  | LIV |  | Green | Failure to Perform Adequate Foreign Material Closeout Inspection of Safety-Related Breaker |  |  | TE?: N | 05000281 Surry 2 |  | 71153
Region: II | Surry | 126594 | 02/12/2020 |  |  | LIV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000280 Surry 1 05000281 Surry 2 |  | 71124.01
Region: II | Turkey Point | 125722 | 08/16/2019 09/30/2019 | 2019011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Qualify D.C. Combination Starter Panel 4N1405-A for Minimum Operating Time |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 | Equipment Performance | 71111.21N | The NRC identified a Green NCV of 10 CFR 50.49.(e)(1), "Temperature and Pressure," for the licensee's failure to qualify direct current (D.C) combination starter panel 4N1405-A for a period of at least one hour in excess of the time assumed in the acciden
Region: II | Turkey Point | 125723 | 08/16/2019 09/30/2019 | 2019011-03 | NRC | NCV | Mitigating Systems | Green | Two Examples of Failure to Verify Design Inputs to Qualification Criteria |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 | Equipment Performance | 71111.21N | The NRC identified a Green NCV of 10 CFR 50 Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of qualification testing and installation requirements in accordance with Quality Instruction (QI) 1.7, "Nuclear Eng
Region: II | Turkey Point | 124831 | 03/31/2019 05/14/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Quality Records in Accordance with License Renewal Commitments |  | H.7 - Documentation | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 | Equipment Performance | 71003 | The NRC identified a finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion XVII, “Quality Assurance Records,” for the licensee’s failure to maintain quality records in accordance with established requirements.
Region: II | Turkey Point | 124832 | 03/31/2019 05/14/2019 | 2019001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Structures Monitoring Program Inspections in Accordance with License Renewal Commitments |  | H.14 - Conservative Bias | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 | Equipment Performance | 71003 | The NRC identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for multiple examples of the licensee’s failure to inspect several safety related structures in accordance with license renewal commitment
Region: II | Turkey Point | 124741 | 03/31/2019 05/14/2019 | 2019001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Reset the 'C' AFW Pump T&T Lever |  | H.8 - Procedure Adherence | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 | Equipment Performance | 71111.12 | A self-revealing, Green, Non-cited violation (NCV) of procedure 3-NOP-075, Auxiliary Feedwater System, was identified when the licensee failed to use the procedure to reset the mechanical trip lever on the ‘C’ auxiliary feedwater pump trip and throttle (T
Region: II | Turkey Point | 124535 | 03/01/2019 04/15/2019 |  | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedures to Ensure Flood Protection for the 4A and 4B RHR trains |  | H.11 - Challenge the Unknown | TE?: N | 05000251 Turkey Point 4 |  | 71152B | The NRC identified a green, NCV of Technical Specification 6.8.1, for the licensee’s failure to establish, implement and maintain written procedures to prevent foreign material from potentially degrading the residual heat removal (RHR) pump room sump pump
Region: II | Turkey Point | 124684 | 03/01/2019 04/15/2019 |  | NRC | NCV | Mitigating Systems | Green | Preconditioning of safety-related check valves prior to retesting |  | H.9 - Training | TE?: N | 05000250 Turkey Point 3 |  | 71152B | The NRC identified a green, non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, in that the licensee failed to comply with procedure 0-ADM-502, In-Service Testing Program, when preconditioning of safety related check valves was conducted prio
Region: II | Turkey Point | 124688 | 03/01/2019 04/15/2019 |  | NRC | NCV | Mitigating Systems | Green | Failure to comply with the ASME OM code during safety-related check valve testing |  | P.1 - Identification | TE?: N | 05000250 Turkey Point 3 |  | 71152B | The NRC identified a green, Non-cited Violation (NCV) of 10 CFR 50.55a(f)(4), when the licensee failed to declare safety-related valves inoperable and failed to take corrective action after a failed IST as required by the ASME OM code.
Region: II | Turkey Point | 38861 | 12/31/2018 02/12/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Missed Corrective Actions to Repair Concrete Delamination in HHSI Trenches |  | P.3 - Resolution | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | An NRC-identified Green NCV of 10 CFR 50, Appendix B, Criterion XVI, was identified when FPL failed to ensure that concrete delamination in the Unit 3 and Unit 4 HHSI trenches, safety-related structures that provide support to HHSI suction piping, was cor
Region: II | Turkey Point | 38862 | 12/31/2018 02/12/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct A Risk Informed Fire Protection Plant Change Evaluation |  | H.8 - Procedure Adherence | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | A Green NRC-identified NCV of Renewed Facility Operating License Condition 3.D., Fire Protection, was identified for the failure to adequately implement and maintain in effect all provisions of the approved fire protection program. Specifically, FPL ident
Region: II | Turkey Point | 24682 | 09/30/2018 11/07/2018 | 2018003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperable Auxiliary Feedwater Steam Supply Flow Path |  | NPP | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing Green NCV of 10 CFR 50, Appendix B, Criterion V, Procedures, was identified when FPL failed to ensure that the torque arm of the 4A steam generator (SG) auxiliary feedwater (AFW) steam supply valve, MOV-4-1403, remained engaged with its v
Region: II | Turkey Point | 23998 | 03/31/2018 05/10/2018 | 2018001-01 | NRC | NCV | Barrier Integrity | Green | Failure to conduct post maintenance testing in accordance with ASME OM code |  | H.8 - Procedure Adherence | TE?: N | 05000251 Turkey Point 4 |  | 71111.19 | A Green NRC-identified NCV of 10 CFR 50.55a, “Codes and Standards,” was identified for the failure to adequately perform post maintenance testing on valve CV-4-2906, 4B emergency containment cooler (ECC) air-operated outlet valve, in accordance with the A
Region: II | Turkey Point | 23536 | 01/22/2018 05/10/2018 | 2018001-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure of radiation workers to notify Radiation Protection upon a spill of radioactively contaminated water. |  | H.8 - Procedure Adherence | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71124.01 | A self-revealing Green NCV of Technical Specification (TS) 6.8.1, “Procedures and Programs”, was identified for failure of radiation workers to notify Radiation Protection (RP), in accordance with procedure RP-AA-100-1002, “Radiation Worker Instruction an
Region: II | Turkey Point | 23203 | 12/31/2017 02/08/2018 | 2017004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform an Adequate ASME BPVC Section XI Repair/Replacement Plan for a Code Class 1 and 2 Replacement |  | H.8 - Procedure Adherence | TE?: N | 05000251 Turkey Point 4 |  | 71111.19 | A NRC-identified NCV of 10 CFR 50.55a, “Codes and Standards,” was identified for the failure to adequately perform a Boiler and Pressure Vessel Code class 1 and 2 replacement activity in accordance with the Turkey Point Plant American Society of Mechanica
Region: II | Turkey Point | 23204 | 12/31/2017 02/08/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Deficient CCW Penetration Seal Configuration that Exacerbates External Piping Corrosion Conditions |  | P.1 - Identification | TE?: N | 05000251 Turkey Point 4 |  | 71152 | A NRC-identified NCV of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” was identified for the licensee’s failure to promptly identify and correct an adverse condition to quality that led to continued corrosion and significant scaling and pitti
Region: II | Turkey Point | 23205 | 12/31/2017 02/08/2018 | 2017004-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Installation of Outdoor Use Electrical Enclosures Results in Manual Reactor Trip |  | NPP | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing finding was identified for failure to ensure the 4B and 4C main feedwater regulating valve (MFRV) control circuits remained free from the effects of water intrusion or condensation in electrical enclosures. Specifically, a hand selector s
Region: II | Turkey Point | 21673 | 09/30/2017 11/09/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct CCW Pipe Corrosion |  | P.1 - Identification | TE?: N | 05000250 Turkey Point 3 |  | 71111.04S | An NRC-identified NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified for the licensee’s failure to promptly identify and correct component cooling water (CCW) external pipe corrosion that led to a through-wall flaw a
Region: II | Turkey Point | 23464 | 09/30/2017 11/09/2017 | 2017003-02 | NRC | FIN | Initiating Events | Green | Inadequate Operator Fundamentals during Diesel Driven Fire Pump Surveillance Testing |  | H.12 - Avoid Complacency | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.05Q | An NRC-identified finding was identified for the failure to adequately implement OP-AA-100-1000, “Conduct of Operations” procedure. Specifically, non-licensed operators (NLOs) failed to identify that the diesel driven fire pump (DDFP) was operating in a d
Region: II | Turkey Point | 21674 | 09/30/2017 11/09/2017 | 2017003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Rule (a)(4) Risk Assessment for the High Head Safety Injection Pumps |  | H.9 - Training | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.13 | An NRC-identified NCV of 10 CFR 50.65, “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” paragraph (a)(4), was identified for the licensee’s failure to adequately assess and manage the Unit 3 and Unit 4 online risk as
Region: II | Turkey Point | 22284 | 08/18/2017 10/02/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Verification of Electrical Protective Device Selective Coordination |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” for failure to verify that coordination exists between the protective devices on safety related switchgear in order to
Region: II | Turkey Point | 22285 | 08/18/2017 10/02/2017 | 2017007-02 | NRC | NCV | Initiating Events | Green | Failure to Perform Design Verification for Under Frequency Trip of the Main Generator Breakers |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” for failure to verify or check the adequacy of design of the under frequency trip feature of the main generator circuit
Region: II | Turkey Point | 22286 | 08/18/2017 10/02/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of CCW isolation from Supplemental Cooling System (SCS) |  | H.9 - Training | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to verify the adequacy of design of temperature set points used for isolation of the Compone
Region: II | Turkey Point | 22287 | 08/18/2017 10/02/2017 | 2017007-04 | NRC | NCV | Initiating Events | Green | Failure to Verify the Adequacy of Design for Component Protective Covers |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a Green non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to verify the adequacy of design for the non-safety related component protective cover
Region: II | Turkey Point | 22288 | 08/18/2017 10/02/2017 | 2017007-05 | NRC | NCV | Mitigating Systems | Green | Failure to adequately perform discharge testing on 3B Battery |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion XI, “Test Control,” for the licensee’s failure to perform surveillance testing on station battery 3B in accordance with the requirements of In
Region: II | Turkey Point | 22290 | 08/18/2017 10/02/2017 | 2017007-06 | NRC | NCV | Mitigating Systems | Green | Failure to verify the adequacy of design for the Emergency Containment Cooler (ECC) and CCW Systems |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to verify the Emergency Containment Cooler (ECC) unit 4A auto start circuitry would not resu
Region: II | Turkey Point | 22291 | 08/18/2017 10/02/2017 | 2017007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Identify ICW Pipe Corrosion |  | P.1 - Identification | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to inspect Intake Cooling Water (ICW) piping in accordance with licens
Region: II | Turkey Point | 22292 | 08/18/2017 10/02/2017 | 2017007-08 | NRC | NCV | Barrier Integrity | Green | Failure to Correct a Non-Conforming Condition Impacting Containment |  | NPP | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.21M | The NRC identified a non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to take timely corrective action to maintain the unit 3 and 4 containment cathodic protec
Region: II | Turkey Point | 792 | 06/30/2017 08/11/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform 100 Percent General Visual Examinations of Containment Moisture Barriers Associated with Containment Liner Leak Chase Test Connections |  | P.5 - Operating Experience | TE?: N | 05000250 Turkey Point 3 |  | 71111.08P | A NRC-identified Green NCV of 10 CFR 50.55a, "Codes and Standards," was identified for the failure to perform general visual examinations of moisture barrier materials in the reactor containment leak-chase channel test connections in accordance with the A
Region: II | Turkey Point | 793 | 06/30/2017 08/11/2017 | 2017002-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Foreign Materials Exclusion Controls for Thermo-Lag Activities Renders Electrical Equipment Inoperable and Results in a High Energy Arc Flash | EA Case: 2017095 | H.1 - Resources | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | A self-revealing Green (NCV) of Technical Specification (TS) 6.8.1.a., "Procedures and Programs," was identified for the failure to appropriately implement foreign material exclusion (FME) controls during Thermo-Lag fire barrier modifications. Specificall
Region: II | Turkey Point | 23463 | 06/30/2017 08/11/2017 | 2017002-03 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Fire Detection |  | H.9 - Training | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A NRC-identified Green finding was identified for the licensee's failure to follow plant procedure O-ADM-016, "Fire Protection Program," Rev. 19. Specifically, the licensee failed to properly implement fire watches following a HEAF on the 3A 4kV switchgea
Region: II | Turkey Point | 790 | 03/31/2017 05/11/2017 | 2017001-01 | NRC | FIN | Initiating Events | Green | Inadequate Operational Decision-Making Procedure Implementation Results in Feedwater Heater Water Hammer |  | H.1 - Resources | TE?: N | 05000250 Turkey Point 3 |  | 71152 | Green: A self-revealing finding was identified for the failure to adequately implement OP-AA-105-1000, "Operational Decision Making" (ODM) procedure that was used to establish plant conditions for the repair of the Unit 3 condensate tube leak in the 3B fe
Region: II | Turkey Point | 785 | 12/31/2016 01/25/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unrecognized Inoperable Reactor Protection System Instrument Channel |  | H.1 Resources | TE?: N | 05000251 Turkey Point 4 |  | 71153 | Green: A self-revealing NCV of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.1 was identified for the licensee's failure to input the correct Eagle 21 resistance temperature detector (RTD) coefficients into the Eagle 21 reactor p
Region: II | Turkey Point | 775 | 09/28/2016 11/10/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate flood protection for the 4A RHR train |  | H.5 Work Management | TE?: N | 05000251 Turkey Point 4 |  | 71111.06 | Green: The NRC inspectors identified a non-cited violation (NCV) of Technical Specification (TS) 6.8.1, for the licensee's failure to implement required housekeeping controls in the 4A residual heat removal (RHR) pump room to ensure flood protection devic
Region: II | Turkey Point | 782 | 09/28/2016 11/10/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Improper ECC Fuse Installation |  | H.12 Avoid Complacency | TE?: N | 05000250 Turkey Point 3 |  | 71153 | Green: A self-revealed Green finding and associated Non-cited Violation (NCV) of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.2.2 was identified for the failure to properly insert the control power fuse for the 3B Emergency Cont
Region: II | Turkey Point | 783 | 09/13/2016 10/22/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Guidance to Prevent LCSWGR Heat-up |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | Green: The NRC identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to provide adequate procedural guidance to ensure that the temperature in the Load Center
Region: II | Turkey Point | 784 | 09/13/2016 10/22/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Reactor Coolant Loop Check Valve 312-A's Failure to Fully Seat |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | Green: The NRC identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to correct an identified condition adverse to quality involving a failure of charging system check valve 3
Region: II | Turkey Point | 762 | 06/29/2016 08/12/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality Associated with the Eagle 21 System |  | H.14 Conservative Bias | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | NONE | Green. NRC reactor inspectors identified Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for a failure to correct a condition adverse to quality. The licensee identified that the ability to test the Eagle 21 wa
Region: II | Turkey Point | 763 | 06/29/2016 08/12/2016 | 2016002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Post a High Radiation Area |  | H.7 Documentation | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71124.01 | Green. A self-revealing, Green, NCV of TS 6.12.1, was identified for the failure to post a high radiation area (HRA). Specifically, on April 6, 2016, the licensee failed to post the area by the exterior wall of the U4 spent fuel pool (SFP) on the Auxiliar
Region: II | Turkey Point | 754 | 03/31/2016 05/03/2016 | 2016001-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Fully Implement Procedure QI3-PTN-1, Design Control (Section 4OA3) |  |  | TE?: N | 05000250 Turkey Point 3 |  | 71153 | Green: A self-revealing finding was identified for the licensee's failure to provide complete instructions in Maintenance Support Package (MSP) 06-053 for the Isophase Bus Enclosure Collar replacement modification in the Turkey Point switchyard. Specifica
Region: II | Turkey Point | 753 | 12/31/2015 01/27/2016 | 2015004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to correctly follow procedure 3 PMI 072.6, "Steam Dump to Atmosphere Control Loop Calibration." |  | H.8 Procedure Adherence | TE?: N | 05000251 Turkey Point 4 |  | 71111.2 | A self-revealing NCV of Technical Specification (TS) 6.8.1, "Procedures and Programs," was identified when the licensee failed to properly implement procedure 3 PMI-072.6, "Steam Dump to Atmosphere Control Loop Calibration." Specifically, the licensee inc
Region: II | Turkey Point | 740 | 06/30/2015 07/31/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Inadequate General Operating Procedure to Prevent Inadvertent AFAS While Performing a Reactor Plant Planned Shutdown |  | H.1 Resources | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures," was identified for the licensee's failure to maintain adequate guidance in procedure 4-GOP-103, "Power Operation to Hot Standby." Specifically, 4-GOP-103 did n
Region: II | Turkey Point | 742 | 05/12/2015 11/04/2015 | 2015003-01 | NRC | FIN | Initiating Events | Green | Inadequate Work Instructions for Replacing Main Generator Current Transformers (Section 4OA3) |  | H.1 Resources | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing finding was identified for the licensee's failure to provide adequate instructions for performing work on the Unit 4 main generator protection control circuitry. As a result, the lugged connections on an installed current transformer lack
Region: II | Turkey Point | 732 | 02/23/2015 03/17/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Reasonable Maintenance Effectiveness Demonstration for Unit 3 Containment Atmospheric Temperature System |  | P.2 Evaluation | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.17T | Green: The NRC identified a Green non-cited violation (NCV) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately monitor the performance or condition of the Uni
Region: II | Turkey Point | 725 | 12/31/2014 01/30/2015 | 2014005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Non Compliance With HRA Entry Requirements |  | H.12 Avoid Complacency | TE?: N | 05000250 Turkey Point 3 |  | 71124.01 | Green: A self-revealing NCV of Technical Specification (TS) 6.12.1, High Radiation Area, was identified when a worker did not comply with a radiological barrier and entered a high radiation area (HRA) without proper authorization. Specifically, on March 2
Region: II | Turkey Point | 726 | 12/31/2014 01/30/2015 | 2014005-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure to Realign Steam Supply to the Gland Sealing Steam System |  | H.1 Resources | TE?: N | 05000251 Turkey Point 4 |  | 71153 | Green. A self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.8.1, "Procedures", was identified for the licensee's failure to maintain an adequate procedure for gland sealing steam supply realignment. Specifically, the licensee faile
Region: II | Turkey Point | 727 | 12/31/2014 01/30/2015 | 2014005-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform an Adequate Design Verification |  | H.1 Resources | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71153 | Green: A self-revealing finding was identified for the licensee's failure to ensure an adequate design change was implemented during Unit 3 and Unit 4 instrument air compressor system upgrade modifications completed in 2013. Specifically, plant modificati
Region: II | Turkey Point | 730 | 12/31/2014 01/30/2015 | 2014005-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Fully Implement Emergency Operating Procedure 3-EOP-ES-0.1, Reactor Trip Response |  | H.9 Training | TE?: N | 05000250 Turkey Point 3 |  | 71153 | Green: A self-revealing non-cited violation (NCV) of TS 6.8.1, Procedures, was identified when the licensee failed to fully implement procedure 3-EOP-ES-0.1, "Reactor Trip Response." Specifically, the licensee failed to take effective action to implement
Region: II | Turkey Point | 723 | 08/20/2014 10/23/2014 | 2014004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Unsealed Condulet to Prevent Water Intrusion |  |  | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A self-revealing, non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to implement corrective actions to prevent water intrusion into electrical conduits that affected safe
Region: II | Turkey Point | 722 | 06/30/2014 07/31/2014 | 2014003-01 | NRC | NCV | Initiating Events | Green | Failure to implement a surveillance procedure to perform a RCS unidentified leak rate statistical calculation |  | H.8 Procedure Adherence | TE?: N | 05000251 Turkey Point 4 |  | 71111.22 | The NRC identified a non-cited violation (NCV) of Technical Specification 6.8.1, Procedures, for the licensee's failure to implement procedure 4-OSP-041.1, Reactor Coolant System (RCS) Leak Rate Calculation. Specifically, the licensee did not perform a Un
Region: II | Turkey Point | 720 | 03/31/2014 05/01/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Actions to Correct Flow Induced Vibration Leads to CCW Piping Weld Failures. |  | P.2 Evaluation | TE?: N | 05000251 Turkey Point 4 |  | 71152 | A Green self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified when the licensee failed to implement corrective actions that addressed the low stress high cycle fatigue of component cooling wate
Region: II | Turkey Point | 721 | 03/31/2014 05/01/2014 | 2014002-02 | Self - Revealed | NCV | Mitigating Systems | Green | TS Channel Calibration of ESF Steam Line Protection Channel III Not Performed |  | H.5 Work Management | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A Green self-revealing non-cited violation (NCV) of TS Section 3.3.2, "Engineered Safety Features Actuation Instrumentation," (ESF) was identified when the licensee failed to perform the channel calibration of Unit 3 ESF steam pressure protection channel
Region: II | Turkey Point | 718 | 03/07/2014 04/03/2014 | 2014008-01 | NRC | FIN | Initiating Events | Green | Failure to Properly Program the Turbine Generator Digital Control System Load Drop Anticipatory Circuit Results in a Manual Reactor Trip |  | H.8 Procedure Adherence | TE?: N | 05000250 Turkey Point 3 |  | 71153 | A self-revealing green finding was identified for the failure to establish new digital software set points for the load drop anticipatory (LDA) logic circuit associated with an extended power uprate (EPU) digital turbine electro-hydraulic control (EHC) sy
Region: II | Turkey Point | 719 | 02/28/2014 04/07/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Time Critical Operator Action Program Procedure |  | H.8 Procedure Adherence | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a green non-cited violation of Technical Specification 6.8.1, "Procedures and Programs," for the licensee's failure to implement procedure 0-ADM-232, Time Critical Action Program, to ensure time critical actions (TCAs) important to mit
Region: II | Turkey Point | 716 | 12/31/2013 01/31/2014 | 2013005-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Test Precautions, Limitations, and Instructions for Performing Harmonic Testing on the Unit 4 Turbine Generator |  | H.3(a) Work Planning | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing Green finding was identified for the licensee's failure to provide adequate test precautions, limitations, and instructions for performing harmonic testing on the Unit 4 turbine generator control circuitry while in Mode 1 operation. As a
Region: II | Turkey Point | 703 | 09/30/2013 10/31/2013 | 2013004-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate procedure to vent 3B SGFP results in AFW actuation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A self-revealing non-cited violation of Technical Specification 6.8.1, "Procedures," was identified for the licensee's failure to maintain an adequate procedure for venting the 3B steam generator feed pump (SGFP). Specifically, the licensee had failed to
Region: II | Turkey Point | 709 | 09/30/2013 10/31/2013 | 2013004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to follow procedure to switch running SGFPs results in AFW actuation |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A self-revealing non-cited violation of Technical Specification 6.8.1, "Procedures," was identified for the licensee's failure to implement Section 2.0 of procedure 3-NOP-074, "Steam Generator Feedwater System," for starting the 3A steam generator feedwat
Region: II | Turkey Point | 710 | 09/30/2013 10/31/2013 | 2013004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to provide adequate instructions during maintenance on the gland seal steam system |  | H.3(a) Work Planning | TE?: N | 05000250 Turkey Point 3 |  | 71152 | A self-revealing finding was identified due to the licensee's failure to provide adequate work instructions for throttling the Unit 3 gland seal steam bypass valve. As a result of the licensee's inadequate work instructions, an operator opened the spill b
Region: II | Turkey Point | 711 | 09/30/2013 10/31/2013 | 2013004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Power operated relief vlave inoperable for greater than allowed outage time due to lifted heads |  | H.4(b) Procedural Compliance | TE?: N | 05000251 Turkey Point 4 |  | 71153 | A self-revealing non-cited violation of the limiting condition for operation specified by Unit 4 Technical Specification (TS) 3.4.9.3, "Overpressure Mitigating System," was identified due to the inoperability of a reactor coolant system (RCS) power-operat
Region: II | Turkey Point | 714 | 09/30/2013 10/31/2013 | 2013004-05 | Self - Revealed | NCV | Initiating Events | Green | Safety injection flow path not isolated due to manual valve out of position |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000250 Turkey Point 3 |  | 71153 | The inspectors identified a self-revealing non-cited violation of the limiting condition for operation specified by Unit 3 Technical Specification (TS) 3.4.9.3, "Overpressure Mitigating Systems," which occurred as a result of the licensee's failure to loc
Region: II | Turkey Point | 701 | 06/30/2013 07/30/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Pressure Boundary Through Wall Leak on the 3A CCW Pump Casing Vent Pipe |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000250 Turkey Point 3 |  | 71111.15 | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a through wall pressure boundary leak on the 3A component cooling water (CCW) pump casing vent
Region: II | Turkey Point | 715 | 06/28/2013 08/07/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to ensure that structural steel that was part of a fire barrier was provided with a three hour fire proofing |  |  | TE?: N | 05000250 Turkey Point 3 |  | 71111.05T | An NRC-identified non-cited violation (NCV) of Turkey Point Unit 3 operating license condition (OLC) 3.D, Fire Protection, was identified for the failure to ensure that structural steel that was part of a fire barrier for fire zone (FZ) 104 was provided w
Region: II | Turkey Point | 686 | 03/31/2013 04/24/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Timely Corrective Actions to Test Molded Case Circuit Breakers |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | NONE | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to establish a test program to demonstrate that safety-related 120 VAC and 125 VDC molded case circuit breakers (MCCBs) w
Region: II | Turkey Point | 690 | 03/31/2013 04/24/2013 | 2013002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Noncompliance with Radiological Barrier |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 |  | 71124.02 | A Green self-revealing non-cited violation (NCV) of Technical Specification (TS) 6.12.1 was identified when a worker did not comply with a radiological barrier and entered a high radiation area (HRA) without proper authorization. Specifically, the worker
Region: II | Turkey Point | 689 | 03/31/2013 04/24/2013 | 2013002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Flow-Induced Vibration Leads to CCW Piping Weld Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000251 Turkey Point 4 |  | 71152 | A Green self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified when the licensee failed to implement corrective actions that addressed low stress high cycle fatigue of component cooling water (CC
Region: II | Turkey Point | 684 | 12/31/2012 01/30/2013 | 2012005-01 | NRC | FIN | Initiating Events | Green | Failure to verify 1B feedwater heater drain valve closed |  | H.4(b) Procedural Compliance | TE?: N | 05000251 Turkey Point 4 |  | 71111.11Q | A self-revealing finding was identified when the licensee failed to follow procedure 0-ADM-222, Drain and Vent Rig Controls, while installing a temporary drain hose on Turkey Point Unit 4 in-service equipment. Operations and maintenance workers failed to
Region: II | Turkey Point | 680 | 09/30/2012 10/30/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Operation at power with Unit 3 feedwater flow transmitter connected incorrectly |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 |  | 71111.19 | A self-revealing, non-cited violation (NCV) of Turkey Point Technical Specification (TS) 3.3.1 Reactor Trip System Instrumentation was identified when process tubing to a Unit 3 feedwater flow transmitter was found incorrectly installed. As a result, one
Region: II | Turkey Point | 681 | 08/02/2012 10/05/2012 | 2012011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Requirements into Plant Procedures and Calculations for CCW Heat Balance Equation |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | An NRC identified non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified for the licensee's failure to translate the worse case total post accident ICW flow rate for CCW heat exchangers, as documented in calculat
Region: II | Turkey Point | 682 | 08/02/2012 10/05/2012 | 2012011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Following Identification of a Non-conservative Technical Specification |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | An NRC identified non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified when the licensee's failure to take timely corrective action to address a nonconforming condition of Technical Specification (TS) 3/4.5.2 S R4
Region: II | Turkey Point | 679 | 06/30/2012 07/31/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Analysis for the Permanent Removal of Main Steam Pipe Whip Restraints |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000250 Turkey Point 3 |  | 71111.17T | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the licensee's failure to perform an analysis for the removal of the Unit 3 main steam pipe whip restraints. These restraints are credi
Region: II | Turkey Point | 672 | 03/31/2012 04/26/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Emergency lighting to auxiliary feedwater area disabled |  | H.3(a) Work Planning | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.05Q | The inspectors identified a non-cited violation of the Units 3 and 4 operating licenses condition 3.D, Fire Protection, when the licensee failed to provide emergency lighting in the common auxiliary feedwater (AFW) cage and other areas. The electrical pan
Region: II | Turkey Point | 673 | 03/31/2012 04/26/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Control power cables repeatedly submerged in ground water, contrary to design |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.06 | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified when FPL did not maintain safety-related power cables in the environment for which they were designed and tested. Specifically, 125 volt DC
Region: II | Turkey Point | 667 | 12/31/2011 01/26/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Valve Deficiency Results in Both Headers of Intake Cooling Water Inoperable |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | A self-revealing Non-cited violation of 10 CFR 50 Criterion XVI was identified when the licensee failed to correct a degraded butterfly valve in the Unit 3 intake cooling water system. On August 11, 2011, failure of this valve led to a loss of intake cool
Region: II | Turkey Point | 665 | 09/30/2011 10/27/2011 | 2011004-01 | NRC | NCV | Barrier Integrity | Green | Failure to control defective component results in safety system surveillance failure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000250 Turkey Point 3 |  | 71111.12 | (Green) A Self-revealing Non-cited violation of Technical Specification requirements was identified for failure to implement procedures to control a defective component and prevent its use in a safety-related system. Specifically, the licensee installed a
Region: II | Turkey Point | 659 | 08/12/2011 09/16/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify or Check the Adequacy of Design for Safety-Related Components with Four Examples |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify or check the adequacy of design for with four examples. The licensee entered these issues into their
Region: II | Turkey Point | 660 | 08/12/2011 09/16/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Records to Support Acceptance Criteria in Design Calculations |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | . The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," for the licensee's failure to maintain sufficient records to furnish evidence of activities affecting quality. Specifically, the licensee was not able
Region: II | Turkey Point | 661 | 08/12/2011 09/16/2011 | 2011008-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Voltage Calculations |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to perform adequate voltage calculations for safety-related equipment with two examples. The licensee entered these issues into their corr
Region: II | Turkey Point | 662 | 08/12/2011 09/16/2011 | 2011008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Test the SBO Cross-Tie under Loaded Conditions |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a NCV of 10 CFR 50.63 for the licensee's failure to test the station blackout (SBO) cross-tie components under loaded conditions. Since 1991, the licensee failed to verify the capability of the SBO cross-tie and associated components t
Region: II | Turkey Point | 656 | 06/30/2011 07/27/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to properly perform a procedure results in damage to an RHR pump |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.04Q | A self-revealing, non-cited violation (NCV) of Technical Specifications 6.8.1.a, Procedures, was identified when operators did not properly align the RHR system from shutdown cooling mode to injection mode. As a result, the 4A RHR pump was left running wi
Region: II | Turkey Point | 654 | 03/31/2011 04/28/2011 | 2011002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Monitor a Reactivity Change Results in Power Operation Above 100 Percent |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 |  | 71111.22 | The inspectors identified a non-cited violation (NCV) of Technical Specifications 6.8.1.a, Procedures, when operators did not adequately monitor reactor power nor the position of valve TC-3-144A, a valve which affects reactivity, during a letdown valve in
Region: II | Turkey Point | 636 | 12/31/2010 01/27/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate procedure guidance results in degradation of boration flow path and loss of charging flow |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000250 Turkey Point 3 |  | 71111.04Q | -Green. The inspectors identified a Non-cited violation (NCV) of Technical Specification 6.8, Procedures, when plant alarm response and off-normal procedures were not adequate to prevent lifting of a charging relief valve. As a result, during operations t
Region: II | Turkey Point | 637 | 12/31/2010 01/27/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Scaffold blocked access to fire areas used in a control room evacuation event |  | H.3(a) Work Planning | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.05Q | The inspectors identified a Non-cited violation (NCV) of very low safety significance when scaffolding was placed as a barricade against personnel access to doors to fire zones 108B and 104. The barricade impeded access to the 3B and 3A DC Equipment rooms
Region: II | Turkey Point | 638 | 12/31/2010 01/27/2011 | 2010005-03 | NRC | NCV | Barrier Integrity | Green | Welders failed to measure preheat and interpass temperatures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000250 Turkey Point 3 |  | 71111.08P | -Green. The inspectors identified a Non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" associated with licensee contract personnel's failure to adhere to welding procedures during the 2010 Unit 3
Region: II | Turkey Point | 645 | 12/31/2010 01/27/2011 | 2010005-04 | NRC | NCV | Barrier Integrity | Green | Inadequate implementation of corrective actions fail to correct a condition adverse to quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 |  | 71111.2 | -Green: The inspectors identified an NCV of 10 CFR, Part 50, Appendix B, Criterion XVI, for the licensee's failure to implement timely corrective actions to address conditions adverse to quality on the Unit 3 fuel handling manipulator crane. As a result,
Region: II | Turkey Point | 34850 | 09/30/2010 10/29/2010 | 2010004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to provide adequate instructions when working on the reactor protection system results in reactor trip |  | H.3(b) Work Activity Coordination | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.12 | A self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified when the licensee started corrective maintenance on the Unit 4 reactor protection system with an inadequate procedure.
Region: II | Turkey Point | 647 | 06/30/2010 07/29/2010 | 2010003-01 | NRC | NCV | Public Radiation Safety | Green | Failure to perform adequate surveys to ensure proper estimation of radionuclide concentrations in mechanical filter waste shipments |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | NONE | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 20.1501(a) for the failure to perform adequate surveys to meet the requirements of 10 CFR Part 20 Appendix G. 10 CFR Part 20 Appendix G states that shippers of radioactive waste mu
Region: II | Turkey Point | 648 | 06/30/2010 07/29/2010 | 2010003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to implement TS requirements regarding rod position indication |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71153 | A Self-Revealing Non-cited Violation of technical specification requirements was identified on Unit 3 when position indication for two rod control cluster assemblies (RCCs) drifted out of tolerance with the associated rod group position indication. Contra
Region: II | Turkey Point | 34844 | 05/21/2010 07/02/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate procedure implementation resulting in snubber failure. |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | The NRC identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, for the licensee's failure to implement procedures during a visual inspection of safety related seismically qualified snubber SN-4-1039. Specifically, the licensee failed to i
Region: II | Turkey Point | 34842 | 03/31/2010 04/28/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement design controls in a temporary modification. |  | H.4(b) Procedural Compliance | TE?: N | 05000251 Turkey Point 4 |  | 71111.18 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for failing to maintain control of temporary equipment installed on unit 4 A residual heat removal pump piping when the permanent component cooling water flow indica
Region: II | Turkey Point | 34832 | 12/30/2009 01/28/2010 | 2009005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Implement Required TS Controls for a High Radiation Area with Dose Rates in Excess of 1000 mrem/hr |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000251 Turkey Point 4 |  | 7112101 | A Self-revealing Non-cited Violation of Technical Specification (TS) 6.12.2, was identified for failure to meet high radiation area (HRA) control requirements for an accessible location, i.e., Unit 4 (U4) reactor auxiliary building (RAB) roof, with radiat
Region: II | Turkey Point | 34818 | 06/30/2009 07/30/2009 | 2009003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Procedures for Conducting AValve Alignment Causes Spill of Reactor Coolant And Contamination Of A Plant Employee |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.04Q | A Self-revealing Non-cited Violation of Technical Specification (TS) 6.8.1 was identified for failure to follow procedures that assure that valves are maintained in the proper positions. As a result of mis-positioning of letdown system valves, a spill of
Region: II | Turkey Point | 34821 | 06/30/2009 07/30/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Implement TS Requirements Resulting From Loss Of Configuration Control Of The 3C Main Steam Isolation Valve |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.04Q | A Self-Revealing Non-cited violation of TS 3.7.1.5 requirements was identified when the Unit 3 C main steam isolation valve (MSIV) failed to close on demand on May 4, 2009. Licensee evaluation has found the root cause of the failure to be an inadequate po
Region: II | Turkey Point | 34822 | 06/30/2009 07/30/2009 | 2009003-03 | NRC | FIN | Mitigating Systems | Green | Failure To Maintain Lighting Impedes Compensatory Measure For Failed Fire Detection. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.04Q | The inspectors identified a Green finding for failure to correct failed lighting in a Unit 4 electrical penetration room that prevented the hourly rover from adequately compensating for fire detection that was out of service. The inspectors determined tha
Region: II | Turkey Point | 34823 | 06/30/2009 07/30/2009 | 2009003-04 | NRC | NCV | Mitigating Systems | Green | Failure To Assure That Design Controls Were Maintained During Maintenance On The 3B Main Steam Isolation Valve (MSIV). |  | H.4(b) Procedural Compliance | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.12 | The inspectors identified a Non-cited violation of 10 CFR50, Appendix B, Criterion III, Design Control when maintenance personnel failed to follow procedure during reassembly of 3B main steam isolation valve and did not maintain proper configuration of a
Region: II | Turkey Point | 34824 | 06/30/2009 07/30/2009 | 2009003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Design Controls When Modifying Safety Equipment During Painting Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.18 | A Self-revealing Non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V was identified for failing to implement procedures that assure design control during an alteration to the 4C intake cooling water pump motor, a safety-related component. As a
Region: II | Turkey Point | 34829 | 06/30/2009 07/30/2009 | 2009003-06 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Evaluation Of Damaged Rod Control Extension Results In High Risk Evolution And Risk Condition Yellow |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.2 | A Self-revealing Finding was identified when the licensee did not manage maintenance activities adequately to identify and repair a damaged rod control drive component on Unit 3 prior to setting the reactor vessel closure head on the reactor vessel flange
Region: II | Turkey Point | 34830 | 06/30/2009 07/30/2009 | 2009003-07 | NRC | NCV | Barrier Integrity | Green | Failure to implement TS requirements Regarding structural integrity of code class 2 main steam isolation components |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.2 | The inspectors identified a Non-cited violation of TS 3.4.10 requirements on Unit 3 regarding required components, when plant operation continued although a structural flaw in Class 2 main steam isolation valve steam trap piping had been identified. As a
Region: II | Turkey Point | 34814 | 11/17/2008 12/18/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Verification Affecting AFW Flow Control Valves and Unit 3 EDG Building Room Ventilation |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a finding of very low safety significance involving two examples of a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, Design Control. Specifically, in one example, the licensee failed to establish design control meas
Region: II | Turkey Point | 34815 | 11/17/2008 12/18/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Limiting Value Adequacy for Safety-Related Battery Intercell Resistance |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the failure to verify and ensure that the 125 VDC safety-related batteries would remain operable if all the inter-cell
Region: II | Turkey Point | 34813 | 09/30/2008 10/30/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | Failure To Implement Technical Specification Requirements Regarding Structural Integrity of Reactor Coolant System Components |  |  | TE?: N | 05000251 Turkey Point 4 |  | 71111.22 | The inspectors identified a Non-cited violation of Technical Specification (TS) 3.4.10, when the licensee failed to either isolate a flawed ASME Code Class 1 crack or place Unit 4 in a condition where the TS did not apply. As a result, plant operation was
Region: II | Turkey Point | 34804 | 06/30/2008 07/30/2008 | 2008003-01 | Self - Revealed | FIN | Initiating Events | Green | Maintenance causes smoke and fumes to enter the control room causing fire alarms. |  | H.4(b) Procedural Compliance | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.05A | A Self-Revealing finding of very low safety significance was identified after smoke and welding fumes from maintenance entered the control room through the ventilation system causing smoke alarms. When identified, the licensee stopped the maintenance and
Region: II | Turkey Point | 34805 | 06/30/2008 07/30/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to implement procedures that assure component lineups prior to power escalation. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.2 | The inspectors identified a non-cited violation of Technical Specification (TS) 6.8.1, Procedures for failure to implement Unit 4 plant startup requirements regarding alignment of components that support operability of the recirculation sump. When identif
Region: II | Turkey Point | 34806 | 06/30/2008 07/30/2008 | 2008003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to take timely corrective actions leads to emergency diesel generator failure. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | A Self-revealing Non-cited violation of 10 CFR 50, Appendix B, Criterion XVI was identified when external corrosion of a Unit 3 emergency diesel radiator was not promptly repaired resulting in a diesel failure. The licensee repaired the radiator and enter
Region: II | Turkey Point | 34800 | 03/31/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement procedures regarding overtime hours for plant operations personnel |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | The inspectors identified a Non-cited violation of Technical Specification (TS) 6.8.5 for the failure of the licensee to properly implement procedure requirements regarding the control of overtime for operations personnel that may perform safety-related d
Region: II | Turkey Point | 34796 | 12/31/2007 01/29/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | Failure to implement the fire protection program: unapproved transient combustibles in the cable spreading room |  | H.4(b) Procedural Compliance | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.05Q | The inspectors identified a Non-Cited violation for failure to implement the fire protection program when unapproved transient combustibles (including an ignition source) were found in the cable spreading room without the required evaluation. When identif
Region: II | Turkey Point | 34797 | 12/31/2007 01/29/2008 | 2007005-02 | NRC | FIN | Mitigating Systems | Green | Failure to correct moisture buildup in alternate shutdown panel results in degraded cooldown capability |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7111117A | The inspectors identified a finding when the licensee failed to evaluate excessive moisture and condensation in the Unit 3 alternate shutdown panel. During subsequent testing, all channels of steam generator pressure indication at the panel were inoperabl
Region: II | Turkey Point | 34798 | 12/31/2007 01/29/2008 | 2007005-03 | NRC | NCV | Initiating Events | Green | Failure to periodically update the FSAR with changes made to the cable spreading room fire loading |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.15 | The inspectors identified a Non-Cited violation for failure to update the final safety analysis report (FSAR) regarding fire loading of permanently installed equipment in the cable spreading room to assure that the information included in the FSAR is the
Region: II | Turkey Point | 34785 | 09/30/2007 10/30/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required ASME Code Section XI Leakage Testing |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.08P | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.55a(g)(4) for the failure to perform periodic leakage testing of buried piping portions of the Intake Cooling Water system as required by Section XI of the ASME Code for the third 10-year
Region: II | Turkey Point | 34787 | 09/30/2007 10/30/2007 | 2007004-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Include an Accurate Emergency Response Telephone Number on Radioactive Waste Shipping Papers |  | H.4(a) Human Error Prevention | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7112202 | The inspectors identified an NCV of 10 CFR Part 71.5(a)(1)(v) for the failure of the licensee to follow Department of Transportation (DOT) regulations found in 49 CFR Part 172.201(d) which require shipping papers associated with the transport of radioacti
Region: II | Turkey Point | 34788 | 09/30/2007 10/30/2007 | 2007004-04 | NRC | FIN | Mitigating Systems | Green | Recurring Problems with Alternate Shutdown Communication Equipment |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152 | The inspectors identified a finding when the licensee did not identify and correct an adverse trend of recurring problems with the alternate shutdown communications system. When identified, the licensee entered the issue into the corrective actions progra
Region: II | Turkey Point | 34789 | 09/30/2007 10/30/2007 | 2007004-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Appropriately Procure Replacement Parts Leads to Reactor Shutdown |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71153 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion IV, Procurement Document Control, was identified for improper inserts having been procured and installed in the Unit 3 and Unit 4 rod position circuitry. The inserts were not qualified for the react
Region: II | Turkey Point | 34777 | 06/30/2007 07/17/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design of Valves Important to Safety |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure of the licensee to promptly identify and correct the nonconformance of equipment important to safety, specifically the operation of air
Region: II | Turkey Point | 34778 | 06/30/2007 07/17/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Controls in a Modification |  | H.4(a) Human Error Prevention | TE?: N | 05000251 Turkey Point 4 |  | 7111123 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, Procedures, for failure of the licensee to implement design controls when a wooden and wire structure was installed in the Unit 4 480 volt switchgear room. When identif
Region: II | Turkey Point | 34779 | 06/08/2007 07/06/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Reports for Conditions Adverse to Quality as Required by Procedure |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedure, and Drawings. Specifically, the inspectors identified several conditions adverse to quality where the licensee failed to initiate c
Region: II | Turkey Point | 34780 | 06/08/2007 07/06/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Corrective Actions Associated with Water Intrusion Trends Were Not Taken in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000251 Turkey Point 4 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee failed to promptly correct a previously identified water intrusion trend which resulted in the failure of a
Region: II | Turkey Point | 34781 | 06/08/2007 07/06/2007 | 2007008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Recurring Scaffolding Installation Deficiencies |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action. Specifically, the licensee failed to implement effective corrective actions to prevent recurring deficiencies associated with the erect
Region: II | Turkey Point | 34774 | 12/31/2006 01/26/2007 | 2006005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Indications During a Steam Generator Eddy Current Examination |  |  | TE?: N | 05000251 Turkey Point 4 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions." During the 2003 outage, the licensee failed to identify two tubes in the Steam Generator 'A', that had wear indications that exceeded TS tube pl
Region: II | Turkey Point | 34775 | 12/31/2006 01/26/2007 | 2006005-02 | NRC | NCV | Initiating Events | Green | Failure to Comply with Core Alteration Procedures for Handling of Irradiated Fuel |  | H.4(b) Procedural Compliance | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.2 | The inspectors identified a Green non-cited violation of Technical Specification 6.8.1 for failure to implement procedures during core alterations when operators failed to maintain reliable communications and to place irradiated fuel in a safe storage loc
Region: II | Turkey Point | 34773 | 09/30/2006 10/26/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement adequate corrective actions to prevent recurring deficiencies in flood protection barriers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.06 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, Corrective Actions, for failure to take actions to prevent repeated deficiencies with external flood protection equipment. Although deficiencies with wood
Region: II | Turkey Point | 34751 | 03/31/2006 04/28/2006 | 2006002-01 | NRC | NCV | Barrier Integrity | Green | Failure to ensure emergency operating procedure step is usable |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.11Q | The inspectors identified a non-cited violation of Technical Specification 6.8.1.a, which requires that written procedures be implemented covering the activities recommended by Regulatory Guide 1.33, including procedures for procedure adherence. The viola
Region: II | Turkey Point | 34754 | 03/31/2006 04/28/2006 | 2006002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to install jumpers during maintenance results in diesel inoperability |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 6.8.1, Procedures, was identified during a loss of offsite power event on March 8, 2006, when both Unit 3 emergency diesel generators were made inoperable by installation of ground test devic
Region: II | Turkey Point | 34755 | 03/31/2006 04/28/2006 | 2006002-05 | Self - Revealed | FIN | Initiating Events | Green | Human performance error results in a secondary plant transient |  |  | TE?: N | 05000251 Turkey Point 4 |  | 71111.22 | A self-revealing finding was identified when a maintenance technician operated an incorrect valve while conducting a main steam line pressure transmitter surveillance. The valve that was mistakenly closed was associated with a pressure instrument that was
Region: II | Turkey Point | 34756 | 03/31/2006 04/28/2006 | 2006002-06 | NRC | NCV | Public Radiation Safety | Green | Failure to implement adequate quality controls to ensure representative sampling for particulates in the Plant Vent SPING |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 7112101 | The inspectors identified a non-cited violation of Technical Specification 6.8.1.e for failure to implement quality control activities consistent with guidance in Regulatory Guide 1.21 to maintain representative sampling and monitoring of particulates in
Region: II | Turkey Point | 34749 | 02/17/2006 03/17/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Implement Effective Corrective Actions to Prevent Recurring Scaffolding Installation Deficiencies |  |  | TE?: N | 05000250 Turkey Point 3 05000251 Turkey Point 4 |  | 71152B | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to identify and implement effective corrective actions for recurring problems related to the construction of scaffolding
Region: II | Vogtle | 126193 | 11/08/2019 12/13/2019 | 2019010-01 | NRC | NCV | Barrier Integrity | Green | Inadequate corrective action to implement time critical operator action |  | P.2 - Evaluation | TE?: N | 05000425 Vogtle 2 | Human Performance | 71111.21M | NRC inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” because SNC did not assure that a deficiency associated with the steam generator atmospheric relief isolation valve was promptly ident
Region: II | Vogtle | 13 | 12/31/2018 02/14/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Work Instructions for Checking Lube Oil Level in Nuclear Service Cooling Water Fan Gear Reducer |  | H.5 - Work Management | TE?: N | 05000424 Vogtle 1 |  | 71152 | A Green self-revealing NCV of TS 5.4.1.a, “Procedures,” was identified for the licensee’s failure to check Nuclear Service Cooling Water (NSCW) fan gear reducer lube oil level in accordance with work instructions. As a result, the licensee failed to ident
Region: II | Vogtle | 22609 | 09/30/2018 12/21/2017 | 2017012-01 | NRC | NOV |  | Green | Failure to complete system operator rounds as prescribed by procedure. | EA Case: 17-166 |  | TE?: Y SL-III-NOV | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | 10 CFR 50, Appendix B, Criterion V requires, in part, that activities affecting quality shall be prescribed by documented instructions, procedures, or drawings, of a type appropriate to the circumstances and shall be accomplished in accordance with these
Region: II | Vogtle | 24117 | 06/30/2018 08/09/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Load EDG During 24-Hour Endurance Test |  | H.9 - Training | TE?: N | 05000424 Vogtle 1 |  | 71152 | An NRC-identified Green NCV of Vogtle Nuclear Station TS, Section 5.4.1.a, “Procedures,” was identified for the licensee’s failure to implement the EDG 24-hour endurance surveillance procedure 14668A-1, “Train A Diesel Generator Operability Test,” revisio
Region: II | Vogtle | 24118 | 06/30/2018 08/09/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | High Vibrations on Unit 2 NSCW Pump #3 Result in Pump Inoperability |  | H.6 - Design Margins | TE?: N | 05000424 Vogtle 1 |  | 71152 | An NRC-identified Green NCV of 10 CFR 50 Appendix B, Criterion III, “Design Control,” was identified for the licensee’s failure to ensure that design control measures for the Unit 2 train ‘A’ (2A) nuclear service cooling water (NSCW) pump #3 motor replace
Region: II | Vogtle | 24009 | 05/11/2018 05/11/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Work Instructions for Sealing Around NSCW System Pump Shaft Well Access Openings |  | H.1 - Resources | TE?: N | 05000424 Vogtle 1 |  | 71111.12 | An NRC identified Green NCV of Vogtle Electric Generating Plant Technical Specification (TS), Section 5.4.1.a, “Procedures,” was identified for the licensee’s failure to provide work instructions for the sealing of gaps around cover plates for the nuc
Region: II | Vogtle | 24010 | 05/11/2018 05/11/2018 | 2018001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for Testing of NSCW Pump Discharge Valves |  | H.8 - Procedure Adherence | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.22 | An NRC identified Green NCV of 10 CFR 50.55a(f), "Inservice testing (IST) requirements," subsection (4), American Society of Mechanical Engineers (ASME) Operation and Maintenance of Nuclear Power Plants (OM) code Subsection ISTC-5122, “Stroke Acceptan
Region: II | Vogtle | 24011 | 05/11/2018 05/11/2018 | 2018001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Refurbishment of Emergency Diesel Generator Pneumatic Control System Logic Boards |  | H.1 - Resources | TE?: N | 05000425 Vogtle 2 |  | 71153 | A Green self-revealing NCV of TS Section 5.4.1.a, “Procedures,” was identified for the licensee’s failure to properly preplan and perform maintenance work on the Unit 2 ‘B’ train (2B) emergency diesel generator (EDG) pneumatic control shutdown logic board
Region: II | Vogtle | 23215 | 12/31/2017 02/07/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement and Establish Appropriate Work Instructions for PMT of Namco Limit Switch on 2HV-8920 |  |  | TE?: N | 05000425 Vogtle 2 |  | 71111.15 | A Green, self-revealing, non-cited violation (NCV) of TS 5.4.1.a, “Procedures,” was identified for the licensee’s failure to implement maintenance work instructions and establish appropriate procedures concerning the post maintenance testing (PMT) of
Region: II | Vogtle | 23453 | 12/31/2017 01/23/2018 | 2017009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Install Drain Hole |  |  | TE?: N | 05000425 Vogtle 2 |  | 71111.21N | The NRC identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, “Corrective Action,” for licensee’s failure to verify drain holes were installed as assigned, following the licens
Region: II | Vogtle | 23233 | 10/30/2017 10/30/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement and Establish Appropriate Work Instructions Affecting Safety-Related Chiller |  | H.11 - Challenge the Unknown | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.22 | A Self-Revealing, Green, non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.a, “Procedures,” was identified for the licensee’s failure to implement maintenance work instructions and establish appropriate procedures concerning the use of fl
Region: II | Vogtle | 23234 | 10/30/2017 10/30/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain ECCS Flow Balance and Check Valve Inservice Test Procedure |  | H.1 - Resources | TE?: N | 05000425 Vogtle 2 |  | 71111.22 | An NRC-Identified, Green, NCV of TS 5.4.1.a, “Procedures,” was identified for the licensee’s failure to maintain a Unit 2 surveillance procedure that demonstrated satisfactory performance of the forward flow safety function of emergency core cooling sys
Region: II | Vogtle | 23452 | 10/30/2017 10/30/2017 | 2017003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Cleanliness of Motor Operated Valve Limit Switch Compartment |  | H.12 - Avoid Complacency | TE?: N | 05000425 Vogtle 2 |  | 71152 | A Self-Revealing, Green, NCV of TS 5.4.1.a, “Procedures,” was identified for the licensee’s failure to perform an adequate cleanliness inspection of the Unit 2 nuclear service cooling water (NSCW) system pump no. 6 discharge motor-operated-valve (MOV) l
Region: II | Vogtle | 23217 | 08/16/2017 02/07/2018 | 2017004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain NEMA Type 4 Qualification for the Nuclear Service Cooling Water Pumps |  | H.1 - Resources | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | (Green). A Green, self-revealing, NCV of TS 5.4.1.a, “Procedures,” was identified for the licensee’s failure to properly implement and establish procedures to maintain watertight requirements of the nuclear service water system (NSCW) pumps’ motor main po
Region: II | Vogtle | 1511 | 07/21/2017 07/21/2017 | 2017002-01 | NRC | NCV | Initiating Events | Green | Failure to Correct a Condition Adverse to Quality Involving an MSIV Manufacturing Deficiency |  |  | TE?: N | 05000424 Vogtle 1 |  | 71153 | (Green). A self-revealing, Green, non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure to identify and correct a condition adverse to quality (i.e., manufacturing deficiency), which
Region: II | Vogtle | 1514 | 07/21/2017 07/21/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Work Instructions for Implementation of Open Phase Protection System |  | H.8 - Procedure Adherence | TE?: N | 05000424 Vogtle 1 |  | 71153 | (Green). A self-revealing, Green, non-cited violation of Technical Specifications 5.4.1.a, "Procedures," was identified for the licensee's failure to redline new wiring installation associated with an open phase protection system modification installation
Region: II | Vogtle | 1515 | 03/10/2017 04/19/2017 | 2017007-01 | NRC | FIN | Mitigating Systems | Green | Failure to identify a Degraded Atmospheric Relief Valve |  | P.3 Resolution | TE?: N | 05000424 Vogtle 1 |  | 71152B | Green: The NRC identified a Green finding for the licensee's failure to identify the reduced reliability of Unit 1 loop 3 atmospheric relief valve (ARV) 1PV-3020 as a degraded/nonconforming condition, as required by NMP-AD-012, "Operability Determination
Region: II | Vogtle | 1509 | 12/31/2016 02/07/2017 | 2016004-01 | NRC | NCV | Initiating Events | Green | NCV 05000425/2016004-01, Failure to Implement Maintenance Procedure for SOV Electrical Connectors |  | H.8 Procedure Adherence | TE?: N | 05000425 Vogtle 2 |  | 71111.12 | A self-revealing non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.a, "Procedures," was identified for the licensee's failure to properly install shims when assembling electrical connectors on Unit 2 main steam isolation valve (MSIV) HV-302
Region: II | Vogtle | 1503 | 11/04/2016 12/23/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Capability of EDGs Under Maximum Frequency and Voltage |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for failure to correctly translate the appropriate permissible limits for frequency and voltage from technical spe
Region: II | Vogtle | 1504 | 11/04/2016 12/23/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure Adequate Unit 1 Emergency Diesel Generator Surveillance Acceptance Criteria |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to have adequate instructions and acceptance criteria to confirm t
Region: II | Vogtle | 1505 | 11/04/2016 12/23/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Isolation Requirements When Incorporating Non-Class 1E Components into Class 1E electrical Circuits |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III "Design Control," for installing non-safety related Individual Cell Equalizer devices into the Class 1E battery charging circuits wit
Region: II | Vogtle | 1506 | 11/04/2016 12/23/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required In-Service Testing of Unit 2 CST Swap over Valves |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green non-cited violation of Technical Specification 5.5.8, "Inservice Testing Program," for Vogtle Unit 2 failure to perform the required testing in accordance with the American Society of Mechanical Engineers Operation and Maintenan
Region: II | Vogtle | 1507 | 11/04/2016 12/23/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Periodic Testing Of Safety-Related Valve Interlocks |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green, non-cited violation of Title 10 Code of Federal Regulations Part 50.55a(h)(2) "Protection Systems," because the licensee failed to perform periodic testing of safety-related valve interlocks to ensure an adequate single failure
Region: II | Vogtle | 1508 | 11/04/2016 12/23/2016 | 2016007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Assure Auxiliary Feedwater Design Basis Capability |  | H.6 Design Margins | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The NRC identified a Green non-cited violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to translate the Auxiliary Feedwater (AFW) pumps design bases into adequate acceptance c
Region: II | Vogtle | 1502 | 09/30/2016 11/03/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Fire Door Inspections |  | H.9 Training | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | An NRC-identified Green non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.d, "Procedures," was identified for the licensee's failure to correctly verify fire door gaps at the strike plate area and between meeting edges of double swinging me
Region: II | Vogtle | 1300 | 06/30/2016 07/29/2016 | 2016002-01 | NRC | NCV | Initiating Events | Green | Failure to properly implement a maintenance procedure caused a Reactor Trip |  | H.12 Avoid Complacency | TE?: N | 05000425 Vogtle 2 |  | 71153 | A self-revealing non-cited violation (NCV) of Technical Specifications (TS) 5.4.1.a, Procedures, was identified for the licensee's failure to properly implement procedure 24750-2, "Steam Generator Level (Narrow Range) Protection Channel II 2L-519 Channel
Region: II | Vogtle | 1500 | 05/13/2016 06/09/2016 | 2016502-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Adequately Maintain Emergency Response Facilities |  | H.3 Change Management | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71114.04 | The inspectors identified a non-cited violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50.54(q)(2), for the licensee's failure to maintain the effectiveness of its emergency plan by ensuring that adequate emergency facilities and
Region: II | Vogtle | 1298 | 12/31/2015 01/29/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Preventive Maintenance Procedure for 7300 Process Protection and Control System Printed Circuit Board |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.12 | A Green self-revealing NCV of TS 5.4.1, "Procedures," was identified for the licensee's failure to implement replacement schedules for 7300 process protection and control (PP&C) system cards in accordance licensee fleet maintenance procedures. As a result
Region: II | Vogtle | 1293 | 09/30/2015 11/06/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Requalification Examination Integrity |  | H.8 Procedure Adherence | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | An NRC-identified Non-cited Violation (NCV) of 10 CFR 55.49, "Integrity of examinations and tests," was identified for the licensee's failure to adhere to requirements of NMP-TR-424, License Operator Continuing Training Exam Development, Version 3.1. NMP-
Region: II | Vogtle | 1292 | 09/30/2015 11/06/2015 | 2015003-02 | NRC | FIN | Mitigating Systems | Green | NRC Biennial Written Examinations Did Not Meet Qualitative Standards |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.11B | An NRC-identified finding was identified when between 20 and 40 percent of the written examination questions administered to licensed operators during the biennial requalification examination did not meet the requirements of NMP-TR-424, "Licensed Operator
Region: II | Vogtle | 1294 | 09/30/2015 11/06/2015 | 2015003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area |  |  | TE?: N | 05000425 Vogtle 2 |  | 71124.01 | A self-revealing NCV of Technical Specification (TS) 5.7.1, "High Radiation Area," for an unauthorized entry into a high radiation area (HRA). The radiological aspects were not discussed in the pre-job brief, the health physics (HP) technician in containm
Region: II | Vogtle | 1287 | 07/31/2015 09/14/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Close and Latch Plant Fire Doors |  | H.8 Procedure Adherence | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.05T | An NRC-identified Green non-cited violation of Vogtle Units 1 and 2 Operating License Conditions 2.G, was identified for the licensee's failure to ensure that fire doors V22108L1A67, V12111L1238, and V12111L1A41 in 3-hour rated fire barriers were fully cl
Region: II | Vogtle | 1291 | 07/31/2015 09/14/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Repair a Degraded Fire Penetration Seal |  | H.12 Avoid Complacency | TE?: N | 05000424 Vogtle 1 |  | 71111.05T | An NRC-identified Green non-cited violation of Vogtle Unit 1 Operating License Condition 2.G was identified for the licensee's failure to identify and repair degraded fire penetration seal 1-11-759A, as required by the approved fire protection program (FP
Region: II | Vogtle | 1285 | 06/30/2015 08/04/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degraded Foreign Material Cover Plates for the NSCW Pump Wells |  | P.2 Evaluation | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.12 | An NRC-identified, Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to identify and correct conditions adverse to quality associated with the cover plates for the
Region: II | Vogtle | 1274 | 03/31/2015 05/01/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Maintenance Procedure for Containment Spray Pump |  |  | TE?: N | 05000425 Vogtle 2 |  | 71153 | A self-revealing NCV of TS 5.4.1.a, "Procedures," was identified for the licensee's failure to verify that the total indicated run-out (TIR) for the Unit 2 'B' train containment spray pump was within the limits of procedure 27052-C, Gould 3415 Pump Mainte
Region: II | Vogtle | 1267 | 12/31/2014 01/28/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Implement Control Rod Drive System Procedure During Reactor Startup Activities |  | H.9 Training | TE?: N | 05000425 Vogtle 2 |  | 71111.2 | A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a, "Procedures," was identified for the licensee's failure to implement system operating procedure SOP 13502-2, "Control Rod Drive and Position Indication System," version 42
Region: II | Vogtle | 1268 | 12/31/2014 01/28/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Restore Nuclear Service Cooling Water Manual Valves to their Required 'Locked-Open'Position |  | H.7 Documentation | TE?: N | 05000425 Vogtle 2 |  | 71111.2 | The NRC identified an NCV of TS 5.4.1.a, "Procedures" for the licensee's failure to properly implement administrative control procedure 10019-C, "Control of Safety Related Locked Valves," version 15.3. As a result, two nuclear service cooling water (NSCW)
Region: II | Vogtle | 1269 | 12/31/2014 01/28/2015 | 2014005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures Renders Safety Related Battery Charger Inoperable |  | H.11 Challenge the Unknown | TE?: N | 05000425 Vogtle 2 |  | 71111.22 | A self-revealing NCV of TS 5.4.1.a, "Procedures" was identified for the licensee's failure to properly implement approved maintenance procedures and work order instructions and inadvertently removed the 2AD1CB safety-related battery charger from service w
Region: II | Vogtle | 1258 | 09/30/2014 10/31/2014 | 2014004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correctly Implement a Condensate and Feedwater Systems Procedure for Startup |  | H.8 Procedure Adherence | TE?: N | 05000424 Vogtle 1 |  | 71111.11Q | Green: A self-revealing non-cited violation (NCV) of Technical Specification (TS) 5.4.1.a, "Procedures," was identified for the licensee's failure to implement system operating procedure (SOP) 13615-1, "Condensate and Feedwater Systems," Version 84. Speci
Region: II | Vogtle | 1259 | 09/30/2014 10/31/2014 | 2014004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inoperability of Unit 1 Emergency Containment Coolers due to Incorrect Tagout |  | H.11 Challenge the Unknown | TE?: N | 05000424 Vogtle 1 |  | 71111.2 | Green: A self-revealing NCV of TS 5.4.1.a, "Procedures," was identified for the licensee's failure to specify and verify the correct unit designation in clearance and tagout instructions for removing the Unit 2 nuclear service cooling water (NSCW) system
Region: II | Vogtle | 1260 | 09/30/2014 10/31/2014 | 2014004-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Loss of Plant Effluent Monitoring Capability |  | P.1 Identification | TE?: N | 05000425 Vogtle 2 |  | 71124.06 | Green: A self-revealing NCV of TS 5.5.4, "Radioactive Effluent Controls Program," occurred when the licensee failed to maintain continuous, representative monitoring of the Unit 2 plant vent gaseous effluents as required by the offsite dose calculation ma
Region: II | Vogtle | 1265 | 09/30/2014 10/31/2014 | 2014004-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correctly Implement a Chemical and Volume Control System Procedure for Reactor Water Makeup |  | H.12 Avoid Complacency | TE?: N | 05000424 Vogtle 1 |  | 71152 | Green: A self-revealing NCV of TS 5.4.1.a, "Procedures," was identified for the licensee's failure to implement SOP 13009-1, "CVCS Reactor Makeup Control System," Version 50.1. Specifically, on July 9, 2014, the licensee conducted a blended makeup to the
Region: II | Vogtle | 1246 | 06/30/2014 08/06/2014 | 2014003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Maintenance Procedure Results in a Failed MSIV and a Manual Reactor Trip |  | H.1 Resources | TE?: N | 05000424 Vogtle 1 |  | 71111.12 | Green. A self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion V, "Instructions, Procedures, and Drawings," was identified for failure to provide adequate work instructions in the maintenance procedure used for main steam isolation va
Region: II | Vogtle | 1254 | 06/30/2014 08/06/2014 | 2014003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized entry into a High Radiation Area |  | H.12 Avoid Complacency | TE?: N | 05000424 Vogtle 1 |  | 71124.01 | Green. A self-revealing NCV of Technical Specification (TS) 5.7.1, "High Radiation Area", was identified for an entry into a high radiation area (HRA) without meeting the entry requirements as specified therein. Specifically, on March 17, 2014, an operato
Region: II | Vogtle | 1255 | 06/30/2014 08/06/2014 | 2014003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Maintenance Procedures and Usage Results in a Failed MFRV and an Automatic Reactor Trip |  | H.8 Procedure Adherence | TE?: N | 05000425 Vogtle 2 |  | 71153 | Green. A self-revealing NCV of 10 CFR 50 Appendix B Criterion V, "Instructions, Procedures, and Drawings," was identified for failure to provide adequate work instructions as well as failure to follow the maintenance procedure used to install flexible and
Region: II | Vogtle | 1243 | 12/31/2013 01/31/2014 | 2013005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to meet the conditions of TS LCO 3.8.4 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000424 Vogtle 1 |  | 71111.19 | A Green, self-revealing non-cited violation (NCV) of plant Technical Specification (TS) 3.8.4, "DC Sources - Operating," was identified for failure to meet the conditions of TS limiting condition for operation (LCO) 3.8.4. Specifically, placing the 1AD1CA
Region: II | Vogtle | 1227 | 08/30/2013 09/25/2013 | 2013007-01 | NRC | FIN | Mitigating Systems | Green | Failure to Correct a Condition Affecting EDG Recovery Capability under Station Blackout Conditions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | Green. The team identified a Green finding for the licensee's failure to follow guidance in nuclear management procedure NMP-GM-002-001, "Corrective Action Program Instructions," Version 30.1, which resulted in their failure to correct a condition that ad
Region: II | Vogtle | 1223 | 03/31/2013 05/02/2013 | 2013002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Operations and Maintenance Procedures Results in High RCP Seal Leakoff Flow and Manual Reactor Trip |  |  | TE?: N | 05000425 Vogtle 2 |  | NONE | Green A self-revealing non-cited violation (NCV) of 10 CFR 50 Appendix B Criterion V, "Instructions, Procedures, and Drawings" was identified for failure to provide adequate work instructions in the operations procedure used to change out the reactor cool
Region: II | Vogtle | 1224 | 03/31/2013 05/02/2013 | 2013002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedures Results in Failure of the Inboard Bearing on the Unit 1A CCW pump #1 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000424 Vogtle 1 |  | 71111.12 | Green: A self-revealing non-cited violation (NCV) of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for failure to provide appropriate quantitative or qualitative acceptance criteria for determining that im
Region: II | Vogtle | 1225 | 03/31/2013 05/02/2013 | 2013002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Human Performance Error Renders 1A CS Pump Inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000424 Vogtle 1 |  | 71111.2 | Green. A self-revealing non-cited violation (NCV) for failure to meet the requirements of plant Technical Specification (TS) 5.4, Procedures was identified. While realigning equipment to support the filling and venting of the Unit 2 containment spray head
Region: II | Vogtle | 1217 | 12/31/2012 02/01/2013 | 2012005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate maintenance procedure results in inoperability of NSCW cooling tower fan |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000425 Vogtle 2 |  | 71111.19 | A self-revealing non-cited violation (NCV) for failure to meet the requirements of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for failure to provide adequate work instructions in the maintenance procedu
Region: II | Vogtle | 1218 | 12/31/2012 02/01/2013 | 2012005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized entry into a high radiation area |  | H.4(b) Procedural Compliance | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71124.02 | The inspectors identified a Green, self-revealing, Non-cited Violation of technical specification 5.7.1, "High Radiation Area", for an unauthorized entry into a High Radiation Area (HRA). A maintenance worker entered a HRA in Unit 1 containment without be
Region: II | Vogtle | 1219 | 12/31/2012 02/01/2013 | 2012005-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate operations and maintenance procedures results in brittle failure of the loop 2 and loop 3 outboard MSIV stems |  | H.3(a) Work Planning | TE?: N | 05000424 Vogtle 1 |  | NONE | A self-revealing non-cited violation (NCV) for failure to meet the requirements of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for failure to provide adequate work instructions in the operations and main
Region: II | Vogtle | 1213 | 09/30/2012 10/30/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Ineffective corrective action renders Unit 1A ESF chiller inoperable |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000424 Vogtle 1 |  | 71111.12 | A NRC identified, non-cited violation (NCV) for failure to meet the requirements of 10 CFR 50, Appendix B, Criterion XVI was identified. Specifically, the licensee's failure to follow the requirements of 10 CFR 50, Appendix B, Criterion XVI to promptly id
Region: II | Vogtle | 1214 | 09/30/2012 10/30/2012 | 2012004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to follow procedure results in a misplaced fuel assembly |  | H.4(a) Human Error Prevention | TE?: N | 05000424 Vogtle 1 |  | 71111.2 | A self-revealing NCV of technical specification (TS) 5.4.1 was identified for failure to follow procedure 93641-C Rev.19.2, Development and Implementation of the Fuel Shuffle Sequence Plan during spent fuel pool fuel moves in preparation for an upcoming f
Region: II | Vogtle | 1221 | 07/13/2012 08/24/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify and repair an inoperable fire penetration seal |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000425 Vogtle 2 |  | NONE | An NRC-identified non-cited violation of Vogtle Unit 2, Operating License Condition 2.G, was identified for the licensee's failure to identify and repair an inoperable fire penetration seal. The NCV was associated with the licensee's failure to identify a
Region: II | Vogtle | 1222 | 07/13/2012 08/24/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to install freeze protection for exposed fire protection piping |  |  | TE?: N | 05000424 Vogtle 1 |  | NONE | An NRC-identified non-cited violation of Vogtle Unit 1, Operating License Condition 2.G, was identified for the licensee's failure to provide proper freeze protection for an 8" diameter above ground fire water line located along side the Unit 1 Main Steam
Region: II | Vogtle | 1212 | 06/30/2012 07/30/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow procedures renders safety related battery chargers inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.22 | The inspectors identified a self-revealing NCV of Technical Specification (TS) 5.4.1, for two instances of failure to properly implement approved maintenance procedures and work order instructions. Specifically, maintenance electricians inadvertently remo
Region: II | Vogtle | 1208 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Work Practice Error Renders Unit 2 TDAFW Pump Inoperable |  | H.4(b) Procedural Compliance | TE?: N | 05000425 Vogtle 2 |  | 71111.22 | Green: A self-revealing NCV of technical specification (TS) 5.4.1 was identified for failure to properly implement approved maintenance procedures. Specifically, maintenance technicians failed to properly re-land control wires, as required by procedure, o
Region: II | Vogtle | 1206 | 12/31/2011 01/27/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Human Performance Error Results in Inoperability of TDAFW Pump |  | H.4(a) Human Error Prevention | TE?: N | 05000425 Vogtle 2 |  | 71111.22 | -Green: A Green self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified. Specifically, the licensee inadvertently operated the Unit 2 turbine driven auxiliary feedwater (TDAF
Region: II | Vogtle | 1207 | 12/31/2011 01/27/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to ensure Unit 1 and Unit 2 reactor coolant process variables can be maintained within those predicted for a loss of normal ac power for a large main control room fire. |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | Green: A Green NRC identified NCV of Unit 1 Operating License Condition 2.G and Unit 2 Operating License Condition 2.G for failure to implement and maintain in effect all provisions of the approved Fire Protection Program (FPP) as described in the FSAR fo
Region: II | Vogtle | 1205 | 09/30/2011 10/28/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Installation of non-conforming safety-related breakers due to a failure to implement corrective action to prevent recurrence to address a significant condition adverse to quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for failure to develop and implement adequate corrective action to prevent recurrence (CAPR) in response to a significant condition adverse to qual
Region: II | Vogtle | 1191 | 06/30/2011 07/29/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to establish and implement adequate post maintenance testing for 1HV-0943B |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000424 Vogtle 1 |  | 71111.19 | A self-revealing, non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for failure to specify and implement adequate post maintenance testing to ensure important maintenance activitie
Region: II | Vogtle | 1189 | 03/31/2011 04/29/2011 | 2011002-01 | NRC | NCV | Barrier Integrity | Green | Failure to perform general visual examination of containment metallic liner in reactor vessel cavity underneath the reactor vessel |  | P.2(b) Implementing Operating Experience | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.08P | The NRC identified a Green NCV of 10 CFR Part 50.55a, "Codes and Standards," for the licensee's failure to conduct a general visual examination of the Units 1 and 2 containment metallic liner around the reactor cavity underneath the reactor vessel. The li
Region: II | Vogtle | 1190 | 03/31/2011 04/29/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Depressurization of main firewater header |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | A self-revealing NCV of Vogtle Unit 1 operating license condition 2.G. and Vogtle Unit 2 operating license condition 2.G. was identified for failure to maintain the main firewater header pressurized. Specifically, in response to two firewater header low
Region: II | Vogtle | 1184 | 12/31/2010 01/27/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | Failure to utilize the Corrective Action Program to identify a condition adverse to quality |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for the failure of the licensee to identify within their CAP to correct a condition adverse to quality. Plant personnel had knowled
Region: II | Vogtle | 1179 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct instrument uncertainty associated with the ECCS accumulators |  | H.3(b) Work Activity Coordination | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | An NRC-identified Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, was identified for failure to promptly correct an equipment deficiency. Specifically, in February 2006, the licensee identified an issue with the instrument uncer
Region: II | Vogtle | 1177 | 06/30/2010 07/29/2010 | 2010003-01 | NRC | NCV | Initiating Events | Green | Failure to inspect tube R1C2 of steam generator 2 during the steam generator eddy current examination in 2007 |  |  | TE?: N | 05000425 Vogtle 2 |  | 71111.08P | -Green: An NRC identified non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for failure to adhere to steam generator eddy current examination procedures during the 2007 Unit 2 refu
Region: II | Vogtle | 1178 | 06/30/2010 07/29/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to verify purchased equipment conformed to design specifications |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.18 | Green: A self revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion VII, Control of Purchased Material, Equipment, and Services, was identified for failure to establish measures to assure that purchased material, equipment, and services
Region: II | Vogtle | 1169 | 03/31/2010 04/29/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Ineffective corrective action renders Unit 2 CCW pump #4 inoperable |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000425 Vogtle 2 |  | 71111.12 | A self-revealing non-cited violation (NCV) for failure to meet the requirements of 10 CFR 50, Appendix B, Criterion XVI was identified. Specifically, for ineffective corrective maintenance performed on the Unit 2 Component Cooling Water (CCW) Pump #4. The
Region: II | Vogtle | 1170 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Operation of NSCW system with tower return valves in open bypass |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | -Green. A NRC-identified NCV for failure to enter TS LCO 3.7.8 Condition A as required was identified. Specifically, the licensee's failure to follow the requirements of TS LCO 3.0.2 and enter TS LCO 3.7.8 Condition A when the NSCW tower return valves are
Region: II | Vogtle | 1171 | 12/31/2009 01/28/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate surveillance procedures for TS SR 3.7.8.2 |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | -Green. A NRC-identified NCV for inadequate surveillance procedures was identified. Specifically, TS SR 3.7.8.2 requires the licensee to periodically verify that each NSCW system automatic valve in the system flow path actuates to the correct position on
Region: II | Vogtle | 1172 | 12/31/2009 01/28/2010 | 2009005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Human performance error results in manual reactor trip section |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000425 Vogtle 2 |  | NONE | -Green. A self-revealing non-cited violation (NCV) of Technical Specification 5.4, Procedures was identified. Specifically, a human performance error associated with inadvertently isolating instrument air to the turbine building, auxiliary building, and c
Region: II | Vogtle | 1176 | 12/31/2009 01/28/2010 | 2009005-04 | NRC | NCV | Mitigating Systems | Green | Failure to properly maintain the approved fire protection program with regard to the relocation of the plant the fire alarm annunciation signal outside of the MCRs. |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71111.05Q | -Green. NRC identified a NCV of Vogtle Nuclear Plant Units 1 & 2 Operating License Condition 2.G, "Fire Protection," for failure to properly maintain the NRC-approved fire protection program with regard to the location of the fire alarm computer audible a
Region: II | Vogtle | 1161 | 09/30/2009 10/30/2009 | 2009004-01 | Self - Revealed | NCV | Barrier Integrity | Green | MOV program procedures were inadequate with regard to periodicity of preventive maintenance activities for stem lubrication |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 71152 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified. Specifically, Vogtle Electric Generating Plant's (VEGP) MOV preventative maintenance (PM) procedures lacked specific instructions that p
Region: II | Vogtle | 1162 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Human performance error renders 2BEDG inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000425 Vogtle 2 |  | NONE | A self-revealing non-cited violation (NCV) was identified for a human performance error associated with inadvertently racking out the 2B emergency diesel generator (EDG) output breaker. The system operator racked out the incorrect breaker while performing
Region: II | Vogtle | 1139 | 09/30/2009 10/30/2009 | 2009004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Human performance error renders NSCW pump #5 inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000425 Vogtle 2 |  | NONE | A self-revealing non-cited violation (NCV) was identified for a human performance error associated with failure of an operator to verify that the discharge valve on the Nuclear Service Cooling Water (NSCW) pump #5 went closed after securing the pump as re
Region: II | Vogtle | 1154 | 12/31/2008 01/20/2009 | 2008005-01 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Entries Into High Radiation Areas |  | H.4(a) Human Error Prevention | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7112101 | Two examples of a self-revealing non-cited violation of Technical Specification 5.7.1, High Radiation Area, [were] identified for unauthorized entry into High Radiation Areas (HRAs). Inadequate communication between workers and Health Physics department r
Region: II | Vogtle | 1153 | 09/30/2008 10/29/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | Human Performance Error Results in Unplanned Reactivity Addition |  | H.4(b) Procedural Compliance | TE?: N | 05000424 Vogtle 1 |  | 71153 | Green. A self-revealing non-cited violation of TS 5.4, Procedures, was identified when the licensed control room operator failed to perform step 4.3.5.10.b of procedure 3010- 1, Boron Thermal Regeneration System, Rev 57. Failure to properly perform this s
Region: II | Vogtle | 1152 | 06/30/2008 07/31/2008 | 2008003-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedures Associated with Degraded Ability to Detect Boric Acid Leakage |  |  | TE?: N | 05000424 Vogtle 1 |  | 71111.08P | A NRC-identified non-cited violation of 10 CFR 50, Appendix B, Criterion V, was identified for lack of procedures to address compensatory measures for containment conditions which would mask indications of boric acid leakage. A combination of condensation
Region: II | Vogtle | 1143 | 03/30/2008 04/30/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Violation of 10CFR50, Appendix B, Criterion XI for Failure To Establish Adequate Test Control Measures For TS SR 3.7.5.2 |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | Green. The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for failure to consider the effects of instrument uncertainty, water temperature, or system orifice resistance during auxiliary feedwater (AFW) pump technic
Region: II | Vogtle | 1149 | 03/30/2008 04/30/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Capability of Auxiliary Feedwater System to Meet Design and Licensing Requirements |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | NONE | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to include the cumulative effects of the replacement of the 1A motor driven auxiliary feedwater (AFW) pump rotating element, accuracy of AFW system
Region: II | Vogtle | 1140 | 11/30/2007 01/14/2008 | 2007007-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Control Transient Combustibles |  | H.3(a) Work Planning | TE?: N | 05000425 Vogtle 2 |  | 71111.05T | The team identified a non-cited violation of Vogtle Unit 2 Operating License Condition 2.G, for the licensee's failure to properly implement fire protection program procedures for control of transient combustible materials. Transient combustible materials
Region: II | Vogtle | 1141 | 11/30/2007 01/14/2008 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Safe Shutdown Procedure 18068-2 Not Consistent With Analysis |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000425 Vogtle 2 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.4.1, Procedures, in that Unit 2 safe shutdown procedure 18038-2, was not consistent with the safe shutdown analysis for Fire Zone 105-2. Specifically, certain time critical operator ma
Region: II | Vogtle | 1142 | 11/30/2007 01/14/2008 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Emergency Lighting Units Not Installed as Required by the Fire Protection Program |  |  | TE?: N | 05000425 Vogtle 2 |  | 71111.05T | The team identified a non-cited violation of Vogtle Unit 2 Operating License Condition 2.G, in that the licensee failed to install emergency lighting units (ELUs) in accordance with the approved fire protection program. Specifically, there were no ELUs in
Region: II | Vogtle | 1135 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Replacement Strainer Clearances Greater than Design Procurement Specifications |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000425 Vogtle 2 |  | 2515/166 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion VII, Control of Purchased Materials, Equipment, and Services, for failure to identify deviations from the procurement specifications regarding the maximum allowable
Region: II | Vogtle | 1131 | 06/04/2007 07/19/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Safety-Related 480 VAC Molded Case Circuit Breakers On MCC 1ABF, 1BBF, 2ABF, and 2BBF Not Tested |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The inspectors identified a violation of 10 CFR 50, Appendix B, Criterion XI, Test Control, for failure to implement a test program to assure that all installed safety related molded case circuit breakers (MCCBs) will perform satisfactorily in service. Un
Region: II | Vogtle | 1132 | 06/04/2007 07/19/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Maximum Differential Pressure for Containment Emergency Sump Isolation Valves Not Calculated |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7111121 | The inspectors identified a violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to evaluate the impact of an increase of the residual heat removal (RHR) system pressure during the RHR pump operation in a minimum flow alignment i
Region: II | Vogtle | 1124 | 03/31/2007 04/30/2007 | 2007002-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Instructions for Maintenance Resulted in the Failure of Unit 1 Loop 2 Main Feedwater Regulating Valve |  |  | TE?: N | 05000424 Vogtle 1 |  | 71153 | A self-revealing finding was identified for poor work practices associated with the installation of the loop 2 main feedwater regulating valve (MFRV) electro-pneumatic transducer. The transducer was mounted in a manner that did not prevent water ingress a
Region: II | Vogtle | 1122 | 12/31/2006 01/22/2007 | 2006005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to use only NIOSH certified respiratory protection equipment. |  |  | TE?: N | 05000424 Vogtle 1 05000425 Vogtle 2 |  | 7112102 | The inspectors identified a non-cited violation of 10 CFR Part 20.1703(a) for the use of respiratory protection equipment that had not been certified as safe by the National Institute for Occupational Safety and Health (NIOSH). The licensee discontinued u
Region: II | Vogtle | 1117 | 09/30/2006 10/30/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Instruments with Environmental Qualification Deficiencies |  |  | TE?: N | 05000425 Vogtle 2 |  | 71152 | The inspectors identified an NCV of 10CFR50, Appendix B, Criterion XVI, for a failure to promptly identify and correct a condition adverse to quality. During an environmental qualification (EQ) self-assessment in June, 2005, the licensee discovered that t
Region: II | Vogtle | 1116 | 09/30/2006 10/30/2006 | 2006004-02 | Self - Revealed | FIN | Initiating Events | Green | Poor Workmanship and Inadequate Work Instructions for Maintenance on Reactor Coolant Pump Resulted in a Reactor Trip Due |  |  | TE?: N | 05000425 Vogtle 2 |  | 71153 | A self-revealing finding was identified for inadequate work instructions and poor work practices associated with the installation of a surge arrestor design change on the Unit 2 loop 4 reactor coolant pump (RCP). This condition resulted in short circuitin
Region: II | Watts Bar | 125403 | 06/30/2019 08/12/2019 | 2019002-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Work Hour Controls for Covered Workers |  | H.1 - Resources | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.2 | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR 26.205(d)(4), Work Hours, which requires covered workers, working on outage activities, must have one day off in any (rolling) seven-day period. Specifically, the
Region: II | Watts Bar | 125405 | 06/30/2019 08/12/2019 | 2019002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality Associated with Inoperable Ice Condenser Intermediate Deck Doors. |  | H.12 - Avoid Complacency | TE?: N | 05000391 Watts Bar 2 | Human Performance | 71111.2 | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for the failure to identify a condition adverse to quality. Specifically, inspectors identified two inopera
Region: II | Watts Bar | 125086 | 06/30/2019 08/12/2019 | 2019002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiological Surveys Adequate to Identify a High Radiation Area |  | H.1 - Resources | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 | Program & Process | 71124.01 | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR 20.1501 and Technical Specification (TS) 5.11, when the licensee failed to perform adequate radiological surveys. Specifically, the licensee failed to perform
Region: II | Watts Bar | 125404 | 06/30/2019 08/12/2019 | 2019002-05 | NRC | NCV | Initiating Events | Green | Failure to Follow Clearance Procedure Results in Inoperability of the Unit 2 Power Range Nuclear Instrument. |  | H.11 - Challenge the Unknown | TE?: N | 05000391 Watts Bar 2 | Equipment Performance | 71153 | The inspectors identified a Green finding and associated non-cited violation (NCV) of Technical Specification (TS) 5.7.1.1.a, when the licensee failed to follow procedure NPG-SPP-10.2, Clearance Procedure to Safely Control Energy. Specifically, when devel
Region: II | Watts Bar | 125406 | 06/30/2019 08/12/2019 | 2019002-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow System Status Control Procedure Results in a Gap in a Bellows Seal and Inoperability of the Unit 2 Shield Building. |  | H.8 - Procedure Adherence | TE?: N | 05000391 Watts Bar 2 | Human Performance | 71153 | The inspectors identified a self-revealed Green finding and associated non-cited violation (NCV) of Technical Specifications 5.7.1.1.a, Procedures, for the failure to follow the requirements of Tennessee Valley Authority (TVA) procedure NPG-SPP-10.1, Syst
Region: II | Watts Bar | 124632 | 03/31/2019 05/13/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control which led to an Internal Flooding Event that caused the Inoperability of the Turbine Driven Auxiliary Feedwater Pump. |  | H.4 - Teamwork | TE?: N | 05000390 Watts Bar 1 | Equipment Performance | 71111.15 | The inspectors identified a Green finding and associated non-cited Violation (NCV) of Technical Specification (TS) 5.7.1.1.a when the licensee failed to maintain configuration control of the plant in accordance with NPG-SPP-10.1, “System Status Control.”
Region: II | Watts Bar | 124707 | 03/31/2019 05/13/2019 | 2019001-02 | NRC | NCV | Barrier Integrity | Green | Failure to Meet Acceptance Criteria for Containment Closure in Mode 6 |  | H.11 - Challenge the Unknown | TE?: N | 05000390 Watts Bar 1 | Human Performance | 71111.2 | An NRC-identified Green finding and associated non-cited violation (NCV) of Technical Specifications 5.7.1.1.a, “Procedures,” was identified for the failure to meet acceptance criteria in procedure TI-68.002, “Containment Penetrations and Closure Control,
Region: II | Watts Bar | 124543 | 03/31/2019 05/13/2019 | 2019001-03 | NRC | NCV | Mitigating Systems | Green | Failure to account for degradation mechanisms in Barton transmitters |  | NPP | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 | Design Control | 71111.21N | The NRC identified a Green finding and associated non-cited violation (NCV) of Title 10 Code of Federal Regulations (CFR) 50.49(e)(5), for the licensee’s failure to account for all significant types of degradation of the Barton 764 instruments inside cont
Region: II | Watts Bar | 124709 | 03/31/2019 05/13/2019 | 2019001-05 | Self - Revealed | NCV | Barrier Integrity | Green | Containment Air Return Fan 1B Inoperable due to Inadequate Post Maintenance Test |  | H.5 - Work Management | TE?: N | 05000390 Watts Bar 1 | Procedure Quality | 71153 | A self-revealed Green finding and associated non-cited violation (NCV) of Technical Specifications (TS) 3.6.10, “Air Return System,” was identified for the 1B containment air return fan (CARF) being inoperable for a time period longer than allowed by TS d
Region: II | Watts Bar | 124365 | 01/31/2019 03/13/2019 | 2019010-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure the Auto Start Feature for the Standby Annulus Vacuum Fan results in Inoperability of Shield Building. |  | NPP | TE?: N | 05000391 Watts Bar 2 | Procedure Quality | 71152B | A self-revealed, Green, NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified on May 11, 2018, when the licensee failed to provide procedural guidance to ensure the auto start feature for the standby annu
Region: II | Watts Bar | 124368 | 01/31/2019 03/13/2019 | 2019010-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Implement Annunciator Response Procedure results in Inoperability of Containment Purge Valves |  | H.13 - Consistent Process | TE?: N | 05000391 Watts Bar 2 | Human Performance | 71152B | A self-revealed Green finding and associated NCV of Watts Bar Unit 2 Technical Specification 5.7.1, “Procedures,” was identified on July 27, 2018, when the licensee did not implement procedures to verify a main control room annunciator indicating the malf
Region: II | Watts Bar | 19 | 12/31/2018 02/05/2019 | 2018004-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow work order steps results in equipment unavailability |  | H.11 - Challenge the Unknown | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.13 | A self-revealed Green finding and associated Non-cited Violation (NCV) of Technical Specification 5.7.1, “Procedures,” was identified when the licensee failed to follow the requirements of work order (WO) 118973001. Specifically, WO step 5.15 requires an
Region: II | Watts Bar | 20 | 12/31/2018 02/05/2019 | 2018004-07 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow procedure results in turbine driven auxiliary feed water pump inoperability |  | H.9 - Training | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.13 | A self-revealed Green finding and associated Non-cited Violation (NCV) of Technical Specification 5.7.1.a, “Procedures,” was identified when the licensee failed to install measuring and test equipment (M&TE) in accordance with surveillance instruction 1-S
Region: II | Watts Bar | 24 | 12/31/2018 02/05/2019 | 2018004-08 | Self - Revealed | NCV | Initiating Events | Green | Failure to follow system status control procedure results in Unit 1 trip |  | H.13 - Consistent Process | TE?: N | 05000390 Watts Bar 1 |  | 71111.13 | A self-revealed Green finding and associated Non-cited Violation (NCV) of Technical Specification 5.7.1, “Procedures,” was identified when the licensee failed to follow the requirements of procedure NPG[NS1] [NJ2] -SPP-10.1, System Status Control, Revisio
Region: II | Watts Bar | 24656 | 09/30/2018 11/01/2018 | 2018003-01 | Self - Revealed | NCV | Initiating Events | Green | Configuration Control Error Results in Actual Auxiliary Building Internal Flooding Event |  | H.12 - Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71111.06 | A self-revealed Green finding and associated NCV of Technical Specification (TS) 5.7.1, “Procedures,” was identified when the licensee failed to maintain adequate configuration control in the high pressure fire protection (HPFP) system in accordance with
Region: II | Watts Bar | 24659 | 09/30/2018 11/01/2018 | 2018003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry Into a High Radiation Area |  | H.4 - Teamwork | TE?: N | 05000391 Watts Bar 2 |  | 71124.01 | A self-revealed Green finding and associated NCV of TS 5.11.1.e was identified when the licensee failed to maintain current survey information and failed to inform a worker of increased dose rates in a high radiation area. As a result, a worker received a
Region: II | Watts Bar | 24664 | 09/30/2018 11/01/2018 | 2018003-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Collect Compensatory Samples for an Out-of-Service Effluent Monitor |  | H.12 - Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71124.06 | The inspectors identified a Green finding and associated NCV of TS 5.7.2.3 when the licensee failed to take compensatory samples in accordance with Table 1.1-1 of the Offsite Dose Calculation Manual when the Unit 1 steam generator blowdown effluent monito
Region: II | Watts Bar | 24657 | 09/30/2018 11/01/2018 | 2018003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Sensitive Equipment Control Results in Unit 2 Reactor Trip on April 12, 2018 |  | H.5 - Work Management | TE?: N | 05000391 Watts Bar 2 |  | 71153 | A self-revealed Green finding and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, Drawings,” was identified for the licensee’s use of a procedure that was not appropriate to
Region: II | Watts Bar | 24359 | 06/30/2018 08/07/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Exceeding the Design Pressure of the RHR Piping |  | H.1 - Resources | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.15 | A self-revealed Green NCV was identified when the licensee failed to consider potentially adverse system interactions when developing procedures affecting quality. Specifically, the licensee exposed Unit 1 residual heat removal system piping to higher tha
Region: II | Watts Bar | 23526 | 03/31/2018 05/15/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Misapplication of Technical Specification Limiting Conditionfor Operation 3.0.6 |  | H.6 - Design Margins | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.15 | Inspectors identified a Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations Part 50 (10 CFR 50), Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” when the licensee failed to adhere to the
Region: II | Watts Bar | 23157 | 12/31/2017 02/13/2018 | 2017004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure for Temporary Configuration Changes |  | H.5 - Work Management | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.18 | Green. A self-revealed Green NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified for inadequacies associated with TVA procedure NPG-SPP-09.5, Temporary Modifications Temporary Configuration Changes, Rev
Region: II | Watts Bar | 23152 | 12/31/2017 02/13/2018 | 2017004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify a Condition Adverse to Quality for a Boric Acid Leak on 2-SMV-68-548 |  | H.5 - Work Management | TE?: N | 05000391 Watts Bar 2 |  | 71111.2 | Green. An NRC identified NCV of very low safety significance (Green) associated with 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified for the failure to promptly identify and correct a condition adverse to quality. Specif
Region: II | Watts Bar | 21694 | 09/30/2017 11/22/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Procedures for Response to a Loss of Coolant Accident |  | H.7 - Documentation | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.15 | An NRC-identified non-cited violation (NCV) was identified for the failure to maintain written procedures for emergencies. Emergency procedure 1-E-1, Revision 7 and 2-E-1 Revision 0, both titled Loss of Reactor or Secondary Coolant, were updated to includ
Region: II | Watts Bar | 21682 | 09/30/2017 11/22/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Unit Cooldown from Hot Standby to Cold Shutdown |  | H.12 - Avoid Complacency | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.15 | An NRC-identified non-cited violation (NCV) of Technical Specification (TS) 5.7.1.1.a, “Procedures,” was identified for the failure to maintain TVA procedures 1-GO-6 and 2-GO-6, both titled Unit Shutdown from Hot Standby to Cold Shutdown. The licensee fai
Region: II | Watts Bar | 22688 | 09/30/2017 11/22/2017 | 2017003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow a Surveillance Procedure Led to an Inadvertent Lift of a Pressurizer Power Operated Relief Valve |  | H.11 - Challenge the Unknown | TE?: N | 05000391 Watts Bar 2 |  | 71111.22 | Green. A self-revealed NCV of (TS) 5.7.1.1.a, “Procedures,” was identified for the failure to follow TVA procedure 2-SI-68-86, 18 month Channel Calibration of Remote Shutdown Monitoring Narrow Range Pressurizer Pressure Loop 2-LPP-68-337C, revision 4. T
Region: II | Watts Bar | 4416 | 06/30/2017 08/11/2017 | 2017002-01 | NRC | NCVIV | Barrier Integrity | Green | Inadequate Chemistry Procedure Results in Inoperable Containment Isolation Valves |  | H.5 - Work Management | TE?: Y SL-IV-NCVIV | 05000391 Watts Bar 2 |  | 71153 | -A self-revealed severity level (SL) IV non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when implementing an inadequate procedure resulted in rendering the steam generator chemistry sampl
Region: II | Watts Bar | 4415 | 06/30/2017 08/11/2017 | 2017002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Implement Clearance on Containment Isolation Valve Results in TS 3.6.3 Violation |  | H.12 - Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealed finding and associated non-cited violation of Technical Specification (TS) 3.6.3, "Containment isolation Valves," was identified for a failure to properly implement a clearance for containment isolation valve surveillance testing. Clearanc
Region: II | Watts Bar | 4417 | 06/30/2017 08/11/2017 | 2017002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure Results in Reactor Coolant Pump Failure to Transfer and Unit 1 Reactor Trip |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealed Green finding was identified for the failure to follow procedure NPG-SPP-22.207, "Procedure Use and Adherence" Revision 4, which requires that applicable procedures are used for all activities controlled by a written procedure. The license
Region: II | Watts Bar | 4422 | 06/23/2017 08/07/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Replace Namco Limit Switch Gasket to Maintain EQ Qualification |  | H.7 - Documentation | TE?: N | 05000390 Watts Bar 1 |  | 71111.21N | The NRC identified a Green non-cited violation (NCV) of title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to implement instructions to replace Namco limit s
Region: II | Watts Bar | 4423 | 06/23/2017 08/07/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Record of Qualification |  | NPP | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.21N | The NRC identified a Green NCV of 10 CFR 50.49(j), for the licensee's failure to maintain a complete record of qualification for Brand-Rex cables under environmental qualification binder WBNEQ-CABL-050. Specifically, the licensee could not produce a certi
Region: II | Watts Bar | 22684 | 03/31/2017 05/12/2017 | 2017001-01 | NRC | NCV | Initiating Events | Green | Failure to Maintain the Abnormal Operating Instruction for Tornados |  | P.1 - Identification | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.01 | Green. An NRC-identified non-cited violation (NCV) of Technical Specification (TS) 5.7.1.1.a, “Procedures,” was identified for a failure to maintain procedure 0-AOI-8, Tornado Watch or Warning. The entry criteria were inadequate to ensure that the requir
Region: II | Watts Bar | 23161 | 03/31/2017 05/12/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Immediate Determination of Operability |  | P.1 - Identification | TE?: N | 05000391 Watts Bar 2 |  | 71111.04Q | Green. An NRC-identified finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings” was identified for the failure to follow TVA procedure OPDP-8, Operability De
Region: II | Watts Bar | 23178 | 02/21/2017 03/10/2017 | 2016013-01 | NRC | FIN | Mitigating Systems | Green | Failure Implement the Program Requirement to Enter Issues into the CAP |  | P.1 - Identification | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71152B | The NRC identified a Finding for the licensee’s failure to consistently implement the program requirements of the CAP. Specifically, the licensee failed to implement NPG-SPP-22.301, section 3.2.2 which required the licensee’s staff to initiate a Condition
Region: II | Watts Bar | 4404 | 12/31/2016 02/09/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Immediate Determination of Operability for Essential Raw Cooling Water Pumps |  | H.4 Teamwork | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.15 | The NRC identified a non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to base an immediate determination of operability (IDO) for Essential R
Region: II | Watts Bar | 4410 | 12/31/2016 02/09/2017 | 2016004-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Immediate Determination of Operability for Containment Penetration X-65 |  | P.2 Evaluation | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The NRC identified a non-cited violation of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to address all the design criteria for check valve, 1-CHV-31-3407, in t
Region: II | Watts Bar | 4411 | 12/31/2016 01/24/2017 | 2016501-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Minimum On-Shift Emergency Response Staffing Levels |  | P.4 Trending | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71114.03 | The NRC identified a non-cited violation of 10 Code of Federal Regulations (CFR) 50.47(b)(2) for the licensee's failure to maintain the effectiveness of its emergency plan, when on more than one occasion, the number of control room operators fell below mi
Region: II | Watts Bar | 4383 | 09/30/2016 11/10/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inappropriate Procedure used for Work Order Scope Change Results in Loss of 1B-B Shutdown Board |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | 71152 | A self-revealed non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for the licensee's failure to use a procedure appropriate to the circumstances when work
Region: II | Watts Bar | 4395 | 08/26/2016 10/06/2016 | 2016011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Unit 1 Emergency Diesel Generator Surveillance Instructions |  | H.7 Documentation | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The NRC identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to have adequate instructions and acceptance criteria in the emergency diesel generator surveillance instruct
Region: II | Watts Bar | 4396 | 08/26/2016 10/06/2016 | 2016011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Net Positive Suction Head to the Unit 1 AFW Pumps |  | H.6 Design Margins | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The NRC identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly evaluate the available net positive suction head to the Unit 1 auxiliary feedwater pumps. These issues were entered int
Region: II | Watts Bar | 4403 | 06/30/2016 08/12/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that a Train of Source Range Detection was Available to Monitor Neutron Population During a Fire Event |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The NRC identified a Green NCV of Operating License Condition 2.F for the licensee's failure to ensure that a train of source range detection was available to monitor neutron population during the initial stages of a fire event on Unit 1. This issue wa
Region: II | Watts Bar | 4369 | 06/30/2016 08/12/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Requirements into a Maintenance Procedure for the 1B-B Charging Pump Room Cooler |  | H.6 Design Margins | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The inspectors identified an apparent violation of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion III, Design Control for the licensee's failure to specify nominal shaft size along with specific acceptance criteria for shaft tolerance meas
Region: II | Watts Bar | 4376 | 06/30/2016 08/12/2016 | 2016002-06 | NRC | NCV | Barrier Integrity | Green | Failure to Satisfy TS LCO 3.6.3 |  | H.14 Conservative Bias | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The NRC identified a Green NCV of TS for the failure to recognize and take the required actions in TS 3.6.3 for inoperable containment penetration flow paths. Specifically, the required actions of TS 3.6.3 applied on November 21, 2015, and were not taken
Region: II | Watts Bar | 4355 | 03/31/2016 04/08/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Use a Procedure Appropriate to the Circumstances for the Auxiliary Control Air System Train A |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | 71111.12 | A self-revealing non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, Procedures was identified for the licensee's failure to use a procedure appropriate to the circumstances for work associated with the A-A auxil
Region: II | Watts Bar | 4356 | 03/31/2016 04/08/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Immediate Determination of Operability for the Auxiliary Control Air System Train A |  | H.14 Conservative Bias | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The NRC identified an NCV of 10 CFR 50, Appendix B, Criterion V, Procedures, for the licensee's failure to follow TVA procedure OPDP-8, Operability Determination Process and Limiting Conditions for Operation Tracking, Revision 21. Specifically, the lice
Region: II | Watts Bar | 4357 | 03/31/2016 04/08/2016 | 2016001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Administration of Site Technical Procedures for TDAFW Pump Governor Calibration |  | H.8 Procedure Adherence | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The NRC identified an NCV of TS 5.7.1.1.a, Procedures, for the licensee's inadequate implementation of procedure NPG-SPP-01.2, Administration of Site Technical Procedures, Revision 8. Specifically, the licensee determined applicable acceptance criteria st
Region: II | Watts Bar | 4358 | 03/31/2016 04/08/2016 | 2016001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Place the RHR System in ECCS-Standby Mode Prior to Exceeding an RCS Temperature of 212 ¦F |  | H.12 Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71153 | The NRC identified an NCV of TS 5.7.1.1.a, Procedures, for the licensee's failure to place the residual heat removal (RHR) system into ECCS-Standby Mode prior to the reactor coolant system (RCS) temperature exceeding 212 ¦F as required by procedure 1-GO-1
Region: II | Watts Bar | 4359 | 03/31/2016 04/08/2016 | 2016001-05 | NRC | NCV | Mitigating Systems | Green | Failure to Use Approved Procedures to Place RHR Letdown In Service |  | S.1 SCWE Policy | TE?: N | 05000390 Watts Bar 1 |  | 71153 | The NRC identified an NCV of TS 5.7.1.1.a, Procedures, for the licensee's failure to use any approved procedures to place RHR Letdown in service. The licensee entered this issue into their corrective action program as CR 1127691. The performance defic
Region: II | Watts Bar | 4366 | 03/31/2016 04/08/2016 | 2016001-06 | NRC | NCV | Mitigating Systems | Green | Failure to Track Applicable Technical Specification Action Statement for Charging Pump Inoperability |  | H.11 Challenge the Unknown | TE?: N | 05000390 Watts Bar 1 |  | 71153 | The NRC identified an NCV of TS 5.7.1.1.a, Procedures, for the licensee's failure to implement OPDP-8, Operability Determinations and LCO tracking. Specifically, the licensee failed to track the applicability of action statement 'B' of TS LCO 3.5.3, ECCS-
Region: II | Watts Bar | 4370 | 03/31/2016 04/08/2016 | 2016001-10 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Surveillance Procedure for Emergency Core Cooling System Venting |  | H.3 Change Management | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified an apparent violation of TS 5.7.1.1.a, Procedures, for the licensee's failure to maintain procedure 1-SI-63-10.1-A, "ECCS Discharge Pipes Venting - Train A Inside Containment," Revisions 11-16, in accordance with the requireme
Region: II | Watts Bar | 4393 | 03/25/2016 05/03/2016 | 2016008-01 | NRC | NCVIV | MISC | Green | Failure to Perform 50.59 Screenings For Procedures |  | H.3 Change Management | TE?: Y SL-IV-NCVIV | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.17T | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," at Watts Bar Unit 1 for the licensee's failure to perform 10 CFR 50.59 screening reviews for new technical procedures and ch
Region: II | Watts Bar | 4394 | 03/25/2016 05/03/2016 | 2016008-02 | NRC | NCVIV | MISC | Green | Failure to Perform Verification and Validation for Abnormal Operating Instructions |  | H.3 Change Management | TE?: Y SL-IV-NCVIV | 05000390 Watts Bar 1 05000391 Watts Bar 2 |  | 71111.17T | The NRC identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," at Watts Bar Unit 1 for the licensee's failure to perform verification and validation for abnormal operating instructions as
Region: II | Watts Bar | 4350 | 12/31/2015 02/12/2016 | 2015004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform ISI General Visual Examination of Containment Moisture Barrier Associated with Containment Liner Leak-chase Test Connection Threaded Pipe Plug |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.08P | The inspectors identified a Green NCV of Title 10 of the10 CFR Part 50.55a, "Codes and Standards," involving the licensee's failure to properly apply Subsection IWE of American Society of Mechanical Engineers, Section XI, for conducting general visual exa
Region: II | Watts Bar | 4352 | 12/31/2015 02/12/2016 | 2015004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Source Range Neutron Flux Channel Technical Specification Requiprements |  | H.12 Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71111.2 | A self-revealing Green non-cited violation (NCV) of Technical Specification (TS) 3.3.1, Table 3.3.1-1, Function 5, required action J.1 and TS 3.0.4.a, was identified because two source range neutron flux channels were inoperable with the reactor trip brea
Region: II | Watts Bar | 4353 | 12/31/2015 02/12/2016 | 2015004-05 | NRC | NCV | Occupational Radiation Safety | Green | Core Barrel Lift Error Resulted in Unintended high Dose Rates |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | NONE | A self-revealing Green NCV of TS 5.7.1, "Procedures, Programs and Manuals," was identified when the unit one core barrel (CB) was raised above the height limit specified in licensee procedure1-MI-68.003, "Removal and Replacement of the Unit 1 Reactor Vess
Region: II | Watts Bar | 4354 | 12/31/2015 02/12/2016 | 2015004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality for Unacceptable Preconditioning of the 1A-A Charging Pump Discharge Check Valve |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The NRC identified a Green NCV of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify a condition adverse to quality. Specifically, the licensee unacceptably precond
Region: II | Watts Bar | 4314 | 06/30/2015 08/04/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Residual Heat Removal Flow Control Valves Not Scoped in In-Service Testing Program |  | H.14 Conservative Bias | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The NRC-identified a NCV of 10 CFR 50.55a, "Codes and Standards," for the licensee's failure to meet the test requirements set forth in the American Society of Mechanical Engineers ASME Operation and Maintenance (OM) for Residual Heat Removal (RHR) flow c
Region: II | Watts Bar | 4315 | 06/30/2015 08/04/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Track Applicable Technical Specification Action Statement for Residual Heat Removal System |  | H.12 Avoid Complacency | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The NRC identified a NCV of technical specification (TS) 5.7.1.1.a, Procedures, for the licensee's failure to implement OPDP-8, Operability Determinations and Limiting Conditions for Operations (LCO) tracking. Specifically, the licensee failed to track th
Region: II | Watts Bar | 4316 | 06/30/2015 08/04/2015 | 2015002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Consider The Effects Of A Break In Non-Seismic ERCW Piping in AFWP design calculations |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The NRC identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to consider the effects of a break in the non-seismic portion of the essential raw cooling water (ERCW) discharge flow path to the cooling
Region: II | Watts Bar | 4323 | 06/30/2015 08/04/2015 | 2015002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure during SSPS Testing |  | H.8 Procedure Adherence | TE?: N | 05000390 Watts Bar 1 |  | 71111.22 | A self-revealing, Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified for the licensee's failure to follow procedure 1-SI-99-10-A, 62 Day Functional Test of Solid State Protection S
Region: II | Watts Bar | 4302 | 03/04/2015 03/11/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure To Perform An Adequate Water Hammer Test |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The NRC identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to perform an adequate test to verify that anticipated water hammer forces would not exceed design limitations at hig
Region: II | Watts Bar | 4305 | 03/04/2015 03/11/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure To Identify A Condition Adverse To Quality For Negative Fouling Factors |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000390 Watts Bar 1 05000390 Watts Bar 1 |  | 7111121 | The NRC identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify a condition adverse to quality. Specifically, following post cleaning tests of the A and C co
Region: II | Watts Bar | 4300 | 12/31/2014 02/09/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assure Qualification Testing Met Specified Requirements |  | P.3 Resolution | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified a Green NCV of 10 CFR Part 50 Appendix B Criterion VII for the licensee's failure to assure that purchased chillers for the main control room (MCR) and shutdown board room (SDBR) conformed to the procurement documents. Specifical
Region: II | Watts Bar | 4301 | 12/31/2014 02/09/2015 | 2014501-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Effectiveness of Emergency Plan |  | P.2 Evaluation | TE?: N | 05000390 Watts Bar 1 |  | 71114.05 | A self-revealing non-cited violation (NCV) of 10 CFR 50.54(q)(2) was identified for the licensee's failure to maintain 1-RM-90-404 A/B radiation monitors as required by their Radiological Emergency Plan and NRC-approved Emergency Action Level scheme. The
Region: II | Watts Bar | 4288 | 09/30/2014 10/29/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to follow scaffold procedure impacts Appendix R operator manual actions (Section 1R05) |  | H.14 Conservative Bias | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified a Green non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, for the licensee's failure to follow procedure MMTP-108, Erection of Scaffolds/Temporary Work Platforms and Ladders, Revision
Region: II | Watts Bar | 4292 | 09/30/2014 10/29/2014 | 2014004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform an Adequate Post Maintenance Test Results in Draining of the Unit 1 RWST to a Level Below Technical Specification Limit (Section 1R19) |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | 71111.19 | A Green self-revealing finding was documented by the inspectors for the licensee's failure to adequately perform a post maintenance test for Design Change Notice (DCN) 60683, Stage 8, resulting in draining approximately 3300 gallons of radioactive contami
Region: II | Watts Bar | 4282 | 06/30/2014 08/01/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct a condition adverse to quality |  | P.1 Identification | TE?: N | 05000390 Watts Bar 1 |  | 71152 | An NRC-identified NCV of 10 Code of Federal Regulations (CFR) 50 Appendix B, Criterion XVI, Corrective Action, was documented for the licensee's failure to adequately identify a condition adverse to quality associated with the installation of 480 volt bre
Region: II | Watts Bar | 4283 | 06/30/2014 08/01/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate a condition adverse to quality |  | P.2 Evaluation | TE?: N | 05000390 Watts Bar 1 |  | 71152 | A NRC-identified non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was documented for the licensee's failure to adequately identify a condition adverse to quality associated with the installation of relief valve 1-RFV-67-1026D
Region: II | Watts Bar | 4284 | 06/30/2014 08/01/2014 | 2014003-03 | NRC | FIN | Initiating Events | Green | Failure to comply with desgin drawing results in a reactor trip |  | H.5 Work Management | TE?: N | 05000390 Watts Bar 1 |  | 71153 | An NRC-identified finding was documented by the inspectors for the licensee's failure to comply with a design drawing during a modification resulting in a trip of Unit 1 reactor. The inspectors determined that the licensee's failure to properly impleme
Region: II | Watts Bar | 4278 | 03/31/2014 04/30/2014 | 2014002-01 | NRC | NCV | Barrier Integrity | Green | Failure to follow plant procedures for replacement of NAMCO limit switches |  | H.8 Procedure Adherence | TE?: N | 05000390 Watts Bar 1 |  | 71111.19 | An NRC-identified NCV of Technical Specification (TS) 5.7.1, Procedures, was documented for the licensee's failure to follow plant procedures which resulted in the undocumented modification of the upper NAMCO limit switch for valve 1-FCV-61-110-A, Glycol
Region: II | Watts Bar | 4280 | 03/31/2014 04/30/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to correct a condition adverse to quality |  | P.2 Evaluation | TE?: N | 05000390 Watts Bar 1 |  | 71152 | An NRC-identified non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50 Appendix B, Criterion XVI, Corrective Action, was documented for the licensee's failure to correct a condition adverse to quality associated with the inadequate perform
Region: II | Watts Bar | 4281 | 03/31/2014 04/30/2014 | 2014002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to comply with technical specification 3.7.5, auxiliary feedwater system |  | H.2 Field Presence | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing NCV of TS 3.7.5, Auxiliary Feedwater (AFW) System, was documented for the licensee's failure to ensure that three fully qualified, independent trains of AFW were operable in Modes 1, 2 and 3. Specifically, the licensee failed to ensure th
Region: II | Watts Bar | 4277 | 12/30/2013 02/07/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately Control Non-Conforming or Degraded Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The NRC identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XV, for the licensee's failure to segregate three pressure switches to prevent their inadvertant use or installation. The inspectors determined that the finding was of very low s
Region: II | Watts Bar | 4269 | 09/27/2013 11/06/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Failure to validate Appendix R abnormal operating instructions in accordance with station procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71111.05T | An NRC identified Green NCV of Technical Specification 5.7.1, Procedures, was identified for the licensee's failure to validate Appendix R abnormal operating instructions (AOI) in accordance with station procedures. The issue was entered into the licensee
Region: II | Watts Bar | 4274 | 09/27/2013 11/06/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate compensatory actions to minimize the effects of impaired fire protection equipment on fire safe shutdown |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.05T | An NRC identified Green NCV of Operating License Condition (OLC) 2.F was identified for the licensee's failure to ensure that established operating requirements (ORs) for the high pressure fire protection (HPFP) system accounted 2 for affected and credit
Region: II | Watts Bar | 4265 | 06/30/2013 08/07/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to meet a critical drill objective in accordance with the approved fire protection plan |  | P.3(a) Self-Assessment | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | Green. The inspectors identified a Green NCV of the Unit 1 Operating License Condition 2.F for the licensee's failure to implement procedures required for fire protection program implementation in accordance with the approved Fire Protection Plan (FPP). S
Region: II | Watts Bar | 4266 | 06/29/2013 07/25/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions to Identify and Evaluate Effects of Harmonics on Degraded Voltage Relay Function |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to implement corrective actions to identify and evaluate the effects of electrical system harmonics on safety-related un
Region: II | Watts Bar | 4251 | 03/31/2013 05/10/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correctly implement procedure for pressurizer pressure channel calibration |  | H.4(a) Human Error Prevention | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing (Green) NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified for failure to properly follow plant procedures to perform a surveillance test for calibration of pressurizer pressure channel
Region: II | Watts Bar | 4255 | 02/22/2013 04/08/2013 | 2013007-01 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure BP-529 "Oversight of Supplemental Personnel" |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | NONE | Inspectors identified a finding of very low safety significance for failure to follow procedure BP-259, "Oversight of Supplemental Personnel," Rev. 9. Specifically, during the licensee's review of the vendor instructions for performing maintenance on turb
Region: II | Watts Bar | 4249 | 01/18/2013 03/12/2013 | 2012009-04 | NRC | NCV | Mitigating Systems | Green | Failure to adequately protect savety-related equipment during flood mode preparation |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | NONE | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to adequately protect safety-related equipment during flood mode preparation. The licensee's failure to adequately
Region: II | Watts Bar | 4250 | 01/18/2013 03/12/2013 | 2012009-05 | NRC | NCV | Mitigating Systems | Green | Failure to correct conditions adverse to quality related to IPS CKV-040-0604 and IPS 3A and 3B sump pumps | EA Case: 2013018 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | NONE | The inspectors identified two examples of an NCV of the 10 CFR 50 Criteria XVI, "Corrective Action," for failure to correct conditions adverse to quality for the intake pumping station (IPS) CKV-040-0604, pump 3B, discharge check valve which resulted in i
Region: II | Watts Bar | 4235 | 12/31/2012 02/13/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately develop and implement ice condenser ice basket repairs |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71111.18 | A NCV of 10 CFR 50 Appendix B, Criterion III, Design Control, for the licensee's failure to adequately develop and implement ice condenser ice basket repairs in accordance with approved engineering and maintenance documents. Specifically, the inspectors o
Region: II | Watts Bar | 4237 | 12/31/2012 02/13/2013 | 2012005-04 | Self - Revealed | NCV | Emergency Preparedness | Green | Late state notification of unusual event |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000390 Watts Bar 1 |  | 71114.05 | A self-revealing non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) 50.54q(2) for failure to follow the approved emergency plan. Specifically, on August 10, 2012, state officials were not notified within 15 minutes of the declaration of an
Region: II | Watts Bar | 4238 | 12/31/2012 02/13/2013 | 2012005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow procedure resulted in failing to remove jumpers inhibiting proper operation of the steam generator blowdown system |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing NCV of Technical Specifications (TS) 5.7.1, Procedures, was identified for failing to adhere to OPDP-1, Conduct of Operations, Section 5.1, Procedure Adherence. The licensee failed to ensure a jumper was removed prior to placing the steam
Region: II | Watts Bar | 4222 | 09/30/2012 10/31/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to follow scaffold procedure threatens ERCW pump operability |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71111.01 | The inspectors identified a NCV of Technical Specification 5.7.1, Procedures, for the licensee's failure to properly implement Maintenance Procedure MMTP-102, Erection of Scaffolds/Temporary Work Platforms and Ladders, Revision 7. Specifically, a temporar
Region: II | Watts Bar | 4225 | 09/30/2012 10/31/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate corrective actions for the C ERCW pump breaker |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified a NCV of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct an identified deficiency in the C-A ERCW pump breaker on July 25, 2012. This uncorrected defi
Region: II | Watts Bar | 4219 | 06/30/2012 08/14/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure to maintain steam generator blowdown isolation valves in the environmental qualification program |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.17T | The team identified a Green non-cited violation (NCV) of 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control", for the licensee's failure to maintain steam generator blowdown (SGBD) isolation valves 1-FCV-1-181, 182, 1
Region: II | Watts Bar | 4220 | 06/30/2012 08/14/2012 | 2012003-04 | NRC | NCV | Mitigating Systems | Green | Failure to identify degraded auxiliary charging pump and initiate corrective actions |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified a Green NCV of 10CFR50 Appendix B Criterion XVI for failure to identify that the 1A auxiliary charging pump (ACP) was degraded based on previous questionable testing results. The inspectors determined that no acceptable testing h
Region: II | Watts Bar | 4206 | 05/15/2012 06/13/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Test Procedures to Assure Satisfactory auxiliary control air subsystem (ACAS) Performance during Design Basis Accidents |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to perform capacity (volumetric flow) testing on the safety-related auxiliary control air subsystem (ACAS). The licensee had documented that
Region: II | Watts Bar | 4207 | 05/15/2012 06/13/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Test the AFW Discharge Check Valves |  | P.3(a) Self-Assessment | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a test program that demonstrated the adequacy of the auxiliary feedwater (AFW) discharge check valves. Specifica
Region: II | Watts Bar | 4208 | 05/15/2012 06/13/2012 | 2012008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria in Maintenance and Surveillance Procedures (5 Examples) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The team identified five examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate vendor specifications and design calculations into maintenance and surveillance p
Region: II | Watts Bar | 4197 | 03/31/2012 04/30/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Procedure AOI-30.2 C.36, Fire Safe Shutdown Room 737-A1A, Non-feasible Operator Manual Action. |  | H.3(b) Work Activity Coordination | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified an NCV of 10 Code of Federal Regulations (CFR) 50 Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to ensure that an operator manual action for fire safe shutdown (FSSD) could be feasibly performed under
Region: II | Watts Bar | 4198 | 03/31/2012 04/30/2012 | 2012002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification 3.4.12 by Allowing a Safety Injection Pump to inject into the RCS in Mode 5. |  | H.4(a) Human Error Prevention | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A Green, self revealing NCV of Technical Specification (TS) 3.4.12 was identified for failure to ensure that no safety injection pump was capable of injecting into the reactor coolant system while in Mode 5. The finding was determined to be greater than m
Region: II | Watts Bar | 4199 | 03/31/2012 04/30/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification 3.8.4, 3.8.5 and 3.0.3 by failing to recognize Vital Batteries III and IV degradation. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A Green, NRC-identified NCV of TS 3.8.4, DC Sources Operating, was identified. The licensee's failure maintain TS operability by accurately identifying that vital battery III was approaching end-of-life was a performance deficiency. It is more than minor
Region: II | Watts Bar | 4165 | 12/31/2011 01/31/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Develop and Implement Corrective Actions for Probable Maximum Precipitation Drainage Path Impact on Unit 1 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71111.01 | The inspectors identified an NCV of 10 Code of Federal Regulations (CFR) 50 Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to develop and implement corrective actions to address the unauthorized placement of temporary structures
Region: II | Watts Bar | 4170 | 12/31/2011 01/31/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Store Transient Combustible Materials in a Safety-Related/Critical Area of the Auxiliary Building in Accordance With the Approved Fire Protection Plan |  | H.3(a) Work Planning | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | An NCV of the Unit 1 Operating License Condition 2.F was identified for the licensee's failure to store transient combustible materials in a safety-related/critical area of the auxiliary building in accordance with the approved Fire Protection Plan (FPP).
Region: II | Watts Bar | 4172 | 12/31/2011 01/31/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Identifying Accumulated Gas in ECCS Systems |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000390 Watts Bar 1 |  | 2515/177 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish adequate procedures to identify accumulated gas in emergency core coo
Region: II | Watts Bar | 4145 | 09/30/2011 10/28/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to fully implement corrective actions for a motor boat necessary for flood mode preparation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71111.01 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to fully implement corrective actions to address a motor boat necessary for flood mode preparation in accordance with Abnormal Operatin
Region: II | Watts Bar | 4146 | 09/30/2011 10/28/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to fully implement corrective actions for the unapproved storage of oil in a safety related area |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to fully implement corrective actions to address the unapproved storage of a large quantity of oil in a safety-related area of the auxi
Region: II | Watts Bar | 4147 | 09/30/2011 10/28/2011 | 2011004-04 | NRC | NCV | Initiating Events | Green | Inadequate corrective action involving the failure of a shutdown board to transfer |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's repeat occurrence of a level A problem evaluation report (PER) 176604 written July 17, 2009. The licensee's failure to ensure that all correc
Region: II | Watts Bar | 4153 | 09/30/2011 10/28/2011 | 2011004-05 | NRC | NCV | Initiating Events | Green | Failure to adequately control non-conforming or degraded equipment |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XV, Nonconforming Materials, Parts, or Components, for the licensee's failure to ensure that 6.9Kv breaker 0-BKR-569-4605025-S, which had been identified as defective, was not labeled or
Region: II | Watts Bar | 4131 | 06/30/2011 08/05/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure The Operability of an Emergency Battery Lighting Unit in Accordance with the Approved Fire Protection Plan |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified an NCV of the Unit 1 Operating License Condition 2.F for the licensee's failure to maintain the operability of Appendix R emergency lighting in accordance with the approved Fire Protection Plan (FPP). Specifically, both lamps for
Region: II | Watts Bar | 4139 | 06/30/2011 08/05/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Procedure AOI-30.2 C.36, Fire Safe Shutdown Room 737-A1A, Non-feasible Operator Manual Action |  | H.3(b) Work Activity Coordination | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified an NCV of Technical Specification 5.7.1, Procedures, for the licensee's failure to maintain a plant procedure to ensure that an operator manual action for fire safe shutdown (FSSD) could be feasibly performed under the current ph
Region: II | Watts Bar | 4140 | 06/30/2011 08/05/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Transient Combustible Evaluation for Storage of Oil in a Safety Related Area in Accordance with the Approved Fire Protection Plan |  | H.3(a) Work Planning | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified an NCV of the Unit 1 Operating License Condition 2.F for the licensee's failure to store transient combustible materials in a safety-related/critical area of the auxiliary building in accordance with the approved FPP. Specificall
Region: II | Watts Bar | 4141 | 06/30/2011 08/05/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Moderate Energy Line Break Study Output into a Plant Procedure |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.06 | Thee inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control for the licensee's failure to correctly translate a design document into operating procedures. Specifically, from original Licensing until the beginning of this
Region: II | Watts Bar | 4116 | 03/31/2011 05/05/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish adequate compensatory measures for a degraded sprinkler system in accordance with the approved fire protection plan |  | H.3(a) Work Planning | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified a NCV of the Unit 1 Operating License Condition 2.F for the licensee's failure to establish adequate compensatory measures for an impaired sprinkler system in accordance with the approved Fire Protection Plan (FPP). Specifically,
Region: II | Watts Bar | 4117 | 03/31/2011 05/05/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to ensure adequacy of AOI-13, loss of essential raw cooling water, revision 0038 |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.06 | The inspectors identified a NCV of Technical Specification 5.7.1, Procedures, for the licensee failure to establish and implement an adequate Abnormal Operating Instruction (AOI) to address flooding in the Auxiliary Building from a pipe break in the Essen
Region: II | Watts Bar | 4096 | 12/31/2010 01/28/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately monitor the performance of the B MCR air conditioning train under 10 CFR 50.65 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000390 Watts Bar 1 |  | 71111.12 | -Green. The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2), was identified by the inspectors for the licensee's failure to set goals and monitor the performance and condition of the B Main Control Room (MCR) Air Conditioning system as r
Region: II | Watts Bar | 4100 | 12/31/2010 01/28/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately qualify molded-case circuit breakers to safety-related application through commercial grade dedication. |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | -Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the failure to assure that appropriate quality standards were specified and included in design documents and that deviations from such sta
Region: II | Watts Bar | 4101 | 12/31/2010 01/28/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to use worst case 6900 VAC bus voltage in design calculations |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | -Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the failure to assure that applicable regulatory requirements and the design basis for structures, systems, and components are correctly t
Region: II | Watts Bar | 4071 | 06/30/2010 07/30/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to assure that adequate test requirements were developed and implemented following a repair. |  | H.3(b) Work Activity Coordination | TE?: N | 05000390 Watts Bar 1 |  | 71111.19 | The inspectors identified a NCV of TS 5.7.1, Procedures, for the licensee failing to develop and implement an adequate post-maintenance test procedure for valve 0-CKV-067-0502C, air release valve for C ERCW pump, resulting in the valve not being fully tes
Region: II | Watts Bar | 4072 | 06/30/2010 07/30/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Lack of procedure implementation results in 1B EDG being started with 15 cylinder plugs open. |  | H.4(a) Human Error Prevention | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing, non-cited violation (NCV) of Technical Specifications (TS) 5.7.1, Procedures, was identified for the licensee's failure to adhere to OPDP-1, Conduct of Operations, Section 5.1, Procedure Adherence, resulting in the 1B Emergency Diesel Ge
Region: II | Watts Bar | 4070 | 04/27/2010 06/11/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate assessment of seismic qualification of ERCW strainers |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The team identified a Green NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for the licensee's failure to update ERCW strainer mounting (seismic/structural) calculations to reflect the as-built conditions, a failure which was allowed to exist
Region: II | Watts Bar | 4065 | 03/31/2010 04/29/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to assure that test requirements were satisfied following a design change |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.19 | The inspectors identified a violation of very low safety significance and an associated non-cited violation of 10 CFR 50 Appendix B Criterion XI, Test Control, for the licensee's failure to assure that test requirements were satisfied following a design c
Region: II | Watts Bar | 4066 | 03/31/2010 04/29/2010 | 2010002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to establish adequate instructions or procedure for determining vital inverter frequency |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71152 | A self-revealing, non-cited violation (NCV) of TS 5.7.1, Procedures, was identified for the licensee's failure to properly implement SPP-2.2, Standard Programs and Processes Administration of Site Technical Procedures. Specifically, while performing vital
Region: II | Watts Bar | 4062 | 12/31/2009 01/29/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Analysis for Failed Auxiliary Charging Pumps |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000390 Watts Bar 1 |  | 71111.01 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.55a(f)(4) for the licensee's failure to meet in-service test requirements for the 1B auxiliary charging pump. Between December 2008 and December 2009, l
Region: II | Watts Bar | 4057 | 09/30/2009 10/30/2009 | 2009004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to incorporate existing design criteria into temporary secondary containment boundary doors |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing, non-cited violation (NCV) of 10 CFR 50 Appendix B, Criterion III, Design Control, was identified for failure to correctly translate the personal access door design basis into the specifications for the temporary ABSCE boundary doors inst
Region: II | Watts Bar | 4061 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate corrective actions to preclude additional temporary secondary containment boundary doors failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A self-revealing NCV of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified for the licensee's failure take prompt corrective actions to preclude repetition of the failure of the temporary auxiliary building secondary containment envelo
Region: II | Watts Bar | 4048 | 06/30/2009 07/30/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to impliment proc. to maintain design of intake pumping station missile shield |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71152 | 10 CFR 50 Appendix B, Criterion V states, in part, that activities affecting quality shall be prescribed by documented instructions or procedures of a type appropriate to the circumstances and shall be accomplished in accordance with these instructions or
Region: II | Watts Bar | 4049 | 06/26/2009 07/29/2009 | 2009006-01 | Self - Revealed | NCV | Mitigating Systems | Green | failure to promptly correct a condition adverse to quality --- A shutdown boardroom chiller |  | H.3(b) Work Activity Coordination | TE?: N | 05000390 Watts Bar 1 |  | 71152B | Green. A self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI was identified for failure to take timely and effective corrective action to maintain the capillary line to the Essential Raw Cooling Water (ERCW) condenser water te
Region: II | Watts Bar | 4054 | 06/26/2009 07/29/2009 | 2009006-02 | Self - Revealed | NCV | Public Radiation Safety | Green | failure to follow plant proceedures for cancelling preventative maintenance |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71152B | Green. A self-revealing NCV of Technical Specification 5.7.1 was identified for the licensee's failure to follow plant procedures which resulted in the failure of the Unit 1 Shield Building Vent Radiation Monitor System, an effluent radiation monitor.
Region: II | Watts Bar | 4033 | 12/31/2008 01/12/2009 | 2008005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure toTranslate ERCW Pump Coupling Material Change into Procedures |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.18 | A Green self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion III, Design Control, was identified for the failure to adequately translate material specifications into procedures. As a result, the B-A essential raw cooling water (ERCW) pump
Region: II | Watts Bar | 4037 | 12/31/2008 01/12/2009 | 2008005-02 | NRC | NCV | Initiating Events | Green | Failure to Incorporate Design Parameters into Plant Setpoint Document for the Containment Particulate Radiation Monitor |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000390 Watts Bar 1 |  | 71152 | The NRC identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for failure to translate revised design parameters into the setpoint and scaling document for the lower containment particulate radiation monitor. As
Region: II | Watts Bar | 4038 | 12/31/2008 01/12/2009 | 2008005-03 | Self - Revealed | FIN | Initiating Events | Green | jPerforming Non-Authorized Activities on Exciter Field Breaker Results In Reactor Trip |  | H.4(a) Human Error Prevention | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A Green self-revealing finding was identified for the failure to obtain authorization prior to opening the main generator exciter field breaker compartment and operating the de-latching bar. The licensee's procedures for controlling sensitive plant equipm
Region: II | Watts Bar | 4042 | 12/31/2008 01/12/2009 | 2008005-04 | NRC | NCV | Mitigating Systems | Green | Carbon Dioxide System in Fire Area 48 Failed to Meet Design Criterion |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The NRC identified a Green, non-cited violation of Unit 1 Operating License Condition 2.F for not having a carbon dioxide (CO2) suppression system for the Unit 1 auxiliary instrumentation room with the capability to maintain the design basis gas concentra
Region: II | Watts Bar | 4028 | 06/30/2008 08/07/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Plant Startup with Inoperable AFW Automatic Start on Trip of All MFW Pumps |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71152 | A Green, NRC-identified non-cited violation of Technical Specification (TS) 3.0.4.a was identified for entering Modes 2 and 1 without an operable channel of auxiliary feedwater automatic start on a trip of all main feedwater pumps as required by TS 3.3.2.
Region: II | Watts Bar | 4029 | 06/30/2008 08/07/2008 | 2008003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification 3.3.2 to Have Two Trains of Automatic Actuation Logic and Actuation Relays for Safety Injection and Feedwater Isolation Operable |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A Green, self-revealing non-cited violation of Technical Specification 3.3.2 was identified for failure to have two trains of safety injection (SI) automatic actuation logic and two trains of feedwater isolation actuation logic operable while in Mode 3. U
Region: II | Watts Bar | 4025 | 03/31/2008 04/30/2008 | 2008002-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Properly Prepare a Radioactive Material Package for Shipment |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7112202 | Green. A self-revealing NCV of 10 CFR 71.5 was identified for failure to properly package radiological material such that, under conditions normally incident to transportation, the radiation levels at the external surface of the package would not exceed a
Region: II | Watts Bar | 4026 | 03/31/2008 04/30/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulted in Inadequate Control of Materials Brought into Containment |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71152 | Green. The inspectors identified a NCV of Technical Specification (T.S.) 5.7.1 for failure to properly implement procedural requirements and engineering controls for materials brought into containment while the plant was at power. The procedural violation
Region: II | Watts Bar | 4035 | 03/14/2008 10/29/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | Installation of Different RHR Flow Limiters Than Prescribed by Procedure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000390 Watts Bar 1 |  | 71153 | A Green, NRC-identified, non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for installing flow limiting devices, on A-train residual heat removal (RHR) system valves, which were not equivale
Region: II | Watts Bar | 4023 | 12/31/2007 01/30/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Reactivate RO/SRO Licenses in Accordance with Procedure OPDP-1, "Conduct of Operations" |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | NONE | The inspectors identified a non-cited violation of Technical Specification 5.7.1.1(a) for the procedure adherence to OPDP-1, "Conduct of Operations," and 10 CFR 55, Part 55.53 f(2), Conditions of Licenses, which resulted in two licensee employees failing
Region: II | Watts Bar | 4024 | 12/31/2007 01/30/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Fire Protection Program Did Not Demonstrate Eight-Hour Emergency Light Unit Battery Capacity |  |  | TE?: N | 05000390 Watts Bar 1 |  | NONE | The Triennial Fire Inspection Team identified a non-cited violation of Unit 1 License Condition 2F and 10 CFR 50, Appendix R, Section III.J, Emergency Lighting, for having a fire protection program which failed to demonstrate that the emergency lighting u
Region: II | Watts Bar | 4011 | 09/30/2007 10/29/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct an Identified Procedural Deficiency Prior to Subsequent Maintenance |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000390 Watts Bar 1 |  | 71111.12 | Green. The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified. The licensee failed to correct, in a timely manner, a procedural d
Region: II | Watts Bar | 4012 | 09/30/2007 10/29/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct the Failure of Safety Injection Relief Valves to Reseat after Actuation |  | P.2(b) Implementing Operating Experience | TE?: N | 05000390 Watts Bar 1 |  | NONE | Green. The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified. The licensee failed to identify incorrect as-found nozzle ring set
Region: II | Watts Bar | 4010 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Risk Assessment for Work In Progress (Section 1R13) |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.13 | Green. The inspectors identified a finding associated with 10 CFR 50.65 (a)(4), Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, for the licensee's failure to perform an adequate risk assessment which resulted in an un
Region: II | Watts Bar | 4016 | 06/15/2007 07/30/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Safe Shutdown Procedure for Portions of FA 8 Not Consistent With Underlying Analysis |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.7.1, Procedures, in that post-fire safe shutdown procedure AOI-30.2, Revision 23, was not consistent with the underlying circuit analysis for a portion of Fire Area 8. The finding i
Region: II | Watts Bar | 4017 | 06/15/2007 07/30/2007 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Feeder Cables for Vital Inverter not Protected with One-Hour Fire Barrier |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.05T | The team identified a non-cited violation of Unit 1 License Condition 2F and 10 CFR 50, Appendix R, Section III.G.2, for not enclosing vital inverter power supply cables in Fire Area 20 in a one-hour fire barrier. The finding is more than minor because
Region: II | Watts Bar | 4021 | 06/15/2007 07/30/2007 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Emergency Light at Location of Local Operator Action Important to Safe Shutdown |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.05T | The team identified a non-cited violation of Unit 1 License Condition 2F and 10 CFR 50, Appendix R, Section III J, for not providing an emergency light to illuminate the interior of a panel in which a local operator action to pull fuses was directed by th
Region: II | Watts Bar | 4008 | 03/31/2007 04/24/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct an Identified Equipment Malfunction |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000390 Watts Bar 1 |  | 71152 | A finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified by the inspectors. The licensee failed to investigate and correct, in a timely manner, an interlock
Region: II | Watts Bar | 4009 | 03/16/2007 04/20/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Violation of Technical Specification 5.7.1 for TVA's failure to develop a procedure that will provide tornado depressurization protection of the DGB |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7111121 | The team identified a [Green non-cited] violation of Technical Specification 5.7.1 associated with failure to develop a procedure that will provide tornado depressurization protection of the emergency diesel generator building. The finding involves a torn
Region: II | Watts Bar | 3999 | 10/31/2006 10/27/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Fire Header Inoperable Due to Failure to Follow Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71111.05Q | The inspectors identified a non-cirted violation of the Fire Protection Report Operating Requirement which requires that fire watches be established when portions of the fire protection system are disabled. As a result of improper procedure implementation
Region: II | Watts Bar | 4000 | 10/06/2006 10/27/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure During Preventive Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000390 Watts Bar 1 |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification (TS) 5.7.1 for failing to follow procedures while performing maintenance on an essential raw cooling water valve which supports the A-train electric boardroom (EBR) chiller. This d
Region: II | Watts Bar | 4005 | 10/06/2006 10/27/2006 | 2006004-03 | NRC | NCV | Mitigating Systems | Green | Inappropriate Crediting of Operator Restoration Actions Causes Inadequate Risk Assessment |  | H.3(a) Work Planning | TE?: N | 05000390 Watts Bar 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4) for failure to perform an adequate risk assessment for maintenance and testing activities affecting the emergency gas treatment system (EGTS) and auxiliary building gas treatment system
Region: II | Watts Bar | 4006 | 10/06/2006 10/27/2006 | 2006004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Have an AFW Autostart Signal on Loss of All MFW Pumps During Plant Startup |  |  | TE?: N | 05000390 Watts Bar 1 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specifications (TS) 3.0.4 for entering Modes 1 and 2 with the automatic auxiliary feedwater start signal for a loss of normal feedwater (TS 3.3.2.6.e) inoperable. The licensee inappropriately co
Region: II | Watts Bar | 3990 | 06/30/2006 07/25/2006 | 2006003-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Comply with Technical Specification Required Actions for Two Inoperable Containment High Range Radiation Monitors |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000390 Watts Bar 1 |  | 71152 | An NRC-identified non-cited violation of Technical Specification 3.3.3, "Post Accident Monitoring (PAM) Instrumentation," was identified for failure to take the required actions when the containment high range radiation monitors were not restored to opera
Region: II | Watts Bar | 3991 | 06/30/2006 07/25/2006 | 2006003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to establish controls in such a way as does not prevent individuals from exiting a high radiation area |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7112101 | A self-revealing non-cited violation of 10 CFR 20.1601(d) was reviewed by the inspectors for failure to establish controls in a way that does not prevent individuals from exiting a high radiation area. This event involved workers being locked inside the c
Region: II | Watts Bar | 3996 | 06/30/2006 07/25/2006 | 2006003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to use procedural controls to control occupational exposure |  | H.3(b) Work Activity Coordination | TE?: N | 05000390 Watts Bar 1 |  | 7112101 | A self-revealing non-cited violation of 10 CFR 20.1101(b) was reviewed by the inspectors for failure to use, to the extent practical, procedural and engineering controls based on sound radiation protection principles to achieve occupational doses that are
Region: II | Watts Bar | 3997 | 06/30/2006 07/25/2006 | 2006003-04 | NRC | NCV | Emergency Preparedness | Green | Failure to perform air quality test for compressors used to supply emergency preparedness SCBA breathing air tanks |  |  | TE?: N | 05000390 Watts Bar 1 |  | 7112103 | An NRC-identified non-cited violation of 10 CFR 50.47(b)(8) was identified for the failure to maintain respiratory protection equipment required for emergency response activities. Specifically, from October 2004 through April 2006, the licensee failed to
Region: II | Watts Bar | 124705 | 05/13/2019 | 2019001-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow System Status Control Procedure Results in Valve Misposition and Inoperability of the A train of ABGTS |  | H.13 - Consistent Process | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 | Configuration Control | 71153 | A self-revealed Green finding and associated non-cited violation (NCV) of Technical Specifications 5.7.1.1.a, “Procedures,” was identified for the failure to the requirements of TVA procedure NPG-SPP-10.1, System Status Control, Revision 9. Specifically,
Region: II | Watts Bar | 125032 | 08/19/2019 | 2019013-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Analyze Common Station Service Transformers A and B to Design Bases Requirements |  | NPP | TE?: N | 05000390 Watts Bar 1 05000391 Watts Bar 2 | Design Control | 71111.21M | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III when the licensee failed to adequately analyze common station service transformer’s (CSST) A and B capability as qualified offs
Region: III | Braidwood | 124343 | 04/10/2019 04/23/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate the Design Basis for the Refueling Water Storage Tank Hatch Barrier Modification |  | UNABLE | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 | Protection Against External Factors | 71111.21M | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to correctly translate the design basis for the
Region: III | Braidwood | 124660 | 04/10/2019 04/23/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Bases Information for the Turbine Building High Energy Line Break Mitigation Strategy |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 | Design Control | 71111.21M | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to correctly translate regulatory requirements a
Region: III | Braidwood | 25935 | 12/31/2018 02/06/2019 | 2018004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Weld Preparation Activities Resulted in Blockage of Instrument Sensing Line and Unit Trip |  | H.12 - Avoid Complacency | TE?: N | 05000456 Braidwood 1 |  | 71153 | A self-revealed finding of very low safety significance (i.e., Green) was identified for the licensee’s failure to have adequately implemented established welding requirements contained in CC–AA–501–1021, Exelon Nuclear Welding Program Repair of Welds and
Region: III | Braidwood | 25936 | 12/31/2018 02/06/2019 | 2018004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Evaluate the Adequacy of a Design Change Resulted in a Feedwater Pump Trip and Manual Reactor Trip Due to Lowering Steam Generator Water Levels |  | H.11 - Challenge the Unknown | TE?: N | 05000456 Braidwood 1 |  | 71153 | A self-revealed finding of very low safety significance (i.e., Green) and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” were identified for the licensee’s failure to have evaluated the adequacy of
Region: III | Braidwood | 24685 | 09/30/2018 10/31/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Detail in Maintenance Procedure for Emergency Diesel Generator 2-Year Inspection Contributed to 1A Emergency Diesel Generator Fuel Rack Binding |  | H.7 - Documentation | TE?: N | 05000456 Braidwood 1 |  | 71153 | A self-revealed finding of very low safety significance (i.e., Green) and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified for the licensee’s failure to have adequ
Region: III | Braidwood | 24099 | 06/30/2018 08/07/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Detail in Maintenance Work Instructions Resulted in Failed Gearbox Oil Cooler Head Gasket and Inoperable 2B Auxiliary Feedwater Pump |  | H.9 - Training | TE?: N | 05000457 Braidwood 2 |  | 71111.12 | A self-revealed finding of very low safety significance (i.e., Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified for the licensee’s failure to have adequate detail within thei
Region: III | Braidwood | 24100 | 06/30/2018 08/07/2018 | 2018002-02 | Self - Revealed | FIN | Initiating Events | Green | Work Instruction Error Results in Reactor Coolant System Pressure Transient |  | H.3 - Change Management | TE?: N | 05000456 Braidwood 1 |  | 71111.15 | A self-revealed finding of very low safety significance (i.e., Green) was identified due to the licensee’s failure to follow work instructions while performing a digital upgrade to plant control systems. Specifically, while working on the volume control t
Region: III | Braidwood | 24101 | 06/30/2018 08/07/2018 | 2018002-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Test Activity Coordination Results in Unintended Valve Actuation and Reactor Coolant System Pressure Drop |  | H.4 - Teamwork | TE?: N | 05000456 Braidwood 1 |  | 71111.19 | A self-revealed finding of very low safety significance (i.e., Green) and an associated NCV of Technical Specification 5.4, “Procedures,” was identified for the licensee’s failure to have properly coordinated testing activities associated with redundant U
Region: III | Braidwood | 22676 | 12/31/2017 02/14/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Failure to have a Pre-Fire Plan for the RWST Pipe Tunnels |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | A finding of very low safety significance and an associated NCV of License Condition 2.E were identified by the inspectors for the licensee’s failure to have an adequate pre-fire plan for the refueling water storage tank (RWST) tunnel. Specifically, the l
Region: III | Braidwood | 22337 | 12/15/2017 12/15/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to prevent Secondary Missiles Following a Postulated High Energy Line Break |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to ensure that the design basis
Region: III | Braidwood | 22339 | 12/15/2017 12/15/2017 | 2017008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Correct Errors in Design Analysis for Main Steam Line Break in Main Steam Tunnel |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” when the licensee failed to promptly correct errors in the design analysis for a main steam line b
Region: III | Braidwood | 22341 | 12/15/2017 12/15/2017 | 2017008-05 | NRC | NCV | Mitigating Systems | Green | Inaccurate Analysis of Record |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to maintain an accurate and up-to-date analysis of record for a postulated H
Region: III | Braidwood | 22338 | 11/16/2017 12/15/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Blow Out Panel Design Control |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee originally designed the MSSV blow out panels in a manner that prevented them from f
Region: III | Braidwood | 22340 | 11/16/2017 12/15/2017 | 2017008-04 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action for Secondary Missiles |  | NPP | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” when the licensee failed to promptly address the identification of secondary missiles following a
Region: III | Braidwood | 22274 | 09/30/2017 11/02/2017 | 2017003-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Implement Adequate Radiological Controls for Treated Liquid Radioactive Effluents Containing Tritium |  | H.11 - Challenge the Unknown | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71124.06 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 20.1406(c), when the licensee failed to conduct operations to minimize the introduction of residual radio
Region: III | Braidwood | 6085 | 06/30/2017 08/07/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Surveillance Frequency Program for the Deferral of a Technical Specification Surveillance |  | H.5 Work Management | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.5.19.b, "Surveillance Frequency Program," were identified by the inspectors for the failure to implement the requirements contained in the surveillance frequ
Region: III | Braidwood | 6086 | 06/30/2017 08/07/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Technical Specification Surveillance Frequency Requirements into Implementing Procedures |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified by the inspectors for the licensee's failure to have appropriate implementing procedures
Region: III | Braidwood | 6092 | 06/30/2017 08/07/2017 | 2017002-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately Implement and Maintain the Radiological Environmental Monitoring Program by Collecting Representative Samples from the Principal Food Pathways |  | H.3 Change Management | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71124.07 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix I, Section IV(B), were identified by the inspectors for the licensee's failure to establish an appropriate surveillance and monitoring program in order to provide
Region: III | Braidwood | 6084 | 12/31/2016 01/27/2017 | 2016004-01 | NRC | NCV | Initiating Events | Green | INADEQUATE CONTROL OF WELDING DURING FW SYSTEM PIPE REPLACEMENT |  | H.2 Field Presence | TE?: N | 05000456 Braidwood 1 |  | 71111.08P | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion IX, "Control of Special Processes," was identified by the inspectors for the licensee's failure to assure
Region: III | Braidwood | 6078 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ERECT SCAFFOLDING IN ACCORDANCE WITH STATION PROCEDURES |  | H.4 Teamwork | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow Revision 7 of NES-MS-04.1, "Seismic Prequalified Scaf
Region: III | Braidwood | 6079 | 09/30/2016 11/08/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW INSERVICE TESTING REQUIREMENTS FOR THE 2A ESSENTIAL SERVICE WATER PUMP LEADS TO AN INVALID TEST |  | H.9 Training | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow Revision 9 of Procedure 2BwOSR 5.5.8.SX-6A, "Comprehe
Region: III | Braidwood | 6075 | 07/29/2016 09/23/2016 | 2016007-01 | Self - Revealed | NCV | Mitigating Systems | Green | OPERATION OF SX SYSTEM VALVES RESULTS IN CAVITATION DAMAGE AND PIPE LEAKAGE |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to prescribe essent
Region: III | Braidwood | 6065 | 06/30/2016 07/27/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Multiple Failure to Follow Procedures Leads to Inadequate Monitoring of Gas Susceptible Locations |  | H.12 Avoid Complacency | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow Revision 3 of procedure ER-AA-2009, "Managing Gas Acc
Region: III | Braidwood | 6071 | 06/30/2016 07/27/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Manage Gas Accumulation in the 2A SI Train |  | H.11 Challenge the Unknown | TE?: N | 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to manage gas accumulation in the safety injection (SI) system
Region: III | Braidwood | 6057 | 03/31/2016 05/11/2016 | 2016001-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW FIRE PREVENTION FOR HOT WORK PROCEDURE |  | H.5 Work Management | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05A | The inspectors identified a finding of very low safety significance and an associated NCV of License Condition 2.E when licensee personnel failed to follow the requirements of the Fire Prevention for Hot Work procedure on two separate occasions. Specifica
Region: III | Braidwood | 6058 | 03/31/2016 05/11/2016 | 2016001-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO HAVE ADEQUATE WORK INSTRUCTIONS AND PROCEDURES LEADS TO A LOSS OF INVENTORY FROM THE VOLUME CONTROL TANK |  | H.5 Work Management | TE?: N | 05000457 Braidwood 2 |  | 71111.13 | . A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on February 1, 2016, when licensee personnel failed to have appropriate work instruct
Region: III | Braidwood | 6062 | 03/31/2016 05/11/2016 | 2016001-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECT A CONDITION ADVERSE TO QUALITY LEADS TO LOSS OF ONE TRAIN OF SHUTDOWN COOLING IN MODE 6 |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.13 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was self revealed when the licensee failed to ensure that a condition adverse to quality was promptly identified and correc
Region: III | Braidwood | 6064 | 03/31/2016 05/11/2016 | 2016001-04 | NRC | FIN | Mitigating Systems | Green | FAILURE TO ENSURE UNIT 2 STARTUP FEEDWATER PUMP AVAILABILITY |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | . The inspectors identified a finding of very low safety significance when licensee personnel failed to ensure that the Unit 2 startup feedwater pump (SUFWP) was available during an 18 month operating cycle. Specifically, the licensee had failed to ensure
Region: III | Braidwood | 6056 | 03/25/2016 04/26/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Air Intake for Diesel Driven Auxiliary Feedwater Pump was Adequately Protected from a High Energy Line Break. (Section 1R21.3b (2)) |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the diesel dr
Region: III | Braidwood | 6048 | 03/25/2016 04/26/2016 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Tripping Characteristic of Molded Case Circuit Breakers (MCCBs) Used as Isolation Devices for the 120 Vac Instrument Power System. (Section 1R21.3b (1)) |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to test the 120 Vac molded case circuit
Region: III | Braidwood | 6046 | 12/31/2015 02/02/2016 | 2015004-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO ESTABLISH ADEQUATE FEEDWATER PUMP OPERATIONAL GUIDANCE DURING PLANT SHUTDOWN |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of Technical Specification 5.4.1, "Procedures," was self-revealed on October 5, 2015, due to the licensee's failure to establish and maintain adequate guidance for operating the Unit 1 and Un
Region: III | Braidwood | 6047 | 12/31/2015 02/02/2016 | 2015004-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH A WRITTEN PROCEDURE FOR A LOSS OF FEEDWATER EVENT IN MODE 3 |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of Technical Specification 5.4.1, "Procedures," was self revealed on October 5, 2015, due to the licensee's failure to establish a written procedure for combating emergencies and other signif
Region: III | Braidwood | 6043 | 08/28/2015 10/05/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Circuits Associated with Pressurizer PORVs and Block Valves Were Free of Fire Damage (Section 1R05.6.b) |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | Green. The inspectors identified a finding of very low safety significance, and an associated NCV of the Braidwood Station facility operating license condition 2.E associated with the Fire Protection Program for the licensee's failure to ensure that the s
Region: III | Braidwood | 6040 | 06/30/2015 08/04/2015 | 2015002-01 | NRC | NCVIV | Initiating Events | Green | FAILURE TO UPDATE THE UFSAR - THIMBLE TUBE INSPECTION PROGRAM |  |  | TE?: Y SL-IV-NCVIV | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.08P | The inspectors identified a Severity Level IV NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.71(e), "Periodic Update of the Updated Final Safety Analysis Report (UFSAR)," and an associated Green finding for the licensee's failure to update
Region: III | Braidwood | 6041 | 06/30/2015 08/04/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | MECHANIC JOINT LEAKAGE ACCEPTED FOR CONTINUED SERVICE WITHOUT CODE CORRECTIVE ACTIONS |  | H.14 Conservative Bias | TE?: N | 05000456 Braidwood 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow a procedure for completing an American Soci
Region: III | Braidwood | 6042 | 06/30/2015 08/04/2015 | 2015002-03 | Self - Revealed | NCV | Mitigating Systems | Green | CONTROL ROOM CHILLER INOPERABILITY DUE TO HIGH OIL CONTENT IN THE REFRIGERANT |  | P.3 Resolution | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.12 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on April 28, 2015, when licensee personnel failed to establish adequate procedural cont
Region: III | Braidwood | 6036 | 03/31/2015 04/30/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT TEMPORARY STRUCTURES DID NOT ADVERSELY IMPACT SAFETY DURING POSTULATED PROBABLE MAXIMUM PRECIPITATION EVENT |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", when licensee personnel failed to establish adequate measures to ensure that temporary equipment and
Region: III | Braidwood | 6037 | 03/31/2015 04/30/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY EVALUATE OPERABILITY OF A DEGRADED CONTROL ROOM CHILLER |  | H.6 Design Margins | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to adhere to the operability determination proce
Region: III | Braidwood | 6038 | 03/31/2015 04/30/2015 | 2015001-03 | Self - Revealed | NCV | Emergency Preparedness | Green | FAILURE TO ACTIVATE THE EMERGENCY RESPONSE ORGANIZATION DURING AN ACTUAL EVENT |  | H.3 Change Management | TE?: N | 05000456 Braidwood 1 |  | 71114.03 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR 50.54(q)(2) and 10 CFR 50.47(b)(2) was identified on July 23, 2014, when after a Notice of Unusual Event was declared and the Shift Manager activated the Emergency Res
Region: III | Braidwood | 6030 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY EVALUATE OPERABILITY FOLLOWING THE DISCOVERY OF AN UNANALYZED CONDITION INVOLVING THE PROBABLE MAXIMUM PRECIPITATION EVENT |  | H.12 Avoid Complacency | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to adhere to Operability Determination P
Region: III | Braidwood | 6034 | 12/31/2014 02/10/2015 | 2014005-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECT UNDERSIZE ESSENTIAL SERVICE WATER PUMP BEARING CASING DRAIN LINE RESULTED IN SYSTEM INOPERABILITY |  | P.2 Evaluation | TE?: N | 05000456 Braidwood 1 |  | 71152 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control" was self-revealed following the licensee's failure to design the 1B essential service water (SX) pump inboard bearing casing
Region: III | Braidwood | 6035 | 12/31/2014 02/10/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE IMPACT OF PROBABLE MAXIMUM PRECIPITATION EVENT ON TURBINE BUILDING FLOODING AS ASSOCIATED SAFETY-RELATED SSCs |  | H.6 Design Margins | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assess the impact of plant modifications on the PMP event analysis i
Region: III | Braidwood | 6023 | 09/30/2014 11/13/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | ADVERSE IMPACT OF FLOOR DRAIN DESIGN ON FLOODING ANALYSIS |  | P.2 Evaluation | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III "Design Control," when licensee personnel failed to verify the design of bag-strainers in the floor drains of the auxili
Region: III | Braidwood | 6024 | 09/30/2014 11/13/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | MULTIPLE FAILURES TO FOLLOW OPERABILITY EVALUATION PROCESS FOLLOWING DISCOVERY OF A NON-CONFORMING CONDITION IN THE ULTIMATE HEAT SINK |  | H.14 Conservative Bias | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to follow procedure OP-AA-108-115, "Operability
Region: III | Braidwood | 6025 | 09/30/2014 11/13/2014 | 2014004-03 | Self - Revealed | NCV | Mitigating Systems | Green | STATION DIESEL DRIVEN FIRE PUMP RESTORED TO SERVICE NON-FUNCTIONAL DUE TO INCORRECT STOP PUSH BUTTON SWITCH REPLACEMENT |  | H.12 Avoid Complacency | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.19 | A finding of very low safety significance and an associated NCV of Braidwood Operating License Condition 2.E, "Fire Protection Program," was self-revealed during the performance of a scheduled diesel-driven fire pump (DDFP) sequential start surveillance w
Region: III | Braidwood | 6028 | 09/30/2014 11/13/2014 | 2014004-04 | Self - Revealed | NCV | Mitigating Systems | Green | UNIT 2 PRESSURIZER PRESSURE TRANSMITTER 459 RETURNED TO SERVICE WITH INSTRUMENT ISOLATED |  |  | TE?: N | 05000457 Braidwood 2 |  | 71111.19 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on May 21, 2014, when licensee personnel failed to use a quality instruction to reposition
Region: III | Braidwood | 6029 | 09/30/2014 11/13/2014 | 2014004-05 | NRC | NCV | Emergency Preparedness | Green | INADEQUATE EVACUATION TIME ESTIMATE SUBMITTALS |  | H.7 Documentation | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The NRC identified a finding of very low safety significance and an associated NCV of 10 CFR 50.54(q)(2) related to 10 CFR 50.47(b)(10) and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the Braidwood Station Emerge
Region: III | Braidwood | 6016 | 03/31/2014 05/09/2014 | 2014002-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO ENSURE MITIGATING SYSTEM AVAILABILITY AND RELIABILITY DURING WEATHER CONDITIONS THAT COULD PROMOTE FRAZIL ICE AT THE LAKE SCREEN HOUSE |  | P.3 Resolution | TE?: N | 05000456 Braidwood 1 |  | 71111.01 | The inspectors identified a finding of very low safety significance when licensee personnel failed to ensure that the LSH trash rake would be capable of clearing ice buildup on the trash rake bars. Specifically, the licensee failed to ensure that the tras
Region: III | Braidwood | 6009 | 03/31/2014 05/09/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE AOP ENTRY CRITERIA FOR INTAKE FRAZIL ICING CONDITIONS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.4.1, "Procedures" when licensee personnel failed to specify adequate entry conditions in the station Abnormal Operating Procedure (AOP) that would be utilize
Region: III | Braidwood | 6017 | 03/31/2014 05/09/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY FIRE DOORS THAT DO NOT CONFORM TO NFPA CODES AND STANDARDS |  | H.8 Procedure Adherence | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated NCV of Braidwood Operating License Condition 2.E, "Fire Protection Program," when licensee personnel failed to identify fire doors that did not conform to the current li
Region: III | Braidwood | 6007 | 12/31/2013 01/27/2014 | 2013005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO FOLLOW PROCEDURE AND TECHNICAL SPECIFICATION ASSOCIATED WITH CONTROL FOR HIGH AND LOCKED HIGH RADIATION AREAS |  | H.11 Challenge the Unknown | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71124.01 | The inspectors identified a self revealed finding of very low safety significance and an associated NCV of Technical Specification 5.7.1 when licensee personnel failed to adequately monitor and provide positive control over activities within a high radiat
Region: III | Braidwood | 5991 | 12/31/2013 11/14/2013 | 2013008-01 | NRC | VIO | Barrier Integrity | Green | Inaccurate/Incomplete Information For Exemption Request From 10 CFR 50.60. | EA Case: 2013209 |  | TE?: Y SL-V-VIO | 05000457 Braidwood 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV Violation of 10 CFR 50.9 "Completeness and Accuracy of Information," for the licensee's failure to provide information to the NRC that was comp
Region: III | Braidwood | 6002 | 12/31/2013 11/14/2013 | 2013008-02 | NRC | FIN | Barrier Integrity | Green | naccurate/Incomplete Information For Exemption Request From 10 CFR 50.60. |  |  | TE?: Y SL-V-FIN | 05000457 Braidwood 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV Violation of 10 CFR 50.9 "Completeness and Accuracy of Information," for the licensee's failure to provide information to the NRC that was comp
Region: III | Braidwood | 5961 | 09/30/2013 11/14/2013 |  | NRC | NCVIV | Initiating Events | Green | FAILURE TO PERFORM A REQUIRED 10 CFR 50.59 EVALUATION |  |  | TE?: Y SL-IV-NCVIV | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated Severity Level IV NCV of 10 CFR 50.59, "Changes, Tests, and Experiments," when licensee personnel failed to perform and maintain a written evaluation to demonstrate that
Region: III | Braidwood | 5962 | 09/30/2013 11/14/2013 |  | NRC | FIN | Initiating Events | Green | FAILURE TO PERFORM A REQUIRED 10 CFR 50.59 EVALUATION |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated Severity Level IV NCV of 10 CFR 50.59, "Changes, Tests, and Experiments," when licensee personnel failed to perform and maintain a written evaluation to demonstrate that
Region: III | Braidwood | 5976 | 08/30/2013 10/09/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Multiple Failures in the Emergency Operating Procedures (EOPs) 1(2)BwEP ES 1.3, "Transfer to Cold leg Recirculation" as Required by Technical Specification. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Technical Specification, Section 5.4.1b for the licensee's failure to establish the necessary actions as required in Emergency Operating Procedures (EOPs)
Region: III | Braidwood | 5977 | 08/30/2013 10/09/2013 | 2013007-02 | NRC | NCV | Barrier Integrity | Green | Procedures for Shutdown Loss of Coolant Accident (LOCA) Not Appropriate If RCS Leakage Is Isolated. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure abnormal operating Procedures (AOPs)
Region: III | Braidwood | 5963 | 08/30/2013 10/09/2013 | 2013007-03 | NRC | FIN | Initiating Events | Green | Failure to Adequately Evaluate SAT Overcurrent Relay Settings in Design Calculations. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance for the licensee's failure to ensure the system auxiliary transformer (SAT) 242-1 overcurrent relay provided protection coordination with upstream and downstream protective devices as req
Region: III | Braidwood | 5969 | 08/30/2013 10/09/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Six Component Cooling (CC) System Manual Valves Were in the Correct Position as Required by Technical Specification (TS) Surveillance Requirement (SR) 3.7.7.1. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Technical Specification Surveillance Requirement 3.7.7.1, for the licensee's failure to ensure six component cooling (CC) system manual valves in the flow
Region: III | Braidwood | 5970 | 08/30/2013 10/09/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Accident Flows in Component Cooling Water Pump Net Positive Suction Head Calculations. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to incorporate accident flows in component cooling water (CCW) pump net posit
Region: III | Braidwood | 5971 | 08/30/2013 10/09/2013 | 2013007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Adequate Tornado Missile Protection in SX Discharge Pipe. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to consider design control measures commensurate with those applied to the or
Region: III | Braidwood | 5943 | 06/30/2013 08/14/2013 | 2013003-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO IDENTIFY AND CORRECT DEGRADED DOST ROOM SUMP PUMP DISCHARGE CHECK VALVES |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance when licensee personnel failed to identify degraded Diesel Oil Storage Tank (DOST) room sump discharge check valves in 2013 and after performing periodic testing in 2005. The licensee ent
Region: III | Braidwood | 5944 | 06/30/2013 08/14/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO SCOPE NONSAFETY RELATED TURBINE BUILDING TO AUXILIARY BUILDING SUMP PUMP DISCHARGE CHECK VALVES INTO THE MAINTENANCE RULE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50.65(b)(2)(ii) when licensee personnel failed to scope four Unit 1 and Unit 2 Essential Service Water (SX) pump room sump pump discharge c
Region: III | Braidwood | 5947 | 06/30/2013 08/14/2013 | 2013003-03 | Self - Revealed | FIN | Mitigating Systems | Green | INADEQUATE FUNCTIONALITY EVALUATIONS FOR A DEGRADED UNIT 1 BORIC ACID STORAGE TANK BLADDER |  | P.2(b) Implementing Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | A finding of very low safety significance was self revealed when licensee personnel performed inadequate functionality evaluations after previously identifying that the Unit 1 Boric Acid Storage Tank (BAST) bladder was degraded. The licensee entered this
Region: III | Braidwood | 5955 | 06/30/2013 08/14/2013 | 2013003-04 | NRC | NCV | MISC | Green | INADEQUATE CONTROL OF A SPECIAL LIFTING DEVICE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to adhere to design requirements specified for a special lifting devic
Region: III | Braidwood | 5956 | 06/30/2013 08/14/2013 | 2013003-05 | NRC | NCV | Mitigating Systems | Green | INADVERTENT REMOVAL OF THE DESIGN BASIS REQUIREMENT TO COMMENCE A COOLDOWN WITHIN TWO HOURS FOLLOWING THE ESTABLISHMENT OF NATURAL CIRCULATION CONDITIONS AND LOSS OF AIR TO CONTAINMENT |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to maintain the procedural requirement to commence a r
Region: III | Braidwood | 5957 | 06/30/2013 08/14/2013 | 2013003-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ACCOUNT FOR PZR PORV ACCUMULATOR LEAKAGE DURING HOT STANDBY AND SUBSEQUENT COOLDOWN PERIOD FOLLOWING A POSTULATED EARTHQUAKE |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to account for PZR PORV accumulator air system leakage
Region: III | Braidwood | 5940 | 03/31/2013 05/09/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH AN ADEQUATE QUALITY INSTRUCTION FOR DETERMINING PRESSURIZER POWER OPERATED RELIEF VALVE OPERABILITY |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to account for pressurizer (PZR) power operated relief valve (PORV)
Region: III | Braidwood | 5938 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | NCVIV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE 10 CFR 50.59 EVALUATION REMOVING THE POSITIVE DISPLACEMENT PUMP FROM THE CURRENT LICENSING BASIS |  |  | TE?: Y SL-IV-NCVIV | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV NCV of 10 CFR 50.59 when licensee personnel failed to perform an adequate 10 CFR 50.59 safety evaluation that revised the Updated Final Safety
Region: III | Braidwood | 5939 | 03/31/2013 05/09/2013 | 2013002-03 | NRC | FIN | Mitigating Systems | Green | POSITIVE DISPLACEMENT PUMPS NOT AVAILABLE TO PERFORM THEIR MITIGATING FUNCTIONS ASSOCIATED WITH BOTH NORMAL AND ABNORMAL OPERATIONS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV NCV of 10 CFR 50.59 when licensee personnel failed to perform an adequate 10 CFR 50.59 safety evaluation that revised the Updated Final Safety
Region: III | Braidwood | 5651 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN WATERTIGHT DOOR SAFETY FUNCTION AFTER ROUTINE PASSAGE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee's Plant Barrier Impairment (PBI) control program perm
Region: III | Braidwood | 5652 | 12/31/2012 02/07/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PBI ALLOWANCE FOR ONE EDG DOST WATERTIGHT DOOR INOPERABLE |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to recognize that when one of the two Un
Region: III | Braidwood | 5653 | 12/31/2012 02/07/2013 | 2012005-03 | NRC | FIN | Mitigating Systems | Green | INADEQUATE FUNCTIONALITY EVALUATION OF BLOCK WALLS FOR HIGH ENERGY LINE BREAK LOADS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to perform an adequate technical review to determine the operability of auxiliary building safety-related block walls affected by High Energy Line B
Region: III | Braidwood | 5926 | 12/31/2012 02/07/2013 | 2012005-04 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE WORK INSTRUCTIONS FOR ENSURING 2A EDG JACKET WATER HEAT EXCHANGER GASKET COMPRESSION |  | P.2(b) Implementing Operating Experience | TE?: N | 05000457 Braidwood 2 |  | 71111.22 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when on October 23, 2012, the 2A EDG lower jacket water cooler developed a leak
Region: III | Braidwood | 5624 | 09/30/2012 11/08/2012 | 2012004-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO ADEQUATELY EVALUATE OPERATION CREW PERFORMANCE FOR A REACTOR TRIP AND FAILURE TO ADEQUATELY EVALUATE EMERGENCY OPERATING PROCEDURE STANDARDS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to implement a Caution Note in Emergency Operating Procedure (EOP) 2BwEP ES-0.1, "Reactor Trip Response," during a July 30, 2009, Unit 2 reactor tri
Region: III | Braidwood | 5636 | 09/30/2012 11/08/2012 | 2012004-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO ADEQUATELY EVALUATE THE SPECIFIED TS CST FUNCTION AFTER THE IDENTIFICATION OF A NON-CONFORMING CONDITION ADVERSELY EFFECTING SG PORV FLOW RATES |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to adhere to Corrective Action and Operability Determination Program standards after identifying a non conforming condition associated with reduced
Region: III | Braidwood | 5637 | 09/30/2012 11/08/2012 | 2012004-03 | NRC | VIO | Barrier Integrity | Green | FAILURE TO ANALYZE RECYCLE HOLDUP TANK INLET PIPING LOADS |  | P.1(d) Implementation of Corrective Actions | TE?: Y SL-IV-VIO | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated cited violation (VIO) of 10 CFR 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to evaluate the effect of dynamic loads on inlet
Region: III | Braidwood | 5641 | 09/30/2012 11/08/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TRAIN FIRE BRIGADE MEMBERS ON THE USE OF ELEVATORS |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Braidwood Operating License Condition 2.E, "Fire Protection Program," when licensee personnel failed to ensure that fire brigade members retained knowledg
Region: III | Braidwood | 5617 | 08/24/2012 09/24/2012 | 2012008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Install Foam-Water Sprinklers In Accordance With Sprinkler Standard |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance associated with cited violation of License Condition 2.E for the licensee's failure to implement the approved Fire Protection Program by failing to install foam-water sprinklers in accord
Region: III | Braidwood | 5618 | 08/24/2012 09/24/2012 | 2012008-01 | NRC | FIN | Mitigating Systems | Green | Failure to Properly Address Fire Brigade Performance Deficiencies |  | H.4(a) Human Error Prevention | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance for the licensee's failure to properly address fire brigade drill performance deficiencies identified after completion of an unannounced fire drill. Specifically, the licensee failed to a
Region: III | Braidwood | 5605 | 06/30/2012 08/09/2012 | 2012003-01 | NRC | FIN | Initiating Events | Green | FAILURE TO IMPLEMENT ABNORMAL OPERATING PROCEDURES WHEN ENTRY CONDITIONS WERE PRESENT |  | H.2(d) Facilities & Equipment | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to implement adverse weather Abnormal Operating Procedures (AOPs) when entry conditions were present. Specifically, the site was not aware of a seve
Region: III | Braidwood | 5606 | 06/30/2012 08/09/2012 | 2012003-02 | NRC | NCV | Initiating Events | Green | STEAM GENERATOR PRIMARY MANWAY BOLTS EXAMINED WITH UNQUALIFIED PROCEDURE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 |  | 71111.08P | A finding of very low safety significance (Green) and an associated NCV of 10 CFR 50.55a(g)4 was identified by the inspectors when licensee personnel failed to establish an ultrasonic test (UT) examination procedure for steam generator primary manway bolt
Region: III | Braidwood | 5607 | 06/30/2012 08/09/2012 | 2012003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO ACCOMPLISH CORRECTIVE ACTIONS FOLLOWING IDENTIFIED BORIC ACID LEAKAGE ON REACTOR HEAD PENETRATION NO. 77 |  | H.3(a) Work Planning | TE?: N | 05000456 Braidwood 1 |  | 71111.08P | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors when licensee personnel failed to accomplish corrective actions following identifie
Region: III | Braidwood | 5608 | 06/30/2012 08/09/2012 | 2012003-04 | NRC | FIN | Mitigating Systems | Green | OPERABILITY DETERMINATION STANDARDS NOT FOLLOWED FOR HELB RELATED STRUCTURAL ISSUES IDENTIFIED BY THE NRC |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to follow the Operability Determination process after identifying potential safety related structural loading issues created by a postulated turbine
Region: III | Braidwood | 5616 | 06/29/2012 08/08/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW CORRECTIVE ACTION PROGRAM PROCEDURE |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to initiate IRs in accordance with the C
Region: III | Braidwood | 5612 | 06/29/2012 08/08/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | NON-CONFORMING PIPING CONDITION NOT CORRECTED |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 |  | 71152B | A finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors when a non-conforming condition previously identified by the NRC was not corrected. Spec
Region: III | Braidwood | 5613 | 06/29/2012 08/08/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | SURVEILLANCE PROCEDURE NOT FOLLOWIED |  | H.4(b) Procedural Compliance | TE?: N | 05000456 Braidwood 1 |  | 71152B | A finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when licensee personnel failed to adhere to Surveillance Procedure Bw
Region: III | Braidwood | 5615 | 06/29/2012 08/08/2012 | 2012007-04 | NRC | FIN | Initiating Events | Green | UNTIMELY COMPLETION OF A CORRECTIVE ACTION TO PREVENT RECURRENCE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | A finding of very low safety significance (Green) was identified by the inspectors when licensee personnel failed to follow procedure LS-AA-125-1001, "Root Cause Analysis Manual," Attachment 12, in the implementation of corrective actions to prevent recur
Region: III | Braidwood | 5594 | 03/31/2012 05/08/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN APPROVED FIRE PROTECTION PROGRAM REGARDING SAFE SHUTDOWN FIRE DAMPER QUALIFICATION |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated NCV of License Condition 2.E when licensee personnel failed to adequately maintain the approved fire protection program after receiving information that adversely affect
Region: III | Braidwood | 5599 | 03/31/2012 05/08/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT CONDITIONS ADVERSE TO QUALITY |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," when licensee personnel failed to promptly correct conditions adverse to quality. Specifically, fr
Region: III | Braidwood | 5600 | 03/31/2012 05/08/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO SCOPE SAFETY-RELATED HELB BARRIERS INTO THE MAINTENANCE RULE |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(1), 10 CFR 50.65(a)(2), and 10 CFR 50.65(b) when licensee personnel failed to scope numerous high energy line break (HELB) hazard barrier dampers
Region: III | Braidwood | 5601 | 03/31/2012 05/08/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | INCORRECT CLASSIFICATION OF ENVIRONMENTAL QUALIFICATION ZONES |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.49(e) when licensee personnel failed to correctly classify the EDGs, essential switchgear (ESG), and MEERs containing electrical equipment important to
Region: III | Braidwood | 5564 | 12/31/2011 02/10/2012 | 2011005-01 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO MAINTAIN ADEQUATE CIRCULATING WATER BLOWDOWN PROCEDURE DURING LIQUID RADIOLOGICAL RELEASES |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification 5.4.1, "Procedures," when licensee personnel failed to adequately maintain procedure BwOP CW-12, "Circulating Water Blowdown System Fill,
Region: III | Braidwood | 5565 | 12/31/2011 02/10/2012 | 2011005-02 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO EVALUATE EMERGENCY COMMUNICATION SYSTEM PERFORMANCE AGAINST MAINTENANCE RULE CRITERIA |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(1) when licensee personnel failed to adequately monitor the performance of nonsafety related systems and components that exceeded performance crit
Region: III | Braidwood | 5569 | 12/31/2011 02/10/2012 | 2011005-04 | NRC | FIN | Mitigating Systems | Green | OPERAILITY EVALUATION NOT PERFORMED IN ACCORDANCE WITH STATION STANDARDS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance when licensee personnel failed to adhere to Operability Determination Process standards after identifying a non-conservative assumption related to closure times for hazard barrier dampers
Region: III | Braidwood | 5591 | 12/31/2011 02/10/2012 | 2011005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW AND ESTABLISH ADEQUATE HAZARD BARRIER IMPAIRMENT PROCEDURES |  | P.2(b) Implementing Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when the licensee's process for the control of
Region: III | Braidwood | 5579 | 12/31/2011 02/10/2012 | 2011005-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO ADHERE TO MAINTENANCE RULE IMPLEMENTATION PROCEDURES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance when licensee personnel failed to adhere to licensee procedure ER AA 310, "Implementation of the Maintenance Rule." Specifically, procedural requirements for the use of operator restorati
Region: III | Braidwood | 5538 | 09/30/2011 11/09/2011 | 2011004-01 | NRC | FIN | Initiating Events | Green | FAILURE TO ADHERE TO STANDARDS OF OUTDOOR SECURED MATERIAL ZONES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance when licensee personnel failed to adhere to station housekeeping procedures to ensure materials that could become missile hazards during high winds or tornado conditions were not stored i
Region: III | Braidwood | 5539 | 09/30/2011 11/09/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONTROL HIGH ENERGY LINE BREAK BARRIER DOORS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to ensure that Unit 1 and Unit 2 boundary doors credited as shut in de
Region: III | Braidwood | 5551 | 09/30/2011 11/09/2011 | 2011004-05 | Self - Revealed | NCV | Mitigating Systems | Green | ASIATIC CLAMS IDENTIFIED IN THE ESSENTIAL SERVICE WATER SYSTEM SUPPLY TO THE AUXILIARY FEEDWATER SYSTEM |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000457 Braidwood 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of TS 3.7.5, "Auxiliary Feedwater (AF) System," was self-revealed when, on various occasions between March and July 2011, asiatic clam shells were identified in the 2A AF essential service wa
Region: III | Braidwood | 5553 | 09/30/2011 11/09/2011 | 2011004-07 | NRC | FIN | Mitigating Systems | Green | MODIFICATION OF THE AUXILIARY FEEDWATER SYSTEM WITHOUT PRIOR NRC APPROVAL |  | P.2(b) Implementing Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance when licensee personnel failed to obtain a license amendment prior to implementing a proposed change to the plant that resulted in a more than minimal increase in the likelihood of occurr
Region: III | Braidwood | 5557 | 09/30/2011 11/09/2011 | 2011004-08 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW MAINTENANCE RULE PROCEDURE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to adhere to licensee procedure ER AA 310, "Impl
Region: III | Braidwood | 5558 | 09/30/2011 11/09/2011 | 2011004-09 | NRC | NCV | Mitigating Systems | Green | DESIGN OF AUXILIARY FEEDWATER SYSTEM INCLUDED VOIDS IN SAFETY-RELATED ALTERNATE SUCTION FLOWPATHS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to properly analyze the configuration of the SX connections to
Region: III | Braidwood | 5559 | 09/30/2011 10/28/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Embedment Plate Design Deficiencies |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to properly evaluate the structural steel embedment plate which
Region: III | Braidwood | 5563 | 09/30/2011 10/28/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Permanent Lead Shielding Added to Safety Injection and Chemical Volume and Control System Piping. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to properly evaluate the Unit 1 SI subsystem 1SI06 and the Unit
Region: III | Braidwood | 5521 | 06/30/2011 08/09/2011 | 2011003-01 | NRC | FIN | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURAL STANDARDS RELATED TO THE STORAGE OF OUTSIDE MATERIAL THAT COULD IMPACT OFSITE POWER AVAILABILITY |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance when licensee personnel failed to adhere to housekeeping and severe weather abnormal operating procedures to ensure specified materials were not stored in the vicinity of the station offs
Region: III | Braidwood | 5526 | 06/30/2011 08/09/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | STRUCTURAL STEEL BEAM MISSING FIRE PROOFING MATERIALS |  |  | TE?: N | 05000456 Braidwood 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated NCV of Braidwood Operating License Condition 2.E when licensee personnel failed to fireproof a structural steel beam to achieve a required 3 hour fire rating. Specifical
Region: III | Braidwood | 5527 | 06/30/2011 08/09/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM POST VT-3 EXAMINATION ILLUMINATION VERIFICATION IN ACCORDANCE WITH ASME CODE |  | H.4(b) Procedural Compliance | TE?: N | 05000457 Braidwood 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.55a(g)4 when a licensee vendor examiner failed to perform VT 3 visual examinations in accordance with the American Society of Mechanical Engineers (ASME
Region: III | Braidwood | 5528 | 06/30/2011 08/09/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT THE DESIGN OF THE AUXILIARY FEEDWATER SUCTION PIPING WAS ADEQUATE TO PREVENT AIR ENTRAINMENT FOLLOWING A SEISMIC OR TORNADO EVENT |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to analyze whether the design of the auxiliary feedwater (AF) system e
Region: III | Braidwood | 5533 | 06/30/2011 08/09/2011 | 2011003-07 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE DURING REACTOR VESSEL HEAD LIFT |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000457 Braidwood 2 |  | 71111.19 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1 was self revealed on April 21, 2011, when licensee personnel failed to suspend a reactor vessel head lift after it became apparent that there was a large
Region: III | Braidwood | 5534 | 06/30/2011 08/09/2011 | 2011003-08 | NRC | NCV | Mitigating Systems | Green | INADEQUATE QUALITY REVIEW OF TEMPORARY CONSTRUCTED SCAFFOLDS INSTALLED THROUGHOUT THE PLANT |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," related to an inadequate quality review of temporarily constructed scaffolds in
Region: III | Braidwood | 5535 | 06/30/2011 08/09/2011 | 2011003-09 | Self - Revealed | NCV | Mitigating Systems | Green | INCORRECT EQUIPMENT USED DURING AN AUXILIARY FEEDWATER SUCTION PIPING FLUSH SURVEILLANCE |  | H.4(a) Human Error Prevention | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when incorrect equipment was used during an AF suction piping flush surveillance. Speci
Region: III | Braidwood | 5509 | 05/04/2011 06/16/2011 | 2011012-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Document and Justify Continued Operability of the Auxiliary Feedwater System. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 93812 | A finding of very low safety significance was identified at the Braidwood and Byron Stations by the inspectors when licensee personnel failed to adequately document and justify continued operability of the auxiliary feedwater (AF) system. Specifically, li
Region: III | Braidwood | 5510 | 05/04/2011 06/16/2011 | 2011012-03 | Self - Revealed | FIN | Mitigating Systems | Green | Incorrect Installation of Annunciator System Wiring. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 93812 | A finding of very low safety significance was self-revealed at Braidwood Station when licensee personnel failed to properly install portions of the annunciator system circuitry in accordance with design specifications. Specifically, wiring in the annuncia
Region: III | Braidwood | 5511 | 05/04/2011 06/16/2011 | 2011012-04 | NRC | NCV | Emergency Preparedness | Green | Untimely Declaration of a Notice of Unusual Event |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 93812 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR 50.54(q) at Braidwood Station after licensee personnel failed to promptly declare a Notice of Unusual Event in accordance with the
Region: III | Braidwood | 5505 | 03/31/2011 05/02/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ACCOUNT FOR VORTEXING WHEN CALCULATING THE MAXIMUM AVAILABLE TIME TO SECURE THE CONTAINMENT SPRAY ADDITIVE TANK |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having a very low safety significance (Green) for the failure to account for vortexing when determining the maximum available time to secure th
Region: III | Braidwood | 5506 | 03/31/2011 05/02/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE INSTRUCTIONS FOR MEASURING ECCS VOIDS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | A finding of very low safety significance and associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to establish instructions for me
Region: III | Braidwood | 5507 | 03/31/2011 05/02/2011 | 2011002-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO EVALUATE THE EFFECTS OF DYNAMIC LOADS AT THE CONTAINMENT SPRAY DISCHARGE PIPING |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | The inspectors identified a Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having a very low safety significance (Green) for the failure to evaluate the effects of dynamic loads at the containment spray discharge pipin
Region: III | Braidwood | 5497 | 02/10/2011 02/28/2011 | 2010503-02 | NRC | FIN | Emergency Preparedness | Green | Changes Made to EAL Basis that Decreased the Effectiveness (1EP4.1) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71114.04 | A Green finding involving a Severity Level IV, Cited Violation of 10 CFR 50.54(q) was identified by the inspector for the licensee's change to the emergency plan which decreased the effectiveness of the plan without NRC approval. Specifically, the license
Region: III | Braidwood | 5484 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | DEGRADED FIRE SEAL BETWEEN TWO FIRE ZONES |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000457 Braidwood 2 |  | 71111.05Q | A finding of very low safety significance and an associated NCV of License Condition 2.E was identified by the inspectors when licensee personnel failed to maintain a fire seal between Unit 2 Fire Zone 11.6 2 on the 426 elevation and Unit 2 Fire Zone 11.5
Region: III | Braidwood | 5485 | 12/31/2010 02/08/2011 | 2010005-03 | NRC | FIN | Initiating Events | Green | INADEQUATE EVALUATION OF OPERATING EXPERIENCE CONTRIBUTES TO A UNIT 2 REACTOR TRIP |  |  | TE?: N | 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance was identified by the inspectors when licensee personnel failed to adequately utilize operating experience that ultimately contributed to an August 16, 2010, Unit 2 reactor trip. Specifically, the licensee did not
Region: III | Braidwood | 5452 | 09/30/2010 11/05/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES FOR TEMPORARY SCAFFOLDS |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.18 | The inspectors identified a Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," related to the control of temporary scaffolds. Specifically, the licensee's procedure for
Region: III | Braidwood | 5453 | 09/30/2010 11/05/2010 | 2010004-03 | Self - Revealed | NCV | Mitigating Systems | Green | UNPLANNED COOLING WATER FLOW REDUCTION DURING SX IST SURVEILLANCE TEST |  | H.4(a) Human Error Prevention | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.22 | A self-revealed Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified after the licensee failed to follow procedures during an essential service water inser
Region: III | Braidwood | 5462 | 09/30/2010 11/12/2010 | 2010010-01 | NRC | NCV | Mitigating Systems | Green | FOREBAY INSPECT-AND-CLEAN ACTIVITIES DID NOT ENSURE THAT SSCs WILL BE CAPABLE OF ERFORMING THEIR SAFETY FUNCTION |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 93812 | The inspectors identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish adequate controls to ensure that forebay inspect-and-clean a
Region: III | Braidwood | 5463 | 09/30/2010 11/12/2010 | 2010010-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO REPLACE LOW MARGIN FUSES IN MCC131X1 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000456 Braidwood 1 |  | 93812 | A self-revealed finding of very low safety significance and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to establish measures for the selection and review for suitability
Region: III | Braidwood | 5473 | 09/30/2010 11/12/2010 | 2010010-03 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO IDENTIFY AND CORRECT WATER DISCHARGED TO THE TURBINE BUILDING FLOOR DURING CONDENSATE REJECT |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 93812 | A self-revealed finding of very low safety significance (Green) was identified for the failure to correct a condition that resulted in water being discharged to the turbine building floor during the reject of condensate from the condenser hotwell. Specifi
Region: III | Braidwood | 5474 | 09/30/2010 11/12/2010 | 2010010-04 | Self - Revealed | FIN | Initiating Events | Green | EVALUATION OF OPERATING EXPERIENCE CONCERNING REACTOR BUILDING FLASHING |  |  | TE?: N | 05000456 Braidwood 1 |  | 93812 | A self-revealed finding of very low safety significance was identified for the inadequate evaluation of operating experience done in accordance with the station procedure. Specifically, the licensee evaluated an event at another plant where building mater
Region: III | Braidwood | 5456 | 09/17/2010 10/27/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Operability Determination Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a Green finding and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to adhere to Operability Determination Procedure OP AA 108-115 after identifyin
Region: III | Braidwood | 5461 | 09/17/2010 10/27/2010 | 2010006-02 | NRC | NCV | Barrier Integrity | Green | Untimely Corrective Action for Lack of Water Hammer Analysis on the Recycle Hodup tank. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a Green finding and an associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when licensee personnel failed to promptly correct a previously identified NCV regarding the lack of analysis for water hammer lo
Region: III | Braidwood | 5446 | 06/30/2010 07/29/2010 | 2010003-02 | Self - Revealed | FIN | Initiating Events | Green | UNIT 2 LOSS OF OFFSITE POWER COINCIDENT WITH A REACTOR TRIP DUE TO LOSS OF 2C REACTOR COOLANT PUMP |  |  | TE?: N | 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance was self-revealed on July 30, 2009, after the Unit 2 reactor tripped due to a trip of the 2C reactor coolant pump on overcurrent. The 2C reactor coolant pump tripped on overcurrent following an automatic bus trans
Region: III | Braidwood | 5433 | 04/02/2010 05/06/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | DDAFW Pump Battery Racks were not restored to their Design Basis Seismic Category I |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to restore the Diesel Driven Auxiliary Feedwater (DDAFW) battery racks to their design basis qu
Region: III | Braidwood | 5434 | 04/02/2010 05/06/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Lack of Calculation for the DDAFW Minimum Fuel oil Tank Setpoint Level |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance related to the licensee's failure to develop a calculation for the DDAFW pump minimum fuel oil tank level setpoint. Specif
Region: III | Braidwood | 5435 | 04/02/2010 05/06/2010 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Potential Clogging of Essential Service Water (SX) Throttle Valves for Pump Room Coolers |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for the licensee's failure to include appropriate quantitative or qualitative acceptance criteria fo
Region: III | Braidwood | 5436 | 04/02/2010 05/06/2010 | 2010007-04 | NRC | NCV | Mitigating Systems | Green | Adverse Impact of Flood Drain Strainer Design Modification on Flooding Analysis |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to fully verify the adequacy of a design modification important to safety. Specifically, the li
Region: III | Braidwood | 5444 | 04/02/2010 05/06/2010 | 2010007-05 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Acceptance Criteria for CS Pump Performance Testing |  | P.2(b) Implementing Operating Experience | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance for the licensee's failure to ensure adequate acceptance limits were incorporated into test procedures. Specifically, the lic
Region: III | Braidwood | 5445 | 04/02/2010 05/06/2010 | 2010007-06 | NRC | NCV | Mitigating Systems | Green | EDGs Fuel Oil Consumption Calculation Failed to Account for Frequency Variations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to translate the allowable frequency variations, for the emergency diesel generators (EDGs), in
Region: III | Braidwood | 5098 | 03/31/2010 05/14/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY A CONDITION ADVERSE TO QUALITY |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000457 Braidwood 2 |  | 71111.15 | The NRC identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a Condition Adverse to Quality associated with t
Region: III | Braidwood | 5103 | 03/31/2010 05/14/2010 | 2010002-03 | Self - Revealed | NCV | Barrier Integrity | Green | PERFORMANCE OF TROUBLESHOOTING LEADS TO AUXILIARY BUILDING VENTILATION FAN FIRE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Procedures," was self-revealed when, on January 9, 2010, auxiliary building ventilation fan 0VA01CC caught fire, resulting in the decla
Region: III | Braidwood | 5104 | 03/31/2010 05/14/2010 | 2010002-04 | NRC | NCV | Mitigating Systems | Green | DIESEL OIL STORAGE TANK ROOM SPRINKLER OBSTRUCTIONS |  |  | TE?: N | 05000457 Braidwood 2 |  | 71153 | A finding of very low safety-significance and an associated Non-Cited Violation of Unit 2 License Condition 2.E was identified by the inspectors for the licensee's failure to provide foam sprinklers in the 2B diesel oil storage tank room that were free of
Region: III | Braidwood | 5088 | 12/31/2009 02/03/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH 2 TO 1 WELD PROFILE ON AF CROSS-TIE DRAIN LINE SOCKET WELDS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000457 Braidwood 2 |  | 71111.08P | ed Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to follow work order instructions and establish a 2-to-1 weld profile on the auxiliary feedwater system cross-tie pipe drain line socket welds. Licensee correcti
Region: III | Braidwood | 5089 | 12/31/2009 02/03/2010 | 2009005-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES DURING RESTORATION OF 2SX173 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000457 Braidwood 2 |  | 71111.15 | A Green finding and an associated Non-Cited Violation of Technical Specification 5.4.1 was self-revealed for the failure to follow procedures during the restoration of the essential service water supply valve to the engine driven cooling water pump for th
Region: III | Braidwood | 5094 | 12/31/2009 02/03/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW MAINTENANCE PROCEDURES AND WORK INSTRUCTIONS |  | H.3(b) Work Activity Coordination | TE?: N | 05000457 Braidwood 2 |  | 71111.19 | The inspectors identified a Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," related to post maintenance testing. Specifically, the licensee failed to follow maintena
Region: III | Braidwood | 5097 | 12/31/2009 02/03/2010 | 2009005-08 | NRC | NCV | Initiating Events | Green | FAILURE TO FULLY IMPLEMENT ABNORMAL OPERATING PROCEDURES FOLLOWING A SEISMIC EVENT |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | The inspectors identified a Green finding and an associated Non-Cited Violation of Technical Specification 5.4.1 for the failure to fully implement an abnormal procedure following a seismic event. Specifically, on April 18, 2008, following a seismic event
Region: III | Braidwood | 5081 | 09/30/2009 11/13/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE CONTINUOUS MONITORING OF A FIRE DOOR |  | H.4(b) Procedural Compliance | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | tection Program," for the licensee's failure to take adequate compensatory measures following the failure of electronic supervision of a fire door. Specifically, when continuous electronic supervision of a fire door in an area with gaseous fire suppressio
Region: III | Braidwood | 5082 | 09/30/2009 11/13/2009 | 2009004-02 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE OF FIRE PROTECTION VALVE STROKE PROCEDURE RESULTS IN TRIP OF B TRAIN OF MAIN CONTROL ROOM VENTILATION |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | A NCV of 10 CFR 50, Appendix B, Criterion V, was self-revealed on September 22, 2009, when performance of a fire protection valve stroke procedure resulted in a trip of the B Train of the Main Control Room Ventilation System. Specifically, conflicting pro
Region: III | Braidwood | 5083 | 09/30/2009 11/13/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE OF THE LICENSEE'S STAFF TO PROPERLY MANAGE ON-LINE RISK ASSOCIATED WITH TESTING OF THE 2A AUXILIARY FEEDWATER PUMP SLAVE RELAYS |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.13 | The inspectors identified a NCV of 10 CFR Part 50.65 (a)(4), due to the licensee's failure to properly assess and manage the risk associated with scheduled slave relay testing for the 2A Auxiliary Feedwater (AF) system. Specifically, the licensee declared
Region: III | Braidwood | 5069 | 06/30/2009 08/14/2009 | 2009003-01 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO CONTROL AND SECURE MATERIAL ADJACENT TO UNIT 1 TRANSFORMER YARD WHICH COULD BECOME POTENTIAL MISSILES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000456 Braidwood 1 |  | 71111.01 | The inspector identified a Green finding associated with the failure to control or remove material adjacent to the Unit 1 main power transformers, station auxiliary transformers and unit auxiliary transformers. Plant personnel failed to identify these dis
Region: III | Braidwood | 5070 | 06/30/2009 08/14/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | ISOLATION OF LOWER CABLE SPREADING ROOM CARBON DIOXIDE FIRE SUPPRESSION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | A Non-Cited Violation of License Condition 2.E, "Fire Protection Program," was self-revealed when the automatic carbon dioxide (CO2) fire suppression system was isolated from the Unit 1 and Unit 2 Lower Cable Spreading Rooms from July 23, 2007, through Au
Region: III | Braidwood | 5072 | 06/30/2009 08/14/2009 | 2009003-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY EVALUATE INSTALLATION OF ECCS THROTTLE VALVES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | A NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for failure to install a modified Emergency Core Cooling System throttle valve design commensurate with the design control measures applicable to the origina
Region: III | Braidwood | 5073 | 06/30/2009 08/14/2009 | 2009003-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY IDENTIFY BRYOZOA INFESTATION CAUSED 2A SX SUBSYSTEM TO BE INOPERABLE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000457 Braidwood 2 |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action Program," associated with the licensee's failure to promptly identify that the 2A Essential Service Water (SX) subsystem was inoperable and hence, entry into
Region: III | Braidwood | 5080 | 06/30/2009 08/14/2009 | 2009003-07 | NRC | NCV | Mitigating Systems | Green | BRYOZOAN INFESTATION AT THE LAKE SCREENHOUSE CIRCULATING WATER FOREBAYS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action Program," having very low safety significance, associated with the licensee's failure to identify a significant condition adverse to quality and to develop correct
Region: III | Braidwood | 5067 | 03/31/2009 05/13/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | SAFETY INJECTION PIPE SUPPORT DEFICIENCIES |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000457 Braidwood 2 |  | NONE | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to properly evaluate the addition of lead shielding to Unit 2 safet
Region: III | Braidwood | 5068 | 03/31/2009 05/13/2009 | 2009002-02 | Self - Revealed | FIN | Initiating Events | Green | REACTOR TRIP ON UNIT AUXILIARY TRANSFORMER 241-1 SUDDEN PRESSURE RELAY ACTUATION DUE TO 2C HEATER DRAIN PUMP MOTOR ELECTRICAL FAULT |  |  | TE?: N | 05000457 Braidwood 2 |  | 71153 | A Green finding was self-revealed on December 27, 2008, when excessively long motor leads caused a phase to phase overcurrent trip of the 2C heater drain pump and subsequent Unit 2 reactor trip. Specifically, adequate procedural guidance on re terminating
Region: III | Braidwood | 5064 | 03/06/2009 03/19/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Effective Corrective actions to Maintain Capability of foam Suppression Systems |  |  | TE?: N | 05000457 Braidwood 2 |  | 71111.05T | A finding of very low safety significance and associated NRC of License Condition 2.E was identified by the inspectors for the licensee's failure to promptly correct an item adverse to quality. Specifically, although there was evidence of leakage from the
Region: III | Braidwood | 5066 | 03/06/2009 03/19/2009 | 2009006-03 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Validation for Safe Shutdown Manual Actions |  |  | TE?: N | 05000456 Braidwood 1 |  | 71111.05T | A finding of very low safety significance was identified by the inspectors for the failure to perform a validation of added safe shutdown manual actions. The failure to perform a validation resulted in less than adequate emergency lighting for the safe sh
Region: III | Braidwood | 5055 | 12/31/2008 02/09/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of High Pressure Gas Cylinders |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.04Q | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified by the inspectors for the failure to properly control high pressure gas cylinders in proximity to
Region: III | Braidwood | 5056 | 12/31/2008 02/09/2009 | 2008005-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Action for Failure to Promptly Correct Auxiliary Tunnel Feedwater tunnel Hatch Cover Design Deficiencies |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for failure to promptly identify and correct the auxiliary feedwater tun
Region: III | Braidwood | 5057 | 12/31/2008 02/09/2009 | 2008005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Containment Spray Add Tank Drain Drain Valve |  | H.4(a) Human Error Prevention | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.15 | A Green finding and associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, was self-revealed when leak-by of valve 2CS023 led to a 100 gallon sodium hydroxide (NaOH) spill that leaked into the 2A RH pump room and rendered the 2A RH pump u
Region: III | Braidwood | 5058 | 12/31/2008 02/09/2009 | 2008005-05 | NRC | NCV | Barrier Integrity | Green | Failure to Analyze Inlet Piping Loads and Establish an Adequate HUT Quench Volume |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance, associated with the licensee's failure to analyze and establish an adequate quench volume within the boron recycle system
Region: III | Braidwood | 5052 | 10/24/2008 12/04/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Failure to take timely corrective action for a previously identified NRC violation. |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, for failure to take timely corrective actions to address a previously issued NCV regarding the substitution of manual actions for automatic actions on the A train auxiliary fee
Region: III | Braidwood | 5048 | 09/30/2008 11/14/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | FAILURE TO COMPLY WITH THE SPACING STANDARD FOR SPRINKLER SYSTEMS IN ACCORDANCE WITH THE LICENSEE FIRE PROTECTION PROGRAM REQUIREMENTS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | A finding of very low safety significance and associated NCV of Braidwood's License Condition 2.E was identified by the inspectors for failure to comply with the spacing standard for sprinkler systems in accordance with the licensee Fire Protection Progra
Region: III | Braidwood | 5043 | 06/30/2008 08/13/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PROPERLY IMPLEMENT MATERIAL CONTROL PROCEDURES |  | H.4(b) Procedural Compliance | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.01 | The inspectors identified a performance deficiency involving a NCV of Technical Specifications 5.4.1, related to the unauthorized and improper storage of loose material in the designated material exclusion area around the Unit 1 and Unit 2 transformers. T
Region: III | Braidwood | 5044 | 06/30/2008 08/13/2008 | 2008003-02 | NRC | NCV | Initiating Events | Green | INADEQUATE PROCEDURE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a performance deficiency involving a NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," related to a plant barrier impairment (PBI) procedure.
Region: III | Braidwood | 5046 | 06/30/2008 08/13/2008 | 2008003-04 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO SAMPLE A TEMPORARY TANK AT THE REQUIRED PERIODICITY |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | A finding of very low safety significance and associated NCV of the Technical Requirements Manual, Appendix L, and Technical Specifications 5.4.1(a) were identified by the inspectors. On May 1, 2008, the inspectors identified that the licensee had failed
Region: III | Braidwood | 5047 | 06/30/2008 08/13/2008 | 2008003-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONTROL LABELING ON BOTH UNITS CONTROL PANELS AND SIMULATOR |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | The inspectors identified a performance deficiency involving a NCV of Technical Specifications 5.4.1, for the licensee's failure to provide procedural controls for the unique identification of Regulatory Guide 1.97 post accident instrumentation to aid the
Region: III | Braidwood | 5041 | 05/15/2008 05/15/2008 | 2008002-01 | NRC | NCV | Barrier Integrity | Green | INADEQUATE ACCEPTANCE CRITERIA ESTABLISHED IN TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENT |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.22 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, Instructions Procedures and Drawings was identified by the inspectors for the licensee's failure to establish adequate acceptance criteria
Region: III | Braidwood | 4988 | 03/28/2008 04/23/2008 | 2008006-01 | NRC | NCV | Barrier Integrity | Green | This is a security Related Finding - see inspection report for details. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02-
Region: III | Braidwood | 4989 | 03/28/2008 04/23/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | This is a security Related Finding - see inspection report for details. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02
Region: III | Braidwood | 5039 | 12/31/2007 02/01/2008 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN EVALUATION ON A BOLTED CONNECTION |  | H.4(b) Procedural Compliance | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.08P | The inspectors identified a Non-Cited Violation of 10 CFR 50.55a(a)(3)(i) for failure to apply an approved alternative to the American Society of Mechanical Engineers Code to evaluate susceptibility of bolting corrosion and the potential for failure after
Region: III | Braidwood | 5038 | 09/30/2007 11/13/2007 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Meet TRM Requirements for Spent Fuel Building Crane Interlocks and Physical Stops (1R20) |  | H.4(b) Procedural Compliance | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | NONE | A finding of very low safety significance and associated Non-Cited Violation of Technical Specification 5.4.1 was identified by the inspectors for failure to have and follow procedures, which met the surveillance requirements of Technical Requirements Man
Region: III | Braidwood | 5031 | 08/24/2007 10/05/2007 | 2007009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate test control for safety-related heat exchangers |  | P.3(a) Self-Assessment | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," related to the failure to establish a formal heat exchanger testing program capable of identifying an unacc
Region: III | Braidwood | 5032 | 08/24/2007 10/05/2007 | 2007009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate safety-related heat exchanger examination procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a finding of very low safety significance involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with regard to the licensee's heat exchanger examination procedure. S
Region: III | Braidwood | 5033 | 08/24/2007 10/05/2007 | 2007009-03 | NRC | NCV | Mitigating Systems | Green | Failure to take corrective action |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very low safety significance. Specifically, the inspectors determined that the licensee failed to identify that operability of the AF
Region: III | Braidwood | 5028 | 06/30/2007 07/26/2007 | 2007004-01 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO IMPLEMENT A RADIATION PROTECTION PROGRAM COMMENSURATE WITH THE EXTENT OF PLANT RADIOLOGICAL HAZARDS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance and an associated NCV of 10 CFR 20.1101(a) was identified by the inspectors for the licensee's failure to implement a radiation protection program commensurate with licensed activities and the ongoing radiological
Region: III | Braidwood | 5029 | 06/30/2007 07/26/2007 | 2007004-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO POST AREAS THAT CONTAIN RADIOACTIVE MATERIAL |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71153 | A finding of very low safety significance and an associated NCV of 10 CFR 20.1902(e) was identified by the inspectors for the failure to post areas in which licensed material is used or stored. Specifically, two waste water lagoons, located within the Pro
Region: III | Braidwood | 5024 | 06/12/2007 06/12/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | THE LICENSEE'S FAILURE TO MAINTAIN A PROCEDURE ADEQUATE COULD HAVE RESULTED IN SECURING THE ONLY REMAINING RESIDUAL HEAT REMOVAL PUMP |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a violation of Technical Specification 5.4.1, "Procedures," for the licensee's failure to provide an adequate procedure to ensure the continued operation of the "A" residual heat removal pump, during cold leg recirculation mode o
Region: III | Braidwood | 5025 | 06/12/2007 06/12/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE EXTENT OF CONDITION REVIEW WHICH FAILED TO IDENTIFY THAT IST TESTING WAS NOT PERFORMED FOR COMPONENT COOLING WATER SYSTEMS VALVES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71152B | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee failed to include several manual component cooling water system valves, that were required to perform a safety function, in t
Region: III | Braidwood | 5023 | 03/31/2007 05/15/2007 | 2007003-01 | NRC | FIN | Mitigating Systems | Green | DEGRADED QUALIFICATION OF ELECTRICAL PANELS DUE TO FAILURE TO SECURE DOORS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.06 | The inspectors identified a finding of very low safety-significance for failing to maintain the control panels for the control room ventilation system chillers and the auxiliary feedwater system, as well as numerous others, fully latched closed. As a resu
Region: III | Braidwood | 5014 | 01/26/2007 02/23/2007 | 2007002-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Basis in 10 CFR 50.59 Evaluation for Installation of Sulfuric Acid System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111102 | Green. The inspectors identified a Severity Level IV NCV of 10 CFR 50.59 "Changes, Tests, and Experiments," having very low safety significance (Green) for the licensee's failure to perform an adequate safety evaluation review for changes made to the faci
Region: III | Braidwood | 5015 | 01/26/2007 02/23/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Lack of 50.59 Evaluation for Substitution of Manual Actions for Automatic Start Signals on the A Motor Driven AFW Pump |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7111102 | Green. The inspectors identified a Severity Level IV NCV of 10 CFR 50.59(d)(1) for the licensee's failure to document an evaluation which provides a basis for the determination that the change, test, or experiment did not require a license amendment. Spec
Region: III | Braidwood | 5016 | 12/31/2006 02/13/2007 | 2006005-01 | NRC | NCV | Initiating Events | Green | TRANSIENT COMBUSTIBLES STAGED DIRECTLY BENEATH SAFETY RELATED HORIZONTAL CABLE TRAYS |  | H.3(b) Work Activity Coordination | TE?: N | 05000457 Braidwood 2 |  | 71111.05Q | The inspectors identified a non-cited violation of the Braidwood Station Operating License, having very low safety significance, for the failure to implement the licensee's procedure for control of combustible materials for 27 charcoal filter trays. Speci
Region: III | Braidwood | 5013 | 09/30/2006 11/08/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN ELECTRICALLY SUPERVISED FIRE DOORS IN ACCORDANCE WITH THE FIRE PROTECTION PROGRAM |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | The inspectors identified a non-cited violation of Braidwood Facility Operating License Nos. NPF-72 and NPF-77, condition 2.E, for failing to maintain electrical supervision for fire doors between the diesel generator rooms and their associated ventilatio
Region: III | Braidwood | 5011 | 06/30/2006 08/04/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN FIRE BARRIER IN ACCORDANCE WITH FIRE PROTECTION PROGRAM |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05Q | The inspectors identified a Non-Cited Violation of Braidwood Facility Operating License Nos. NPF-72 and NPF-77, Condition 2.E, for failing to maintain the firewall separating the fuel handling building and the auxiliary building in accordance with the app
Region: III | Braidwood | 5008 | 06/30/2006 08/07/2006 | 2006009-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Control Transient Combustibles |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | Failure to implement the licensee's procedure for control of combustible materials. Licensee personnel staged unattended transient combustible materials near vertical cable tray risers in the auxiliary building contary to the licensee's procedure for cont
Region: III | Braidwood | 5009 | 06/30/2006 08/07/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Pre-Fire Plan |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | A finding for a violation of Braidwood's license condition 2.E for fire protection. The licensee failed to include information in the Braidwood's pre-fire plans to assist the fire brigade in being better prepared to fight a fire. Specifically, the license
Region: III | Braidwood | 5010 | 06/30/2006 08/07/2006 | 2006009-03 | NRC | NCV | Barrier Integrity | Green | Failure to Take Effective Corrective Action |  |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 71111.05T | A finding of very low safety significance was identified by the inspectors associated with a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." Specifically, the licensee failed to identify and revise a Braidwood's procedure to p
Region: III | Braidwood | 5006 | 05/25/2006 05/25/2006 | 2006008-04 | NRC | NCV | Public Radiation Safety | Green | Braidwood Tritium WHITE finding - failure to maintain records (50.75g) | EA Case: 2006081 |  | TE?: N | 05000456 Braidwood 1 05000457 Braidwood 2 |  | 7112201 | 10 CFR 50.75(g) requires each licensee to keep records of information important to the safe and effective decommissioning of the facility in an identified location until the license is terminated by the Commission. The Commission considers information imp
Region: III | Braidwood | 4987 | 03/31/2006 05/15/2006 | 2006002-01 | Self - Revealed | NCV | Barrier Integrity | Green | LICENSED MAXIMUM POWER LEVEL EXCEEDED DUE TO FEEDWATER HEATER TRANSIENT |  |  | TE?: N | 05000456 Braidwood 1 |  | 71153 | A finding of very low safety significance and associated Non-Cited Violation of Licensee Condition 2.C(1) "Maximum Power Level," was self-revealed during the November 18, 2004, feedwater heater transient, which resulted in an increase of reactor power as
Region: III | Braidwood | 126443 | 01/24/2020 |  |  | LIV |  | Green | Inadequate Compensatory Actions for Inoperable Fire Suppression System |  |  | TE?: N | 05000457 Braidwood 2 |  | 71111.05Q
Region: III | Byron | 125550 | 09/30/2019 11/13/2019 | 2019003-01 | Self - Revealed | FIN | Initiating Events | Green | Loss of Feedwater Flow in Mode 3 due to Securing Startup Feedwater Pump on High Inboard Bearing Temperature |  | NONE | TE?: N | 05000455 Byron 2 | Protection Against External Factors | 71153 | A self-revealed finding of very low safety significance (i.e., Green) was identified for the licensee’s failure to implement an established change in work scope requirements as contained in MA-AA-716-010, Maintenance Planning, Revision 21. Specifically, p
Region: III | Byron | 24104 | 06/30/2018 08/07/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Overspeed Trip of 2B Auxiliary Feedwater Pump During Surveillance |  | H.12 - Avoid Complacency | TE?: N | 05000455 Byron 2 |  | 71152 | A finding of very low safety significance and associated Non-cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures and Drawings,” was self-revealed when the 2B diesel driven auxiliary feedwater (AF) pump tripped on ov
Region: III | Byron | 24006 | 04/05/2018 05/07/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Prescribe Motor Driven Auxiliary Feedwater Pump Test Procedures that Accounted for the Allowed Emergency Diesel Generator Frequency Variation |  | P.2 - Evaluation | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.21M | The inspectors identified a Green finding and an associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the failure to prescribe motor driv
Region: III | Byron | 24034 | 04/05/2018 05/07/2018 | 2018010-02 | NRC | NCV | Barrier Integrity | Green | Failure to Periodically Test Check Valves Associated with Air-Operated Containment Isolation Valves |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.21M | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the failure to periodically test instrument air check valves associated with air-operated containment isolation valves. Specif
Region: III | Byron | 24007 | 04/05/2018 05/07/2018 | 2018010-03 | NRC | NCV | Barrier Integrity | Green | Failure to Verify the Adequacy of the Air Pressure Regulator Setpoint Value for Containment Isolation Valves 1(2)RF026 |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.21M | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the failure to verify the adequacy of the air pressure regulator setpoint value for air-operated containment isolation valv
Region: III | Byron | 22669 | 12/31/2017 02/12/2018 | 2017004-01 | Self - Revealed | NCV | Initiating Events | Green | Fire Barrier Impaired without Authorization |  | H.12 - Avoid Complacency | TE?: N | 05000455 Byron 2 |  | 71111.05Q | A finding of very low safety significance (Green) and associated NCV of Technical Specification 5.4.1.c “Procedures” was self-revealed when an Operations department supervisor found that a fire door separating two rooms containing safety related equipment
Region: III | Byron | 22343 | 12/15/2017 12/15/2017 | 2017010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Secondary Missiles Following a Postulated HELB |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to ensure that the design basis for the main steam safety valve (MSSV) roo
Region: III | Byron | 22344 | 12/15/2017 12/15/2017 | 2017010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Blow Out Panel Design Control |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee originally designed the MSSV blow out panels in a manner that prevented them from f
Region: III | Byron | 22345 | 12/15/2017 12/15/2017 | 2017010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Correct Errors in Design Analysis for Main Steam Line Break in Main Steam Tunnel |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” when the licensee failed to promptly correct errors in the design analysis for a main steam line b
Region: III | Byron | 22346 | 12/15/2017 12/15/2017 | 2017010-04 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action for Secondary Missiles |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” when the licensee failed to promptly address the identification of secondary missiles following a
Region: III | Byron | 22347 | 12/15/2017 12/15/2017 | 2017010-05 | NRC | NCV | Mitigating Systems | Green | Inaccurate Analysis of Record |  | NPP | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to maintain an accurate and up-to-date analysis of record for a postulated H
Region: III | Byron | 21637 | 08/25/2017 10/03/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Maintenance in Accordance with Performance Centered Maintenance Template |  | H.5 - Work Management | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.4.1, "Procedures," when licensee personnel failed to perform maintenance in accordance with written procedures as required by Regulatory Guide 1.33. Specific
Region: III | Byron | 21638 | 08/25/2017 10/03/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Degraded Reactor Containment Fan Cooler Circuitry |  | P.4 - Trending | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," when the licensee failed to promptly identify a condit
Region: III | Byron | 11766 | 06/30/2017 08/07/2017 | 2017002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Verify Computer Software during Transformer Replacement Modification |  | H.11 Challenge the Unknown | TE?: N | 05000454 Byron 1 |  | 71152 | Green. A finding of very low safety significance was self-revealed on March 28, 2017, when operators rapidly reduced generator load in response to a loss of forced cooling for the newly installed Unit 1 East main power transformer (1E MPT) and an indicate
Region: III | Byron | 11767 | 05/19/2017 06/29/2017 | 2017009-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform 10 CFR 50.59 Evaluation for UFSAR Change (Section 1R17.1b) |  |  | TE?: Y SL-IV-NCVIV | 05000454 Byron 1 05000455 Byron 2 |  | 71111.17T | Severity Level IV. The inspectors identified a Severity Level IV, Non-Cited Violation of 10 CFR 50.59, "Changes, Tests, and Experiments," Section(d)(1) and an associated finding of very low safety significance (Green) for the licensee's failure to provide
Region: III | Byron | 11760 | 09/30/2016 11/08/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | DOST Flood Barrier Door Left Open |  | H.12 Avoid Complacency | TE?: N | 05000454 Byron 1 |  | 71111.06 | Green. A finding of very low safety significance and an associated NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self-revealed on September 14, 2016, when a station employee discovered that the flood barrier door f
Region: III | Byron | 11761 | 09/30/2016 11/08/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Use Alteration Log Resulted in Fuel Oil Leak |  | H.12 Avoid Complacency | TE?: N | 05000455 Byron 2 |  | 71111.15 | Green. A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1.a, "Written Procedures," was self-revealed on August 24, 2016, when a fuel oil leak of approximately one-eighth gallon per minute was identified c
Region: III | Byron | 11765 | 09/30/2016 11/08/2016 | 2016003-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Properly Block and Brace a Radioactive Shipment for Transport |  | H.1 Resources | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71124.08 | Green. A finding of very low safety significance and an associated NCV of 10 CFR 71.5(a) and 49 CFR 171.1(b)(12) was self-revealed when the licensee failed to properly block and brace a Radioactive Waste (Radwaste) Shipment that was shipped to a waste pro
Region: III | Byron | 11751 | 06/30/2016 07/26/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Failure to Perform ASME Code Case Required Extent of Condition to Identify Unacceptable Piping Flaws |  | P.2 Evaluation | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.12 | Green. A finding of very-low safety significance was identified by the inspectors when, upon identification of a through-wall leak, the licensee declared the structural integrity of Class 3 fire protection piping to be operable, but failed to perform augm
Region: III | Byron | 11752 | 06/30/2016 07/26/2016 | 2016002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply With Radiation Work Permit Requirements Resulting In An Unplanned Dose Rate Alarm |  | H.11 Challenge the Unknown | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71124.01 | Green. A finding of very low safety significance and an associated Non-Cited Violation (NCV) of Technical Specification 5.4.1 was self-revealed when an engineer violated a radiation work permit by entering an area that was outside of the scope of the radi
Region: III | Byron | 11749 | 03/31/2016 04/25/2016 | 2016001-02 | Self - Revealed | NCV | Initiating Events | Green | Entry into Mode 3 with Turbine trip Function of SSPS Disabled |  | H.5 Work Management | TE?: N | 05000454 Byron 1 |  | 71153 | Green. A finding of very low safety significance and associated non-cited violation (NCV) of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.4 was self-revealed when the licensee transitioned Unit 1 to Mode 3 with the turbine trip
Region: III | Byron | 11740 | 12/31/2015 01/27/2016 | 2015004-01 | NRC | FIN | Barrier Integrity | Green | Inaccurate Technical Basis for Operability Evaluation of Reactor Head Flange Damage |  | H.12 Avoid Complacency | TE?: N | 05000454 Byron 1 |  | 71111.08P | Green. The NRC inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to ensure accuracy of calculations used to support an operability evaluation of the Unit 1 reactor vessel head flange for the impression
Region: III | Byron | 11736 | 12/31/2015 01/27/2016 | 2015004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Mispositioned Valve in Diesel Fuel Oil Transfer Pump Recirculation Flow Path |  | H.6 Design Margins | TE?: N | 05000454 Byron 1 |  | 71111.19 | -Green. A finding of very low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings was self-revealed on October 7, 2015, when the Unit 1
Region: III | Byron | 11741 | 12/31/2015 01/27/2016 | 2015004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Protective Tagging Procedure Requirements |  | H.9 Training | TE?: N | 05000454 Byron 1 |  | 71111.2 | Green: A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1.a, "Procedures," was self-revealed during the Unit 1 refueling outage that ended on October 2, 2015, as a result of the licensee's failure to impleme
Region: III | Byron | 11729 | 09/18/2015 09/18/2015 | 2015007-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Evaluate the Impact of a FLEX-Related Configuration Change on Available DG Fuel Oil Margin. |  | H.12 Avoid Complacency | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to adequately consider the potential impact that a modification wou
Region: III | Byron | 11733 | 09/18/2015 09/18/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability and Reportability in Accordance with the Issue Report Screening Procedure. |  | H.4 Teamwork | TE?: N | 05000454 Byron 1 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings", when the licensee failed to adequately evaluate an issue entered into the CAP for op
Region: III | Byron | 11734 | 09/18/2015 09/18/2015 | 2015007-03 | NRC | VIO | Barrier Integrity | Green | Failure to Analyze RHUT Inlet Piping Loads |  | H.1 Resources | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and an associated VIO of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to evaluate the effect of dynamic loads on inlet piping from U
Region: III | Byron | 11715 | 06/19/2015 07/21/2015 | 2015008-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of Sharing the RWSTs of Both Reactor Units |  |  | TE?: Y SL-IV-NCVIV | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's failure to perform a written safety evaluation that provided the bas
Region: III | Byron | 11716 | 06/19/2015 07/21/2015 | 2015008-04 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of Sharing the RWSTs of Both Reactor Units |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's failure to perform a written safety evaluation that provided the bas
Region: III | Byron | 11717 | 06/19/2015 07/21/2015 | 2015008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement a Design Change Associated with the RWSTs |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate applicable design basis into Technical Specifications (TSs
Region: III | Byron | 11718 | 06/19/2015 07/21/2015 | 2015008-06 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of Changing the SXCT Tornado Analysis as Described in the UFSAR |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's failure to perform a written evaluation that provided the bases for
Region: III | Byron | 11724 | 06/19/2015 07/21/2015 | 2015008-08 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Proper Direction for Low Level Isolation of the RWST in EOPs |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a finding of very low safety significance and an associated NCV of TS 5.4, "Procedures," for the failure to maintain emergency operating procedures (EOPs) for transfer to cold leg recirculation. Specifically, the EOPs for transfer to c
Region: III | Byron | 11725 | 06/19/2015 07/21/2015 | 2015008-09 | NRC | VIO | Mitigating Systems | Green | Failure to Promptly Correct and NRC-Identified NCV Associated with the Capability to Detect and Isolate ECCS Leakage |  | H.13 Consistent Process | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a finding of very-low safety significance (Green), and an associated cited violation of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to correct a Condition Adver
Region: III | Byron | 11726 | 06/19/2015 07/21/2015 | 2015008-10 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain the Instrument Loops Used to Verify Compliance with the Containment Average Air Temperature TS Limit |  | P.1 Identification | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a finding of very-low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have procedures to maintain the accuracy within necessary limits
Region: III | Byron | 11727 | 06/19/2015 07/21/2015 | 2015008-11 | NRC | NCV | Mitigating Systems | Green | Operability Evaluation Relied on Probabilities of Occurrence of the Associated Event |  | H.9 Training | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to make an operability determination without relying on the
Region: III | Byron | 11705 | 03/31/2015 04/28/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Work Instructions that Appropriately Address Foreign Material Exclusion from Safeguards Relays |  | P.2 Evaluation | TE?: N | 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to provide work instructions appropriate to the
Region: III | Byron | 11690 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Measure Interpass Temperature |  | H.8 Procedure Adherence | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for a failure to measure the interpass temperature while performing welding on the on th
Region: III | Byron | 11691 | 12/31/2014 02/10/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Liquid Penetrant (PT) Testing Procedure Did Not Meet ASME Code |  | H.3 Change Management | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the failure to perform a Liquid Penetrant Test (PT) in accordance with the American
Region: III | Byron | 11698 | 12/31/2014 02/10/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Welding Procedure Specifications Variables Changed Without Revision or Ammendment Contrary to ASME Code |  | H.7 Documentation | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the failure to revise or amend a welding procedure specification (WPS) after changing w
Region: III | Byron | 11699 | 12/31/2014 02/10/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability of a TS SSC Upon Discovery of a Support System Degraded Condition |  | H.14 Conservative Bias | TE?: N | 05000455 Byron 2 |  | 71111.15 | Inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions Procedures, and Drawings," for failure to implement procedure OP-AA-108-115, "Operability Determinations (CM-1),"
Region: III | Byron | 11704 | 12/31/2014 02/10/2015 | 2014005-05 | NRC | FIN | Barrier Integrity | Green | Containment Penetration Valves Rendered Inoperable for Operational Convenience |  | H.5 Work Management | TE?: N | 05000455 Byron 2 |  | 71111.2 | Inspectors identified a finding of very low safety significance when the licensee impaired a flood protection boundary that supported a required safety function for operational convenience. Specifically, the licensee removed the flood barriers for auxilia
Region: III | Byron | 11689 | 11/07/2014 11/06/2014 | 2014004-01 | NRC | NCVIV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: Y SL-IV-NCVIV | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The NRC identified a Non-Cited Violation (NCV) of 10 CFR 50.54(q)(2) associated with 10 CFR 50.47(b)(10) and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the Byron Station Emergency Plan, as a result of failing to
Region: III | Byron | 11688 | 03/31/2014 05/07/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO PROPERLY IMPLEMENT A COMPENSATORY FIRE WATCH AS REQUIRED BY THE FIRE PROTECTION PROGRAM |  | H.5 Work Management | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05Q | A finding with two examples of very low safety significance and associated NCV of Technical Specification 5.4.1.c was self-revealed when required compensatory fire watches were discovered to have been terminated while the fire systems were still impaired.
Region: III | Byron | 11665 | 12/31/2013 02/03/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Emergency Service Water Blowdown Isolation Valves Were Not Tested |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to demonstrate the ability to isolate the emergency service water blowdown as c
Region: III | Byron | 11666 | 12/31/2013 02/03/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Intake Structure Silt Level Acceptance Criteria Were Non-Conservative |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to develop appropriate intake structure silt level acceptance criteria. Spec
Region: III | Byron | 11672 | 12/31/2013 02/03/2014 | 2013005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Preventative Maintenance Procedure Repalacement Schedules for Essential Service Water Makeup Pump Diesel Engine Hoses |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.07T | . Inspectors identified a finding of very low safety significance and associated Non-Cited Violation of TS 5.4.1, "Procedures," for failure to establish and implement a preventive maintenance schedule to replace hoses on SX Make Up pump diesel engine. Spe
Region: III | Byron | 11673 | 12/31/2013 02/03/2014 | 2013005-04 | NRC | NCV | Barrier Integrity | Green | Analytical Bases for PTL Curves Not Maintained Consitent With Unit 2 Head Stud Configuration |  | H.14 Conservative Bias | TE?: N | 05000455 Byron 2 |  | 71111.18 | Inspectors identified a finding of very low safety significance and an associated NCV of TS 5.6.6, Reactor Coolant System (RCS) Pressure and Temperature Limits Report (PTLR), for failure to maintain the analytical basis for deriving the pressure temperatu
Region: III | Byron | 11681 | 12/31/2013 02/03/2014 | 2013005-05 | NRC | NCV | Initiating Events | Green | Reactor Vessel Design Documents Not Updated to Reflect Unit 2 Missing Head Stud |  |  | TE?: N | 05000455 Byron 2 |  | 71111.18 | Inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion III "Design Control" for failure to maintain reactor vessel design specification and analysis up-to-date for the 53 stud vessel head
Region: III | Byron | 11682 | 12/31/2013 02/03/2014 | 2013005-06 | NRC | NCV | Initiating Events | Green | Corrosion Effects on the Unit 2 Reactor Vessel Not Monitored |  | P.3 Resolution | TE?: N | 05000455 Byron 2 |  | 71111.18 | Inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion III "Design Control" for failure to maintain reactor vessel design specification and analysis up-to-date for the 53 stud vessel head
Region: III | Byron | 11687 | 12/31/2013 02/03/2014 | 2013005-07 | NRC | NCV | Initiating Events | Green | Inadequate Vessel Stress Analysis for Unit 2 Missing Head Stud |  | H.7 Documentation | TE?: N | 05000455 Byron 2 |  | 71111.18 | Inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion III "Design Control" for failure to perform an adequate thermal-mechanical analysis to support operation with a missing Unit 2 head s
Region: III | Byron | 11658 | 09/27/2013 11/08/2013 | 2013007-01 | NRC | NCV | Initiating Events | Green | INADEQUATE IDENTIFICATION OF FIRE CURTAIN SPRINKLER DEGRADATION FOR AN AUXILIARY BUILDING STAIRWELL |  | P.1 Identification | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of Byron Operating License (OL) Condition 2.C.6 for Unit 1 and 2.E for Unit 2 when licensee personnel failed to identify that a fire sprinkler curtain on Elevation 3
Region: III | Byron | 11659 | 09/27/2013 11/08/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY ASSESS OPERABILITY OF THE 2A EDG FOLLOWING POST-MODIFICATION TESTING |  | H.11 Challenge the Unknown | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification (TS) 3.8.1 when licensee personnel failed to properly assess the operability of the 2A emergency diesel generator (EDG) following a post-m
Region: III | Byron | 11663 | 09/27/2013 11/08/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | ACCEPTANCE CRITERIA FOR BATTERY VOLTAGE IN TS SURVEILLANCE PROCEDURE FAILED TO ACCOUNT FOR TEST EQUIPMENT UNCERTAINTY |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," when licensee personnel failed to account for test instrument uncertainty in the acceptance criteria for
Region: III | Byron | 10975 | 06/30/2013 08/01/2013 | 2013003-01 | NRC | NCV | Barrier Integrity | Green | INACCURATE RISK ASSESSMENT |  | H.3(b) Work Activity Coordination | TE?: N | 05000455 Byron 2 |  | 71111.13 | A finding of very low safety significance and an associated NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified by the inspectors when licensee personnel removed both the 2B and 2D Re
Region: III | Byron | 10976 | 06/30/2013 08/01/2013 | 2013003-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH A PROCEDURE TO CONTROL THE SPENT FUEL POOL COOLING SYSTEM |  | H.4(a) Human Error Prevention | TE?: N | 05000455 Byron 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1 was self-revealed when a configuration control error during a local leak rate test (LLRT) resulted in the inadvertent draining of the spent fuel pool (SF
Region: III | Byron | 10970 | 03/31/2013 04/29/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | EMBEDMENT PLATE DESIGN DEFICIENCIES |  |  | TE?: N | 05000454 Byron 1 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to properly evaluate the structural steel embedment plate whic
Region: III | Byron | 10971 | 03/31/2013 04/29/2013 | 2013002-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PROPERLY SCOPE ALL PERTINENT EXTERNAL FLOOD PROTECTION FEATURES INTO WALKDOWN LISTS IN ACCORDANCE WITH INDUSTRY GUIDANCE NEI 12-07 |  | H.4(a) Human Error Prevention | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to develop inspection lists that included all external flood protection features credited in current licensing bases (CLB) documents as specified in
Region: III | Byron | 10913 | 12/31/2012 02/05/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PREVENT EXCESSIVE SILT BUILDUP IN THE 1b SAFETY INJECTION PUMP OIL COOLER |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 |  | 71111.15 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when the licensee failed to properly address 1B SI pump oil cooler silting on A
Region: III | Byron | 10914 | 12/31/2012 02/05/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE WORK INSTRUCTIONS LEAD TO FAILURE OF THE 1B SX PUMP MOTOR |  |  | TE?: N | 05000454 Byron 1 |  | 71111.15 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when the 1B SX pump tripped when a motor lug failed as a result of an inadequat
Region: III | Byron | 10893 | 12/31/2012 02/05/2013 | 2012005-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO SUBMIT A 10 CFR 50.73(A)(2)(V) REPORT FOR INOPERABLE CONTAINMENT AREA RADIATION MONITORS |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71151 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.73(a)(2)(v) when licensee personnel failed to report a condition that resulted in a loss of safety function when both containment area radiation monitors were declared inoperable. Specifically
Region: III | Byron | 10962 | 06/30/2012 08/07/2012 | 2012003-01 | Self - Revealed | NCV | Initiating Events | Green | Leakage Detection Trough with Large Accumulation of Boric Acid Identified |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000454 Byron 1 |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when licensee personnel failed to identify boric acid accumulation that
Region: III | Byron | 10963 | 06/30/2012 08/07/2012 | 2012003-02 | NRC | NCV | Initiating Events | Green | Failure to Have Instructions Appropriate to the Circumstances |  | H.4(a) Human Error Prevention | TE?: N | 05000454 Byron 1 |  | 71111.15 | A self-revealed finding with two examples of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when licensee personnel failed to properly torque an RCS p
Region: III | Byron | 10954 | 06/15/2012 07/27/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Non-Conforming 480/120 Vac Motor Control Contactors |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure qualified components were installed in the plant. Specifically
Region: III | Byron | 10955 | 06/15/2012 07/27/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the CCW System Capability to Withstand a Thermal Barrier Break |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the component cooling water (CCW) system was capable of withst
Region: III | Byron | 10956 | 06/15/2012 07/27/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Calibration Tolerance Limits for Electrical Relay Settings |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to specify in a design calculation the allowable relay setpoint calibrat
Region: III | Byron | 10957 | 06/15/2012 07/27/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Design Analyses Did Not Adequately Address Potential Flooding of the Auxiliary Building |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately analyze potential design basis internal flooding events in
Region: III | Byron | 10961 | 06/15/2012 07/27/2012 | 2012007-05 | NRC | NCV | Barrier Integrity | Green | Failure to Provide Means to Detect Leak in Emergency Core Cooling Flow Path |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to provide a means to detect and isolate a leak in the emergency core co
Region: III | Byron | 10943 | 03/31/2012 05/10/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | Structural Steel Beam Missing Fireproofing Materials |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000455 Byron 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Byron Operating License Condition 2.E when fireproofing material on a structural beam in the 2A Safety Injection (SI) Pump Room was identified as missing.
Region: III | Byron | 10946 | 03/31/2012 05/10/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | Incomplete Component Cooling Water System and Essential Service Water System Code Examinations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.55a(g)(4) when licensee personnel failed to perform system leakage testing in a timely manner as required by Section XI of the ASME Code following modif
Region: III | Byron | 10947 | 03/31/2012 05/10/2012 | 2012002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Control the Operating Status of Eight New Valves Affecting Two Safety Related Systems |  | H.3(b) Work Activity Coordination | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, App B, Criterion XIV, "Inspection, Test, and Operating Status," when licensee personnel failed to control the operating status of eight manual iso
Region: III | Byron | 10936 | 12/31/2011 02/07/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY VOIDED SECTIONS OF AF PIPING |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," when licensee personnel failed to identify non-conforming conditions associated with voided p
Region: III | Byron | 10937 | 12/31/2011 02/07/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | HIGH ENERGY LINE BREAK OPEERABILITY EVALUATION |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.15 | The inspectors identified that the licensee did not meet multiple Operability Determination Process standards after identifying a non-conservative condition related to assumed closure times for hazard barrier dampers separating the turbine building from v
Region: III | Byron | 10941 | 12/31/2011 02/07/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY HAZARDOUS MATERIALS ON TRANSPORTATION MANIFEST |  | H.3(b) Work Activity Coordination | TE?: N | 05000454 Byron 1 |  | 71124.08 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR 71.5 was evaluated by the inspectors. Specifically, the licensee failed to comply with 49 CFR 172.203(c) and shipped a package of radioactive material with a transport
Region: III | Byron | 10922 | 09/30/2011 11/03/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY ELEVATED RISK STATUS |  | H.3(a) Work Planning | TE?: N | 05000455 Byron 2 |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear power Plants," when licensee personnel failed to accurately assess
Region: III | Byron | 10929 | 09/30/2011 11/03/2011 | 2011004-03 | NRC | FIN | Mitigating Systems | Green | MODIFICATION OF THE AUXILIARY FEEDWATER SYSTEM WITHOUT PRIOR NRC APPROVAL |  | P.2(b) Implementing Operating Experience | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) when licensee personnel failed to obtain a license amendment prior to implementing a proposed change to the plant that resulted in a more than minimal increase in the likelihood o
Region: III | Byron | 10930 | 09/30/2011 11/03/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | DESIGN OF AUXILIARY FEEDWATER SYSTEM INCLUDED VOIDS IN SAFETY RELATED ALTERNATE SUCTION FLOWPATHS |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71153 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to properly analyze the configuration of the Essential Service Wate
Region: III | Byron | 10931 | 09/02/2011 10/17/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | UNTIMELY CORRECTIVE ACTION FOR PREVIOUSLY IDENTIFIED NON-CITED VIOLATIONS (sECTION 40a2.1.B.3.I) |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," when licensee personnel failed to implement timely corrective actions to address two previously issued
Region: III | Byron | 10935 | 09/02/2011 10/17/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO INITIATE ISSUE REPORTS |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to initiate IRs during the review of OPEX in accordan
Region: III | Byron | 10921 | 08/26/2011 10/04/2011 | 2011016-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Extent of Cause for 2A EDG Lube Oil Leak |  | P.3(a) Self-Assessment | TE?: N | 05000455 Byron 2 |  | 95001 | The inspector identified a finding of very low safety significance when licensee personnel failed to perform an adequate extent of cause review in the root cause evaluation for the 2A EDG lube oil cooler leak. Specifically, the root cause evaluation ident
Region: III | Byron | 10910 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT THE DESIGN OF THE AF SUCTION PIPING WAS ADEQUATE TO PREVENT AIR ENTRAINMENT FOLLOWING A SEISMIC OR TORNADO EVENT |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to analyze whether the design of the auxiliary feedwater system ensure
Region: III | Byron | 10912 | 06/22/2011 07/21/2011 | 2010502-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: III | Byron | 10915 | 06/16/2011 07/22/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Specify and Perform Required Independent Quality Verification Hold Point Inspections. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that independent quality verification (QV) inspection hold points (HPs) were spec
Region: III | Byron | 10916 | 06/16/2011 07/22/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Requirements for Temporary Scaffolds that Remain in Place for Over 90 Days. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," related to inadequate control of installed temporary scaffolds. Specifically, l
Region: III | Byron | 10917 | 06/16/2011 07/22/2011 | 2011009-03 | NRC | NCV | Mitigating Systems | Green | EDG Usable Fuel Calculations Failed to Consider Appropriate EDG Frequency Variations. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate applicable design basis (calculations) into specifi
Region: III | Byron | 10903 | 05/04/2011 06/16/2011 | 2011015-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Document and Justify Continued Operability of the Auxiliary Feedwater System. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 93812 | A finding of very low safety significance was identified at the Braidwood and Byron Stations by the inspectors when licensee personnel failed to adequately document and justify continued operability of the auxiliary feedwater (AF) system. Specifically, li
Region: III | Byron | 10891 | 03/31/2011 05/03/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | AUXILIARY FEEDWATER PUMP LUBE OIL HEAT EXCHANGER CONFIGURED INCORRECTLY |  |  | TE?: N | 05000454 Byron 1 |  | 71111.07A | An NRC-identified finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when licensee personnel failed to install the Unit 1 Tra
Region: III | Byron | 10892 | 03/31/2011 05/03/2011 | 2011002-02 | Self - Revealed | NCV | Barrier Integrity | Green | SELF-REVEALED LOW FLOW TO REACTOR CONTAINMENT FAN COOLER |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000455 Byron 2 |  | 71111.22 | A self-revealed finding of very low safety significance was identified on January 21, 2011, when licensee personnel failed to ensure that surveillance procedures for measuring essential service water flow through reactor containment fan coolers was adequa
Region: III | Byron | 10895 | 03/31/2011 05/03/2011 | 2011002-03 | NRC | NCV | Occupational Radiation Safety | Green | OUT-OF-DATE/EXPIRED RESPIRATOR CARTRIDGES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71124.03 | An NRC-identified finding of very low safety significance and an associated NCV of TS 5.4.1 was identified by the inspectors when out of date respirator cartridges were found available for use. Radiation protection procedures that cover respiratory protec
Region: III | Byron | 10896 | 03/31/2011 05/03/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | INADEQUATE INSTRUCTIONS FOR MEASURING ECCS VOIDS |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | An NRC-identified finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when licensee personnel failed to establish instructions
Region: III | Byron | 10897 | 03/31/2011 05/03/2011 | 2011002-05 | NRC | NCV | Barrier Integrity | Green | FAILURE TO EVALUATE THE EFFECTS OF DYNAMIC LOADS AT THE CS DISCHARGE PIPING |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | An NRC-identified finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors when licensee personnel failed to evaluate the effects of dynamic loads at the
Region: III | Byron | 10884 | 12/31/2010 01/31/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Instructions for the Inspection of the River Screen House and Essential Service Water Cooling Tower |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.07T | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when licensee personnel failed to establish specific instructions for in
Region: III | Byron | 10882 | 12/03/2010 01/06/2011 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Guidance in Safe-Shutdown Procedures |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05T | A finding of very low safety-significance and associated NCV of Technical Specification 5.4.1.c for Units 1 and 2 was identified by the inspectors for the licensee's failure to provide adequate guidance in safe shutdown procedures. Specifically, the licen
Region: III | Byron | 10883 | 12/03/2010 01/06/2011 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Test 125 Vdc Molded Case Circuit Breakers |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05T | . A finding of very low safety significance and associated NCV of the Byron Station facility operating licensee conditions for fire protection was identified by the inspectors for the licensee's failure to periodically test samples of molded case circuit
Region: III | Byron | 10873 | 09/30/2010 11/03/2010 | 2010004-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM ADEQUATE EVALUATION FOR CRANE UPGRADE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 60854.1 | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of Title 10 Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control" was identified by the inspectors for the licensee's failure to perfor
Region: III | Byron | 10865 | 06/30/2010 07/27/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | 0B FIRE PUMP DISCHARGE VALVE DISCOVERED CLOSED (SECTION 1R12) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.12 | A self-revealed finding of very low safety significance and associated Non-Cited Violation of Byron Operating License Condition 2.C(6) for Unit 1 and 2.E for Unit 2 for the licensees failure to identify the separation of the 0B Fire Pump discharge valve,
Region: III | Byron | 10857 | 06/30/2010 07/27/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE EVALUATION OF SHIM PACK FOR THE UPPER STEAM GENERATOR LATERAL SUPPORTS |  |  | TE?: N | 05000455 Byron 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the inadequate design evaluation of the shim packs for the Upper Steam Generator Lat
Region: III | Byron | 10866 | 06/30/2010 07/27/2010 | 2010003-03 | NRC | NCV | Initiating Events | Green | WATER INTRUSION LEADS TO LOSS OF ANNUNCIATORS (SECTION 1R15.b) |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of Byron Operating License Condition 2.C(6) for Unit 1 and 2.E for Unit 2 for the licensee failing to provide an adequate floor drain system as required by the Fire Pro
Region: III | Byron | 10863 | 06/30/2010 07/27/2010 | 2010003-04 | NRC | NCV | Mitigating Systems | Green | LOOSE DEBRIS INSIDE OF UNIT CONTAINMENT AT THE START OF THE REFUELING OUTAGE |  | H.3(b) Work Activity Coordination | TE?: N | 05000455 Byron 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure BAP 1450-1, "Access to C
Region: III | Byron | 10864 | 06/30/2010 07/27/2010 | 2010003-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO APPROPRIATELY ANALYZE THE DEGRADED VOLTAGE TIMER SETTINGS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified by the inspectors for the licensee's failure to have an appropriate analysis for the second level und
Region: III | Byron | 10871 | 06/30/2010 07/27/2010 | 2010003-07 | NRC | NCV | Mitigating Systems | Green | FAILURE TO REPORT AN AUTOMATIC RPS AND AUXILIARY FEEDWATER ACTUATION WHILE SHUTDOWN . |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000455 Byron 2 |  | 71153 | A Green Finding and associated NCV of 10 CFR 50.72(b)(3)(iv)(A) was identified by the inspectors for the licensee's failure to recognize that a valid Unit 2 automatic Reactor Protection System (RPS) and Auxiliary Feedwater (AF) actuation while shut down w
Region: III | Byron | 10856 | 03/31/2010 05/05/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | FIRE BARRIER WITH UNSEALED PENETRATION BETWEEN UNIT 1 AF PUMP ROOMS |  |  | TE?: N | 05000454 Byron 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated NCV of the Byron Unit 1 Operating License (OL), Condition 2.C.(6) for failure to comply with the fire barrier sealing requirements of the fire Protection Program (FPP). Spe
Region: III | Byron | 10853 | 12/31/2009 01/26/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH 10 CFR PART 26.203(b)(2) |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and the associated NCV of 10 CFR Part 26.203(b)(2),"Procedures," for the licensee's failure to adhere to work hour rule procedures. Specifically, a licensed reactor operator who was worki
Region: III | Byron | 10855 | 12/31/2009 01/26/2010 | 2009005-03 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO COMPLY WITH 10 CFR PART 20 APPENDIX G |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance and the associated NCV of 10 CFR Part 20, Appendix G, Section III.A.3. Specifically, the licensee did not establish a Quality Assurance Program sufficiently to assure conformance with 10
Region: III | Byron | 10844 | 09/01/2009 10/15/2009 | 2009008-02 | NRC | NCV | Initiating Events | Green | Untimely Corrective Actions for Sprinkler Obstructions |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000454 Byron 1 |  | 71152B | The inspectors identified a Green NCV of Byron License Condition 2.C.(6) for Unit 1 for failure to take timely corrective actions as described in the Fire Protection Program to address a previously issued NCV regarding sprinkler obstruction by scaffolding
Region: III | Byron | 10836 | 06/30/2009 08/07/2009 | 2009003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO COMPLY WITH TS 3.4.13.B RCS PRESSURE BOUNDARY LEAKAGE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 |  | 71111.15 | A finding of very low safety significance and associated Non-Cited Violation of Technical Specification 3.4.13.B was identified by the NRC inspectors on June 26, 2009, when RCS pressure boundary leakage was identified but not repaired or isolated within t
Region: III | Byron | 10828 | 03/31/2009 05/13/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE RISK ASSESSMENT THAT ACCOUNTED FOR ALL RISK SIGNIFICANT STRUCTURES, SYSTEMS AND COMPONENTS THAT WERE UNAVAILABLE PRIOR TO MAINTENANCE ACTIVITIES. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(4) was identified by the inspectors for the licensee's failure to perform a risk assessment that accounted for the inability of the Unit 1 Essential Service Water suction valv
Region: III | Byron | 10829 | 03/31/2009 05/13/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADHERE TO SCAFFOLD PROCEDURES |  |  | TE?: N | 05000454 Byron 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," during a routine inspection of the Auxiliary Building on February 21. The inspectors observed scaffold construction
Region: III | Byron | 10832 | 03/27/2009 05/11/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain/Extend the Qualification Basis for Molded-Case Circuit Breakers (MCCBs) Used in Safety Related Applications Greater than 20 Years. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | Green. A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to maintain the qualification bases for safety-related equipment.
Region: III | Byron | 10833 | 03/27/2009 05/11/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Molded-Case Circuit Breaker Test Data. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | -Green. A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified by the inspectors for the failure to identify, and take corrective action to address adverse mo
Region: III | Byron | 10826 | 12/31/2008 02/10/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO REMOVE OR EVALUATE LOOSE DEBRIS INSIDE OF CONTAINMENT PRIOR TO APPLICABLE MODE |  | H.3(b) Work Activity Coordination | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure BAP 1450-1, "Acces
Region: III | Byron | 10827 | 12/31/2008 02/10/2009 | 2008005-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO EVALUATE RADIOLIGICAL HAZARDS FOR AIRBORNE RADIOACTIVITY |  | H.4(a) Human Error Prevention | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7112101 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation (NCV) of Technical Specification (TS) 5.4.1 for failure to implement procedures required to evaluate radiological hazards for airborne radioactivity. Sp
Region: III | Byron | 10822 | 10/10/2008 11/12/2008 | 2008009-02 | NRC | NCV | Barrier Integrity | Green | Failure to Analyze Inlet Piping Loads and Establish an Adequate HUT Quench Volume |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | Green. The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance, associated with the licensee's failure to analyze and establish an adequate quench volume within the boron recycle
Region: III | Byron | 10823 | 09/30/2008 11/13/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | ISOLATING CARBON DIOXIDE FIRE SUPPRESSION SYSTEM IN UPPER CABLE SPREADING ROOMS WITHOUT PRIOR NRC APPROVAL |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05Q | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of Byron Unit 1 Operating License Condition 2.C(6) and Byron Unit 2 Operating License Condition 2.E was identified for the licensee's failure to obtain NRC approval befo
Region: III | Byron | 10824 | 09/30/2008 11/13/2008 | 2008004-02 | NRC | FIN | Initiating Events | Green | INADEQUATE PREVENTIVE MAINTENANCE FOR THE UNIT 2 TRAIN B STATION AIR COMPRESSOR |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000455 Byron 2 |  | 71111.13 | A finding of very low safety significance was self-revealed when the Unit 2 Train B (2B) station air compressor (SAC) tripped on two separate occasions due to inadequate preventive maintenance. The license entered this issue into the corrective action pro
Region: III | Byron | 10825 | 09/30/2008 11/13/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | MISSED VENTING OF THE SAFETY INJECTION SYSTEM PIPING |  | H.3(b) Work Activity Coordination | TE?: N | 05000455 Byron 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow the Adverse Condition Monitoring Plan for safety injection system check v
Region: III | Byron | 10805 | 06/30/2008 08/14/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | FIRE SUPPRESSION SPRINKLER OBSTRUCTION IN THE DIESEL OIL STORAGE TANK ROOM |  | H.4(b) Procedural Compliance | TE?: N | 05000454 Byron 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated NCV of the Byron Operating License Condition 2.C.6 for failure to comply with the spacing standard for sprinkler systems of the Fire Protection Program. Specifically, a per
Region: III | Byron | 10806 | 06/30/2008 08/14/2008 | 2008003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO CORRECTLY EVALUATE AND DISPOSITION OF A WELD INDICATION |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Section 50.55a, for the failure to correctly disposition an ultrasonic (UT) examination indication fou
Region: III | Byron | 10811 | 06/30/2008 08/14/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM EVALUATION OF A LEADING BOLTED CONNECTION |  | H.4(b) Procedural Compliance | TE?: N | 05000454 Byron 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to perform adequate evaluations of the boric acid leak
Region: III | Byron | 10812 | 06/30/2008 08/14/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECTLY TIGHTEN FITTINGS LEADS TO FAILURE TO START DURING A SURVEILLANCE OF THE 0B SX AMKEUP PUMP |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.12 | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4, "Procedures," was self-revealed on May 27, 2008, when the 0B essential service water (SX) system makeup pump failed to start during a planned monthly surveil
Region: III | Byron | 10813 | 04/05/2008 08/14/2008 | 2008003-05 | Licensee - Identified | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN UPDATED RISK EVALUATION PRIOR TO SURVEILLANCE TESTING OF THE UNIT 1 TRAIN A DIESEL GENERATOR BASED ON EXISTING PLANT CONDITIONS | EA Case: 2008197 |  | TE?: N | 05000455 Byron 2 |  | 71111.13 | AV. The licensee identified an apparent violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," (a)(4) for failure to perform an updated risk evaluation prior to surveillance testing of the Unit 1
Region: III | Byron | 10801 | 03/30/2008 05/14/2008 | 2008002-01 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO EVALUATE RADIOLOGICAL HAZARDS FOR ALPHA RADIATION |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7112101 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation (NCV) of Technical Specification 5.4.1 for failure to implement procedures required to evaluate radiological hazards for alpha contamination. The correc
Region: III | Byron | 10802 | 03/30/2008 05/14/2008 | 2008002-02 | NRC | NCV | Barrier Integrity | Green | PLANT BARRIER IMPAIRMENT PERMIT NOT FOLLOWED |  | H.3(a) Work Planning | TE?: N | 05000455 Byron 2 |  | 71152 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to follow plant procedures. Plant mai
Region: III | Byron | 10791 | 02/14/2008 02/21/2008 | 2007009-01 | NRC | NCV | Mitigating Systems | Green | Operating Experience Procedure Not Followed for Service Water Corrosion Event |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 93812 | -Green. The team identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow Procedure LS-AA-115, "Operating Experience
Region: III | Byron | 10799 | 02/14/2008 02/21/2008 | 2007009-04 | NRC | NCV | Mitigating Systems | Green | TRM Change Bypasses Procedure Change and Safety Evaluation Processes |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 93812 | -Green. The team identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to ensure that Revision 54 of the Technical Requirem
Region: III | Byron | 10800 | 02/14/2008 02/21/2008 | 2007009-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Corroded 0SX138B Valve Bolting During VT-2 Examination |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 93812 | -Green. The team identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify severely corroded bolts (condition adverse to quality
Region: III | Byron | 10794 | 01/31/2008 03/13/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Motor Operated Valve Breaker Magnetic Trip Settings |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.17T | The inspectors identified an NCV having very low safety significance of 10 CFR Part 50, Appendix B, Criterion XVI for the licensee's failure to take prompt corrective actions for a condition adverse to quality. specifically, when it was identified in 2003
Region: III | Byron | 10795 | 01/31/2008 03/13/2008 | 2008006-03 | NRC | NCV | Initiating Events | Green | Unauthorized Transient Combustibles |  | H.3(a) Work Planning | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.17T | The inspectors identified an NCV, having very low safety significance, of license condition 2.C(6) in that the licensee failed to implement and maintain in effect all provisions of the approved fire protection program. specifically, the inspectors identif
Region: III | Byron | 10785 | 12/31/2007 02/13/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | UNIT 0 TRAIN A ESSENTIAL SERVICE WATER BASIN LEVEL DROP |  | H.3(b) Work Activity Coordination | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.13 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50.65(a)(4), for the licensee's failure to conduct an adequate risk assessment of the maintenance performed at the Unit 0 Train B essential service water basin. Specifically, the maintenance
Region: III | Byron | 10762 | 12/31/2007 02/13/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | UNIT 1 TRAIN B AUXILIARY FEEDWATER PUMP LUBE OIL LEAK |  |  | TE?: N | 05000454 Byron 1 |  | 71111.15 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion V, for the licensee's failure to classify safety related part appropriately. Specifically, the replacement rocker cover gasket for the Unit 1 Train B (1B) diesel dri
Region: III | Byron | 10782 | 09/30/2007 11/14/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE COMMON MODE FAILURE EVALUATION |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000454 Byron 1 |  | 71111.12 | The inspectors identified a NCV of Technical Specification 3.8.1 for the licensee's failure to determine the applicability of a potential common cause failure for the remaining operable Diesel Generator (D/G)following the failure during testing of the Uni
Region: III | Byron | 10784 | 09/30/2007 11/14/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | DISCREPANCIES WITH TORNADO ANALYSIS |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the ultimate heat sink (UHS) capability of mitigating the effects of tornado missiles. Specifically, the inspecto
Region: III | Byron | 10778 | 06/30/2007 08/08/2007 | 2007003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FIRE PROOF STRUCTURAL STEEL BEAMS TO ACHIEVE A 3-HOUR FIRE RATING. |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05Q | The inspectors identified an NCV of Byron Station's Operating License Condition 2.C.6 for failure to maintain a 3-hour rated firewall in the control room heating, ventilation and air conditioning (HVAC) equipment room. Specifically, the walls between the
Region: III | Byron | 10779 | 06/30/2007 08/08/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | ALTERNATIVE SHUTDOWN USING THE REMOTE SHUTDOWN PANEL. |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to ensure that all testing necessary to demonstrate that the Unit 1 and 2 remote shutdown pa
Region: III | Byron | 10780 | 06/30/2007 08/08/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM A MT EXAMINATION IN ACCORDANCE WITH ASME SECTION XI. |  |  | TE?: N | 05000455 Byron 2 |  | 71111.08P | The inspectors identified an NCV of 10 CFR 50.55(a)(g)(4) for failure to perform a Magnetic Particle (MT) examination of the full required exam surface on a steam generator (SG) main feedwater nozzle weld (2RC01BA) in accordance with the American Society
Region: III | Byron | 10781 | 06/30/2007 08/08/2007 | 2007003-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PROPERLY REINSTALL A FLOOD SEAL HATCH / HIGH ENERGY LINE BREAK BARRIER. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000454 Byron 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1 regarding procedure adherence when a flood seal hatch, which also served as a High Energy Line Break (HELB) barrier, was found
Region: III | Byron | 9577 | 06/30/2007 08/08/2007 | 2007003-05 | NRC | NCV | Initiating Events | Green | DESIGN BASIS ANALYSIS FOR THE POSTULATED DROP OF A REACTOR VESSEL HEAD DURING REFUELING WAS NOT UP-TO-DATE. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated NCV for a failure to establish measures to assure that regulatory requirements and the design basis were correctly translated into procedures as required by 10 CFR 50 Appen
Region: III | Byron | 10771 | 03/31/2007 05/15/2007 | 2007002-01 | NRC | FIN | Mitigating Systems | Green | INADEQUATE SETPOINT CONTROL OF THE OIL LEVEL TO SAFETY RELATED PUMPS. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.04S | The inspectors identified a finding for the licensee's failure to maintain setpoint control of the constant level oilers. Specifically, the licensee did not incorporate the vendor's recommendation on setting the oil level for the essential service water p
Region: III | Byron | 10777 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | ADEQUACY OF SAFE SHUTDOWN PROCEDURES TO ADDRESS DRAINING OF THE RWST. |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | NONE | The inspectors identified a Non-Cited Violation (NCV) of the Byron Station Operating License for the failure to have adequate alternate safe shutdown procedure. Specifically, licensee's procedure BOP FR-1, "Fire Response Guidelines," did not include adequ
Region: III | Byron | 10770 | 03/31/2007 05/15/2007 | 2007002-03 | NRC | URI | Barrier Integrity | Green | OPERABILITY OF THE FLOOD SEALS TO THE UNIT 1 AFW TUNNEL WITH ONE CORNER RAISED UP. |  |  | TE?: N | 05000455 Byron 2 |  | 71111.06
Region: III | Byron | 10769 | 01/16/2007 02/12/2007 | 2006005-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO HAVE SETPOINT CONTROL OF THE CONSTANT LEVEL OILERS ON SAFETY-RELATED PUMPS |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152 | The inspectors identified a finding of very low safety significance associated with the failure to maintain control of the setpoints for constant level oilers. This condition increased the challenges to the proper functioning of the lubricating oil and th
Region: III | Byron | 10763 | 12/01/2006 01/12/2007 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Errors in Unverified Design Input Data Used to Determine the Impact of Core Power Uprate on Medium Voltage Loads |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | Green. The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance. The power uprate electrical loading calculation used incorrect design input for the 4160 Vac engineered safety features (
Region: III | Byron | 10764 | 12/01/2006 01/12/2007 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Acceptance Criteria for Safety Injection Pump NPSH Not Met |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111121 | Green. The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance. Specifically, the calculation for evaluating the net positive suction head (NPSH) for the safety injection pump contained
Region: III | Byron | 9586 | 09/30/2006 11/08/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN FIRE BARRIERS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.05Q | The inspectors identified a Non-Cited Violation of Byron Facility Operating License Nos. NPF-37 and NPF-66, Condition 2.c.6, for failing to maintain the firewall separating the Auxiliary Building from the penetration area in accordance with the approved f
Region: III | Byron | 9587 | 09/30/2006 11/08/2006 | 2006004-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO POST AND CONTROL A HIGH RADIATION AREA. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7112101 | An inspector-identified finding of very low safety significance and two associated Non-Cited Violations of NRC requirements were identified for the failure to post and control access to High Radiation Areas, as required by 10 CFR Part 20, to notify indivi
Region: III | Byron | 9588 | 09/30/2006 11/08/2006 | 2006004-03 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO EVALUATE THE POTENTIAL RADIOLOGICAL HAZARD ASSOCIATED WITH THE LEAKAGE OF WATER FROM THE VACUUM BREAKER VALVE VAULT. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7112201 | An inspector-identified finding of very low safety significance and an associated Non-Cited Violation of NRC requirements were identified for the failure to perform surveys that are necessary to comply with the regulations in 10 CFR Part 20 and that are r
Region: III | Byron | 9589 | 09/30/2006 11/08/2006 | 2006004-04 | NRC | URI | Occupational Radiation Safety | Green | IMPACT OF NONFUNCTIONAL DOSIMETERS ON DOSE TRACKING AND TECHNICAL SPECIFICATION COMPLIANCE. |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71151
Region: III | Byron | 9580 | 03/31/2006 05/12/2006 | 2006002-01 | NRC | NCV | Barrier Integrity | Green | DEGRADED INCORRECT PLANT BARRIER IMPAIRMENT EVALUATION RESULTED IN AN AUXILIARY BUILDING INTEGRITY |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71111.13 | A finding of very low safety significance and associated Non-Cited Violation (NCV) of Technical Specification 5.4.1, regarding procedure adherence was inspector identified when the inspectors identified that ventilation barrier requirements were not being
Region: III | Byron | 9582 | 03/31/2006 05/12/2006 | 2006002-03 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE RESULTED IN UNTIMELY COMPLETION OF OPERABILITY EVALUATION |  |  | TE?: N | 05000454 Byron 1 |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specifications 5.4.1, "Procedures," was self-revealed. Specifically, licensee personnel conducted unauthorized troubleshooting activities after an abnormal flow condition was encoun
Region: III | Byron | 9578 | 03/24/2006 04/28/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Into Procedures for Service Water Flow to the CC Heat Exchangers |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111102 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to correctly translate the design basis into procedures. Specifically, the licen
Region: III | Byron | 9579 | 03/24/2006 04/28/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | Reduction of Fire Suppression Capacity and Capability |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 7111117B | The inspectors identified a Non-Cited Violation of 10 CFR 50.48(a)(1) having very low safety significance for the licensee's failure to provide fire fighting systems of appropriate capacity and capability to minimize the adverse effects of fires on struct
Region: III | Byron | 125579 | 11/13/2019 |  | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entry Into a High Radiation Area Where Dose Rates Had Not Been Determined. |  | H.5 - Work Management | TE?: N | 05000455 Byron 2 | Program & Process | 71124.01 | A finding of very low safety significance (Green) and an associated Non-cited Violation of Technical Specification 5.7.2. (e), High Radiation Areas, was self-revealed when the licensee allowed an individual to make entry into a high radiation area where d
Region: III | Byron | 125890 | 11/13/2019 |  |  | LIV |  | Green | Incorrect Respiratory Protection Fit Tests |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71124.03
Region: III | Byron | 126279 | 01/17/2020 |  |  | LIV |  | Green | Failure to Perform Fire Protection Compensatory Actions per Technical Requirements Manual |  |  | TE?: N | 05000454 Byron 1 05000455 Byron 2 |  | 71152
Region: III | Clinton | 125957 | 12/31/2019 02/12/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Breaker Maintenance Frequency |  | NPP | TE?: N | 05000461 Clinton | Equipment Performance | 71153 | A self-revealed Green finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified when the licensee failed to review for suitability of application of materials that were essential to the
Region: III | Clinton | 125206 | 06/30/2019 08/13/2019 | 2019002-01 | NRC | FIN | Initiating Events | Green | Failure to Properly Evaluate the Plant Risk for an Emergent Condition |  | H.9 - Training | TE?: N | 05000461 Clinton |  | 71111.13 | The inspectors identified a Green finding for the licensee’s failure to follow Procedure WC-AA-100-1006, “On-Line Risk Management.” Specifically, the licensee failed to contact the site risk management engineer when they encountered a non-quantified confi
Region: III | Clinton | 125411 | 06/21/2019 07/31/2019 | 2019040-01 | NRC | NCV | Mitigating Systems | Green | Failure to Complete an Effectiveness Review for a Corrective Action to Prevent Recurrence that Challenged the Corrective Actions |  | H.14 - Conservative Bias | TE?: N | 05000461 Clinton |  | 95001 | An NRC identified Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion II, “Quality Assurance Program,” for the failure to accomplish activities affecting quality in accordance with the Quality Assurance Topical Rep
Region: III | Clinton | 124808 | 03/31/2019 05/07/2019 | 2019001-01 | Self - Revealed | FIN | Initiating Events | Green | Failure To Take Conservative Action Resulting in an Automatic Reactor Scram |  | H.1 - Resources | TE?: N | 05000461 Clinton | Human Performance | 71153 | A self-revealed Green finding was identified for the failure to follow Station Procedure OP-AA-300, "Reactivity Management," Revision 12. Specifically, the licensee failed to take conservative action in response to pressure control challenges experienced
Region: III | Clinton | 124588 | 03/29/2019 05/08/2019 | 2019011-01 | NRC | FIN | Mitigating Systems | Green | Failure to Have Procedures Ensuring Satisfactory Performance of Decay Heat Removal Systems during Station Blackout Event |  | NPP | TE?: N | 05000461 Clinton | Procedure Quality | 71111.21M | The inspectors identified a Green finding for the licensee's failure to have procedures ensuring the satisfactory performance of the high pressure core spray (HPCS) system and the suppression pool during a station blackout out (SBO) event as delineated in
Region: III | Clinton | 25908 | 12/31/2018 02/12/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent the Installation of Non-Conforming Parts in a Safety-Related System |  | NPP | TE?: N | 05000461 Clinton |  | 71111.12 | A self-revealed Green finding and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XV, “Nonconforming Materials, Parts, or Components,” was identified when the licensee failed to prevent the installation of non-conforming p
Region: III | Clinton | 25909 | 12/31/2018 02/12/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Degraded Condition in the RHR 'B' Shutdown Cooling System |  | H.14 - Conservative Bias | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to establish measure to ensure that conditions adverse to quality, such as failures, malfunctions
Region: III | Clinton | 25910 | 12/31/2018 02/12/2019 | 2018004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Acceptance Criteria for the Division 3 EDG Air Start System |  | P.3 - Resolution | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to include appropriate acceptance criteria to ensure the Division 3 emergency
Region: III | Clinton | 25911 | 12/31/2018 02/12/2019 | 2018004-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedures Resulting in a Control Rod Drive Pump Trip |  | H.12 - Avoid Complacency | TE?: N | 05000461 Clinton |  | 71152 | A self-revealed Green finding and associated NCV of TS 5.4.1 was identified for the failure to follow Station Procedure CPS 3304.01, “Control Rod Hydraulic & Control,” Revision 38, which resulted in the trip of the running CRD pump as a result of a human
Region: III | Clinton | 25880 | 10/19/2018 11/28/2018 | 2018041-01 | NRC | NCV | Mitigating Systems | Green | Failure to Close Corrective Action to Prevent Recurrence in Accordance with Quality Assurance Topical Report Implementing Procedure |  | H.1 - Resources | TE?: N | 05000461 Clinton |  | 95001 | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion II, “Quality Assurance Program,” for the failure to accomplish activities affecting qualit
Region: III | Clinton | 25882 | 10/19/2018 11/28/2018 | 2018041-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Acceptance Criteria for Component Performance Monitoring |  | H.13 - Consistent Process | TE?: N | 05000461 Clinton |  | 95001 | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, “Instruction Procedures, and Drawings,” for the failure to establish acceptance criteria in a
Region: III | Clinton | 25881 | 10/19/2018 11/28/2018 | 2018041-03 | NRC | FIN | Mitigating Systems | Green | Failure to Establish an Adequate Effectiveness Review |  | H.8 - Procedure Adherence | TE?: N | 05000461 Clinton |  | 95001 | The inspectors identified a Green finding for the failure to establish an effectiveness review in accordance with PI–AA–125–1004, “Effectiveness Review Manual,” Revision 2. Specifically, the licensee failed to establish an effectiveness review that analyz
Region: III | Clinton | 24698 | 09/30/2018 11/07/2018 | 2018003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Revise an Operability Evaluation When No Longer Meeting a Compensatory Measure |  | H.3 - Change Management | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a Green finding for the failure to revise an operability evaluation when no longer meeting a compensatory measure, in accordance with OP–AA–115, “Operability Determinations,” Revision 21. Specifically, the licensee failed to revi
Region: III | Clinton | 24385 | 08/03/2018 08/23/2018 | 2018050-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality |  | H.12 - Avoid Complacency | TE?: N | 05000461 Clinton |  | 93812 | On May 17, 2018, a Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” were self-revealed for the licensee’s failure to promptly identify that the safety-related Division 2 Emergency Diese
Region: III | Clinton | 24386 | 08/03/2018 08/23/2018 | 2018050-03 | Self - Revealed | NCV | Mitigating Systems | Green | Equipment Operator Rounds Points Inadequate Acceptance Criteria |  | H.6 - Design Margins | TE?: N | 05000461 Clinton |  | 93812 | On May 17, 2018, a Green finding and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” were self-revealed for the licensee’s failure to include appropriate quantitative acceptance crite
Region: III | Clinton | 24143 | 06/30/2018 08/03/2018 | 2018002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform an Operability Determination for Suspected Leakage Past Shutdown Service Water Isolation Valves |  | H.6 - Design Margins | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a Green finding for the failure to perform an operability determination in accordance with Procedure OP–AA–108–115, “Operability Determinations (CM–1).” Specifically, the licensee failed to determine and document the operability
Region: III | Clinton | 24144 | 06/30/2018 08/03/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Adequate Leak Rate Test Procedures for Shutdown Service Water Isolation Valve Testing |  | NPP | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a Green finding and a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the failure to ensure testing of the shutdown service water (SX) isolation valves was performed with procedures whic
Region: III | Clinton | 23525 | 03/31/2018 04/18/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Unplanned Reactor Core Isolation Cooling Unavailability |  | H.4 - Teamwork | TE?: N | 05000461 Clinton |  | 71111.22 | A self-revealed Green finding and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures and Drawings,” was identified when the licensee failed to follow station proc
Region: III | Clinton | 23550 | 03/31/2018 04/18/2018 | 2018001-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify a Single Point Vulnerability Results in Manual Reactor Scram |  | NPP | TE?: N | 05000461 Clinton |  | 71153 | A self-revealed Green finding was identified for the licensee’s failure to identify a single point vulnerability in accordance with procedure ER–AA–2004, Revision 1. Specifically, during a site single point vulnerability review of the feedwater system, th
Region: III | Clinton | 24419 | 12/31/2017 02/08/2018 | 2017004-01 | Self - Revealed | FIN | Initiating Events | Green | REACTOR DOWN POWER DUE TO REACTOR RECIRCULATION PUMP MOTOR LOWER BEARING OIL LEAK |  | H.5 - Work Management | TE?: N | 05000461 Clinton |  | 71153 | A self-revealed finding of very low safety significance was identified for the licensee’s failure to comply with the requirements of station procedure MA–AA–716–004, “Compression Fittings Inspection, Installation, Remake and Repair,” Revision 3. Specifica
Region: III | Clinton | 22647 | 12/31/2017 02/08/2018 | 2017004-02 | NRC | NCV | Initiating Events | Green | FAILURE TO ASSESS AND MANAGE RISK ASSOCIATED WITH THE PERFORMANCE OF CONTROL ROD TIME TESTING |  | H.5 - Work Management | TE?: N | 05000461 Clinton |  | 71153 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50.65(a)(4), “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” for the licensee’s failure to assess and manage th
Region: III | Clinton | 23501 | 12/31/2017 02/08/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify the Extent of Condition for an Inadequate 10 CFR 50.59 Evaluation |  | H.8 - Procedure Adherence | TE?: N | 05000461 Clinton |  | 92723 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion II, “Quality Assurance Program,” for the licensee’s failure to follow a procedure that implemented the Quality Assurance Prog
Region: III | Clinton | 23147 | 12/21/2017 01/29/2018 | 2017012-01 | NRC | NCV | Initiating Events | Green | Failure to Perform a Corrective Action to Prevent Recurrence |  | H.5 - Work Management | TE?: N | 05000461 Clinton |  | 93812 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, “Corrective Actions,” for the licensee’s failure to take corrective action to pre
Region: III | Clinton | 23150 | 12/21/2017 01/29/2018 | 2017012-02 | NRC | FIN | Initiating Events | Green | Failure to Properly Classify Nonsafety-Related Auxiliary Transformers as Operationally Critical Components |  | H.13 - Consistent Process | TE?: N | 05000461 Clinton |  | 93812 | The inspectors identified a finding of very low safety significance for the licensee’s failure to follow procedure ER-AA-200-1001, “Equipment Classification,” Revision 3. Specifically, three nonsafety related 4160 volt to 480 volt transformers were not pr
Region: III | Clinton | 21636 | 09/30/2017 11/07/2017 | 2017003-01 | Self - Revealed | NCV | Barrier Integrity | Green | MSIV TS Leakage Limits Exceeded Due to Condition Based Maintenance Approach |  | H.6 - Design Margins | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors documented a self-revealed finding of very low safety significance and an associated NCV of TS limiting condition for operation (LCO) 3.6.1.3, for the failure to follow station procedure ER–AA–200, “Preventative Maintenance Program,” Revisi
Region: III | Clinton | 21668 | 09/30/2017 11/07/2017 | 2017003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO ADEQUATELY CONTROL ACCESS IN LOCKED HIGH RADIATION AREA |  | H.1 - Resources | TE?: N | 05000461 Clinton |  | 71124.01 | A finding of very low safety significance and an associated NCV of TS 5.4.1 was self-revealed when individuals failed to adequately control access in locked high radiation areas (LHRAs). Specifically, the failure to meet all of the requirements of Procedu
Region: III | Clinton | 21669 | 09/30/2017 11/07/2017 | 2017003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM EVALUATION TO DETERMINE THE CAUSE OF FAILURE OF SNUBBERS |  | H.13 - Consistent Process | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to demonstrate c
Region: III | Clinton | 21670 | 09/30/2017 11/07/2017 | 2017003-04 | Self - Revealed | NCV | Initiating Events | Green | FLOW CONTROL VALVES NOT LOCKED OUT RESULTS IN REACTOR RECIRCULATION PUMP RUNBACK |  | H.14 - Conservative Bias | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1, “Procedures,” for the licensee’s failure to establish sufficient instructions in station procedure Clinton Power
Region: III | Clinton | 21671 | 09/30/2017 11/07/2017 | 2017003-05 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO ESTABLISH SECONDARY CONTAINMENT PRIOR TO ENTERING MODE 2 |  | H.9 - Training | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealed finding of very low safety significance and an associated NCV of TS LCO 3.0.4, for the failure to follow station procedure CC–AA–201, “Plant Barrier Control Program,” Revision 11. Specifically, the licensee entere
Region: III | Clinton | 21695 | 09/29/2017 11/06/2017 | 2017007-01 | NRC | NCVIV | Mitigating Systems | Green | FAILURE TO EVALUATE DEFEATING REACTOR CORE ISOLATION COOLING SYSTEM INTERLOCKS AND TRIPS BEFORE ADDING THEM TO AN EMERGENCY OPERATING SUPPORT PROCEDURE |  | H.1 - Resources | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71152B | The inspectors identified a Severity Level IV NCV of Title 10 Code of Federal Regulations (CFR) 50.59(d)(1), “Changes, Test, and Experiments,” and an associated finding, for the licensee’s failure to perform a written evaluation which provided the bases f
Region: III | Clinton | 22388 | 08/11/2017 08/11/2017 | 2017002-02 | NRC | VIO | Barrier Integrity | Green | FAILURE TO PERFORM ADEQUATE EVALUATION OF CRANE RAIL CLIPS |  | P.3 Resolution | TE?: N | 05000461 Clinton |  | 71111.18 | The inspectors identified a finding of very-low safety significance and an associated cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to properly verify the adequacy of design of the fuel building crane and
Region: III | Clinton | 22387 | 06/30/2017 08/11/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE OF OPERATORS TO MEET TIME CRITICAL OPERATOR ACTIONS |  |  | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that applicable regulatory requirements and the desig
Region: III | Clinton | 22389 | 06/30/2017 08/11/2017 | 2017002-03 | Self - Revealed | NCV | Initiating Events | Green | UNEXPECTED START OF THE DIVISION 3 EMERGENCY DIESEL GENERATOR |  | H.12 Avoid Complacency | TE?: N | 05000461 Clinton |  | 71111.2 | The inspectors documented a self-revealed finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for th
Region: III | Clinton | 22390 | 06/30/2017 08/11/2017 | 2017002-04 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO PROVIDE SUFFICIENT WORK INSTRUCTIONS FOR PERFORMING MAINTENANCE ON THE CONTROL ROOM VENTILATION SYSTEM CHARCOAL FILTER |  | H.6 Design Margins | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors documented a self-revealed finding of very low safety significance and an associated non-cited violation of 10 of CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of the licensee to provide suf
Region: III | Clinton | 22391 | 06/30/2017 08/11/2017 | 2017002-05 | Self - Revealed | NCV | Public Radiation Safety | Green | FAILURE TO PROPERLY CLASSIFY A SHIPMENT PER DOT REGULATIONS |  | H.11 Challenge the Unknown | TE?: N | 05000461 Clinton |  | 71124.08 | A finding of very low safety significance and an associated non-cited violation of Title 10 of CFR 71.5(a) and 49 CFR 173.421(b) was self revealed when the licensee failed to properly classify a shipment per Department of Transportation (DOT) regulations.
Region: III | Clinton | 22392 | 06/30/2017 08/11/2017 | 2017002-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PERFORM PREVENTIVE MAINTENANCE ON A SAFETY-RELATED BREAKER CUBICLE |  |  | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance for the licensee's failure to perform maintenance on a safety-related motor control center cubicle. Specifically, the licensee failed to perform thermography on the division 1 shutdown se
Region: III | Clinton | 22393 | 06/30/2017 08/11/2017 | 2017002-07 | NRC | NCV | Initiating Events | Green | ROOT CAUSE EVALUATION FAILED TO IDENTIFY CORRECTIVE ACTION TO PRECLUDE REPETITION |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement a quality assurance program procedure. Specifi
Region: III | Clinton | 22380 | 04/21/2017 05/30/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Surveillances on Multiple Fire Dampers (Section 1R05.2b) |  | H.5 Work Management | TE?: N | 05000461 Clinton |  | 71111.05T | Green. The inspectors identified a finding of very-low safety significance (Green), and an associated Non-Cited Violation of License Condition 2.C(f) for the licensee's failure to adequately implement surveillance procedures and work processes associated
Region: III | Clinton | 22061 | 03/31/2017 05/08/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | PLANT BARRIER CONTROL PROGRAM FAILED TO COMPENSATE FOR AN IMPACTED FLOOD BARRIER |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to i
Region: III | Clinton | 22062 | 03/31/2017 05/08/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | FAILED TO VERIFY AN APPROPRIATE ALTERNATE METHOD OF DECAY HEAT REMOVAL |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50.36(c)(2)(i), "Limiting conditions for operation", for failing to meet/follow the required actions for limiting condition for operation 3
Region: III | Clinton | 22066 | 03/31/2017 05/08/2017 | 2017001-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO DEVELOP AND REVIEW A WORKER TAG OUT |  | H.12 Avoid Complacency | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealed finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1, "Procedures," for the licensee's failure to develop and review a worker tag out in accordance with stati
Region: III | Clinton | 22379 | 03/31/2017 05/08/2017 | 2017001-04 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM MAINTENANCE ON RESIDUAL HEAT REMOVAL PUMP 'C' BREAKER IN ACCORDANCE WITH PROCEDURES |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealed finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to perform maintenance on
Region: III | Clinton | 22029 | 12/31/2016 02/09/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Condition of Flood Seals was being Effectively Controlled |  | P.1 Identification | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50.65(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to demonstr
Region: III | Clinton | 22030 | 12/01/2016 01/12/2017 | 2016009-01 | NRC | NCV | Barrier Integrity | Green | Non Conservative Control Room Radiological Habitability Assessment (Section 1R21.3.b(1)) |  |  | TE?: N | 05000461 Clinton |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee failure to use a technically appropriate analytical methodology in the cont
Region: III | Clinton | 22043 | 12/01/2016 01/12/2017 | 2016009-02 | NRC | NCV | Barrier Integrity | Green | Failure to Scope SFP Temperature and Level Instruments into the Maintenance Rule Program (Section 1R21.3.b(2)) |  | H.3 Change Management | TE?: N | 05000461 Clinton |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of Paragraph (b)(2)(i) of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee failure to
Region: III | Clinton | 22057 | 12/01/2016 01/12/2017 | 2016009-04 | NRC | NCV | Barrier Integrity | Green | Failure to Verify the Adequacy of Design Assumptions Related to Time Critical Operator Actions (Section 1R21.6.b(1)) |  | H.4 Teamwork | TE?: N | 05000461 Clinton |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee failure to verify the adequacy of design assumptions related to time critic
Region: III | Clinton | 22058 | 12/01/2016 01/12/2017 | 2016009-05 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify that the Incapability of the RHR Design to Support TS Operability Requirements Was a CAQ (Section 4OA2.b(1)) |  |  | TE?: N | 05000461 Clinton |  | 7111121 | Green: The team identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee failure to promptly identify
Region: III | Clinton | 22059 | 12/01/2016 01/12/2017 | 2016009-06 | NRC | NCV | Barrier Integrity | Green | Failure to Follow the Operability Determination Process Following the Identification of a Control Room HVAC System Design Issue (Section 4OA2.b(2)) |  | H.9 Training | TE?: N | 05000461 Clinton |  | 7111121 | Green: The team identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," for the licensee failure to follow the operability evaluation procedur
Region: III | Clinton | 22014 | 09/30/2016 11/10/2016 | 2016003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Scope Fuel Building Ventilation Pressure Control into Maintenance Rule |  | H.12 Avoid Complacency | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR 50.65 (b) for the licensee's failure to scope a non-safety related structure, system and component (SSC), whose function is used in one or more Emergency Operating Pr
Region: III | Clinton | 22022 | 09/30/2016 11/10/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Exceeded Technical Specification Allowed Outage Time for Main Turbine Bypass System |  | H.3 Change Management | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification 3.7.6, "Main Turbine Bypass System" for the licensee's failure to meet the limiting conditions for operation and complete the associated r
Region: III | Clinton | 22023 | 09/30/2016 11/10/2016 | 2016003-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a 50.59 Screening for Changing the Frequency of Exercising the Turbine Bypass Valves |  | H.13 Consistent Process | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71111.18 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.59 4(d)(1), "Changes, Tests, and Experiments," and an associated Green finding for the licensee's failure to perform a written evaluation which provided the bases for determining that changing
Region: III | Clinton | 22024 | 09/30/2016 11/10/2016 | 2016003-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Prevent Recurrence of a Significant Condition Adverse to Quality |  |  | TE?: N | 05000461 Clinton |  | 71152 | The inspectors documented a self-revealing finding of very low safety significance and an NCV of 10 CFR 50, Appendix B, Criterion XVI for the licensee's failure to take corrective action to preclude repetition of a significant condition adverse to quality
Region: III | Clinton | 21972 | 09/30/2016 11/10/2016 | 2016003-05 | NRC | NCV | Barrier Integrity | Green | Spent Fuel Pool Liner Design not Verified per Code |  | H.6 Design Margins | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion III for the failure of the licensee's design control measures to provide for the verifying or checking of the adequacy of design of the
Region: III | Clinton | 22013 | 08/09/2016 09/22/2016 | 2016007-01 | NRC | FIN | Mitigating Systems | Green | Failure to have hose configurations that were verified to be able to ensure a timely and successful implementation of a FLEX strategy |  | H.6 Design Margins | TE?: N | 05000461 Clinton |  | 2515/191 | Green. Two examples of a finding of very low safety significance was identified by the inspectors for the licensee's failure to have hose configurations that were verified to be able to ensure a timely and successful implementation of a flexible response
Region: III | Clinton | 21996 | 06/30/2016 08/10/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Material Unsecure in the Secured Material Zone |  | H.2 Field Presence | TE?: N | 05000461 Clinton |  | 71111.01 | The inspectors identified a finding of very low safety significance for the failure to ensure material placed within the transformer secured material zone, was secured as required by station procedure MA-AA-716-026, "Station Housekeeping/Material Conditio
Region: III | Clinton | 21997 | 06/30/2016 08/10/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Inspection Fails to Identify Safety Related Cables Submerged in Cable Vault |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71111.06 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action Program," for the failure to identify a condition adverse to quality. Specifically, the licensee fai
Region: III | Clinton | 21998 | 06/30/2016 08/10/2016 | 2016002-03 | NRC | FIN | Mitigating Systems | Green | Failure to Properly Install Cable Vault Mitigating Equipment |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 71111.06 | The inspectors identified a finding of very low safety significance (Green) for the failure to incorporate human performance standards when developing work package instructions in accordance with MA-AA-716-010,"Maintenance Planning," Revision 23. Specific
Region: III | Clinton | 22002 | 06/30/2016 08/10/2016 | 2016002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Ultrasonic Examination Method Used to Detect Crack-Like Flaws |  | H.8 Procedure Adherence | TE?: N | 05000461 Clinton |  | 71111.08G | On May 17, 2016, the inspectors identified a finding of very-low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure to ensure that nondestructive testing was controlled
Region: III | Clinton | 22003 | 06/30/2016 08/10/2016 | 2016002-05 | NRC | NCV | Barrier Integrity | Green | Lack of Acceptance Criteria for Containment Visual Examinations |  | H.13 Consistent Process | TE?: N | 05000461 Clinton |  | 71111.08G | The inspectors identified a finding of very-low safety significance and associated NCV of 10 CFR 50.55a(g)(4). Specifically, the licensee failed to define acceptance criteria for containment visual examinations. Consequently, active containment liner degr
Region: III | Clinton | 22004 | 06/30/2016 08/10/2016 | 2016002-06 | NRC | NCV | Initiating Events | Green | Failure to Perform Surface Examination Prior to Weld Repair of a Reactor Water Cleanup System Pipe |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71111.08G | The inspectors identified a finding of very-low safety significance and associated NCV of 10 CFR 50.55a(g)(4). Specifically, the licensee failed to perform a surface examination to detect cracking on reactor water cleanup small-bore piping prior to perfor
Region: III | Clinton | 22007 | 06/30/2016 08/10/2016 | 2016002-07 | NRC | NCVIV | Initiating Events | Green | Failure to Obtain License Amendment prior to Operating Reactor Water Cleanup Bypass Switches |  |  | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71111.18 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.59(a)(1), "Changes, Tests, and Experiments," and an associated Green finding for the licensee's failure to perform an adequate written safety evaluation to provide the basis that changes to th
Region: III | Clinton | 21986 | 03/31/2016 05/09/2016 | 2016001-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify a Degraded Safety-Related Support |  | P.2 Evaluation | TE?: N | 05000461 Clinton |  | 71111.04Q | . The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify a condition adverse to quality. Specifically, the license
Region: III | Clinton | 21987 | 03/31/2016 05/09/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Operability Determination Failed to Examine Test Failures |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions Procedures and Drawings," for the failure to follow Station
Region: III | Clinton | 21991 | 03/31/2016 05/09/2016 | 2016001-05 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Assess and Manage Risk Increase for a Proposed Maintenance Activity |  | H.11 Challenge the Unknown | TE?: N | 05000461 Clinton |  | 71153 | A self-revealed finding of very low safety significance and an associated non-cited violation of 10 CFR 50.65 (a)(4) was identified on January 20, 2016, due to the licensee's failure to assess and manage the risk increase from a proposed maintenance activ
Region: III | Clinton | 21992 | 03/31/2016 05/09/2016 | 2016001-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition Associated with an ACE |  | H.8 Procedure Adherence | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to follow a Quality Assurance Program implementing procedur
Region: III | Clinton | 22012 | 02/11/2016 03/03/2016 | 2016010-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Adequate Evaluation of Crane and Crane Support Structure Elements |  | H.6 Design Margins | TE?: N | 05000461 Clinton |  | 60856.1 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure of the licensee's design control measures to provide for the verifying
Region: III | Clinton | 21979 | 02/04/2016 03/17/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform and Adequate Equipment Apparent Cause Evaluation (Section 4OA4) |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 95001 | The inspectors identified a finding of very-low safety significance (Green), and an associated Non-Cited Violation of Title 10, Code of Federal Regulations, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's fai
Region: III | Clinton | 21971 | 12/31/2015 02/04/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Activities Affecting Quality in Accordance with Prescribed Procedures |  | H.11 Challenge the Unknown | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR50, Appendix B, Criterion V, "Instructions Procedures and Drawings," for the failure to ensure that activities affecting quality were accomp
Region: III | Clinton | 21978 | 12/31/2015 02/04/2016 | 2015004-03 | NRC | FIN | Initiating Events | Green | Failure to Follow Station Procedures for Plant Activities |  | H.11 Challenge the Unknown | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance for the failure to ensure that activities were accomplished in accordance with prescribed procedures as required by station procedure HU-AA-104-101 "Procedure Use and Adherence." Specific
Region: III | Clinton | 21967 | 10/09/2015 11/06/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Generate Issue Reports for Conditions Adverse to Quality |  | P.1 Identification | TE?: N | 05000461 Clinton |  | 71152B | The inspectors identified a finding of very low safety significance, and an associated NCV of Title 10, Code of Federal Regulations, Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to perform activities in accordance with p
Region: III | Clinton | 21955 | 09/30/2015 11/06/2015 | 2015003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURE LEAVES CONTROL ROOM CABINET DOORS UNATTENDED IN SEISMICALLY UNANALYSED CONDITION |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to maintain control room doors in a seismically analyzed cond
Region: III | Clinton | 21963 | 09/30/2015 11/06/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT AND COMPLY WITH TRANSIENT EQUIPMENT/MATERIALS PROGRAM |  | H.2 Field Presence | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a green finding and an associated NCV of 10 CFR 50, Appendix B, Criterion V "Instructions, Procedures, and Drawings" for the licensee's failure to implement and comply with station procedure CPS 1019.05, "Transient Equipment/Mate
Region: III | Clinton | 21964 | 09/30/2015 11/06/2015 | 2015003-03 | NRC | NCVIV | Barrier Integrity | Green | FAILURE TO OBTAIN A LICENSE AMENDMENT PRIOR TO MAKING MODIFICATIONS TO SECONDARY CONTAINMENT |  | H.8 Procedure Adherence | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71111.18 | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments" for the licensee's failure to provide a written evaluation, which provided the basis for determining that the change to the secondar
Region: III | Clinton | 21966 | 09/30/2015 11/06/2015 | 2015003-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ENTER APPROPRIATE TS ACTION STATEMENT FOR INOPERABLE RADIATION MONITORS DURING OPDRV ACTIVITIES |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 71153 | The inspectors identified a green finding and associated NCV of T.S. 3.3.6.1 "Primary Containment and Drywell Isolation Instrumentation" and 3.3.6.2 "Secondary Containment Isolation Instrumentation," for the failure to enter the appropriate action stateme
Region: III | Clinton | 21939 | 06/30/2015 08/04/2015 | 2015002-02 | Self - Revealed | NCV | Initiating Events | Green | POST MAINTENANCE TEST FAILED TO DEMONSTRATE REQUIRED FLOW THROUGH RCIC ROOM COOLER |  | H.5 Work Management | TE?: N | 05000461 Clinton |  | 71111.19 | A self-revealed finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50 Appendix B, Criterion XI, Test Control, was documented by the inspectors for the failure to perform adequate post maintenance testing that would ass
Region: III | Clinton | 21950 | 06/30/2015 08/04/2015 | 2015002-03 | NRC | NCV | Occupational Radiation Safety | Green | CONTRACT WORKERS NOT MONITORED FOR OCCUPATIONAL RADIATION EXPOSURE |  | H.3 Change Management | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very-low safety significance and an associated NCV of Technical Specification (TS) 5.4.1, "Procedures," for the failure to monitor the radiation dose received by a group of workers as required by station procedure RP
Region: III | Clinton | 21951 | 06/30/2015 08/04/2015 | 2015002-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO TRANSLATE SUFFICIENT GLAND STRESS TO PACKING GLAND NUTS RESULTED IN VALVE PACKING FAILURE AND PLANT SHUTDOWN |  |  | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR50, Appendix B, Criterion III, "Design Control," was self-revealed on January 19, 2015, when a steam leak developed from the RCIC system inboard steam isolation valve
Region: III | Clinton | 21954 | 06/30/2015 08/04/2015 | 2015002-05 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO EVALUATE THE OPERATIONAL IMPACT OF THE TDRFP LOCKOUT SWITCH POSITION |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71152 | A self-revealed finding was identified for failure to evaluate the consequences of an adverse condition, in accordance with the operational decision making process. Specifically, contrary to station procedure OP-AA-106-101-1006 "Operational Decision Makin
Region: III | Clinton | 21929 | 03/31/2015 05/13/2015 | 2015001-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE CHANNEL CALIBRATION ON SEISMIC INSTRUMENTATION |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a Green Finding associated with the licensee's failure to perform an adequate channel calibration to determine the functionality of the stations seismic monitoring equipmen used for evaluaing earthquakes. Specifically, station pr
Region: III | Clinton | 21935 | 03/31/2015 05/13/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | UNQUALIFIED SAFETY-RELATED CABLES USED IN A SUBMERGED ENVIRONMENT |  | P.3 Resolution | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding and an associated non-citied violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," for the failure to maintain safety-related cables for the SX system in an environment for which they were designed. Specif
Region: III | Clinton | 21937 | 03/20/2015 04/23/2015 | 2015008-01 | NRC | NCVIV | Mitigating Systems | Green | Inadequate 50.59 Evaluation for Switchgear in Seismically Unanalyzed Conditions (Section 1R17.1b.) |  |  | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71111.17T | Severity Level IV Green. The inspectors identified a finding of very-low safety significance, and an associated Non-Cited Violation of Title 10, Code of Federal Regulations Part 50, Section 59, "Changes, Tests and Experiments," (effective January 1, 1997)
Region: III | Clinton | 21915 | 12/31/2014 02/06/2015 | 2014005-01 | NRC | NCV | Initiating Events | Green | STATION PROCEDURES FAILED TO PROVIDE CONTROLS FOR MATERIAL NEAR TRANSFORMERS |  | P.5 Operating Experience | TE?: N | 05000461 Clinton |  | 71111.01 | The inspectors identified a non-cited violation associated with a failure to provide controls for material near the station transformers. Specifically, station procedure CPS 4302.01, "Tornado/High Winds", Revision 21b does not include guidelines or exampl
Region: III | Clinton | 21919 | 12/31/2014 02/06/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TRANSLATE SEISMIC DESIGN REQUIREMENTS INTO APPLICABLE PROCEDURES |  | P.5 Operating Experience | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a green non-cited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, for the failure to adequately translate seismic requirements from a design calculation into applicable procedures. Specifically the licensee fai
Region: III | Clinton | 21920 | 12/31/2014 02/06/2015 | 2014005-04 | NRC | NCVIV | Barrier Integrity | Green | FAILURE TO UPDATE THE UPDATED SAFETY ANALYSIS REPORT - 1VR08C FUNCTION |  |  | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71152 | The inspectors identified a Severity Level IV non-cited violation of Title 10 Code of Federal Regulations (CFR) 50.71(e), "Periodic Update of the USAR" and an associated Green finding for the licensee's failure to update the USAR with the correct descript
Region: III | Clinton | 21926 | 12/31/2014 02/06/2015 | 2014005-05 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE PROCEDURE INSTRUCTION RESULTS IN EXCEEDING TECHNICAL SPECIFICATION HEAT UP RATE DURING PLANT START UP |  | H.5 Work Management | TE?: N | 05000461 Clinton |  | 71153 | The inspectors are documenting a self-revealing non-cited violation of Technical Specification 5.4., "Procedures," for the licensee's failure to establish instructions in station procedure CPS 9059.01, "Reactor Coolant System Leakage Test," Revision 9b. S
Region: III | Clinton | 21897 | 09/30/2014 11/04/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | EXCEEDED TECHNICAL SPECIFICATION ALLOWED OUTAGE TIME FOR ELECTRICAL POWER SYSTEMS DUE TO AUXILIARY EQUIPMENT OUT OF SERVICE |  | H.12 Avoid Complacency | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 3.8.4, "DC Sources - Operating" and Technical Specification 3.8.9, "Distribution Systems - Operating" for failing to enter the technical specifications and complete the associated
Region: III | Clinton | 21901 | 09/30/2014 11/04/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | PROGRAMMATIC FAILURE TO COMPLETE OPERABILITY AND FUNCTIONALITY DETERMINATIONS |  | H.9 Training | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion V, Instructions, Procedures and Drawings, "Procedures," for the failure to accomplish station procedure OP-AA-108-115, "Operability Determinations" Revision 14. Specificall
Region: III | Clinton | 21902 | 09/30/2014 11/04/2014 | 2014004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH SURVEILLANCE PRODEDURE FOR REACTOR CORE ISOLATION COOLING PUMP DUE TO UNACCEPTABLE PRECONDITIONING |  | P.5 Operating Experience | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors determined that the failure to establish a surveillance procedure to test the RCIC system due to unacceptable preconditioning is a performance deficiency. The performance deficiency was more than minor because it was associated with the pro
Region: III | Clinton | 21903 | 09/30/2014 11/04/2014 | 2014004-04 | NRC | NCV | Emergency Preparedness | Green | INCOMPLETE EVACUATION TIME ESTIMATE SUBMITTALS |  | H.7 Documentation | TE?: N | 05000461 Clinton |  | 71114.05 | The inspectors determined that Exelon's failure to submit a complete updated ETE for the Clinton Power Station by December 22, 2012 was a performance deficiency. Specifically, the ETE is an input into the development of protective action strategies prior
Region: III | Clinton | 21904 | 09/30/2014 11/04/2014 | 2014004-05 | NRC | NCVIV | Initiating Events | Green | FAILURE TO UPDATE THE FINAL SAFETY ANALYSIS REPORT (FSAR) - SD STRUCTURAL INTEGRITY FUNCTION |  |  | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71152 | The inspectors identified a Severity Level IV Non-Cited Violation of title 10 Code of Federal Regulations (CFR) 50.71(e), 'Periodic Update of the Final Safety Analysis Report' and an associated Green finding for the licensee's failure to update the Final
Region: III | Clinton | 21911 | 09/30/2014 11/04/2014 | 2014004-06 | NRC | NCVIV | Initiating Events | Green | MODIFICATION TO STEAM DRYER TIE BARS 28 AND 30 WITHOUT A 10 CFR 50.59 SAFETY EVALUATION |  |  | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | 71152 | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59(d)(1), "Changes, Test, and Experiments" for the licensee's failure to perform a written evaluation, which provided the bases for the determination that a change did not requ
Region: III | Clinton | 21895 | 07/11/2014 08/28/2014 | 2014008-01 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO IDENTIFY A LEVEL 1 TEST CRITERION FAILURE |  | H.14 Conservative Bias | TE?: N | 05000461 Clinton |  | 95001 | The inspectors documented a self-revealing Green finding associated with the failure to follow procedures when performing power ascension testing on the digital feedwater (DFW) system. Specifically, contrary to procedure CPS 2894.01, "Digital FWLC [feedwa
Region: III | Clinton | 21400 | 06/30/2014 08/01/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | FOREIGN MATERIAL IN RELAY PREVENTS EMERGENCY DIESEL GENERATOR OUTPUT BREAKER FROM CLOSING |  | H.5 Work Management | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors documented a self-revealing, Green non-cited violation of Clinton Power Station Technical Specification 5.4.1, "Procedures," for a failure to prevent foreign material from entering a relay associated with the Division 1 Diesel Generator. Sp
Region: III | Clinton | 21894 | 06/30/2014 08/01/2014 | 2014003-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO DEVELOP ADEQUATE PROCEDURES FOR PRE-PLANNING AND PERFORMING MAINTENANCE AFFECTING SAFETY-RELATED EQUIPMENT |  |  | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealing, Green non-cited violation (NCV) of Clinton Power Station Technical Specification 5.4.1, "Procedures" for a failure to develop adequate procedures for properly pre-planning and performing maintenance affecting th
Region: III | Clinton | 21890 | 06/30/2014 08/01/2014 | 2014003-03 | Self - Revealed | FIN | Initiating Events | Green | ELECTRO HYDRAULIC CONTROL SYSTEM LEAK RESULTS IN MANUAL SCRAM |  |  | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealing, Green finding associated with a failure to provide adequate work instructions to perform repairs to the shutoff valve for 1TGCV4 main turbine control valve. Specifically, contrary to station procedure MA-AA-716-
Region: III | Clinton | 21891 | 06/30/2014 08/01/2014 | 2014003-04 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO IMPLEMENT ENGINEERING CHANGE RESULTS IN MANUAL REACTOR SCRAM |  | H.7 Documentation | TE?: N | 05000461 Clinton |  | 71153 | The inspectors documented a self-revealing, Green finding associated with a failure to implement engineering change (EC) 380150 "Upgrade Feed Water Level Control and Turbine Speed." Specifically, contrary to station procedure CC-AA-256, "Process for Manag
Region: III | Clinton | 21394 | 02/14/2014 03/14/2014 | 2014007-02 | NRC | NCV | Initiating Events | Green | Failure to Correct Identified Combustibles |  | H.1 Resources | TE?: N | 05000461 Clinton |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of License Condition 2.F for the failure to remove an identified combustible. Specifically, the failure to remove a piece of wood located directly under a safety-relate
Region: III | Clinton | 21385 | 12/31/2013 02/11/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT REQUIREMENTS OF STATION SCAFFOLD INSTALLATION PROCEDURE. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000461 Clinton |  | 71111.2 | Inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings for the failure to follow station procedure MA AA-796-024, "Scaffold Installation, Inspection, and Removal," Revision 8, to obtain engineering approva
Region: III | Clinton | 21386 | 12/31/2013 02/11/2014 | 2013005-03 | Self - Revealed | FIN | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN RADIATION EXPOSURE ALARA DURING 1R13. |  |  | TE?: N | 05000461 Clinton |  | NONE | Inspectors reviewed a self-revealing finding due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee's Radiological Work Planning and Work Execution Program. Specifically, the lice
Region: III | Clinton | 21387 | 12/31/2013 02/11/2014 | 2013005-04 | NRC | FIN | Barrier Integrity | Green | FAILURE TO IDENTIFY EMBEDDED OPERATOR CHALLENGE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71152 | Inspectors identified a finding of very low safety significance associated with the licensee's failure to identify an embedded operator challenge. Specifically, the licensee proceduralized compensatory actions which were necessary in order to maintain a n
Region: III | Clinton | 21392 | 12/31/2013 02/11/2014 | 2013005-05 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ASSESS AND MANAGE RISK ASSOCIATED WITH THE PERFORMANCE OF SURVEILLANCE TESTING ON AVERAGE POWER RANGE MONITORS |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71153 | Inspectors reviewed a self-revealing NCV of 10 CFR 50.65(a)(4) for failing to manage risk when the Division 4 Nuclear System Protection System (NSPS) inverter unexpectedly transferred from its normal direct current (DC) power source to its alternate alter
Region: III | Clinton | 21382 | 12/19/2013 01/31/2014 | 2013009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Insulation Resistance Testing for Unit Substation Transformers Was Incorrectly Performed |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 93812 | A finding of very low safety significance (Green) and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed from an event that resulted in a reactor scram. Specifically
Region: III | Clinton | 21383 | 12/19/2013 01/31/2014 | 2013009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria in the Insulation Resistance Test Procedure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 93812 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have adequate acceptance criteria in testing procedure.
Region: III | Clinton | 21369 | 09/30/2013 10/31/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE AND APPROPRIATELY DOCUMENT BASIS FOR IMMEDIATE OPERABILITY OF THE DIVISION 2 EMERGENCY DIESEL GENERATOR |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000461 Clinton |  | 71111.04Q | An NRC identified non-cited violation of 10CFR50, Appendix B, Criterion V, Instructions, Procedures and Drawings for the failure to follow procedure OP-AA-108-115, "Operability Determinations", Revision 11, and document the basis that a reasonable expecta
Region: III | Clinton | 21381 | 08/30/2013 10/01/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE A DEGRADED/NON-CONFORMING CONDITION ON DIESEL FIRE PUMP. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance associated with the licensee's failure to appropriately evaluate the functionality of the 'B' Diesel Fire Pump (DFP) after identifying a degraded/non-conforming crankcase pressure conditi
Region: III | Clinton | 21368 | 06/30/2013 07/30/2013 | 2013003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO FOLLOW PROCEDURES RESULTED IN THE UNPLANNED INTAKE OF RADIOACTIVE MATERIAL BY FIVE WORKERS. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | NONE | A self-revealing finding of very low safety significance (Green) and associated Non-Cited Violation of Technical Specification 5.4.1.a for the failure to follow procedures associated with the Radiation Work Permit (RWP) on March 28, 2013. The issue result
Region: III | Clinton | 21362 | 03/31/2013 04/23/2013 | 2013002-01 | NRC | NCV | Occupational Radiation Safety | Green | INCOMPLETE ED DOSE RATE ALARM EVALUATION |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 20.1501(a) for the failure to perform surveys to ensure compliance with 10 CFR 20.1201 shallow-dose equivalent (SDE) limits for five indiv
Region: III | Clinton | 21363 | 03/31/2013 04/23/2013 | 2013002-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE PAST OPERABILITY EVALUATION |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to correctly evaluate the past operability of safety-related motor operator valve 1E51-F031, reactor core isolation cooling system suppression pool
Region: III | Clinton | 21361 | 03/31/2013 04/23/2013 | 2013002-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE MOV PREVENTATIVE MAINTENANCE RESULTED IN INOPERABLE RCIC SYSTEM |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | NONE | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings" was self-revealed when safety-related motor operated valve 1E51-F031, reactor core isolation co
Region: III | Clinton | 21348 | 12/31/2012 01/28/2013 | 2012005-01 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO PERFORM PREVENTIVE MAINTENANCE ON STANDBY GAS TREATMENT SYSTEM RELAY 0UAY-VG506D. |  | H.3(b) Work Activity Coordination | TE?: N | 05000461 Clinton |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4.1.a. was self-revealed when the age-related failure of Standy Gas Treatment (VG) system relay 0UAY-VG506D caused the removal of VG Train A
Region: III | Clinton | 21354 | 12/31/2012 01/28/2013 | 2012005-02 | NRC | NCVIV | Mitigating Systems | Green | FAILURE TO SATISFY 10 CFR 50.73 REPORTING REQUIREMENTS FOR A CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS. |  | H.1(a) Systematic Process for Decisions | TE?: Y SL-IV-NCVIV | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance (Green) with an associated Severity Level IV Non-Cited Vilation of the NRC's reporting requirements in 10 CFR 50.73, "Licensee Event Report System." The licensee failed to submit a requir
Region: III | Clinton | 21353 | 12/31/2012 01/28/2013 | 2012005-03 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO COMPLETE AN ADEQUATE EXTENT CONDITION REVIEW AND TO CORRECT A PREVIOUSLY IDENTIFIED DESIGN PROBLEM RESULTED IN A TRIP OF THE EMERGENCY RESERVE AUXILIARY TRANSFORMER |  |  | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance was self-revealed when the emergency reserve auxiliary transformer (ERAT) tripped during troubleshooting activities to isolate a direct current system ground following heavy rainfall. The ERAT trip occurred due to
Region: III | Clinton | 21344 | 09/30/2012 11/05/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECTLY ASSEMBLE DIESEL GENERATOR VENTILATION SYSTEM DAMPER RESULTED IN INOPERABLE DIESEL GENERATOR |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71111.12 | A finding of very low safety significance with an associated non-cited violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings" was self-revealed on March 1, 2012 when the Division 1 diesel generator (DG) ventilation system
Region: III | Clinton | 21345 | 09/30/2012 11/05/2012 | 2012004-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE PAST OPERABILITY EVALUATIONS FOR EMERGENCY CORE COOLING SYSTEM RELIEF VALVES |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to correctly evaluate the past operability of two emergency core cooling system (ECCS) relief valves that failed bench testing following replacement
Region: III | Clinton | 21343 | 06/30/2012 08/06/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE TORNADO MISSLE PROTECTION FOR SAFETY RELATED COMPONENTS |  | H.3(a) Work Planning | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," when permanently installed tornado missile barrier protection was removed without adequat
Region: III | Clinton | 21342 | 06/30/2012 08/06/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH INSTRUCTIONS APPROPRIATE FOR INSTALLATION OF SHUTDOWN AND UPSET LEVEL INSTRUMENT REFERENCE LEG PIPE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on December 18, 2011, when an automatic reactor scram signal and loss of de
Region: III | Clinton | 21338 | 03/31/2012 05/08/2012 | 2012002-02 | NRC | NCV | Barrier Integrity | Green | UNACCEPTABLE PRECONDITIONING OF LOW PRESSURE COOLANT INJECTION FROM RESIDUAL HEAT REMOVAL 'A' CHECK VALVE PRIOR TO LEAK RATE TEST MEASUREMENT |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to establish an adequate procedure to perform r
Region: III | Clinton | 21340 | 03/31/2012 05/08/2012 | 2012002-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO INCORPORATE OPERATING EXPERIENCE INTO PREVENTIVE MAINTENANCE ACTIVITIES. |  | H.3(b) Work Activity Coordination | TE?: N | 05000461 Clinton |  | 71152 | A self-revealed finding of very low safety significance was identified with an associated Non-Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants." The licensee failed to incorporate opera
Region: III | Clinton | 21326 | 12/31/2011 02/01/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY APPLY AN APPROVED ASME CODE CASE |  |  | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.55a due to the licensee's failure to adequately apply American Society of Mechanical Engineers Section XI Code Case N-513-3 when it eva
Region: III | Clinton | 21327 | 12/31/2011 02/01/2012 | 2011005-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO CONTROL THE WORK HOURS OF A COVERED WORKER. |  | H.4(b) Procedural Compliance | TE?: N | 05000461 Clinton |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 26.205(c) and (d) for the licensee's failure to schedule and control the work hours of a covered worker performing surveillance testing on
Region: III | Clinton | 21328 | 12/31/2011 02/01/2012 | 2011005-03 | NRC | URI | Barrier Integrity | Green | REVIEW OF LICENSEE'S COMPLIANCE WHITH TS 3.5.4.3 DURING OPERATIONS WITH THE POTENTIAL TO DRAIN THE REACTOR VESSEL |  |  | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors noted that the licensee utilized the relief afforded by TS 3.0.4.a to commence OPDRV activities during the C1R13 refueling outage with only one VG subsystem operable. The licensee started the operable VG subsystem prior to entering the OPDR
Region: III | Clinton | 21331 | 12/31/2011 02/01/2012 | 2011005-04 | NRC | NCV | Barrier Integrity | Green | UNACCEPTABLE PRECONDITIONING OF REACTOR CORE ISOLATION COOLING SYSTEM CHECK VALVE PRIOR TO LEAK RATE TEST MEASUREMENT |  | P.2(b) Implementing Operating Experience | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to establish an adequate procedure to perform r
Region: III | Clinton | 21332 | 12/31/2011 02/01/2012 | 2011005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO IMPLEMENT APPROPRIATE RADIOLOGICAL CONTROLS FOR THE REMOVAL OF INSULATION IN A POSTED HIGH CONTAMINATION AREA |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | NONE | A self-revealed finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.4.1.a was identified. Specifically, the licensee failed to implement appropriate radiological controls for the removal of insulation
Region: III | Clinton | 21333 | 12/31/2011 02/01/2012 | 2011005-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO IMPLEMENT APPROPRIATE RADIOLOGICAL CONTROLS AFTER RADIATION PROTECTION IDENTIFIED THAT A WORKER WAS POTENTIALLY CONTAMINATED DUE TO INAPPROPRIATE PROTECTIVE CLOTHING. |  |  | TE?: N | 05000461 Clinton |  | NONE | A self-revealed finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.4.1.a was identified. Specifically, the licensee failed to implement appropriate radiological controls after radiation protection id
Region: III | Clinton | 21311 | 09/30/2011 11/03/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM CODE REQUIRED CAUSE AND EFFECT FAILURE EVALUATIONS FOR DIESEL STARTING AIR AND FUEL OIL SYSTEM RELIEF VALVES. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.55a. The licensee failed to perform American Society of Mechanical Engineers (ASME) Code required cause and effect failure evaluations
Region: III | Clinton | 21312 | 09/30/2011 11/03/2011 | 2011004-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO IMPLEMENT PACKAGE DESIGN SPECIFICATIONS |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000461 Clinton |  | 71124.08 | The inspectors identified a finding of very low-safety-significance and an associated non-cited violation of 10 CFR 71.5 for the failure to implement package design specifications. Specifically, the licensee failed to ensure the proper closure of a DOT 7A
Region: III | Clinton | 21316 | 09/30/2011 11/03/2011 | 2011004-03 | NRC | FIN | Mitigating Systems | Green | FAILURE TO CORRECT A CONDITION ADVERSE TO QUALITY FOR IMPROPERLY IMPLEMENTED ENGINEERING CORRECTIVE ACTIONS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding of very low safety significance due to the licensee's failure to effectively implement corrective actions for a condition adverse to quality described in Apparent Cause Evaluation 1095413, "NOS [Nuclear Oversight] Ident
Region: III | Clinton | 21317 | 09/30/2011 11/03/2011 | 2011004-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO MEET TECHNICAL SPECIFICATION 3.7.3 FOR OPERABILITY OF CONTROL ROOM VENTILATION SYSTEM |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | 71153 | The inspectors identified a finding of very low safety significance with an associated non-cited violation of Technical Specification (TS) 3.7.3, "Control Room Ventilation System," following the discovery of a crack on the Train B Control Room ventilation
Region: III | Clinton | 21318 | 09/30/2011 11/03/2011 | 2011004-05 | NRC | FIN | Barrier Integrity | Green | FAILURE TO EVALUATE OPERABILITY OF CONTROL ROOM VENTILATION SYSTEM FOR DEGRADED FLOW CONDITION |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance. The licensee failed to appropriately evaluate the operability of Control Room Ventilation Train A after identifying a degraded/nonconforming system flow condition while performing survei
Region: III | Clinton | 21324 | 09/30/2011 11/03/2011 | 2011004-06 | NRC | NCV | Emergency Preparedness | Green | MISSING RESPIRATOR SPECTACLE KITS |  | H.2(d) Facilities & Equipment | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.54(q) for the failure to provide spectacle adapter kits for all eyeglass wearers (i.e, non-soft contact wearers) who were key emergency response organizati
Region: III | Clinton | 21302 | 06/30/2011 07/29/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | DEFICIENCIES WITH RCIC ROOM HEAT-UP ANALYSES |  |  | TE?: N | 05000461 Clinton |  | 71111.07T | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to include all of the applicable heat loads in the reactor core isolation cooling (RCIC) ro
Region: III | Clinton | 21303 | 06/30/2011 07/29/2011 | 2011003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO MEET SURVEILLANCE TESTING REQUIREMENT FOR REACTOR COOLANT SYSTEM PRESSURE ISOLATION VALVES |  |  | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) with an associated Non Cited Violation of Technical Specification Surveillance Requirement (TSSR) 3.4.6.1. The licensee failed to correctly incorporate the required test pressure
Region: III | Clinton | 21310 | 06/22/2011 07/21/2011 | 2010502-02 | NRC | NCV | Emergency Preparedness | Green | CHANGES TO EAL BASIS DECREASED THE EFFECTIVENESS OF THE PLAN WITHOUT PRIOR NRC APPROVAL (PERFORMANCE DEFICIENCY PORTION) | EA Case: 2011128 |  | TE?: N | 05000461 Clinton |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: III | Clinton | 21301 | 06/03/2011 07/08/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ACCOUNT FOR CABLE RESISTANCE IN OPERABILITY DETERMINATIONS. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | 71152B | The inspectors identified a finding of very low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," related to calculational errors found in the licensee's operability determination. Specifically, on
Region: III | Clinton | 21299 | 06/03/2011 07/08/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN A QUALITY RECORD AS EVIDENCE OF AN ACTIVITY AFFECTING QUALITY OF SAFETY-RELATED EQUIPMENT DUE TO INAPPROPRIATE CORRECTIVE ACTIONS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000461 Clinton |  | 71152B | The inspectors identified a finding of very low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records." Specifically, the licensee failed to maintain a quality record documenting a nondestruct
Region: III | Clinton | 21300 | 06/03/2011 07/08/2011 | 2011008-03 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM EFFECTIVENESS REVIEW. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000461 Clinton |  | 71152B | The inspectors identified a finding of very low safety significance with an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to perform an effectiveness review (EFR) to ensure that correct
Region: III | Clinton | 21290 | 03/31/2011 04/29/2011 | 2011002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL TRANSIENT COMBUSTIBLE MATERIALS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71111.05A | The inspectors identified a finding of very low safety significance with an associated non-cited violation of the Clinton Power Station Unit 1 Operating License (NPF 62, Section 2.F). The licensee failed to implement the Fire Protection Program in accorda
Region: III | Clinton | 21291 | 03/31/2011 04/29/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO MEET SURVEILLANCE TESTING REQUIREMENT FOR HYDROGEN IGNITERS IN ACCESSIBLE AREAS OF THE PRIMARY CONTAINMENT AND DRYWELL. |  |  | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated non-cited violation of Technical Specification Surveillance Requirement (TSSR) 3.6.3.2.4. The licensee failed to verify that each required hydrogen igniter in accessibl
Region: III | Clinton | 21297 | 03/31/2011 04/29/2011 | 2011002-03 | NRC | NCV | Barrier Integrity | Green | INADEQUATE TESTING CONTROLS TO PERFORM SURVEILLANCE TESTING OF HYDROGEN IGNITERS IN THE PRIMARY CONTAINMENT AND DRYWELL. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control." The licensee failed to establish a test program adequate to assure testing of hydrogen ignit
Region: III | Clinton | 21289 | 03/18/2011 04/25/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE FIRE DOOR WAS CLOSED AND LATCHED |  |  | TE?: N | 05000461 Clinton |  | 71111.05T | A finding of very low safety significance and associated NCV of Clinton Power Station Unit 1 Operating License NPF-62, Section 2.F was identified by the inspectors for the licensee's failure to ensure fire doors were closed and latched. Specifically, duri
Region: III | Clinton | 21283 | 12/31/2010 01/31/2011 | 2010005-01 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL TRANSIENT COMBUSTIBLE MATERIALS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71111.05A | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of the Clinton Power Station Unit 1 Operating License (NPF-62, Section 2.F). The licensee failed to implement the Fire Protection Program in accorda
Region: III | Clinton | 21284 | 12/31/2010 01/31/2011 | 2010005-02 | Self - Revealed | FIN | Barrier Integrity | Green | FAILURE TO PERFORM PREVENTATIVE MAINTENANCE OF DIVISION 1 SELF TEST SYSTEM (STS) POWER SUPPLY RESULTS IN SPURIOUS REPOSITIONING OF SAFETY RELATED VALVES. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance was self-revealed on August 24, 2010, when the Reactor Water Cleanup (RT) System return line outboard primary containment isolation valve went closed. Many other unintended valve repositioning events occurred from
Region: III | Clinton | 21263 | 06/30/2010 08/03/2010 | 2010003-03 | NRC | FIN | Mitigating Systems | Green | OPERABILITY ASSESSMENT OF INSERVICE TESTING SURVEILLANCE DISCREPANCIES FOR EXCESS FLOW CHECK VALVES |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to evaluate the functionality of multiple excess flow check valves that had not been tested in accordance with the American Society of Mechanical En
Region: III | Clinton | 21269 | 06/30/2010 08/03/2010 | 2010003-04 | NRC | NCV | Emergency Preparedness | Green | INADEQUATE EMERGENCY PLAN AUGMENTATION CALL-IN DRILLS | EA Case: 2010187 |  | TE?: N | 05000461 Clinton |  | 71114.03 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.54(q) for the licensee's failure to follow and maintain the Emergency Plan, which meets the standards in 10 CFR 50.47(b) and the requir
Region: III | Clinton | 21270 | 06/30/2010 08/03/2010 | 2010003-05 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE RESULTING IN GATE SEAL LEAKAGE. |  | H.4(b) Procedural Compliance | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," was self-revealed on January 29, 2010, when the dryer cavity gate seal depressurized during th
Region: III | Clinton | 21276 | 06/30/2010 08/03/2010 | 2010003-06 | NRC | NCV | Mitigating Systems | Green | Failure to Satisfy 10 CFR 50.72 and 50.73 Reporting Requirements - performance deficiiency portion. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | 71111.06 | The inspectors identified a finding of very low safety significance of the NRC's reporting requirements in 10 CFR 50.72(a)(1), "Immediate Notification Requirements for Operating Nuclear Power Reactors," and 10 CFR 50.73(a)(1), "Licensee Event Report Syste
Region: III | Clinton | 21277 | 06/30/2010 08/03/2010 | 2010003-07 | NRC | NCV | Barrier Integrity | Green | Failure to Perform an Adequate 10 CFR 50.59 Evaluation for CPS Procedure 3711.01 - performance deficiency portion |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | 71111.13 | The inspectors identified a finding of very low safety significance with an associated NCV of 10 CFR 50.59, "Changes, Tests and Experiments." The licensee failed to perform an adequate 10 CFR 50.59 evaluation and obtain a license amendment prior to implem
Region: III | Clinton | 21271 | 06/25/2010 08/06/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | NON CONSERVATIVE ACCEPTANCE CRITERIA FOR RHR PUMP PERFORMANCE TESTING |  | P.2(b) Implementing Operating Experience | TE?: N | 05000461 Clinton |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety-significance for the licensee's failure to ensure adequate acceptance limits were incorporated into test procedures. Specifically, the lic
Region: III | Clinton | 21275 | 06/25/2010 08/06/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE TEST CONTROL OF RHR HEAT EXCHANGERS |  |  | TE?: N | 05000461 Clinton |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety-significance for the licensee's failure to establish test conditions to assure that the 1B residual heat removal heat exchanger would perf
Region: III | Clinton | 21240 | 03/31/2010 05/04/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL TRANSIENT COMBUSTIBLE MATERIALS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71111.05Q | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of the Clinton Power Station Unit 1 Operating License (NPF-62, Section 2.F). The licensee failed to implement the Fire Protection Program in accorda
Region: III | Clinton | 21245 | 03/31/2010 05/04/2010 | 2010002-02 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL COMBUSTIBLE GAS CYLINDERS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 71111.05Q | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of the Clinton Power Station Unit 1 Operating License (NPF-62, Section 2.F). The licensee failed to implement the Fire Protection Program in accorda
Region: III | Clinton | 21246 | 03/31/2010 05/04/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | INTERCONNECTING FLOOR DRAINS BETWEEN THE RESIDUAL HEAT REMOVAL 'A' PUMP ROOM AND RADWASTE PIPE TUNNEL |  |  | TE?: N | 05000461 Clinton |  | 71111.06 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria III, "Design Control," regarding the licensee's failure to correctly translate the design basis into the design o
Region: III | Clinton | 21247 | 03/31/2010 05/04/2010 | 2010002-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO RECOGNIZE EXAMINATION LIMITATIONS FOR A CONTAINMENT PENETRATION WELD |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71111.08G | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure instructions and rec
Region: III | Clinton | 21252 | 03/31/2010 05/04/2010 | 2010002-05 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO CORRECT INADEQUATE FWLCS RESPONSE RESULTED IN HIGH REACTOR VESSEL WATER LEVEL (LEVEL 8 ) SCRAM |  |  | TE?: N | 05000461 Clinton |  | 71111.12 | A finding of very low safety significance was self-revealed from an event that resulted in a Unit 1 reactor scram. The licensee failed to correct a non-conforming condition with inadequate response from the feedwater level control system (FWLCS) that caus
Region: III | Clinton | 21255 | 03/31/2010 05/04/2010 | 2010002-08 | NRC | NCV | Barrier Integrity | Green | INADEQUATE TEST CRITERIA IN STANDBY GAS TREATMENT SYSTEM FLOW/HEATER OPERABILITY SURVEILLANCE TEST |  |  | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings." The licensee failed to include appropriate quantitative or qualitati
Region: III | Clinton | 21238 | 12/31/2009 01/25/2010 | 2009005-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO CORRECTLY TORQUE VALVE PACKING GLAND NUTS RESULTED IN VALVE PACKING FAILURE AND UNPLANNED PLANT SHUTDOWN |  |  | TE?: N | 05000461 Clinton |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," was self-revealed on September 29, 2009, when a steam leak developed from the reactor core iso
Region: III | Clinton | 21239 | 12/31/2009 01/25/2010 | 2009005-04 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECTLY INSTALL RELAYS INSIDE OF THE DIVISION 3 DIESEL GENERATOR CONTROL PANEL |  | H.4(b) Procedural Compliance | TE?: N | 05000461 Clinton |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," was self-revealed on September 23, 2009, when the Division 3 diesel generator (DG) was found t
Region: III | Clinton | 21233 | 09/30/2009 11/10/2009 | 2009004-02 | Self - Revealed | FIN | Mitigating Systems | Green | INEFFECTIVE CORRECTIVE ACTIONS FOR VIBRATION INDUCED STEM/DISC SEPARATION OF FUEL POOL COOLING SYSTEM TRAIN 'A' FLOW CONTROL VALVE 1FC004A. |  |  | TE?: N | 05000461 Clinton |  | 71111.12 | A finding of very low safety significance was self-revealed on May 27, 2009, when fuel pool cooling system flow control valve 1FC004A failed closed. The licensee failed to implement effective corrective actions in response to the same failure mode for the
Region: III | Clinton | 21281 | 09/30/2009 11/10/2009 | 2009004-05 | NRC | NCV | Barrier Integrity | Green | FAILURE THE ADEQUATELY IMPLEMENT REQUIREMENTS OF THE LEAKAGE REDUCTION AND MONITORING PROGRAM. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an assoicated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to adequately implement periodic vi
Region: III | Clinton | 21223 | 06/30/2009 07/28/2009 | 2009003-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO EVALUTE SAFETY FUNCTION OF SUPPRESSION POOL MAKEUP SYSTEM |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to recognize a potential loss of safety function for the suppression pool makeup system following the loss of upper containment pool inventory when
Region: III | Clinton | 21225 | 06/30/2009 07/28/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFROM SURVEILLANCE TESTING ON THE DIVISION 3 SHUTDOWN SERVICE WATER PUMP WITH ADEQUATE MEASURING AND TEST EQUIPMENT. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000461 Clinton |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria XII, "Control of Measuring and Test Equipment," and 10 CFR 50, Appendix B, Criteria XI, "Test Control." The licen
Region: III | Clinton | 21218 | 12/31/2008 01/27/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL TRANSIENT COMBUSTIBLE MATERIALS IN ACCORDANCE WITH FIRE PROTECTION PROGRAM. | EA Case: 2008005 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71111.05Q | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of the Clinton Power Station Unit 1 Operating License (NPF-62, Section 2.F). The licensee failed to implement the fire protection program in accorda
Region: III | Clinton | 21211 | 09/30/2008 11/10/2008 | 2008004-01 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO PERFORM ADEQUATE POST MAINTENANCE TESTING RESULTED IN HIGH REACTOR VESSEL WATER LEVEL (LEVEL 8) SCRAM |  |  | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance associated with a self-revealed event that resulted in a Unit 1 reactor scram. The licensee failed to perform adequate post maintenance testing following replacement of the feedwater leve
Region: III | Clinton | 21215 | 09/30/2008 11/10/2008 | 2008004-02 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO EVALUATE AN UNEXPECTED AND UNKNOWN CAUSE FOR STRAY VOLTAGE IN THE END-OF-CYCLE RECIRCULATION PUMP TRIP CIRCUIT DURING POST MODIFICATION TESTING RESULTED IN A REACTOR RECIRCULATION PUMP TRIP |  | H.3(a) Work Planning | TE?: N | 05000461 Clinton |  | 71111.12 | The inspectors identified a finding of very low safety significance associated with a self-revealed event that resulted in the unexpected loss of a reactor recirculation pump. The licensee failed to evaluate an unexpected and unknown cause for stray volta
Region: III | Clinton | 21216 | 09/30/2008 11/10/2008 | 2008004-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE PREVENTIVE MAINTENANCE ON SHUTDOWN SERVICE WATER VALVE 1SX014A RESULTED IN SIGNIFICANT DEGRADATION AND GROSS SEAT LEAKAGE |  | H.3(b) Work Activity Coordination | TE?: N | 05000461 Clinton |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4.1.a was self-revealed. The licensee failed to perform adequate preventive maintenance on shutdown service water system valve 1SX014A. This
Region: III | Clinton | 21217 | 09/30/2008 11/10/2008 | 2008004-04 | NRC | FIN | Mitigating Systems | Green | FAILURE TO RECOGNIZE THE SAFETY RELATED SYSTEM FUNCTION OF THE 1B RESIDUAL HEAT REMOVAL PUMP SEAL COOLER WHEN EVALUATING PAST OPERABILITY OF THE PUMP. |  |  | TE?: N | 05000461 Clinton |  | 71111.15 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to recognize the safety related system function of the 1B residual heat removal pump seal cooler when initially evaluating the past operability of t
Region: III | Clinton | 20534 | 03/31/2008 05/13/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW APPROVED FIRE PROTECTION PROGRAM PROCEDURES CONCERNING CONTROL OF TRANSIENT COMBUSTIBLE MATERIAL. | EA Case: 2008002 | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71111.05Q | The inspectors identified a performance deficiency involving a Non-Cited Violation (NCV) of Clinton Power Station Operating License NPF-62, Section 2.F for failure to implement the fire protection program in accordance with program requirements. The inspe
Region: III | Clinton | 20535 | 03/31/2008 05/13/2008 | 2008002-02 | NRC | FIN | Initiating Events | Green | THE LICENSEE DISCOVERED THAT THE WRONG COMPONENT WAS INSTALLED IN THE B TURBINE DRIVEN REACTOR FEED PUMP OIL PRESSURE SENSING LOGIC. |  | H.4(b) Procedural Compliance | TE?: N | 05000461 Clinton |  | 71111.19 | A finding of very low safety significance was self-revealed by the automatic runback of the turbine driven reactor feed pump during post outage power ascension. The licensee discovered that the wrong component was installed in the B turbine driven reactor
Region: III | Clinton | 20536 | 03/31/2008 05/13/2008 | 2008002-03 | NRC | NCV | Initiating Events | Green | DURING THE PERFORMANCE OF NRC FINAL DRYWELL CLOSEOUT, THE INSPECTORS NOTED THAT FOREIGN MATERIAL/HOUSEKEEPING SOCK HAD NOT BEEN REMOVED FROM THE DRYWELL FLOOR DRAINS. | EA Case: 2008002 | H.3(b) Work Activity Coordination | TE?: N | 05000461 Clinton |  | 71111.2 | The inspectors identified a finding and an associated NCV of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," having a very low safety significance during drywell closeout inspections. Specifically, during the performance
Region: III | Clinton | 20537 | 03/31/2008 05/13/2008 | 2008002-04 | NRC | URI | Initiating Events | Green | AS FOUND LEAKAGE THROUGH SHUTDOWN SERVICE (SX) VALVE 1SX014A. |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71111.22 | On January 22, 2008, operators identified a significant leak of the 1SX014A valve after the valve was closed. The valve was taken to the closed position by operators to performa a leakage test on the valve per CPS 9861.09D008, "leakage Test on Valve 1SX01
Region: III | Clinton | 20538 | 03/31/2008 05/13/2008 | 2008002-05 | NRC | URI | Initiating Events | Green | CHANGES TO ERO ON-SHIFT AND AUGMENTATION STAFFING LEVELS AND POSITION TITLES. |  | H.4(a) Human Error Prevention | TE?: N | 05000461 Clinton |  | 71114.03 | In response to problems identified during a declared Alert on February 13, 1998, the licnesee added five positions to its ten required on-shift ERO staffing positions, removed the eleven 30-minute ERO augmentation positions, and added six positions to the
Region: III | Clinton | 20539 | 03/31/2008 05/13/2008 | 2008002-06 | NRC | NCV | Barrier Integrity | Green | FAILURE TO EVALUATE HYDRAULIC POWER UNIT PIPING FOR IMPACT WITH CONTAINMENT ATMOSPHERE MONITORING LINE. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 71152 | The inspectors identified a finding and an associated NCV of 10 CFR Part 50, Appendix b, Criterion XVI, "Corrective Actions," having very low safety significance, in that, inevaluating whether the reactor recirculation flow control valve "A" hydraulic pow
Region: III | Clinton | 20540 | 03/31/2008 05/13/2008 | 2008002-07 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO BARRICADE AND LOCK A LOCKED HIGH RADIATION AREA. |  | H.4(b) Procedural Compliance | TE?: N | 05000461 Clinton |  | 7112101 | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification 5.7.2 for failure to barricade, lock, or continuously guard a high radiation area with dose rates greater than 1000 millirem per hour. On
Region: III | Clinton | 20527 | 12/31/2007 02/04/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | Failure to implement fire protection program in accordance with program requirements |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71111.05Q | Identified a performance deficiency involving a NCV of Clinton Power Station Operating License NPF-62, Section 2.F for failure to implement fire protection program in accordance with program requirements. Inspectors identified multiple instances of the li
Region: III | Clinton | 20526 | 12/31/2007 02/04/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM POST MODIFICATION TESTING TO SHUTDOWN SERVICE WATER VACUUM BREAKERS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 7111117A | Identified a NCV of 10 CFR Part 50, App B, Crit XI, Test Controls, having a low safety significance for failure to properly test a permanent plant modification to the Div 1 & 2 SX. This resulted in two of four vacuum breakers that failed the minimal desig
Region: III | Clinton | 20528 | 12/19/2007 02/04/2008 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Continuously Submerged Cables Design Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000461 Clinton |  | 7111121 | The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving inadequate cable design. Specifically, the team identified that the licensee failed to incorporate appropriate licensi
Region: III | Clinton | 20529 | 12/19/2007 02/04/2008 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Division 3 Emergency Diesel Generator Neutral Ground Resistor Design Inadequacy |  |  | TE?: N | 05000461 Clinton |  | 7111121 | The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving inadequate equipment design. Specifically, the Division 3, emergency diesel generator (EDG) neutral ground resistor wa
Region: III | Clinton | 20530 | 12/19/2007 02/04/2008 | 2007008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design of Emergency Diesel Generator Exhaust |  |  | TE?: N | 05000461 Clinton |  | 7111121 | The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving inadequate design of the emergency diesel generator (EDG) exhaust sub-systems. Specifically, the licensee failed to pr
Region: III | Clinton | 20507 | 12/19/2007 02/04/2008 | 2007008-04 | NRC | NCV | Mitigating Systems | Green | Residual Heat Removal Pipe Support Calculation Deficiencies |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | 7111121 | The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving a temporary installation that added lead shielding to the Unit 1 residual heat removal (RHR) piping. Specifically, the
Region: III | Clinton | 20508 | 12/19/2007 02/04/2008 | 2007008-05 | NRC | NCV | Mitigating Systems | Green | Inappropriate SX Pump Test Acceptance Criteria |  |  | TE?: N | 05000461 Clinton |  | 7111121 | The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance, in that, the shutdown service water (SX) pump tests conducted did not appropriately demonstrate that the SX pumps met design basis
Region: III | Clinton | 20518 | 09/30/2007 11/06/2007 | 2007004-02 | NRC | NCV | Barrier Integrity | Green | INADEQUATE PROCUREMENT SPECIFICATION FOR CHARCOAL RESULTS IN INOPERABLE CONTROL ROOM VENTILATION SUBSYSTEM. |  |  | TE?: N | 05000461 Clinton |  | NONE | A performance deficiency involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion IV, "Procurement Document Control," was self revealed following receipt of laboratory results that showed that Division 1 control room ventilation system cha
Region: III | Clinton | 20519 | 09/30/2007 11/06/2007 | 2007004-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION 3.4.5 FOR RCS PRESSURE BOUNDARY LEAK |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000461 Clinton |  | NONE | The inspectors identified a performance deficiency involving a Non-Cited Violation of Technical Specifications when the licensee failed to meet the required completion time for an action statement in Technical Specification 3.4.5. Specifically, Technical
Region: III | Clinton | 20525 | 09/30/2007 11/06/2007 | 2007004-04 | NRC | NCV | Barrier Integrity | Green | INADEQUATE PROCEDURE RESULTS IN SPENT FUEL BUNDLE INCIDENT |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000461 Clinton |  | NONE | A performance deficiency involving a Non-Cited Violation of 10 CFR Part 50 Appendix B, Criteria V, "Instructions, Procedures, and Drawings," was self-revealed following an event on August 17, 2007, where a spent fuel bundle being moved to a temporary stor
Region: III | Clinton | 20512 | 03/31/2007 04/19/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE OF THE ELECTRICAL CIRCUIT CARD RESULTED IN A LOSS OF SAFETY FUNCTION FOR THE MAIN TURBINE BYPASS VALVES. |  |  | TE?: N | 05000461 Clinton |  | 71153 | A finding of very low safety significance involving a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, was self revealed when a low main condenser vacuum alarm was recieved in the main control room. The alarm was caused by the failure of an elec
Region: III | Clinton | 20513 | 03/31/2007 04/19/2007 | 2007002-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE CONFIGURATION CONTROL RISK EVALUATION WAS A PERFORMANCE DEFICIENCY WARRANTING A SIGNIFICANCE EVALUATION. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000461 Clinton |  | 71153 | A finding of very low safety significance was self-revealed following the loss of the division 3 shutdown service water (SX) system on August 17, 2006. The loss of division 3 of SX occurred when a security guard bumped an SX circuit breaker hand switch fo
Region: III | Clinton | 20516 | 03/23/2007 05/01/2007 | 2007007-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW CLINOTN PROCEDURE 1019.05, "TRANSIENT EQUIPMENT/MATERIALS," RESULTED IN VIOLATION OF 10 CFR PART 50, APPENDIX B, CRITERION V. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000461 Clinton |  | 71152B | The inspectors identified an NCV of 10 CFR Part 50, Appendix V, "Instructions, Procedures, and Drawings," for failure to assure that activites affecting quality be accomplished in accordance with prescribed documented instructions, procedures, or drawings
Region: III | Clinton | 20510 | 11/17/2006 11/29/2006 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | POTENTIAL INOPERABILITY OF RCIC DUE TO VORTEXING |  |  | TE?: N | 05000461 Clinton |  | 7111121 | A finding of very low safety significance was identified by the inspectors for an Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" requirements. Specifically, in Calculation IP-M-0384, "Evaluation of Vortex in the RCIC [W
Region: III | Clinton | 20506 | 09/30/2006 11/02/2006 | 2006007-01 | NRC | NCV | Initiating Events | Green | THE INSPECTORS DETERMINED THAT THE FAILURE TO APPROPRIATELY IDENTIFY AND CORRECT THE CAUSE OF THE DIVISION 4 NSPS INVERTER IN MARCH WAS A PERFROMANCE DEFICIENCY. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000461 Clinton |  | 71153 | A finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, was self revealed following a reactor scram on August 27, 2006, due to the licensee's failure to identify and correct a condition adverse to
Region: III | Clinton | 20498 | 03/31/2006 05/08/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL DURING REVIEW OF ENGINEERING CHANGE PACKAGE 356820 "SHUTDOWN COOLING HEADER LEAK-OFF LINE". |  |  | TE?: N | 05000461 Clinton |  | 7111117A | In February 2006, a finding of very low safety significance involving a Non-Cited Violation of 10 CFR 50, Appendix B, Criteria III, "Design Control," was identified. During a review of Engineering Change Package 356820, "Shutdown Cooling Header Leak-off l
Region: III | Clinton | 20499 | 03/31/2006 05/08/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE TEST CONTROL DURING THE REVIEW OF THE LICENSEE'S SURVEILLANCE TEST TO DETERMINE OPERABILITY OF THE SHUTDOWN SERVICE WATER SYSTEM. |  |  | TE?: N | 05000461 Clinton |  | 71111.22 | On February 2, 2006, the inspectors identified a finding involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Controls." During a review of the licensee's surveillance test to determine the operability of the shutdown service
Region: III | Clinton | 20503 | 03/31/2006 05/08/2006 | 2006002-03 | NRC | FIN | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN COLLECTIVE RADIATION DOSE TO OCCUPATIONAL WORKERS INVOLVED IN REFUEL FLOOR WORK ALARA. |  |  | TE?: N | 05000461 Clinton |  | 7112102 | An inspector-identified finding of very low safety significance was identified for the failure to maintain the collective dose As-Low-As-Is-Reasonably-Achievable (ALARA) for refuel floor non-cavity work that was conducted during the February 2006 refuelin
Region: III | Clinton | 20504 | 03/20/2006 08/03/2006 | 2006004-01 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE WORKMANSHIP RESULTED IN GENERATOR TRIP AND REACTOR SCRAM. |  |  | TE?: N | 05000461 Clinton |  | 71153 | The inspectors considered the failure to adequately tighten terminal screws in the main generator output current transformer circuit a performance deficiency. This issue was caused by inadequate workmanship. The inspectors determined it was more than mino
Region: III | Clinton | 125755 | 10/24/2019 |  |  | LIV |  | Green | Failure to Scan or Assess for Vulnerabilities Associated with Digital Test Equipment |  |  | TE?: N | 05000461 Clinton |  | 71130.10P
Region: III | D.C. Cook | 126095 | 12/31/2019 02/12/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Unqualified Reactor Vessel Shell Weld Examination |  | H.2 - Field Presence | TE?: N | 05000316 D.C. Cook 2 | Human Performance | 71111.08P | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations (10 CFR), Appendix B, Criterion IX “Control of Special Processes,” for the licensee’s failure to ensure the Unit 2 reactor vesse
Region: III | D.C. Cook | 126455 | 12/31/2019 02/12/2020 | 2019004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Test Program to Verify Overtemperature Delta Temperature and Overpower Delta Temperature Turbine Runback would Function when the Modification was Put into Service |  | NPP | TE?: N | 05000316 D.C. Cook 2 | Procedure Quality | 71111.18 | A finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was self-revealed on November 5, 2019, when the licensee was performing, for the first time, a complete so
Region: III | D.C. Cook | 126456 | 12/31/2019 02/12/2020 | 2019004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure Results in a Power Transient Due to the Loss of Two Feedwater Heater Drain Pumps and the Isolation of Extraction Steam to the Feedwater Heaters |  | H.1 - Resources | TE?: N | 05000315 D.C. Cook 1 | Human Performance | 71153 | A finding of very low safety significance (Green) was self-revealed on October 23, 2019, when the licensee failed to follow plant procedure 1-OHP-4021-060-014, "Operation of the Heater Drain Pumps," that ensures the proper operation of the pumps and the h
Region: III | D.C. Cook | 126619 | 12/31/2019 02/12/2020 | 2019004-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Engineering Change Procedure for Non-Essential Service Water Strainer Design Modification |  | H.4 - Teamwork | TE?: N | 05000316 D.C. Cook 2 | Design Control | 71153 | A finding of very low safety significance (Green) was self-revealed on July 21, 2019, for the licensee's failure to conduct a failure modes and effects analysis as described in licensee procedure, 12-EHP-5040-MOD-009, Engineering Change Reference Guide, R
Region: III | D.C. Cook | 125799 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Main Steam Stop Valve Dump Valve Inoperable for Longer than its Technical Specification Allowed Outage Time |  | H.14 - Conservative Bias | TE?: N | 05000315 D.C. Cook 1 | Equipment Performance | 71152 | The inspectors identified a finding of very low safety significance (i.e., Green) and an associated Non-Cited Violation (NCV) of Technical Specification (TS) 3.7.2, "Steam Generator Stop Valves (SGVSs)," when licensee personnel failed to have four Unit 1
Region: III | D.C. Cook | 125859 | 09/27/2019 10/28/2019 | 2019012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Acceptance Criteria In Fire Protection Water System Flow Test Procedure |  | H.6 - Design Margins | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 | Protection Against External Factors | 71111.05XT | The inspectors identified a finding of very-low safety significance and associated violation of Technical Specification 5.4 “Procedures,” for the licensee’s failure to maintain fire protection water system flow test procedure. Specifically, the licensee f
Region: III | D.C. Cook | 125511 | 08/01/2019 08/28/2019 | 2019010-01 | Self - Revealed | FIN | Initiating Events | Green | Unit 1 Steam Dump Valves Inadvertently Failed Open |  | H.14 - Conservative Bias | TE?: N | 05000315 D.C. Cook 1 |  | 71152B | A self-revealed Green finding was identified when the licensee failed to ensure that all design specifications for the Unit 1 Alarm Log Computer (ALPC) associated with a reactor controls and instrumentation (RCI) system engineering change were met. Specif
Region: III | D.C. Cook | 125171 | 06/30/2019 08/01/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Procedures for Loss of Electrical Bus |  | NPP | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 | Procedure Quality | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of TS 5.4.1.a when licensee personnel failed to have established procedures for the operation of the electrical distribution system as well as
Region: III | D.C. Cook | 25938 | 12/31/2018 01/29/2019 | 2018004-01 | Self - Revealed | FIN | Initiating Events | Green | Misaligned Heater Level Column Valves Leads to Manual Reactor Trip |  | NPP | TE?: N | 05000315 D.C. Cook 1 |  | 71111.12 | A self-revealed finding of very low safety significance (Green) was identified when a hydraulic leak in the main feed pump controls resulted in operators performing a manual rapid downpower prior to the trip of the pump.A self-revealed, Green finding was
Region: III | D.C. Cook | 24688 | 09/30/2018 11/05/2018 | 2018003-01 | Self - Revealed | FIN | Initiating Events | Green | Misaligned Heater Level Column Valves Leads to Manual Reactor Trip |  | H.5 - Work Management | TE?: N | 05000315 D.C. Cook 1 |  | 71152 | A self-revealed, Green finding was identified when the operators manually tripped the Unit 2 reactor in response to a ‘hi-hi’ level in the Left Moisture Separator Drain Tank. Workers did not follow the test procedure EC–51366–TP–001 step 4.1.7 for th
Region: III | D.C. Cook | 24105 | 06/30/2018 08/08/2018 | 2018002-01 | Self - Revealed | NCV | Initiating Events | Green | Steam Dump Closure Caused by Human Error |  | H.11 - Challenge the Unknown | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | On May 10, 2018, a Green self-revealed finding and associated NCV occurred when licensee personnel caused the Unit 2 steam dump valves to the condenser to close. Specifically, when tuning the controller for the steam dump valves, licensee personnel left t
Region: III | D.C. Cook | 23948 | 03/31/2018 05/02/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Unit 1 Turbine Driven Auxiliary Feedwater Pump to Reach Rated Speed |  | P.5 - Operating Experience | TE?: N | 05000315 D.C. Cook 1 |  | 71111.15 | A self-revealed finding of very low safety significance with an associated Non-Cited Violation of Technical Specification 5.4 “Procedures,” occurred on December 21, 2017, when the Unit 1 Turbine-Driven Auxiliary Feedwater Pump failed to reach rated speed
Region: III | D.C. Cook | 23951 | 03/31/2018 05/02/2018 | 2018001-02 | NRC | NCV | Initiating Events | Green | Operation of Letdown System Leads to Voiding and Subsequent Relief Valve Lift |  | NPP | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of Technical Specification 5.4, “Procedures,” when the licensee failed to maintain a procedure for operating the letdown system. As a result, a water-ha
Region: III | D.C. Cook | 23211 | 12/31/2017 02/13/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Numerous Anchor Darling Double Disc Gate Valve Non-Conformances |  | NPP | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR) 50, Appendix B, Criterion XVI, “Corrective Action” for the licensee’s failure to c
Region: III | D.C. Cook | 22673 | 12/31/2017 02/13/2018 | 2017004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct The CAQ by Not Testing the Component Cooling Water Leak Isolation Valves |  | H.1 - Resources | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | The inspectors identified a finding and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Title 50, Appendix B Criterion XVI for failing to promptly correct a condition adverse to quality (CAQ). Specifically, in Inspection Report (IR) 05
Region: III | D.C. Cook | 22670 | 12/31/2017 02/13/2018 | 2017004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design for a Temporary Modification |  | H.14 - Conservative Bias | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | A finding and associated violation of Title 10 of the Code of Federal Regulations (CFR) Part 50 Appendix B Criterion III self-revealed when licensee personnel could not obtain a water sample from a location designated as a connection point for a safety re
Region: III | D.C. Cook | 25688 | 07/28/2017 08/31/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Operable, but Non-Conforming Conditions |  | P.3 Resolution | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 Code of Federal Regulations (CFR) Part 50, Criterion V for three examples where the licensee failed to follow procedures associated with the li
Region: III | D.C. Cook | 25680 | 06/30/2017 08/11/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Unit 2 CCW HX Monitoring Program Could Demonstrate Its Continued Operability Between Maintenance Intervals |  | H.6 Design Margins | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Title 10 of the Code of Federal Regulations, (CFR) Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a heat exchange
Region: III | D.C. Cook | 25683 | 06/30/2017 08/11/2017 | 2017002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 Containment Equalization Fan Failed Surveillance |  | H.5 Work Management | TE?: N | 05000316 D.C. Cook 2 |  | 71111.15 | A finding of very low safety significance was self revealed on March 23, 2017, when one of the Unit 2 Containment Equalization (CEQ) Fans, 2-HV-CEQ-1, failed its surveillance. Technical Specification (TS) 5.4.1, "Procedures," requires that the applicable
Region: III | D.C. Cook | 25684 | 06/30/2017 08/11/2017 | 2017002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Parts Subject to a Part 21 |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.15 | A self revealed finding and associated violation occurred on April 2, 2012, when the licensee failed to prevent installation of relays identified in a Part 21. Although the performance deficiency occurred in 2012, the consequence of the error did not mani
Region: III | D.C. Cook | 25685 | 06/30/2017 08/11/2017 | 2017002-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Measures to Ensure Leakage Remained Within Analysis |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to have adequate design control measures verify that the Essential Service Wa
Region: III | D.C. Cook | 25686 | 06/30/2017 08/11/2017 | 2017002-06 | Self - Revealed | FIN | Mitigating Systems | Green | Single Point Failure Vulnerability in Annunciator System |  |  | TE?: N | 05000315 D.C. Cook 1 |  | 71153 | A self revealed finding occurred on March 30, 2017, when operation of a work station for the control room annunciators caused a loss of all annunciators in the Unit 1 control room. Specifically, a software error coupled with an overflowing cache caused a
Region: III | D.C. Cook | 25675 | 03/31/2017 05/01/2017 | 2017001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Brief Worker Entry to High Radiation Area Resulting in the Unplanned Dose Rate Alarm |  | H.4 Teamwork | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | NONE | A finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.7.1.b was self revealed for the failure to a make radiation worker aware of the radiation dose rate before entering a high radiation area. The fai
Region: III | D.C. Cook | 25676 | 03/31/2017 05/01/2017 | 2017001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Disconnect Operation |  |  | TE?: N | 05000316 D.C. Cook 2 |  | 71152 | A self revealed finding and associated Non-Cited Violation (NCV) occurred on January 10, 2017, when the licensee caused a loss of a qualified off site circuit while opening a disconnect on the Unit 2 reserve feed transformer. Regulatory Guide 1.33 require
Region: III | D.C. Cook | 25679 | 03/31/2017 05/01/2017 | 2017001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Control Nonconformaing Delivery Valve Holders on Emergency Diesel Generators |  | P.2 Evaluation | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | A self revealed finding of very low safety significance with an associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," occurred when the delivery valve holder
Region: III | D.C. Cook | 25669 | 12/31/2016 02/13/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Designated Individual Not at Airlock |  | H.9 Training | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | The inspectors identified a finding and associated NCV of Technical Specification (TS) 5.4.1 for failing to station a designated individual at the airlocks. Licensee procedure 2-OHP-4030-227-041, Revision 34 required that a designated person be available
Region: III | D.C. Cook | 25670 | 12/31/2016 02/13/2017 | 2016004-02 | Self - Revealed | FIN | Initiating Events | Green | Moisture Separator Reheater Rupture |  | H.12 Avoid Complacency | TE?: N | 05000316 D.C. Cook 2 |  | 71152 | .A self revealed finding of very low safety significance (Green), occurred on July 6, 2016, when a portion of the Unit 2 Right Moisture Separator Reheater (MSR) 'B' bellows assembly ruptured, causing a steam leak which damaged the adjacent turbine buildin
Region: III | D.C. Cook | 25665 | 09/30/2016 11/09/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Backfill Severs Fire Main |  | H.11 Challenge the Unknown | TE?: N | 05000315 D.C. Cook 1 |  | 71111.05Q | A self revealed finding of very low safety significance (Green) and associated NCV of the license condition for a fire protection program occurred when the licensee failed to ensure excavation activities preserved the functionality of the fire main. Speci
Region: III | D.C. Cook | 25666 | 09/30/2016 11/09/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Charging System Thru-Wall Leak |  |  | TE?: N | 05000315 D.C. Cook 1 |  | 71111.12 | A finding of very low safety significance with an associated NCV of Title 10 of the Code of Federal Regulations (CFR) 50 Appendix B, Criterion III, "Design Control," was self revealed when a thru wall leak was identified on a branch connection off of the
Region: III | D.C. Cook | 25667 | 09/30/2016 11/09/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Wetting of Safety-Related Battery Charger |  | H.7 Documentation | TE?: N | 05000316 D.C. Cook 2 |  | 71111.15 | A finding of very low safety significance with an associated NCV of TS 5.4, Procedures, was self revealed on June 21, 2016, when safety related N Train Battery Charger 2-BC-B was found soaked with water from a roof leak above. The licensee failed to follo
Region: III | D.C. Cook | 25674 | 09/02/2016 10/13/2016 | 2016009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Resolution for Double-Break Circuits Design for Several Valves |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05XT | The inspectors identified a finding of very-low safety significance (Green) and an associated Non-Cited Violation of license conditions 2.C(4) and 2.C(3)(o) for the licensee's failure to implement the approved. Specifically, the licensee failed to analyze
Region: III | D.C. Cook | 25653 | 06/30/2016 08/10/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Unanalyzed Scaffold Near Safety-Related Equipment |  | H.5 Work Management | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | . A finding of very low safety significance and associated NCV of Technical Specifications (TS) 5.4, "Procedures," was identified by the inspectors. The licensee constructed a scaffold storage rack adjacent to the Unit 1 Component Cooling Water (CCW) Surg
Region: III | D.C. Cook | 25654 | 06/30/2016 08/10/2016 | 2016002-02 | NRC | NCV | Barrier Integrity | Green | Containment Closure Requirements During Unit 1 2016 Refueling Outage |  | H.1 Resources | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," for the failure to implement all of the requirements of PMP-4100-SDR-001, "Plant Shutdown S
Region: III | D.C. Cook | 25661 | 06/30/2016 08/10/2016 | 2016002-03 | NRC | NCV | Barrier Integrity | Green | Procedure Failed to Establish Two Valve Isolation Between the Reactor Coolants System and Containment Atmosphere |  | H.3 Change Management | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and associated nomn-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," for the licensee failing to maintain procedure 1-OHP-4021-002-001, reactor coolant s
Region: III | D.C. Cook | 25652 | 03/31/2016 05/06/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Auxiliary Feedwater Mission Time |  | H.14 Conservative Bias | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of with Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to ensure that regulat
Region: III | D.C. Cook | 25647 | 12/31/2015 02/05/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Forebay Structure |  | H.3 Change Management | TE?: N | 05000315 D.C. Cook 1 |  | 71111.12 | The inspectors identified a finding of very low safety significance and associated NCV of Facility Operating Licenses DPR-58 condition 1.D for Unit 1 and DPR-74 condition 1.D for Unit 2. Specifically, the licensee failed to perform structural monitoring o
Region: III | D.C. Cook | 25639 | 12/31/2015 02/05/2016 | 2015004-02 | NRC | FIN | Mitigating Systems | Green | Probablistic Risk Assessment Model Errors |  | H.12 Avoid Complacency | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71151 | The inspectors identified a finding of very low safety significance for the failure of the licensee to follow procedure 12-EHP-9010-PRA-001, "PRA Model Update." Procedure 12-EHP-9010-PRA-001 establishes requirements to ensure that Donald C. Cook Probabili
Region: III | D.C. Cook | 25640 | 12/31/2015 02/05/2016 | 2015004-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of TRM Section Deletion |  |  | TE?: Y SL-IV-NCVIV | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | The inspectors identified a Severity Level (SL) IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," with an associated finding of very low safety significance (Green), for the licensee's failure to perform a written safety evaluation that pro
Region: III | D.C. Cook | 25648 | 12/31/2015 02/05/2016 | 2015004-04 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of TRM Section Deletion |  | P.3 Resolution | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | The inspectors identified a Severity Level (SL) IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," with an associated finding of very low safety significance (Green), for the licensee's failure to perform a written safety evaluation that pro
Region: III | D.C. Cook | 25649 | 12/31/2015 02/05/2016 | 2015004-05 | NRC | NCVIV | Mitigating Systems | Green | Deletion of Hot Shutdown Panel Procedures |  | P.3 Resolution | TE?: Y SL-IV-NCVIV | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | The inspectors identified an SL IV NCV of very low safety significance of 10 CFR 50.59 for the licensee's improper deletion of procedures for the operation of the hot shutdown (HSD) panel. Specifically, in 2003, the licensee used a 50.59 screen to delete
Region: III | D.C. Cook | 25379 | 11/20/2015 01/04/2016 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Required Seven Day EDG Fuel Oil Storage (Section 1R21.3.b(1)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the failure to translate the emergency diesel gen
Region: III | D.C. Cook | 25380 | 11/20/2015 01/04/2016 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Acceptability of the Surveillance Acceptance Limits for CRID Inverter Operability (Section 1R21.3.b(2)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the surveillance acceptance limits for control ro
Region: III | D.C. Cook | 25381 | 11/20/2015 01/04/2016 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify CRID Inverter Capability to Function During Fault Conditions (Section 1R21.3.b(3)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the CRID inverter capability to interrupt faulted conditions on i
Region: III | D.C. Cook | 25385 | 11/20/2015 01/04/2016 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Consider All Design Basis CCW Passive Failures (Section 1R21.3.b(4)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify that the component cooling water (CCW) design was capable of acce
Region: III | D.C. Cook | 25386 | 11/20/2015 01/04/2016 | 2015008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Applicable ISI Requirements for All CCW System Portions Within the ASME Code Class 3 Boundary (Section 1R21.3.b(5)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR 50.55a, "Codes and Standards," for the failure to meet the Inservice Inspection (ISI) requirements for all CCW components within the American Soc
Region: III | D.C. Cook | 25387 | 11/20/2015 01/04/2016 | 2015008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Procedures to Provide Starting Air to the EDGs to Recover From a SBO (Section 1R21.3.b(6)) |  | P.5 Operating Experience | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR 50.63, "Loss of All Alternating Current Power," for the failure to develop procedures to provide starting air to the EDGs to restore emergency al
Region: III | D.C. Cook | 25388 | 11/20/2015 01/04/2016 | 2015008-07 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Station's Capability to Isolate Postulated CCW System Out-Leakage (Section 1R21.6.b(1)) |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.21M | Green. The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the CCW design capability to isolate a postulated CCW system out
Region: III | D.C. Cook | 25365 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Fire Brigade Fire Fighting Techniques |  | H.9 Training | TE?: N | 05000315 D.C. Cook 1 |  | 71111.05A | The inspectors identified a finding and associated non-cited violation of Facility Operating Licenses DPR 58 condition 2.C(4) and DPR 74 Condition 2. C(3)(o), "Fire Protection Program." Specifically, the licensee failed to identify and subsequently critiq
Region: III | D.C. Cook | 25371 | 09/30/2015 11/12/2015 | 2015003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure of Steam Dump Valves Results in Plant Trip |  | H.8 Procedure Adherence | TE?: N | 05000316 D.C. Cook 2 |  | 71111.18 | A finding of very low safety significance (Green) was self revealed on April 23, 2015, when two condenser steam dump valves failed open during startup following the Unit 2 refueling outage. In response to the failure, the licensee manually tripped the Uni
Region: III | D.C. Cook | 25373 | 09/30/2015 11/12/2015 | 2015003-04 | NRC | NCVIV | Emergency Preparedness | Green | Changes to Minimum 60-Minute Emergency Responder Staffing Without Prior Approval |  |  | TE?: Y SL-IV-NCVIV | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71114.04 | The inspectors identified a finding of very low safety significance with an associated Severity Level IV (SL IV) Non-Cited Violation of Title 10, Code of Federal Regulations (CFR) 50.54(q)(3) and 10 CFR 50.54(q)(4) related to a staffing change in the lice
Region: III | D.C. Cook | 25348 | 03/31/2015 05/11/2015 | 2015001-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Acceptance Criteria for Containment Spray Heat Exchanger Inspections |  | H.11 Challenge the Unknown | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.07A | The inspectors identified a finding of very-low safety significance, and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow the containment spray (CS) heat exchanger inspection pr
Region: III | D.C. Cook | 25349 | 03/31/2015 05/11/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Essential Service Water Strainer Debris Loading and Isolation Valve Gross Leakage |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.07A | The inspectors identified a finding of very-low safety significance, and associated NCV of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to account for the effects of the maximum strainer
Region: III | D.C. Cook | 25350 | 03/31/2015 05/11/2015 | 2015001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure NFPA-805 Sprinkler System Demands Met |  | P.5 Operating Experience | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.15 | The inspectors identified a finding of very-low safety significance with an associated NCV of the Donald C. Cook Operating Licenses for the failure to ensure minimum fire sprinkler head pressure would be available for all required sprinkler systems. Speci
Region: III | D.C. Cook | 25364 | 03/31/2015 05/11/2015 | 2015001-04 | NRC | NCV | Mitigating Systems | Green | Auxiliary Feedwater Pump Declared Operable Without All Post-Maintenance Testing Complete |  | H.4 Teamwork | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.19 | The inspectors identified a finding of very-low safety significance with an associated NCV of TS 5.4.1.a, "Procedures," for the failure to perform all required post-maintenance testing (PMT) before declaring the Unit 1 West Motor-Driven Auxiliary Feedwate
Region: III | D.C. Cook | 25328 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to Quality Associated with the Unit 1 TDAFW Pump Turbine Oil system |  | H.11 Challenge the Unknown | TE?: N | 05000315 D.C. Cook 1 |  | 71111.15 | A finding of very low safety significance, with an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion 16, "Corrective Actions," was identified by the inspectors for the licensee's failure to promptly identify and correct a condition a
Region: III | D.C. Cook | 25339 | 12/31/2014 02/10/2015 | 2014005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Unplanned Inoperability of the AB Fuel Oil Storage Tank During Maintenance |  | H.5 Work Management | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.15 | A finding of very low safety significance, with an associated non-cited violation of Technical Specification (TS) 5.4, "Procedures," was self revealed when a vacuum was inadvertently drawn on the AB Fuel Oil Storage Tank (FOST) during preparations for sur
Region: III | D.C. Cook | 25340 | 12/31/2014 02/10/2015 | 2014005-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Review of Radiological Impact of the Removal of the Auxiliary Shield Blocks on the Containment Accident Shield Post LBLOCA |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion 3 "Design Control," for the licensee's inadequate radiological review of permanently removing the Auxiliary Missile Blocks (AMBs) from the Unit 1 and Unit 2 containme
Region: III | D.C. Cook | 25345 | 12/31/2014 02/10/2015 | 2014005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Trip of the Unit 1 TDAFW Pump |  | H.8 Procedure Adherence | TE?: N | 05000315 D.C. Cook 1 |  | 71111.19 | A finding of very low safety significance, with an associated non- violation of TS 5.4, "Procedures," was self revealed on November 1, 2014, when the Unit 1 TDAFW pump tripped during an emergent dual unit shutdown. Both units were taken offline by opera
Region: III | D.C. Cook | 25347 | 12/31/2014 02/10/2015 | 2014005-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Identify Deficient Locked High Radiation Area Controls Due to procedure Inadequacy |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71124.01 | The inspectors identified a finding of very low safety significance for inadequate procedures used to verify Locked High Radiation Controls in the Unit 2 Containment with an associated non- violation of TS 5.4, "Procedures." As a result, weekly, from Nove
Region: III | D.C. Cook | 25321 | 09/30/2014 11/13/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Procedure |  | P.2 Evaluation | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.12 | A finding of very low safety significance with an associated non-citied violation of 10 CFR 50, Appendix B, Criterion V, Procedures, was identified by the inspectors for the failure to follow the Operability Determination Procedure, PMP-7030-OPR-001. Spec
Region: III | D.C. Cook | 25327 | 09/30/2014 11/13/2014 | 2014004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Classify the Internal Piping in the Auxiliary Feedwater Pump Room Coolers as ASME Code Class 3 Piping |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) with an associated non-citied violation of 10 CFR 50, Appendix B, Criterion III, for failure to correctly translate regulatory requirements related to the American Society for Mec
Region: III | D.C. Cook | 25314 | 06/30/2014 08/11/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Nonconforming Delivery Valve Holders on Emergency Diesel Generators |  | P.1 Identification | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated non-citied violation of 10 CFR 50, Appendix B, Criterion XV, Nonconforming Materials, Parts, or Components, for the failure to prevent nonconforming parts from being us
Region: III | D.C. Cook | 25316 | 06/30/2014 08/11/2014 | 2014003-03 | NRC | FIN | Mitigating Systems | Green | Deficient Annunciator/Plant Process Computer Design |  | P.2 Evaluation | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance associated with the licensee's failure to design the annunciator and plant process computer (PPC) systems in accordance with design specifications. Specifically, the licensee failed to de
Region: III | D.C. Cook | 25311 | 03/31/2014 05/08/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Degraded Latch Prevents Closure of Fire Door |  | H.5 Work Management | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and associated non-citied violation of License Condition 2.C.4 for Unit 1, for the licensee's failure to ensure that a fire door would be closed at the time of a fire. Specificall
Region: III | D.C. Cook | 25312 | 03/31/2014 05/08/2014 | 2014002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Procedures for Vacuum Fill |  | H.9 Training | TE?: N | 05000315 D.C. Cook 1 |  | NONE | . A finding and associated non-cited violation of technical specification (TS) 5.4.1, Procedures, self revealed pertaining to establishing and maintaining procedures to ensure reliable indication of reactor vessel level during reduced RCS inventory and va
Region: III | D.C. Cook | 25313 | 03/31/2014 05/08/2014 | 2014002-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Procedures for Vaccuum Fill |  | P.3 Resolution | TE?: N | 05000315 D.C. Cook 1 |  | NONE | A finding and associated non-citied violation of TS 5.4.1, Procedures, self revealed pertaining to establishing and maintaining procedures to ensure reliable indication of reactor vessel level during reduced RCS inventory and vacuum fill operations. Speci
Region: III | D.C. Cook | 25305 | 03/27/2014 04/15/2014 | 2014007-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of TRM Section Deletion |  |  | TE?: Y SL-IV-NCVIV | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.17T | The inspectors identified a Severity Level IV Non-Cited Violation of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's failure to perform a written safety evaluation
Region: III | D.C. Cook | 25306 | 03/27/2014 04/15/2014 | 2014007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of TRM Section Deletion |  | P.3 Resolution | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.17T | The inspectors identified a Severity Level IV Non-Cited Violation of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's failure to perform a written safety evaluation
Region: III | D.C. Cook | 25310 | 03/27/2014 04/15/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Heat Exchanger Inspection Procedure |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.17T | The inspectors identified a finding having very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish inspection procedures that were
Region: III | D.C. Cook | 25291 | 09/30/2013 11/26/2013 | 2013004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 Steam Generator #1 Stop Valve Dump Valve 2-MRV-212 Stroke Time Failure due to Operation of Dump Valve Outside its Packing Design |  | P.2 Evaluation | TE?: N | 05000316 D.C. Cook 2 |  | 71111.12 | A self revealed finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.4.1 occurred because the licensee failed to establish, implement, and maintain procedures regarding proper steam generator stop valve dump
Region: III | D.C. Cook | 25298 | 09/30/2013 11/26/2013 | 2013004-02 | Self - Revealed | FIN | Mitigating Systems | Green | Faulted 4KV Qualified Off-site Circuit |  | P.5 Operating Experience | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.15 | A finding of very low safety significance was self-revealed on April 24, 2013, because the licensee failed to comply with requirements contained in procedure PMI 7030, "Corrective Action Program," prior to restoring power to the Unit 1 reserve auxiliary t
Region: III | D.C. Cook | 25299 | 09/30/2013 11/26/2013 | 2013004-03 | Self - Revealed | FIN | Initiating Events | Green | Improper Setting in Digital Control System |  | H.5 Work Management | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | A self revealed finding of very low safety significance (Green) occurred because the licensee failed to adjust a key parameter, (KWINIT), in the turbine digital control system after replacing and calibrating the turbine control system linear variable diff
Region: III | D.C. Cook | 25300 | 09/30/2013 11/26/2013 | 2013004-04 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip Due to Improper Control Valve Setpoint |  | H.7 Documentation | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | A self revealed finding of very low safety significance occurred because the licensee failed to program the automatic controller for the condensate heater condensate bypass control valve, 2 CRV 224, with the correct setpoint. Specifically, the automatic c
Region: III | D.C. Cook | 25304 | 09/30/2013 11/26/2013 | 2013004-06 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Operation of Plant Equipment |  | H.5 Work Management | TE?: N | 05000316 D.C. Cook 2 |  | 71152 | A self revealed finding of very low safety significance and associated non-citied violation of TS 5.4.1 occurred because the licensee failed to implement procedures for equipment control. Specifically, plant workers caused two unplanned Limiting Condition
Region: III | D.C. Cook | 25277 | 07/26/2013 08/13/2013 | 2013009-01 | NRC | NCV | Mitigating Systems | Green | Propped Open Fire Doors Required Manual Actuation of the CO2 System to Close |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of the D. C. Cook Nuclear Power Plant facility operating licensee conditions for the Fire Protection Program for the licensee's failure to ensure fire doors tha
Region: III | D.C. Cook | 25283 | 07/26/2013 08/13/2013 | 2013009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assure that a Second Fire Pump would Start upon Demand at the Setpoint |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of the D. C. Cook Nuclear Power Plant facility operating licensee conditions for the Fire Protection Program for the licensee's failure to ensure fire doors tha
Region: III | D.C. Cook | 25284 | 07/26/2013 08/13/2013 | 2013009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Required Shutdown Guidance into Fire Response Procedure. |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specification 5.4.1.d, "Procedures," for the licensee's failure to provide adequate guidance required for safe shutdown in the response procedures.
Region: III | D.C. Cook | 25285 | 07/26/2013 08/13/2013 | 2013009-04 | NRC | NCV | Initiating Events | Green | Evaluate Routing of Fiber Optic Cable in Combustible Exclusion Zone. |  | H.4 Teamwork | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specification 5.4.1.d, "Procedures," for the failure to control combustibles in accordance with a Fire Protection Program (FPP). Specifically, the
Region: III | D.C. Cook | 25275 | 06/30/2013 08/06/2013 | 2013003-01 | NRC | NCV | Initiating Events | Green | Failure to Identify Through Wall Leak |  | H.3(a) Work Planning | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated non cited violation of Technical Specification (TS) 5.4.1 for failure to implement procedures listed in Regulatory Guide 1.33. Specifically, the licensee's boric acid c
Region: III | D.C. Cook | 25276 | 06/30/2013 08/06/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Scaffold Guidelines Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000315 D.C. Cook 1 |  | 71152 | The inspectors identified a non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," because the licensee failed to properly install seismically qualified scaffolds adjacent to safety related equipment as requir
Region: III | D.C. Cook | 25273 | 05/31/2013 07/08/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Emergency Operating Procedures for Mitigating the Consequences of a SGTR per TS Section 5.4.1, "Procedures" |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding of very low safety significance, with two associated NCVs of Technical Specification (TS), Section 5.4.1, "Procedures," and TS 3.7.4, "Steam Generator (SG) Power Operated Relief Valves (PORVs)," for the failure to imple
Region: III | D.C. Cook | 25274 | 05/31/2013 07/08/2013 | 2013010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Enter the Limiting Condition for Operations and Perform Required Actions per TS 3.7.4, "SG PORVs." |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | This performance deficiency was more than minor because it was associated with the equipment performance attribute of the Mitigating Systems Cornerstone and affected the cornerstone objective of ensuring the availability, reliability, and capability of sy
Region: III | D.C. Cook | 25271 | 03/31/2013 05/09/2013 | 2013002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Feed Pump Control Bands |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000315 D.C. Cook 1 |  | 71152 | One self revealing finding of very low safety significance (Green) with an associated NCV of Technical Specification (TS) 5.4.1 occurred because of a failure to implement plant procedure OHI-4000, Conduct of Operations (COOP). While responding to oscillat
Region: III | D.C. Cook | 25272 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | FIN | Mitigating Systems | Green | Operability Evaluation Relied on Alternate Methods Not Demonstrated to be Technically Appropriate |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | NONE | The inspectors identified a finding of very low safety significance for the failure to follow operability evaluation procedural guidance. Specifically, an evaluation was conducted for past operability of the residual heat removal and containment spray sys
Region: III | D.C. Cook | 25265 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Initiating Events | Green | Failure to Perform an Evaluation on Essential Service Water Piping |  | H.4(b) Procedural Compliance | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.07T | : The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to perform an evaluation required to meet 10 CFR Part 50, Appendi
Region: III | D.C. Cook | 25267 | 12/31/2012 02/11/2013 | 2012005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain High Energy Line Break and Fire Barriers |  | H.4(a) Human Error Prevention | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.12 | A self-revealed finding of very low safety significance (Green) and associated NCV occurred based on two violations of 10 CFR 50 Appendix B, Criterion V in the fourth quarter of 2012. The violations occurred due to failure of licensee personnel to secure
Region: III | D.C. Cook | 25257 | 12/31/2012 01/11/2013 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Non-conservative Condensate Storage Tank (CST) Cross-Tie NPSH Calculation |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure sufficient water volume in the condensate storage tank when bo
Region: III | D.C. Cook | 25204 | 12/31/2012 01/11/2013 | 2012007-05 | NRC | URI | Mitigating Systems | Green | Concerns with Operability of SG PORVs with Control Air Compressor Unavailable |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified an URI related to the operability of the SG PORVs as defined in TS 3.7.4 when the associated CAC was unavailable and incapable of providing its required support function. Specifically, the licensee may have failed to declare the
Region: III | D.C. Cook | 25250 | 09/30/2012 10/30/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Preplan and Perform Maintenance on Safety-related Equipment |  | H.3(a) Work Planning | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance with an associated NCV of Technical Specification (TS) 5.4.1 for the failure to implement procedures to perform preventative maintenance in vaults containing safety related cabling subjec
Region: III | D.C. Cook | 25232 | 07/02/2012 08/16/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Vortexing was not evaluated for the volume control, containment spray additive, refueling water storage tanks. |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to evaluate vortexing in the volume control, containment spray additive,
Region: III | D.C. Cook | 25236 | 07/02/2012 08/16/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Incomplete methodology for developing acceptance criteria for suction voids |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to correctly incorporate the interim methodology f
Region: III | D.C. Cook | 25237 | 07/02/2012 08/16/2012 | 2012008-03 | NRC | NCV | Mitigating Systems | Green | Procedures were not developed for performance monitoring of plant parameters. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish appropriate procedures to implement t
Region: III | D.C. Cook | 25238 | 07/02/2012 08/16/2012 | 2012008-04 | NRC | NCV | Mitigating Systems | Green | Minimum flowrates and time requirements for dynamic flushing were not established |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish minimum flowrate and time required in
Region: III | D.C. Cook | 25239 | 07/02/2012 08/16/2012 | 2012008-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Responding to a MODE 4 LOCA |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to include adequate venting instructions in the pr
Region: III | D.C. Cook | 25243 | 07/02/2012 08/16/2012 | 2012008-06 | NRC | NCVIV | Mitigating Systems | Green | 10 CFR 50.59 evaluation for modification of RHR pump casing drain lines was not performed |  |  | TE?: Y SL-IV-NCVIV | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Severity Level IV violation of 10 CFR 50.59, "Changes, Tests, and Experiments," for the failure to perform a written evaluation, which provided the bases for the determinat
Region: III | D.C. Cook | 25244 | 07/02/2012 08/16/2012 | 2012008-07 | NRC | FIN | Mitigating Systems | Green | 10 CFR 50.59 evaluation for modification of RHR pump casing drain lines was not performed |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Severity Level IV violation of 10 CFR 50.59, "Changes, Tests, and Experiments," for the failure to perform a written evaluation, which provided the bases for the determinat
Region: III | D.C. Cook | 25245 | 07/02/2012 08/16/2012 | 2012008-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for RCS Vacuum Fill During Reduced Inventory Operations |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to establish procedures for reduced inventory operatio
Region: III | D.C. Cook | 25230 | 06/30/2012 08/02/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Replace Post-Accident Monitor Displays |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000315 D.C. Cook 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV for the failure to establish preventive maintenance schedules. Technical Specification (TS) 5.4.1 requires that written procedures be established, implemented and maint
Region: III | D.C. Cook | 25231 | 06/30/2012 08/02/2012 | 2012003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Volts per Hertz Differential Relay Modification per Design |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | One self-revealed finding of very low safety significance was identified for the failure to implement the Unit 2 main generator volts per hertz differential relay modification per design, as required by Engineering Change (EC) 50316, "Unit 2 Replacement o
Region: III | D.C. Cook | 25246 | 06/01/2012 08/16/2012 | 2012008-09 | NRC | URI | Mitigating Systems | Green | Computer Program Used for Operability Evaluation Was Not Benchmarked |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 2515/177 | The inspectors identified an unresolved item (URI) regarding the use of computer program Flow-3D in one past-operability evaluation. Specifically, this computer program was not verified against test data. Flow-3D is a general-purpose computer code for
Region: III | D.C. Cook | 25227 | 03/31/2012 04/19/2012 | 2012002-01 | NRC | FIN | Initiating Events | Green | Failure to Install a Grommet Seal on the Main Turbine Thrust Bearing Probe |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 |  | 71152 | One self revealed finding of very low safety significance was identified for the failure to install a grommet seal on the main turbine thrust bearing probes as required by a site design standard, VTD SKFI 0001, "Eddy Probe Systems Technical Manual," durin
Region: III | D.C. Cook | 25225 | 12/31/2011 01/30/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure for PT Examination on ASME Class 1 Piping Weld |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000315 D.C. Cook 1 |  | 71111.08P | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, procedures, and drawings," was identified by the inspectors on September 27, 2011, for the licensee's failure to follow procedure while
Region: III | D.C. Cook | 25226 | 12/31/2011 01/30/2012 | 2011005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow the Clearance Procdure during Maintenance on Safety-Related Equipment |  | H.3(b) Work Activity Coordination | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | One self revealed finding of very low safety significance with an associated NCV of TS 5.4.1.a was identified for the failure to implement a procedure required during maintenance on safety-related equipment. The licensee did not follow the clearance proce
Region: III | D.C. Cook | 25218 | 06/30/2011 07/22/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Failure to Examine RCS Piping Following Application of Mechanical Stress Improvement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 |  | NONE | A finding of very low safety significance and associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," were identified by the inspectors for the licensee's failure to examine reactor coolant system (RCS) pipe surfaces
Region: III | D.C. Cook | 25216 | 12/31/2010 01/25/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Preplan and Perform Maintenance on Safety-related Equipment |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated Non Citied Violation of Technical Specification 5.4.1 for the failure to adequately preplan and perform maintenance on the containment building divider barrier seal in
Region: III | D.C. Cook | 25214 | 10/21/2010 11/30/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate As-Found Heat Exchanger Inspection Guidance and Acceptance Criteria |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding having very low safety-significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish inspection procedures that were appropriate fo
Region: III | D.C. Cook | 25213 | 06/30/2010 08/05/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Positively Identify Power Cable that was to be Removed and Replaced |  | H.4(a) Human Error Prevention | TE?: N | 05000315 D.C. Cook 1 |  | 71152 | A finding of very low safety significance (Green) with an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self revealed. Specifically, licensee personnel failed to positively identify
Region: III | D.C. Cook | 25202 | 03/31/2010 05/05/2010 | 2010002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement Plant Procedures for Using a Mobile Crane |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | A finding of very low safety significance was self-revealed for the failure to implement procedures for using mobile cranes and the failure to use human error prevention tools. Consequently, a mobile crane boom contacted and severed the middle phase of an
Region: III | D.C. Cook | 25203 | 03/31/2010 05/05/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions in a timely and Effective Manner |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | The inspectors identified one finding of very low safety significance with an associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." Specifically, licensee personnel failed to implement corrective actions for wat
Region: III | D.C. Cook | 25194 | 12/31/2009 01/26/2010 | 2009005-01 | NRC | NCV | Initiating Events | Green | Failure to maintain safety related cables in underground manholes from becoming repeatedly submerged. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance with an associated Non Cited Violation of 10 CFR Part 50 Appendix B, Criterion III, "Design Control," for failing to maintain safety related cables in an environment for which they were d
Region: III | D.C. Cook | 25201 | 12/31/2009 01/26/2010 | 2009005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Installation of non conforming parts on the safety related emergency diesel generators. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | One self revealed finding of very low safety significance with an associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion XV, "Non conforming Materials, Parts, or Components," was identified for installing non conforming parts on the safet
Region: III | D.C. Cook | 25149 | 06/30/2009 08/04/2009 | 2009003-01 | NRC | NCV | MISC | Green | Failure to Maintain an Accurate Abnormal Operating Procedure for Loss of Spent Fuel Pit Cooling |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance with an associated Non Citied Violation of Technical Specification 5.4.1 for the failure to adequately maintain a complete and accurate abnormal operating procedure (AOP) in accordance wi
Region: III | D.C. Cook | 25192 | 06/30/2009 08/04/2009 | 2009003-02 | NRC | NCV | MISC | Green | Maintenance Rule On-line Risk Assessment Inaccurate |  | H.4(a) Human Error Prevention | TE?: N | 05000316 D.C. Cook 2 |  | 71111.13 | The inspectors identified one finding of very low safety significance with an associated Non Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," during planned maintenance on the 69 kilo
Region: III | D.C. Cook | 25193 | 06/30/2009 08/04/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Gap in Remote Strainer Waterway |  | H.3(a) Work Planning | TE?: N | 05000316 D.C. Cook 2 |  | 71111.2 | The inspectors identified one finding of very low safety significance with an associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." Specifically, the inspectors identified a gap in the remote strainer waterway f
Region: III | D.C. Cook | 25160 | 03/31/2009 04/24/2009 | 2009002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Follow the Work Control Process |  | H.3(b) Work Activity Coordination | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71152 | A finding of very low safety significance was identified by the inspectors for the failure to follow the work control process during the execution of a work order associated with the Unit 1 turbine repair project. Specifically, failure to follow establish
Region: III | D.C. Cook | 25191 | 10/17/2008 01/23/2009 | 2008009-01 | NRC | FIN | Mitigating Systems | Green | Failure to Provide Adequate Operator Response Procedures for Fire Protection System Operation |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 93812 | A finding of very low safety significance was identified by the team for the failure to have appropriate procedures for control room operator actions. Specifically, a control room annunciator response procedure for a fire protection alarm panel failed to
Region: III | D.C. Cook | 25180 | 06/30/2008 08/13/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify unacceptable interference between the Unit 1 safety injection system piping and the remote strainer waterway in the annulus. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000315 D.C. Cook 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated Non-cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action." Licensee personnel failed to identify unacceptable interference between the Unit 1 Saf
Region: III | D.C. Cook | 25181 | 06/30/2008 08/13/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to review emergency operating procedures to determine if they were impacted by plant modification. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures and Drawings." Licensee personnel failed to review the Unit 1 emergency operating pro
Region: III | D.C. Cook | 25182 | 06/30/2008 08/13/2008 | 2008003-03 | NRC | NCV | MISC | Green | Failure to Comply with TS 5.2.2.d, Overtime Restrictions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of TS 5.2.2.d. The licensee failed to adhere to the TS overtime restrictions for personnel performing safety related work during the Unit 1 Cycle 22
Region: III | D.C. Cook | 25187 | 06/30/2008 08/13/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Failure to adequately implement surveillance test inspection requirements for the Unit 1 ECCS recirculation sump. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and a Non Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings." The licensee failed to adequately implement surveillance test inspection requirem
Region: III | D.C. Cook | 25188 | 06/30/2008 08/13/2008 | 2008003-05 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to effectively implement dose reducing radiological and engineering controls associated with modifications to the reactor recirculation sump strainer during U2C17. |  | H.3(a) Work Planning | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7112102 | A self-revealed finding of very low safety significance was identified for the failure to effectively implement dose reducing radiological and engineering controls consistent with maintaining occupational doses as-low-as-is-reasonably-achievable (ALARA).
Region: III | D.C. Cook | 25189 | 06/30/2008 08/13/2008 | 2008003-06 | NRC | NCV | Barrier Integrity | Green | Failure to Comply with TS SR 3.6.1.1. Failure to perform and as-found LLRT for containment isolation valves |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000315 D.C. Cook 1 |  | 71153 | The inspectors identified a finding of very low safety significance with an associated Non Cited Violation of Technical Specification Surveillance Requirement 3.6.1.1. Licensee personnel failed to perform an as-found local leak rate test as required for c
Region: III | D.C. Cook | 25179 | 02/22/2008 04/07/2008 | 2008502-02 | NRC | FIN | Emergency Preparedness | Green | Between 1984 and 2007, the licensee made significant changes to the ANS without obtaining required Federal Emergency Management Agency (FEMA) approval for the changes as required by 44 CFR 350 |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 95002 | The inspectors identified that between 1984 and 2007, the licensee made significant changes to the ANS without obtaining required Federal Emergency Management Agency (FEMA) approval for the changes as required by 44 CFR 350, "Review and Approval of State
Region: III | D.C. Cook | 25175 | 12/31/2007 01/24/2008 | 2007006-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Design Review of the Unit 1 Main Feedwater Pump Digital controls system |  |  | TE?: N | 05000315 D.C. Cook 1 |  | 71153 | The inspectors identified a finding of very low safety significance associated with a self-revealed event that resulted in a Unit 1 reactor trip. The licensee failed to correctly evaluate and incorporate the cooling needs of electrical equipment inside th
Region: III | D.C. Cook | 25165 | 06/29/2007 07/19/2007 | 2007004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Foreign Material Exclusion Controls During Painting Surface Preparations Affected Operability of the Unit 2 AB EDG |  |  | TE?: N | 05000316 D.C. Cook 2 |  | 71111.13 | A finding of very low safety significance was identified through a self-revealing event. During painting surface preparation activities in the Unit 2 AB emergency diesel generator (EDG) room, the licensee failed to establish appropriate foreign material e
Region: III | D.C. Cook | 25166 | 06/29/2007 07/19/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Use of Incorrectly Configured Test Leads Rendered Two EDGs Inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000315 D.C. Cook 1 |  | 71111.22 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4.1.a was self-revealed. On two separate occasions, a maintenance craftsman performed procedure steps to connect a multi-meter to an emergen
Region: III | D.C. Cook | 25158 | 03/31/2007 05/09/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Performance or Condition of Nuclear Instruments Were Effectively Controlled Through Performance of Appropriate Preventive Maintenance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and an Non-Cited Violation of 10 CFR 50.65(a)(2). The licensee failed to demonstrate that the performance or condition of the Unit 1 and Unit 2 power range and intermediate range nuclear
Region: III | D.C. Cook | 25159 | 03/31/2007 05/09/2007 | 2007003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify Appropriate Contingency Actions During the Work Risk Review to Adjust Packing on Valve 2-NPS-121-II |  | H.3(b) Work Activity Coordination | TE?: N | 05000316 D.C. Cook 2 |  | 71111.13 | On December 14, 2006, a finding of very low safety significance was self-revealed when the valve packing on 2-NPS-121-II, (instrument shutoff valve for reactor coolant system (RCS) loop 2 hot leg wide range pressure instrument), blew out during a planned
Region: III | D.C. Cook | 25155 | 03/02/2007 04/16/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for the licensee's failure to promptly identify that the Unit 1 Train A (1-CD)
Region: III | D.C. Cook | 25156 | 03/02/2007 04/16/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Inadequate Safety Analysis Dose Calculations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for failure to promptly identify and correct a condition adverse to quality reg
Region: III | D.C. Cook | 25157 | 03/02/2007 04/16/2007 | 2007002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Previously Imposed Compensatory Measures |  | H.1(c) Communication of Decisions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated Non-Citied Violation of 10 CFR Part 50.36, "Technical Specifications." Specifically, the licensee failed to maintain previously imposed administrative limits (i.e.,
Region: III | D.C. Cook | 25150 | 12/31/2006 02/12/2007 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Accept for Continued Service, by Correction, or Evaluation or Test, a Degraded Chemical Volume Control System Support |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000315 D.C. Cook 1 |  | 71111.08P | The inspectors identified a Non-Citied Violation of 10 CFR Part 50.55(a)(g)(4), for failure to accept for continued service, by correction, or evaluation or test, a chemical and volume control system (CVCS) support (2-ACS-R-913) whose examination detected
Region: III | D.C. Cook | 25131 | 06/29/2006 08/10/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Potential External and Internal Flooding Impact on Safe Shutdown Equipment in the Lake Screen House |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria III, "Design Control." The licensee failed to correctly translate the design basis into specifications for the es
Region: III | D.C. Cook | 25132 | 06/29/2006 08/10/2006 | 2006004-02 | NRC | FIN | Initiating Events | Green | Inadequate Preventive/Corrective Maintenance on Turbine Building Sump Overflow Check Valve 12-DR-129 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance. The licensee failed to perform adequate preventive and corrective maintenance on Turbine Building sump overflow check valve 12-DR-129. As a result, the valve was found in a significantly
Region: III | D.C. Cook | 25133 | 06/29/2006 08/10/2006 | 2006004-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Functionality Evaluation for Degraded Check Valve Condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance. The licensee did not adequately evaluate the functionality of Turbine Building sump overflow check valve 12-DR-129, while the valve was in a significantly degraded condition such that it
Region: III | D.C. Cook | 25134 | 06/29/2006 08/10/2006 | 2006004-04 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Loss of Reactor Coolant System Inventory While Placing Emergency Core Cooling Systems in Standby Readiness |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000316 D.C. Cook 2 |  | 7111114 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings" was self-revealed. With Unit 2 in Mode 4 (Hot Shutdown), using an inadequate procedure, plant o
Region: III | D.C. Cook | 25135 | 06/29/2006 08/10/2006 | 2006004-05 | Self - Revealed | FIN | Barrier Integrity | Green | Heavy Load Dropped While Removing Vertical Bulkhead Blocks in Unit 2 Containment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000316 D.C. Cook 2 |  | 7111114 | A finding of very low safety significance was self-revealed, when the lift rig device failed and a 37 ton vertical bulkhead block dropped approximately 15 feet inside Unit 2 containment with the plant in Mode 5 (Cold Shutdown). The plant procedure utilize
Region: III | D.C. Cook | 25136 | 06/29/2006 08/10/2006 | 2006004-06 | NRC | NCV | Barrier Integrity | Green | Failure to Perform As-found Local Leak Rate Testing for a Containment Isolation Valve |  | H.3(b) Work Activity Coordination | TE?: N | 05000316 D.C. Cook 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of TS Surveillance Requirement 3.6.1.1. The licensee failed to perform an as-found local leak rate test (LLRT) for containment isolation valve 2-SI-
Region: III | D.C. Cook | 25139 | 06/29/2006 08/10/2006 | 2006004-08 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Technical Specification Surveillance Acceptance Criteria for the Emergency Diesel Generators |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000316 D.C. Cook 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria III, "Design Control." The licensee failed to establish appropriate Technical Specification (TS) surveillance acc
Region: III | D.C. Cook | 25130 | 06/21/2006 07/07/2006 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Verification of Containment Average Air Temperature |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7111117B | The inspections identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance. Specifically, verification of containment lower compartment average temperature per Surveillance Req
Region: III | D.C. Cook | 25125 | 03/31/2006 05/05/2006 | 2006003-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Perform Adequate Checks of the Automatic Gas Analyzer System Oxygen Monitor Channel |  |  | TE?: N | 05000315 D.C. Cook 1 05000316 D.C. Cook 2 |  | 7112201 | An inspector-identified finding of very low safety significance and an associated violation of NRC requirements were identified for the failure to perform adequate daily checks for the in-service oxygen monitor channel of the automatic gas analyzer system
Region: III | Davis-Besse | 126616 | 12/31/2019 01/31/2020 | 2019004-02 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Injection into Once Through Steam Generator 1 while Running the Emergency Feedwater Pump |  | H.12 - Avoid Complacency | TE?: N | 05000346 Davis-Besse | Procedure Quality | 71152 | A self-revealed finding of very low safety significance (Green) and associated non-cited violation of Technical Specification Section 5.4.1.a for the licensee’s failure to establish a procedure to address the requirements of RG 1.33 Appendix A, Section 9.
Region: III | Davis-Besse | 126361 | 12/31/2019 01/31/2020 | 2019004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Emergency Ventilation System Inadequate Acceptance Criteria |  | H.11 - Challenge the Unknown | TE?: N | 05000346 Davis-Besse | SSC and Barrier Performance | 71153 | A self-revealed finding of very low safety significance and an associated non-cited violation (NCV) of Title 10 Code of Federal Regulations Part 50, Appendix B, criterion V, "Instructions, Procedures, and Drawings," was identified when the licensee failed
Region: III | Davis-Besse | 125888 | 09/30/2019 11/12/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize and Correct Fisher Controls Butterfly Valve Taper Pin Defects |  | P.5 - Operating Experience | TE?: N | 05000346 Davis-Besse |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings” for the licensee’s failure to prescribe instructio
Region: III | Davis-Besse | 125460 | 07/23/2019 09/09/2019 | 2019010-01 | NRC | NCV | Barrier Integrity | Green | Failure to Translate Design Basis for the Main Control Room Boundary Blockwall |  | P.1 - Identification | TE?: N | 05000346 Davis-Besse | SSC and Barrier Performance | 71152B | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” when the licensee failed to correctly translate the design basis requirem
Region: III | Davis-Besse | 125090 | 06/30/2019 08/01/2019 | 2019002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow the Train 2 Containment Radiation Monitor Surveillance Procedure |  | H.5 - Work Management | TE?: N | 05000346 Davis-Besse | Equipment Performance | 71152 | A Green finding with an associated non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on April 9, 2019, when the licensee failed to accomplish the train 2 normal containment ra
Region: III | Davis-Besse | 24707 | 10/05/2018 11/05/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Could Lead to a Potential Water Hammer Event in the Service Water System |  | NPP | TE?: N | 05000346 Davis-Besse |  | 71111.21M | The inspectors identified a finding of very low safety significance (i.e., Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee’s failure to prescribe an adequate procedure for
Region: III | Davis-Besse | 24708 | 10/05/2018 11/05/2018 | 2018011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Fast Bus Transfer Scheme |  | NPP | TE?: N | 05000346 Davis-Besse |  | 71111.21M | The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to verify the adequacy of design of the fast bus transfer scheme.
Region: III | Davis-Besse | 24075 | 06/30/2018 08/10/2018 | 2018002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow the Makeup and Purification Procedure |  | H.12 - Avoid Complacency | TE?: N | 05000346 Davis-Besse |  | 71152 | A self-revealed Green finding and associated Non-Cited Violation of Technical Specification 5.4.1.a, Procedures, was identified when the licensee failed to follow station procedure DB-OP-06006, “Makeup and Purification System.” Specifically, the licensee
Region: III | Davis-Besse | 24333 | 06/30/2018 08/10/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Apply Technical Specification for SFAS Instrumentation |  | H.14 - Conservative Bias | TE?: N | 05000346 Davis-Besse |  | 71153 | The NRC identified a finding of Green significance and an associated NCV of Technical Specification 3.3.5, Safety Features Actuation System (SFAS) Instrumentation for the licensee’s failure to place the reactor in Mode 3 within six hours of identifying th
Region: III | Davis-Besse | 24334 | 06/30/2018 08/10/2018 | 2018002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Procedure Affecting Quality |  | H.8 - Procedure Adherence | TE?: N | 05000346 Davis-Besse |  | 71153 | The NRC identified a finding of Green significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” due to the licensee’s failure to implement DB-OP-03006, “Miscellaneous Instrumen
Region: III | Davis-Besse | 24335 | 06/30/2018 08/10/2018 | 2018002-04 | NRC | FIN | Mitigating Systems | Green | Misapplication of the Operability Determination Process |  | H.13 - Consistent Process | TE?: N | 05000346 Davis-Besse |  | 71153 | The NRC identified a finding of Green significance due to the licensee’s misapplication of NOP-OP-1009, “Operability Determinations and Functionality Assessments.” Specifically, the licensee failed to apply the Operability Determination process in accorda
Region: III | Davis-Besse | 23208 | 01/26/2018 02/14/2018 | 2017004-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Maintain Procedures Associated with Ventilation Air Monitoring Assessment Program |  | H.5 - Work Management | TE?: N | 05000346 Davis-Besse |  | 71124.06 | The inspectors identified a finding of very-low safety significance (Green) and an associated Non-Cited Violation of Technical Specification 5.4.1 for the failure to maintain procedures for Station Vent Releases during planned scenarios. Specifically, the
Region: III | Davis-Besse | 23488 | 12/31/2017 02/14/2018 | 2017004-04 | NRC | FIN | Mitigating Systems | Green | Failure to Document a Degraded Condition on the AFPT 1 Outboard Bearing |  | P.2 - Evaluation | TE?: N | 05000346 Davis-Besse |  | 71152 | The inspectors identified a finding of very low safety significance for the licensee’s failure to document a degraded condition of a safety-related system in the corrective action program (CAP), as required by licensee procedure, NOP–LP–2001. Specific
Region: III | Davis-Besse | 21653 | 09/30/2017 11/14/2017 | 2017003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Adequate Evaluation of Cask Crane Components and Crane Support Structure |  | H.6 - Design Margins | TE?: N | 05000346 Davis-Besse |  | 60856.1 | Green: A finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, “Design Control,” was identified by the NRC inspectors for the f
Region: III | Davis-Besse | 21656 | 09/30/2017 11/14/2017 | 2017003-04 | NRC | NCVIV | Barrier Integrity | Green | Failure to Perform 10 CFR 50.59 Evaluation |  | NPP | TE?: Y SL-IV-NCVIV | 05000346 Davis-Besse |  | 60856.1 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR 50.59(d)(1), “Changes, Tests, and Experiments,” was identified by the NRC inspectors for the licensee’s failure to maintain a record of a change from a method described in t
Region: III | Davis-Besse | 35628 | 05/17/2017 05/23/2017 | 2017008-01 | NRC | FIN | Mitigating Systems | Green | Failure to Maintain Adequate Room Temperature in the Emergency Feedwater Facility |  | H.11 Challenge the Unknown | TE?: N | 05000346 Davis-Besse |  | 2515/191 | A finding of very low safety significance was identified by the inspectors for failing to maintain adequate room temperature in the emergency feedwater facility (EFWF) to support equipment operation. Specifically, the inspectors identified temperatures be
Region: III | Davis-Besse | 23500 | 03/31/2017 05/12/2017 | 2017001-01 | NRC | NOV | Mitigating Systems | Green | Failure to Establish a Test Program that Demonstrates the Emergency Core Cooling System Room Coolers Will Perform Satisfactorily in Service |  | P.2 - Evaluation | TE?: N | 05000346 Davis-Besse |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and an associated Cited Violation of Title 10 of the Code of Federal Regulations, (10 CFR) Part 50, Appendix B, Criterion XI, “Test Control,” for the licensee’s failure to es
Region: III | Davis-Besse | 35624 | 12/31/2016 01/26/2017 | 2016004-01 | Self - Revealed | FIN | Initiating Events | Green | Mispositioned Instrument Air Valves Result in Plant Transient |  | H.12 Avoid Complacency | TE?: N | 05000346 Davis-Besse |  | 71111.12 | A self-revealed finding of very low safety significance was identified for the licensee's failure to appropriately follow station procedures for aligning instrument air valves that support main feedwater (MFW) regulating valve operation. Specifically, two
Region: III | Davis-Besse | 35627 | 12/31/2016 01/26/2017 | 2016004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Evaluate Degraded Turbine Building Roof Vents |  | P.2 Evaluation | TE?: N | 05000346 Davis-Besse |  | 71153 | A finding of very low safety significance was self-revealed on September 10, 2016, when rainwater intrusion into the automatic voltage regulator caused a generator lockout and reactor trip. Specifically, station management failed to adequately assess the
Region: III | Davis-Besse | 35622 | 12/01/2016 01/04/2017 | 2016009-01 | NRC | NCV | Mitigating Systems | Green | Fire Hazards Analysis Report Incorrectly Described Rooms 511 and 512 as being Continuously Staffed |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.05T | The inspectors identified a finding of very-low safety significance (Green), and associated Non-Cited Violation of License Condition 2.C.(4) for the licensee's failure to implement and maintain the Fire Protection Program as described in the Updated Final
Region: III | Davis-Besse | 35615 | 10/01/2016 09/16/2016 | 2016010-01 | NRC | NCVIV | Barrier Integrity | Green | 10 CFR 50.59 Evaluation Failed to Consider Change to Seismic Licensing Basis |  |  | TE?: Y SL-IV-NCVIV | 05000346 Davis-Besse |  | 50001 | A finding of very-low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50.59(b)(1), "Changes, Tests, and Experiments," (effective January 1, 1991) was identified by the inspector for the licensee's failu
Region: III | Davis-Besse | 35616 | 09/30/2016 11/04/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Instructions to Correctly Assemble Electrical Conductor Seal Assemblies |  | H.9 Training | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the licensee's failure to provide adequate instructions to correctly as
Region: III | Davis-Besse | 35621 | 09/30/2016 11/04/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Modification Design Control Measures Result in Reactor Protection System Inoperability |  | H.2 Field Presence | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," were identified for the licensee's failure to have adequately prepared and
Region: III | Davis-Besse | 35031 | 06/30/2016 07/25/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Use the Corrective Action Program to Evaluate and Document Degraded Condition with Auxiliary Feedwater Train 2 |  | P.1 Identification | TE?: N | 05000346 Davis-Besse |  | 71152 | An NRC identified finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the licensee's failure to have entered a degraded condition associate
Region: III | Davis-Besse | 35040 | 06/30/2016 07/25/2016 | 2016002-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Evaluation of Trend Related to A25X Fuse Failures |  | P.3 Resolution | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," were identified for the licensee's failure to have adequately addressed
Region: III | Davis-Besse | 35041 | 06/30/2016 07/25/2016 | 2016002-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Post-Manufacture Quality Control Inspections Performed for ASME Section III, Class 2 Reactor Coolant Pump Seal Cavity Vent Line Flexible Hose |  | H.2 Field Presence | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 3.4.13, "Reactor Coolant System (RCS) Operational Leakage," were identified for the failure of a licensee vendor to have ensured that a replaceme
Region: III | Davis-Besse | 35011 | 03/31/2016 04/26/2016 | 2016001-01 | Self - Revealed | NCV | Mitigating Systems | Green | OPERATION OF SAFETY RELATED BUTTERFLY VALVES IN A MANNER BEYOND DESIGN |  | H.6 Design Margins | TE?: N | 05000346 Davis-Besse |  | 71111.12 | A self-revealed finding of very low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the licensee's failure t
Region: III | Davis-Besse | 35020 | 03/31/2016 04/26/2016 | 2016001-04 | Self - Revealed | FIN | Mitigating Systems | Green | LESS THAN SUFFICIENT WORK PACKAGE DOCUMENTATION AND INSTRUCTIONS RESULTED IN AN INADEQUATE PART BEING INSTALLED INTO THE PLANT'S INTEGRATED CONTROL SYSTEM |  | H.7 Documentation | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance (Green) was identified for the licensee's failure to include an adequate bench check for a replacement integrated control system (ICS) module that was installed into the system during the plant's 201
Region: III | Davis-Besse | 35021 | 03/31/2016 04/26/2016 | 2016001-05 | Self - Revealed | FIN | Mitigating Systems | Green | LACK OF SOFTWARE CHANGE CONTROLS AND INADEQUATE CORRECTIVE ACTION FOR AN OPERATOR WORKAROUND CONTRIBUTES TO COMPLICATIONS EXPERIENCED DURING A REACTOR TRIP |  | P.2 Evaluation | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance (Green) was identified for the licensee's failure to implement a technically correct software change associated with the SG / Reactor Demand ICS control station. Specifically, a known logic error wit
Region: III | Davis-Besse | 35028 | 03/31/2016 04/26/2016 | 2016001-06 | Self - Revealed | NCV | Mitigating Systems | Green | LESS THAN ADEQUATE PROCEDURAL INSTRUCTIONS FOR RESTORING MAIN FEEDWATER FOLLOWING A REACTOR TRIP |  | H.1 Resources | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance (Green), and an associated NCV of TS 5.4.1(a) were identified for the licensee's failure to establish and implement adequate procedural guidance for restoring MFW following a reactor trip. Specifical
Region: III | Davis-Besse | 35010 | 12/31/2015 02/03/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO USE WORST CASE 4160 VAC BUS VOLTAGE IN DESIGN CALCULATIONS |  |  | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding of very low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to have adequate analysis r
Region: III | Davis-Besse | 35006 | 09/30/2015 10/21/2015 | 2015003-01 | Self - Revealed | FIN | Initiating Events | Green | FLOW ACCELERATED CORROSION MODEL NOT MAINTAINED IN ACCORDANCE WITH INDUSTRY STANDARDS AND GUIDANCE |  |  | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance was identified for the licensee's failure to maintain an adequate flow accelerated corrosion (FAC) program in accordance with station procedures and applicable industry guidance. Specifically, an inc
Region: III | Davis-Besse | 35005 | 06/30/2015 05/28/2015 | 2014008-01 | NRC | NCVIV | Barrier Integrity | Green | Departure from Method of Evaluation Required Prior NRC Approval Under 10 CFR 50.59 (c)(2) with respect to licensee acceptance of the shield building laminar cracking. |  |  | TE?: Y SL-IV-NCVIV | 05000346 Davis-Besse |  | 71152 | Severity Level IV - Green. The inspectors identified a Severity Level IV NCV of Title 10, Code of Federal Regulations (CFR) Part 50.59(c)(2), and an associated finding of very low safety significance for the licensee's failure to request and obtain a lice
Region: III | Davis-Besse | 34997 | 02/27/2015 04/10/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Vulnerability of EDG Crosstie to a Non-Essential Bus (1R21.3.b.(1)) |  |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that applicable regulatory re
Region: III | Davis-Besse | 34998 | 02/27/2015 04/10/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with IEEE 308-1971 for the Required Independence of Safety-Related Essential Inverter Distribution Systems (1R21.3.b.(2)) |  |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to demonstrate compliance with Institute of Electrical and Electronics Engin
Region: III | Davis-Besse | 34999 | 02/27/2015 04/10/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate the Design Analysis Required Acceptance Limit into Surveillance Procedure (1R21.3.b.(3)) |  |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee failing to incorporate the design requirements and acceptance limits into test
Region: III | Davis-Besse | 35000 | 02/27/2015 04/10/2015 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Several CCW System Manual Valves Were in the Correct Position (1R21.3.b.(4)) |  |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of Technical Specification (TS) Surveillance Requirement 3.7.7.1, for the licensee's failure to verify several component cooling water (CCW) system manual v
Region: III | Davis-Besse | 35004 | 02/27/2015 04/10/2015 | 2015008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications for the Borated Water Storage Tank (1R21.4.b.(1)) |  | P.5 Operating Experience | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of TS 3.5.4, "Borated Water Storage Tank (BWST)," for the failure to comply with the limiting condition for operation (LCO) while the BWST was aligned to th
Region: III | Davis-Besse | 34995 | 01/09/2015 02/17/2015 | 2014007-01 | NRC | NCV | Initiating Events | Green | Failure to Install and Control RCP Seal Cavity Vent Flexible Hoses Per Design Basis Analysis |  | H.6 Design Margins | TE?: N | 05000346 Davis-Besse |  | 71111.17T | The inspectors identified a finding of very-low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to install and control the Reactor Coolant Pump
Region: III | Davis-Besse | 34994 | 12/31/2014 01/28/2015 | 2014005-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURAL GUIDANCE DURING RESTORATION FROM VALVE MAINTENANCE RESULTS IN FEEDWATER HEATER SYSTEM AND PLANT POWER TRANSIENT |  | H.5 Work Management | TE?: N | 05000346 Davis-Besse |  | 71111.13 | A self-revealed finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1(a) were identified when the licensee failed to provide proper procedural guidance for the restoration from valve maintenance on HD291G, a manu
Region: III | Davis-Besse | 34988 | 09/30/2014 10/23/2014 | 2014004-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PROPERLY PERFORM REQUIRED FIRE WATCH |  | H.14 Conservative Bias | TE?: N | 05000346 Davis-Besse |  | 71111.05Q | An NRC-identified finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.4.1(d) were identified when the licensee failed to properly implement station procedures for fire protection impairments and fire watche
Region: III | Davis-Besse | 34992 | 09/30/2014 10/23/2014 | 2014004-02 | NRC | NCVIV | Mitigating Systems | Green | FAILURE TO MAKE A TIMELY 8-HOUR EVENT REPORT PER 10 CFR 50.72(b)(3)(xiii) |  | H.7 Documentation | TE?: Y SL-IV-NCVIV | 05000346 Davis-Besse |  | 71153 | An NRC-identified finding of very low safety significance and an associated Severity Level IV NCV of the reporting requirements of 10 CFR 50.72(b)(3)(xiii) were identified following the inspectors' review of licensee corrective actions for a previous occu
Region: III | Davis-Besse | 34984 | 07/02/2014 07/22/2014 | 2013010-03 | NRC | NCV | Barrier Integrity | Green | Failure to Completely Repair Shield Building Concrete Voiding |  | H.14 Conservative Bias | TE?: N | 05000346 Davis-Besse |  | 50001 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure in 2011 to properly repair concrete voiding in the
Region: III | Davis-Besse | 34983 | 07/01/2014 07/22/2014 | 2013010-02 | NRC | NCV | Barrier Integrity | Green | Use of Unqualified Procedure for Ultrasonic Examination of Shield Building Rebar |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000346 Davis-Besse |  | 50001 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," when the licensee failed to use a qualified procedure for ultras
Region: III | Davis-Besse | 34972 | 06/30/2014 07/31/2014 | 2014003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PROPERLY PERFORM REQUIRED FIRE WATCH |  | H.4 Teamwork | TE?: N | 05000346 Davis-Besse |  | 71111.05Q | The Inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) 5.4.1(d) when the licensee failed to properly implement station procedures for control of ignition sources. Specifica
Region: III | Davis-Besse | 34973 | 06/30/2014 07/31/2014 | 2014003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO MAINTAIN AN APPROVED HOT WORK PERMIT FOR CONTAINMENT |  | H.12 Avoid Complacency | TE?: N | 05000346 Davis-Besse |  | 71111.05Q | The Inspectors identified a finding of very low safety significance and an associated non-cited violation of TS 5.4.1(d) when the licensee failed to properly implement station procedures for control of ignition sources. Specifically, an invalid hot work p
Region: III | Davis-Besse | 34974 | 06/30/2014 07/31/2014 | 2014003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE AUXILIARY FEEDWATER DESIGN BASES WERE CORRECTLY TRANSLATED INTO DESIGN DOCUMENTS AND PROCEDURES |  | H.12 Avoid Complacency | TE?: N | 05000346 Davis-Besse |  | 71111.07T | The inspectors identified two examples representing one finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure the auxiliary feedwater
Region: III | Davis-Besse | 34980 | 06/30/2014 07/31/2014 | 2014003-04 | NRC | NCV | Mitigating Systems | Green | ACCEPTANCE CRITERIA FOR EMERGENCY CORE COOLING SYSTEM ROOM COOLER INSPECTION WAS NOT SPECIFIED IN INSPECTION PROCEDURE |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.07T | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow the Generic Letter (GL) 89
Region: III | Davis-Besse | 34981 | 06/30/2014 07/31/2014 | 2014003-05 | NRC | FIN | Mitigating Systems | Green | REPAIR WORK PRIORITY DID NOT SUPPORT TIMELY CORRECTIVE ACTION |  | P.3 Resolution | TE?: N | 05000346 Davis-Besse |  | 71153 | The Inspectors identified a finding of very low safety significance following review of licensee corrective actions for a previous occurrence of a reportable condition that took place on May 26, 2014. Specifically, on November 17, 2013, the licensee's con
Region: III | Davis-Besse | 34968 | 04/01/2014 05/12/2014 | 2013009-01 | NRC | URI | Barrier Integrity | Green | Methodology and Acceptance Criteria Utilized for Design and Licensing Basis of the Shield Building with Laminar Cracking |  |  | TE?: N | 05000346 Davis-Besse |  | 71152 | On September 16, 2013, the NRC initiated an inspection related to the licensee's corrective actions associated with re-establishment of the design and licensing basis of the SB with identified laminar cracking. The objectives of the inspection included ve
Region: III | Davis-Besse | 34966 | 03/31/2014 04/23/2014 | 2014002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT FIRE PROTECTION PLAN REQUIREMENTS RELATED TO CONTROL OF IGNITION SOURCES |  | H.4 Teamwork | TE?: N | 05000346 Davis-Besse |  | 71111.05Q | The Inspectors identified a finding of very low safety significance and associated non-cited violations of Technical Specification (TS) 5.4.1(d) when the licensee failed to properly implement station procedures for control of ignition sources. Specificall
Region: III | Davis-Besse | 34967 | 03/31/2014 04/23/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | CONTAINMENT ECCS RECIRCULATION SUMP RELIABILITY DEGRADED DUE TO UNFASTENED DEBRIS GATE |  | P.3 Resolution | TE?: N | 05000346 Davis-Besse |  | 71111.2 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to maintain a containment "trash" ga
Region: III | Davis-Besse | 34962 | 12/31/2013 01/30/2014 | 2013005-01 | Self - Revealed | NCV | Initiating Events | Green | OPERATOR FAILURE TO FOLLOW PROCEDURE RESULTS IN SERVICE WATER SYSTEM TRANSIENT |  | H.12 Avoid Complacency | TE?: N | 05000346 Davis-Besse |  | 71111.11Q | A self-revealed finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1(a) were identified when the licensee failed to properly implement plant procedures for placing component cooling water (CCW) Pump 2 in standby
Region: III | Davis-Besse | 34963 | 12/31/2013 01/30/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | EMERGENCY DIESEL GENERATOR NO. 2 RENDERED UNAVAILABLE BY SCHEDULED MAINTENANCE |  | H.5 Work Management | TE?: N | 05000346 Davis-Besse |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(4) for the licensee's failure to implement appropriate risk management actions during planned maintenance for Emergency Diesel Generator (EDG) No.
Region: III | Davis-Besse | 34910 | 12/31/2013 01/30/2014 | 2013005-03 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO MAINTAIN WRITTEN PROCEDURES TO PROVIDE QUALITY ASSURANCE FOR EFFLUENT MONITORING |  |  | TE?: N | 05000346 Davis-Besse |  | 71124.06 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.4.1. Specifically, the licensee failed to maintain procedures to ensure compliance with TS 5.5.3, "Radioactive Effluent Controls Program." Corrective actions
Region: III | Davis-Besse | 34955 | 09/30/2013 11/01/2013 | 2013004-01 | NRC | FIN | Mitigating Systems | Green | INADEQUATE OPERATIONS CREW TURNOVER |  | H.10 Bases for Decisions | TE?: N | 05000346 Davis-Besse |  | 71111.11Q | The inspectors identified a finding of very low safety significance for the licensee's failure to perform an accurate and detailed shift turnover to ensure oncoming plant operators were aware of plant status. Specifically, cracks identified in two control
Region: III | Davis-Besse | 34956 | 09/30/2013 11/01/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | IMPACT OF A HELB IN THE TURBINE BUILDING ON SAFETY-RELATED ELECTRICAL EQUIPMENT LOCATED IN THE SWITCHGEAR ROOMS |  | P.2 Evaluation | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to ensure design features to protect the low and high
Region: III | Davis-Besse | 34957 | 09/30/2013 11/01/2013 | 2013004-03 | Self - Revealed | FIN | Initiating Events | Green | RCP TRIP, RPS ACTUATION AND REACTOR TRIP RESULTS FROM THE INSTALLATION OF A RCP MOTOR REPAIR PART NOT SUITABLE FOR THE APPLICATION |  | H.1 Resources | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance was identified for the licensee's failure to procure and install appropriate replacement parts for repair of the Reactor Coolant Pump (RCP) 1 2 motor during the 2010 refueling outage. Specifically, a
Region: III | Davis-Besse | 34961 | 09/30/2013 11/01/2013 | 2013004-04 | Self - Revealed | NCV | Initiating Events | Green | OPERATION OF THE PLANT AT POWER WITH REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE |  | P.2 Evaluation | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance and an associated non-cited violation of TS 3.4.13, "Reactor Coolant System (RCS) Operational Leakage," were identified for the licensee's failure to fully evaluate a previously identified degraded c
Region: III | Davis-Besse | 34948 | 06/30/2013 07/22/2013 | 2013003-01 | Self - Revealed | NCV | Initiating Events | Green | OPERATIONS COMMUNICATIONS AND WORK COORDINATION ERROR RESULTS IN SERVICE WATER SYSTEM TRANSIENT |  | H.1(c) Communication of Decisions | TE?: N | 05000346 Davis-Besse |  | 71111.19 | A self-revealed finding of very low safety significance (Green) and associated NCV of TS 5.4.1(a) were identified when the licensee failed to properly implement plant procedures for placing Component Cooling Water (CCW) Pump 3 in spare status. Specificall
Region: III | Davis-Besse | 34941 | 03/31/2013 04/22/2013 | 2013002-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO MAINTAIN STATION BLACKOUT DIESEL GENERATOR OUTPUT CABLES IN AN ENVIRONMENT CONSISTENT WITH DESIGN |  | H.3(b) Work Activity Coordination | TE?: N | 05000346 Davis-Besse |  | 71111.06 | The inspectors identified a finding of very low safety significance for the licensee's failure to maintain normally energized medium voltage cables BPGD302C, C1, D, and D1 in an environment consistent with the cable design. The cables, which are output ca
Region: III | Davis-Besse | 34945 | 03/31/2013 04/22/2013 | 2013002-02 | Self - Revealed | NCV | Barrier Integrity | Green | CONTAINMENT ISOLATION VALVE RENDERED INOPERABLE BY "WRONG COMPONENT" OPERATOR ERROR |  | H.4(a) Human Error Prevention | TE?: N | 05000346 Davis-Besse |  | 71111.13 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," were identified for the licensee's failure to properly implement the procedure for the Hydrogen Di
Region: III | Davis-Besse | 34939 | 12/31/2012 01/25/2013 | 2012005-01 | Self - Revealed | NCV | Initiating Events | Green | OPERATOR ERROR IN RESPONSE TO A SMALL POWER TRANSIENT MOMENTARILY RENDERS TS EQUIPMENT INOPERABLE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71111.11Q | A self-revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1(a) were identified following the control room crew's response to a small power rise that occurred while shifting the plant's Integrated Con
Region: III | Davis-Besse | 34933 | 09/30/2012 10/24/2012 | 2012004-01 | Self - Revealed | NCV | Barrier Integrity | Green | OPERATOR ERROR RESTORING ESSENTIAL MCC TO SERVICE RENDERS TS EQUIPMENT INOPERABLE |  | H.4(a) Human Error Prevention | TE?: N | 05000346 Davis-Besse |  | 71111.13 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the licensee's failure to properly implement the procedure for restorin
Region: III | Davis-Besse | 34934 | 09/30/2012 10/24/2012 | 2012004-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO USE MATERIAL SPECIFIED MINIMUM YIELD STRESS IN STRUCTURAL DESIGN |  |  | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to use material specified minimum yield stress in accordance with American In
Region: III | Davis-Besse | 34926 | 06/30/2012 07/26/2012 | 2012003-01 | Self - Revealed | FIN | Initiating Events | Green | OIL SAMPLE DRAWN FROM RUNNING RCP RESULTED IN ENTRY INTO ABNORMAL OPERATING PROCEDURE AND RCP SHUTDOWN |  | H.3(a) Work Planning | TE?: N | 05000346 Davis-Besse |  | 71111.2 | A self-revealed finding of very low safety significance was identified for the licensee's failure to establish and implement technically appropriate work instructions for the drawing of oil samples from the reactor coolant pump (RCP) lower bearing reservo
Region: III | Davis-Besse | 34921 | 03/31/2012 04/23/2012 | 2012002-01 | NRC | NCV | Emergency Preparedness | Green | SEISMIC INSTRUMENTATION UNAVAILABLE FOR EMERGENCY EVENT CLASSIFICATION |  | H.3(b) Work Activity Coordination | TE?: N | 05000346 Davis-Besse |  | 71114.05 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.54(q) for failing to follow and maintain an emergency plan that meets the requirements of emergency planning standard 10 CFR 50.47(b)(4). Specifically,
Region: III | Davis-Besse | 34922 | 03/31/2012 04/23/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN SAFETY-RELATED DC SYSTEMS DESIGN CONTROL |  |  | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding, with two examples, of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to maintain the electrical separation of the redunda
Region: III | Davis-Besse | 34903 | 12/31/2011 01/31/2012 | 2011005-01 | NRC | NCV | Barrier Integrity | Green | INADEQUATE CONTROL OF WELD FILLER METAL ELECTRODES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | NONE | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" were identified by the inspectors for the licensee's failure to control weld rod oven temperature in accordance
Region: III | Davis-Besse | 34904 | 12/31/2011 01/31/2012 | 2011005-02 | Self - Revealed | FIN | Mitigating Systems | Green | DECAY HEAT PUMP 1-1 DAMAGED AND RENDERED INOPERABLE BY PERSONNEL CLIMBING ON EQUIPMENT |  | H.3(a) Work Planning | TE?: N | 05000346 Davis-Besse |  | 71111.13 | A self-revealed finding of very low safety significance (Green) was identified when low pressure injection equipment was damaged by operators attempting to access an overhead valve. Specifically, by climbing and standing on sensitive plant equipment, the
Region: III | Davis-Besse | 34908 | 12/31/2011 01/31/2012 | 2011005-03 | Self - Revealed | NCV | Mitigating Systems | Green | AIR VOIDS IN COMPONENT COOLING WATER SYSTEM CAUSED BY INADEQUATE FILL AND VENT PROCEDURE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A finding of very low safety significance and an associated NCV of TS 5.4.1(a) were identified by the inspectors for the licensee's failure to establish, implement, and maintain technically adequate procedures to cover the restoration (i.e., filling and v
Region: III | Davis-Besse | 34911 | 12/31/2011 01/31/2012 | 2011005-05 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE INFORMATION ON VALVE INTERLOCKS RESULTED IN INADVERTENT OPERATION AND LOSS OF COMPONENT COOLING WATER SURGE TANK INVENTORY |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.2 | A finding of very low safety significance and an associated NCV of TS 5.4.1(a) were identified by the inspectors for the licensee's failure to establish, implement, and maintain technically adequate procedures and drawings to cover the restoration (i.e.,
Region: III | Davis-Besse | 34912 | 12/31/2011 01/31/2012 | 2011005-06 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE PROCEDURE RESULTED IN WATER INTRUSION INTO SAFETY-RELATED MOTOR CONTROL CENTER |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed finding of very low safety significance was identified for the licensee's failure to establish, implement, and maintain technically adequate procedures to permit the proper switching of feedwater sources for the station's auxiliary boiler,
Region: III | Davis-Besse | 34920 | 12/31/2011 01/31/2012 | 2011005-07 | NRC | NCV | Initiating Events | Green | INCOMPLETE SURFACE EXAMINATION OF THE REPLACEMENT REACTOR VESSEL CLOSURE HEAD |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000346 Davis-Besse |  | 71153 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," were identified by the inspectors for the licensee's failure to perform an adequate review o
Region: III | Davis-Besse | 34893 | 09/30/2011 10/26/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONTROL ECCS ROOM COOLER VALVE POSITION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified by the inspectors for the licensee's failure to control the configuration of the eme
Region: III | Davis-Besse | 34897 | 09/30/2011 10/26/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TAKE TIMELY CORECTIVE ACTIONS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Procedures, Instructions, and Drawings," were identified by the inspectors for the licensee's failure to correct deficiencies, deviations, and/or non
Region: III | Davis-Besse | 34898 | 09/30/2011 10/26/2011 | 2011004-04 | NRC | NCV | Initiating Events | Green | INADEQUATE WELD RECORDS FOR CRDM HOUSINGS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | NONE | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," were identified by the inspectors for the licensee's failure to establish adequate measure
Region: III | Davis-Besse | 34890 | 06/30/2011 07/21/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE TRAINING ON PROCEDURE REQUIREMENTS RESULTS IN AUXILIARY FEEDWATER INOPERABILITY |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the licensee's failure to ensure that activities affecting quality are properly accomplished in acco
Region: III | Davis-Besse | 34885 | 03/31/2011 04/19/2011 | 2011002-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO ADEQUATELY CONTROL CONSTRUCTION MATERIAL ADJACENT TO THE SWITCHYARD |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.01 | A self-revealed Green finding and associated NCV of Technical Specification (TS) 5.4.1 were identified for the licensee's failure to establish and implement procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifical
Region: III | Davis-Besse | 34886 | 03/31/2011 04/19/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | CONTAINMENT ECCS RECIRCULATION SUMP RELIABILITY DEGRADED DUE TO UNFASTENED DEBRIS GATE |  | H.4(a) Human Error Prevention | TE?: N | 05000346 Davis-Besse |  | 71111.2 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified by the inspectors for the failure by the licensee to maintain containment trash gate 3 cl
Region: III | Davis-Besse | 34887 | 03/31/2011 04/19/2011 | 2011002-03 | Self - Revealed | NCV | Barrier Integrity | Green | INADVERTENT REMOVAL OF CONTROL POWER TO CONTAINMENT AIR COOLER ISOLATION VALVE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealed Green finding and associated NCV of TS 3.6.3 were identified for an inadequate clearance that inadvertently removed control power to a containment isolation valve (CIV), SW1358, Containment Air Cooler (CAC) 3 Outlet Temperature Control Val
Region: III | Davis-Besse | 34876 | 09/30/2010 10/25/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | FAILURE TO ASSESS AND MANAGE RISK DURING CONSERVATIVE GRID OPERATIONS |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000346 Davis-Besse |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of 10 CFR 50.65(a)(4), for the failure to implement appropriate risk management actions when conservative grid operations were declared at
Region: III | Davis-Besse | 34881 | 09/09/2010 10/22/2010 | 2010008-01 | NRC | NCV | Initiating Events | Green | Unqualified PT Procedure For CRDM Nozzle Repair Welds | EA Case: 2010087 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 93812 | The team identified a Non-Cited Violation (NCV) of 10 CFR Part 50 Appendix B, Criterion IX for the licensee's failure to use a nondestructive examination procedure qualified in accordance with applicable Codes and Standards for detection of flaws in contr
Region: III | Davis-Besse | 34882 | 09/09/2010 10/22/2010 | 2010008-02 | NRC | NCV | Initiating Events | Green | Unqualified Weld Repair Applied For CRDM Nozzle No. 4 | EA Case: 2010087 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 93812 | The team identified a NCV of 10 CFR Part 50 Appendix B, Criterion IX for the licensee's failure to perform repair welding on control rod drive mechanism nozzle No. 4 using a qualified weld procedure. Specifically, the licensee failed to ensure that the we
Region: III | Davis-Besse | 34883 | 09/09/2010 10/22/2010 | 2010008-03 | NRC | NCV | Initiating Events | Green | Inadequate Procedure For Viewing of Remote PT on Nozzle No. 61 Repair Weld. | EA Case: 2010087 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 93812 | The team identified a NCV of 10 CFR Part 50 Appendix B, Criterion V for the licensee's failure to provide documented instructions appropriate to the circumstances for the remote visual examination of the final dye penetrant examination completed on repair
Region: III | Davis-Besse | 34875 | 06/30/2010 07/23/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to analyze SFRCS unexpectedly re energizing. This condition could cause an inappropriate SFRCS actuation. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000346 Davis-Besse |  | 71111.15 | The inspectors identified a Severity Level IV, non cited violation (NCV) of 10 CFR 50.72(b)(3)(ii)(B), and an associated Green finding, for the licensee's failure to recognize that, when in a shutdown condition, an 8 hour event notification to the NRC was
Region: III | Davis-Besse | 34869 | 03/31/2010 04/27/2010 | 2010002-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO MAINTAIN STATION BLACKOUT DIESEL GENERATOR OUTPUT CABLES IN AN ENVIRONMENT CONSISTENT WITH DESIGN |  | H.3(a) Work Planning | TE?: N | 05000346 Davis-Besse |  | 71111.06 | The inspectors identified a finding of very low safety significance for the licensee's failure to maintain normally energized medium voltage cables BPGD302C, C1, D, and D1 in an environment consistent with the cable design. The cables, which are output ca
Region: III | Davis-Besse | 34870 | 03/31/2010 04/27/2010 | 2010002-02 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE POST-MAINTENANCE TESTING OF ECCS ROOM COOLER |  | H.4(a) Human Error Prevention | TE?: N | 05000346 Davis-Besse |  | 71111.07A | A self-revealed finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified for the failure to adequately implement post-maintenance testing (PMT) when restoring emergency core coo
Region: III | Davis-Besse | 34872 | 03/31/2010 04/27/2010 | 2010002-04 | NRC | NCV | MISC | Green | UNATTENDED TRANSIENT COMBUSTIBLES WITHIN DRY FUEL STORAGE EXCLUSION AREA |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 71111.2 | The inspectors identified an NCV of 10 CFR 72.212, "Conditions of general license issued under 72.210," having very low safety significance for non-compliance with transient combustible material control procedures required for the Davis-Besse spent fuel d
Region: III | Davis-Besse | 34860 | 01/14/2010 02/19/2010 | 2009007-02 | NRC | NCV | Barrier Integrity | Green | Unqualified Bonding Agent Used for Containment Penetration Seal | EA Case: 2009332 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 7111121 | A finding of very low safety-significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure that the bonding material used to join bulk O-ring ends
Region: III | Davis-Besse | 34861 | 01/14/2010 02/19/2010 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Calculation of Induction Motor Load on AC Power System | EA Case: 2009332 | H.2(b) Personnel Training & Qualifications | TE?: N | 05000346 Davis-Besse |  | 7111121 | A finding of very low safety-significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to evaluate worst case motor loads for emergency diesel generator
Region: III | Davis-Besse | 34862 | 01/14/2010 02/19/2010 | 2009007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Take Interim Corrective Actions to Address Structures, Systems, and Components Unprotected from Tornados | EA Case: 2009332 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000346 Davis-Besse |  | 7111121 | A finding of very low safety-significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the failure to take interim corrective actions to address potential tornad
Region: III | Davis-Besse | 34863 | 01/14/2010 02/19/2010 | 2009007-05 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure for a Loss of Coolant Accident Outside Containment | EA Case: 2009332 |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | A finding of very low safety-significance and associated Non-Cited Violation of Technical Specification (TS) Section 5.4.1, "Procedures," was identified by the inspectors for the failure to provide adequate procedural direction to respond to a large loss
Region: III | Davis-Besse | 34271 | 12/31/2009 01/13/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | AFW PUMP 1 OPERABILITY WITH REMOVED INSULATION |  | H.3(b) Work Activity Coordination | TE?: N | 05000346 Davis-Besse |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the removal of insulation from auxiliary feedwater pump 1 turbine inlet piping
Region: III | Davis-Besse | 34275 | 12/31/2009 01/13/2010 | 2009005-03 | Self - Revealed | NCV | Barrier Integrity | Green | TWO REQUIRED TRAINS OF CONTAINMENT AIR COOLER FANS INOPERABLE |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A self revealed finding of very low safety significance and associated NCV of Technical Specification (TS) Limiting Condition for Operation 3.6.6, Condition E, was identified for having two required trains of containment air cooler (CAC) fans inoperable f
Region: III | Davis-Besse | 34276 | 12/31/2009 01/13/2010 | 2009005-04 | Self - Revealed | NCV | Mitigating Systems | Green | INCORRECT WIRING OF SERVICE WATER STRAINER STARTER 2 CONTACTOR CAUSING INOPERABILITY |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to correctly install auxiliary contacts for service water strai
Region: III | Davis-Besse | 34277 | 12/31/2009 01/13/2010 | 2009005-05 | NRC | FIN | Mitigating Systems | Green | FAILURE TO IMPLEMENT SPECIFIED AS-FOUND DIAGNOSTIC TESTING OF MOTOR-OPERATED VALVES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.22 | The inspectors identified a finding of very low safety significance for the licensee's failure to implement motor operated valve (MOV) as-found testing which the licensee specified as a to-be-implemented program improvement. No violation of NRC requiremen
Region: III | Davis-Besse | 34269 | 11/23/2009 12/28/2009 | 2009503-02 | NRC | AV | Emergency Preparedness | Green | Inadequate Procedures for State and local Notifications | EA Case: 2010013 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71153 | The inspector identified a finding and an associated NCV of 10 CFR 50.54(q) and 10 CFR 50.47 (b)(5) for the licensee's failure to maintain adequate emergency procedures to comply with emergency planning requirements to ensure timely notifications to State
Region: III | Davis-Besse | 34261 | 09/30/2009 10/21/2009 | 2009004-01 | Self - Revealed | FIN | Initiating Events | Green | LOSS OF THE SWITCHYARD J BUS DUE TO A FAULTED COUPLING CAPACITOR POTENTIAL DEVICE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71152 | A Green self-revealed finding was identified for the failure to implement a maintenance strategy to replace a capacitive coupled potential device (CCPD) in a timely manner. The CCPD had been installed beyond the 25 year life expectancy and failed catastro
Region: III | Davis-Besse | 34258 | 04/10/2009 05/21/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate molded case circuit breakers that exceed their qualified life. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000346 Davis-Besse |  | 71152B | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct a condition adverse to quality regarding the expired qualification of molded case ci
Region: III | Davis-Besse | 34252 | 03/31/2009 04/23/2009 | 2009002-01 | NRC | NCV | Initiating Events | Green | SWITCHYARD TRANSFORMERS RETURNED TO MAINTENANCE RULE A.2 STATUS WITHOUT APPROPRIATE CORRECTIVE ACTIONS COMPLETED |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.12 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50.65(a)(1), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," because the licensee did not establish appropriate corrective actions to address the poten
Region: III | Davis-Besse | 34253 | 03/31/2009 04/23/2009 | 2009002-02 | NRC | FIN | Initiating Events | Green | IMPROPER INSULATION REPLACEMENT CAUSES RAPID MAIN TURBINE DOWNPOWER DUE TO SMOLDERING OIL-SOAKED INSULATION |  |  | TE?: N | 05000346 Davis-Besse |  | 71152 | A finding of very low safety significance was self-revealed when improper installation of insulation surrounding the main turbine bearing number two oil deflector caused the main turbine to be taken off-line due to smoking insulation. An insulation blanke
Region: III | Davis-Besse | 34254 | 03/31/2009 04/23/2009 | 2009002-03 | NRC | NCV | MISC | Green | INADEQUATE MANAGEMENT OVERSIGHT TO ENSURE SPECIFIED CORRECTIVE ACTIONS WERE BEING ACCOMPLISHED |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," in that the licensee failed to have appropriate qualitative or quantitative measures to ensure that corrective acti
Region: III | Davis-Besse | 34249 | 09/30/2008 10/23/2008 | 2008004-01 | Licensee - Identified | URI | Mitigating Systems | Green | INOPERABILITY OF COMPONENT COOLING WATER TRAIN 1 VENTILATION |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.15 | Licensee identified NCV
Region: III | Davis-Besse | 34250 | 09/30/2008 10/23/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO SCHEDULE AND PERFORM PROCEDURALLY REQUIRED POST-MAINTENANCE TEST |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 71111.19 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for work planning and reviewing licensee personnel's failure to identify applicabl
Region: III | Davis-Besse | 34243 | 06/30/2008 07/21/2008 | 2008003-01 | NRC | NCV | Barrier Integrity | Green | CREVS TRAIN 2 INOPERABLE DUE TO LOSS OF REFRIGERANT CHARGE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71111.13 | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," when the licensee did not correct a condition adverse to quality, associated with a refrigerant leak on the regulating valve for Contr
Region: III | Davis-Besse | 34244 | 06/30/2008 07/21/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE MANAGEMENT OVERSIGHT DURING ORANGE RISK ACTIVITY |  | H.4(b) Procedural Compliance | TE?: N | 05000346 Davis-Besse |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4) for failure to implement a procedurally-required risk management activity for an orange risk activity. The licensee failed to provide required management oversight of a critical step in
Region: III | Davis-Besse | 34248 | 06/06/2008 06/18/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | This is a security Related Finding - see inspection report for details. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02
Region: III | Davis-Besse | 34240 | 03/31/2008 05/05/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW WELDING PROCEDURES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000346 Davis-Besse |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of two contractor welders to adhere to welding procedures for t
Region: III | Davis-Besse | 34241 | 03/31/2008 05/05/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | AIR VOID IN DECAY HEAT/LOW PRESSURE INJECTION SYSTEM DUE TO INADEQUATE VENTING AFTER MAINTENANCE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71152 | A self-revealing NCV of TS 4.5.2b was identified for failure to properly fill and vent a portion of decay heat/low pressure injection train 1 after maintenance which resulted in an approximate 15 cubic foot air void in the discharge piping of the train 1
Region: III | Davis-Besse | 34242 | 03/31/2008 05/05/2008 | 2008002-03 | NRC | FIN | Initiating Events | Green | UNEXPECTED REACTIVITY EXCURSION DUE TO UNIDENTIFIED VALVE POSITION DURING POST REPAIR AIR PRESSURE TESTING |  | H.3(b) Work Activity Coordination | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealing finding was identified for the failure of operators to maintain configuration control of valves during an air pressure test of a repair of a feedwater heater. Specifically, the operators left valve RD198 open during a pressure test of the
Region: III | Davis-Besse | 34233 | 12/31/2007 02/01/2008 | 2007005-01 | Self - Revealed | NCV | Mitigating Systems | Green | REDUCED FLOW THROUGH COMPONENT COOLING WATER 1 HEAT EXCHANGER BECAUSE OF IMPROPER VALVE OPENING LIMIT STOP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for failing to include appropriate quantitative or qualitative acceptance criteria for assuring the proper setting of the travel stops on v
Region: III | Davis-Besse | 34237 | 12/31/2007 02/01/2008 | 2007005-02 | Self - Revealed | FIN | Mitigating Systems | Green | FAILURE TO IMPLEMENT RELEVANT OPERATING EXPERIENCE RESULTS IN EMERGENCY DIESEL GENERATOR TEST FAILURE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000346 Davis-Besse |  | 71111.15 | A self-revealing finding of very low safety significance was identified for the licensee's failure to replace degraded emergency diesel generator (EDG) air start system hoses in accordance with operating experience (OE). Specifically, the licensee did not
Region: III | Davis-Besse | 34238 | 12/31/2007 02/01/2008 | 2007005-03 | NRC | NCV | Initiating Events | Green | INSPECTION PROCEDURE FOR POLAR CRANE OMITTED VISUAL INSPECTION OF STRUCTURAL COMPONENTS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings." Specifically, the licensee failed to provide a procedure to perform visual inspe
Region: III | Davis-Besse | 34239 | 12/31/2007 02/01/2008 | 2007005-04 | NRC | NCV | Initiating Events | Green | INTERNALS HANDLING ADAPTER DESIGN CALCULATION DID NOT CONSIDER MATERIAL FRACTURE TOUGHNESS REQUIREMENTS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to assure and verify that the design of Internals Handling Adapter
Region: III | Davis-Besse | 34223 | 11/30/2007 01/14/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Battery Voltage Drop and Sizing Design Calculation |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, the licensee's measures for verifying the adequacy of design with respect to the battery
Region: III | Davis-Besse | 34224 | 11/30/2007 01/14/2008 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Periodic Testing of 480V Starter Coils Not Implemented |  |  | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to assure and verify, following a design basis accident and deg
Region: III | Davis-Besse | 34225 | 11/30/2007 01/14/2008 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Consider Potential Air Entrainment to ECCS during Suction Transfer |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the design bases analyses for the transfer of the emergency core cooling system pum
Region: III | Davis-Besse | 34230 | 11/30/2007 01/14/2008 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Postulated Failure of AFW Suction Piping |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, the design bases analyses for the turbine driven auxiliary feedwater (AFW) pumps suction
Region: III | Davis-Besse | 34232 | 11/30/2007 01/14/2008 | 2007007-06 | NRC | NCV | Mitigating Systems | Green | Battery Connection Resistance Limit Specified in Technical Specifications Surveillance Requirements Insufficient to Ensure Battery Functionality |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000346 Davis-Besse |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to verify and ensure that the 125 Vdc safety related batteries
Region: III | Davis-Besse | 34221 | 09/30/2007 10/25/2007 | 2007004-01 | NRC | FIN | Initiating Events | Green | IMPROPER DESIGN OF A WELD PATCH FOR A CRACK IN CIRCULATING WATER PIPE |  | H.4(a) Human Error Prevention | TE?: N | 05000346 Davis-Besse |  | 71111.13 | The inspectors identified a finding for the licensee's failure to properly design a temporary repair for a through wall pipe crack found in the circulating water system. Specifically, the inspectors identified that a stress intensification factor, used in
Region: III | Davis-Besse | 34212 | 06/30/2007 07/20/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | IMPROPER IMPLEMENTATION OF INDEPENDENT VERIFICATION REQUIREMENTS IN PERFORMANCE OF INSTRUMENT AND CONTROL SURVEILLANCE TEST PROCEDURES FOR TS REQUIRED MITIGATION SYSTEMS |  | H.4(b) Procedural Compliance | TE?: N | 05000346 Davis-Besse |  | 71111.22 | A non-cited violation (NCV) of Technical Specification 6.8.1 was identified by the NRC regarding adherence to the procedural requirements for independent verifications required by safety-related surveillance procedures for instrumentation and control miti
Region: III | Davis-Besse | 34213 | 06/30/2007 07/20/2007 | 2007003-02 | NRC | NCV | Barrier Integrity | Green | LICENSED REACTOR THERMAL POWER EXCEEDED DURING NORMAL PLANT OPERATIONS |  | H.3(b) Work Activity Coordination | TE?: N | 05000346 Davis-Besse |  | 71153 | A self-revealing NCV of the plant operating license was identified during normal plant operations when on June 8, 2007, control room personnel observed that the plant's computer was not scanning reactor coolant letdown flow after work was performed to upg
Region: III | Davis-Besse | 34214 | 06/30/2007 07/20/2007 | 2007003-03 | NRC | NCV | Emergency Preparedness | Green | OUT OF SERVICE SEISMIC FORCE MONITORING EQUIPMENT AFFECTING EMERGENCY PLAN RESPONSE |  | H.3(a) Work Planning | TE?: N | 05000346 Davis-Besse |  | NONE | Inspectors identified an NCV of 10 CFR 50.54(q) and 50.47.b(4) for the failure to provide alternate event assessment methods while the seismic force monitor was out-of-service during the period of March 29 through April 10, 2007. The licensee failed to pr
Region: III | Davis-Besse | 34208 | 03/31/2007 05/03/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONDUCT SIMULATOR MALFUNCTION PERFORMANCE TESTING IN A SUFFICIENT MANNER TO DEMONSTRATE FIDELITY |  |  | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 55.46(d)(1), "Continued assurance of simulator fidelity," when the facility licensee failed to conduct a simulator "Generator Trip" malfunction performance test in a manner sufficient to ensu
Region: III | Davis-Besse | 34209 | 03/31/2007 05/03/2007 | 2007002-02 | NRC | NCV | MISC | Green | INADEQUATE CORRECTIVE ACTIONS (ISFSI) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000346 Davis-Besse |  | NONE | The inspectors identified a Severity Level IV Non-Cited Violation of the Certificate of Compliance, No. 1004, Condition 1.1.3, Quality Assurance and 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to correct a condition adverse
Region: III | Davis-Besse | 34201 | 12/31/2006 01/30/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | IMPROPER EVALUATION OF PLANT RISK |  | H.1(c) Communication of Decisions | TE?: N | 05000346 Davis-Besse |  | 71111.13 | A finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(4) was identified by the inspectors when the licensee failed to properly evaluate plant risk during station blackout diesel generator (SBODG) maintenance activities during
Region: III | Davis-Besse | 34202 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | FIN | Occupational Radiation Safety | Green | FAILURE TO ADEQUATELY IMPLEMENT ALARA RADIOLOGICAL DOSE CONTROLS |  | H.3(a) Work Planning | TE?: N | 05000346 Davis-Besse |  | 7112102 | A finding of very low safety significance was identified by the inspectors when licensee personnel failed to adequately implement radiological dose controls as a result of ineffective radiological/ALARA planning and controls during Refueling Outage 14 (RF
Region: III | Davis-Besse | 34205 | 11/17/2006 12/28/2006 | 2006007-01 | NRC | NCV | MISC | Green | FAILURE TO INITIATE A CONDITION REPORT FOR CONDITIONS ADVERSE TO QUALITY |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000346 Davis-Besse |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to generate condition reports or notifications to ide
Region: III | Davis-Besse | 34198 | 09/30/2006 10/18/2006 | 2006004-01 | NRC | FIN | Initiating Events | Green | LICENSEE ACTIONS INEFFECTIVE IN ENSURING MATERIAL AROUND SWITCHYARD AND UNDER POWER LINES PROPERLY STORED FOR HIGH WIND CONDITIONS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000346 Davis-Besse |  | 71111.01 | A finding of very low safety significance was identified by the inspectors for the failure to control loose materials located adjacent to the switchyard and under power lines from the switchyard to the station's large power transformers. This material cou
Region: III | Davis-Besse | 34193 | 06/30/2006 08/11/2006 | 2006003-01 | Self - Revealed | FIN | Mitigating Systems | Green | UNPLANNED HEATUP OF RCS DUE TO LOSS OF COMPONENT COOLING WATER TO IN-SERVICE DECAY HEAT COOLER DURING MODE 5 |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.22 | A finding of very low safety significance was self-revealed when, with the plant shut down for a planned refueling outage, an uncontrolled 10 degree Fahrenheit heatup of the reactor coolant system occurred over a period of approximately 1 hour. The licens
Region: III | Davis-Besse | 34196 | 06/30/2006 08/11/2006 | 2006003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | RADIATION WORKERS ENTERED POSTED HIGH RADIATION AREAS WITHOUT PROPER AUTHORIZATION |  |  | TE?: N | 05000346 Davis-Besse |  | 7112101 | A finding of very low safety significance and associated Non-Cited Violation of TS 6.12.1.b was self-revealed when, in three separate instances, radiation workers entered posted high radiation areas (HRAs) without appropriate authorization. Specifically,
Region: III | Davis-Besse | 34194 | 06/30/2006 08/11/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | INOPERABILITY OF EDG2 DUE TO UNTIMELY CORRECTIVE ACTION TO FIND AND REPAIR EXHAUST VALVE ROCKER ARM DAMAGE |  |  | TE?: N | 05000346 Davis-Besse |  | 71152 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors when the licensee failed to investigate and correct an abnormal noise associated
Region: III | Davis-Besse | 34189 | 06/30/2006 08/11/2006 | 2006003-04 | NRC | NCV | MISC | Green | FIRE PROTECTION, TRANSIENT COMBUSTIBLES ON THE DRY FUEL STORAGE PAD |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.05Q | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 72.212, "Conditions of general license issued under º72.210," was identified by the inspectors when the licensee failed to adequately control transient combustible m
Region: III | Davis-Besse | 34195 | 06/30/2006 08/11/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | STARTUP AND BUS TIE TRANSFORMER FAST TRANSFER CAPABILITY NOT REFLECTED IN SR 4.8.1.1.1.b |  |  | TE?: N | 05000346 Davis-Besse |  | 71152 | The inspectors identified a finding of very low safety significance and a Severity Level IV Non-Cited Violation when the licensee failed to adhere to the requirements of TS Section 6.17, "Technical Specifications Bases Control Program." By adding TS Bases
Region: III | Davis-Besse | 34186 | 03/31/2006 05/04/2006 | 2006002-01 | NRC | FIN | Barrier Integrity | Green | UNQUALIFIED EXAMINATION OF A PRESSURIZER SURGE LINE DM WELD |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.08P | The inspectors identified a finding having very low safety significance for failure to use qualified transducers during ultrasonic examination of a dissimilar metal weld on the pressurizer surge line. As a corrective action, the licensee obtained qualifie
Region: III | Davis-Besse | 34187 | 03/31/2006 05/04/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EXPAND CODE WELD EXAMINATION SCOPE |  |  | TE?: N | 05000346 Davis-Besse |  | 71111.08P | The inspectors identified a finding involving a Non-Cited Violation (NCV) violation of 10 CFR 50.55a(g)4 having very low safety significance for failure to expand the scope of weld examinations after identification of a rejectable flaw in the SG 1-2 main
Region: III | Davis-Besse | 34179 | 03/02/2006 03/17/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Flow Testing Acceptance Criteria for the Number 2 HPI and Number 2 LPI Pumps |  |  | TE?: N | 05000346 Davis-Besse |  | 7111102 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance. Specifically, the flow acceptance curves used for two safety-related pumps, the number 2 High Pressur
Region: III | Davis-Besse | 34181 | 03/02/2006 03/17/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Adverse Ampacity Effects of High Temperature Conditions in the Diesel Fire Pump Room |  |  | TE?: N | 05000346 Davis-Besse |  | 7111117B | The inspections identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance, where the licensee had not evaluated and updated the plant cable ampacity calculation to determine t
Region: III | Davis-Besse | 34185 | 03/02/2006 03/17/2006 | 2006006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Testing for Boron Precipitation Control Flow Instrumentation |  |  | TE?: N | 05000346 Davis-Besse |  | 7111117B | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," that was of very low safety significance. Specifically, after performing modifications to implement a new Boron Precipitation Control method for p
Region: III | Dresden | 126397 | 12/31/2019 01/29/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Failure to Identify and Control Hot Work |  | H.2 - Field Presence | TE?: N | 05000237 Dresden 2 |  | 71111.05Q | The inspectors identified a Green finding and associated non-cited violation (NCV) of Technical Specification 5.4.1.c, for the licensee’s failure to establish, implement, and maintain Fire Protection Program procedures which ensure fire prevention for hot
Region: III | Dresden | 126222 | 12/31/2019 01/29/2020 | 2019004-02 | NRC | NCV | Barrier Integrity | Green | Inaccurate and Incomplete Post Maintenance Testing Documentation for Containment Isolation Valve 2-1301-2 |  | P.1 - Identification | TE?: N | 05000237 Dresden 2 | Procedure Quality | 71111.19 | On November 12, 2019, the inspectors identified a Green finding and associated Non-cited Violation when the licensee failed to have acceptance criteria for testing containment isolation valves per Technical Specification Surveillance Requirement 3.6.1.3.5
Region: III | Dresden | 126306 | 12/31/2019 01/29/2020 | 2019004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to have Appropriate Installation Procedure for Relief Valve 2-4899-72 |  | H.9 - Training | TE?: N | 05000237 Dresden 2 |  | 71111.19 | On November 14, 2019, a self-revealed Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings," was identified when the licensee failed to have an appropriate procedure for the installation of t
Region: III | Dresden | 126419 | 12/31/2019 01/29/2020 | 2019004-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Survey for Work Conducted in a High Radiation Area |  | H.14 - Conservative Bias | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 | Program & Process | 71124.01 | An self-revealed finding of very low safety significance (i.e., Green) and an associated Non-Cited Violation (NCV) of 10 CFR 20.1501 (a)(1) “Surveys and Monitoring, General” was identified by inspectors when the licensee did not make surveys to assure com
Region: III | Dresden | 126420 | 12/31/2019 01/29/2020 | 2019004-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Positively Control a Door That Granted Access to a High Radiation Area |  | H.8 - Procedure Adherence | TE?: N | 05000237 Dresden 2 | Program & Process | 71124.01 | A self-revealed finding of very low safety significance (i.e. Green) and an associated Non-Cited Violation (NCV) of 10 CFR 20.1601 (a)(3) was identified by inspectors when the licensee failed to lock and demonstrate positive control over a door that is th
Region: III | Dresden | 125800 | 09/30/2019 11/01/2019 | 2019003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Instructions for Operationally Critical Work |  | H.2 - Field Presence | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 | Procedure Quality | 71152 | A self-revealed finding of very low safety significance was identified for the licensee’s failure to provide adequate work instructions for maintenance activities on multiple occasions in accordance with procedures MA-AA-716-010, Maintenance Planning, and
Region: III | Dresden | 24426 | 06/30/2019 10/31/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Maintenance Procedures for Assembling Unit 3 HPCI Room Cooler Fan |  | H.7 - Documentation | TE?: N | 05000249 Dresden 3 |  | 71111.15 | A self-revealing, Green non-cited violation (NCV) of Technical Specification (TS) 5.4, “Procedures,” was identified for the licensee’s failure to follow maintenance procedures DMP 5700-04, “LPCI and HPCI Room Cooler Maintenance,” and DEP 5700-04, “HPCI Ro
Region: III | Dresden | 124649 | 03/31/2019 05/08/2019 | 2019001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Safety-Related 4 kV Bus Degraded Voltage Relay |  | NPP | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 | Equipment Performance | 71152 | A self-revealed Green finding and associated non-cited violation (NCV) of Technical Specification 5.4.1(a) was identified for the licensee’s failure to develop a procedure for preventive maintenance schedules for the inspection or replacement of parts tha
Region: III | Dresden | 124353 | 03/31/2019 05/08/2019 | 2019001-02 | NRC | NCV | Initiating Events | Green | Loss of Unit 2 Reserve Auxillary Transformer TR22 |  | H.5 - Work Management | TE?: N | 05000237 Dresden 2 | Human Performance | 71153 | The inspectors identified a Green finding and associated NCV of 10 CFR 50.65 a.4 for the failure to adequately assess and manage the increase in risk that resulted from the maintenance activities performed on the Unit 2 Reserve Auxiliary Transformer (RAT)
Region: III | Dresden | 23958 | 03/23/2018 05/07/2018 | 2018012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Thermal Overload Relays are Sized Properly for Throttling Motor |  | NPP | TE?: N | 05000249 Dresden 3 |  | 71111.21M | The team identified a finding having very-low significance and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control." Specifically, Dresden had not verified that thermal over
Region: III | Dresden | 22623 | 12/31/2017 01/22/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure, Results in Non-Functional Fire Door |  | H.9 - Training | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05Q | The inspectors identified a finding of very-low safety significance and associated NCV of Technical Specification 5.4.1.c for the licensee’s failure to implement the established Fire Protection Program procedures which ensure Fire Barrier Integrity. S
Region: III | Dresden | 9007 | 06/30/2017 07/19/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control in the Unit 2 Containment Pressure Suppression System |  | P.3 Resolution | TE?: N | 05000237 Dresden 2 |  | 71111.15 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 5.4.1, "Procedures", was self-revealed on May 26, 2017, for the licensee's failure to maintain configuration control in the Unit 2 containment pre
Region: III | Dresden | 9005 | 03/31/2017 04/20/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with EDG Single Largest Load Rejection Surveillance Testing |  | H.7 Documentation | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | The NRC identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to
Region: III | Dresden | 9006 | 03/31/2017 04/20/2017 | 2017001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Secondary Containment Inoperability Due to Lapse in Procedure Use and Adherence |  | P.1 Identification | TE?: N | 05000237 Dresden 2 |  | 71153 | A self-revealed finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.4.1, "Procedures," occurred on November 8, 2016, due to the licensee's failure to follow procedures designed to ensure secondary contain
Region: III | Dresden | 8998 | 03/02/2017 03/30/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Pre-Fire Plans |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very-low safety significance and associated NCV of license conditions 2.E and 3.G for Units 2 and 3, respectively for the licensee's failure to include the correct information in pre-fire plans. Specifically, the lic
Region: III | Dresden | 8999 | 03/02/2017 03/30/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Steps to Ensure Proper Valve Rotation for Cold Shutdown Repair |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very-low safety significance and associated NCV of Technical Specification 5.4.1.c for the licensee's failure to have appropriate written procedures covering the Fire Protection Program for cold shutdown repairs. Spe
Region: III | Dresden | 9004 | 12/31/2016 01/30/2017 | 2016004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply With Radiation Work Permit Requirements Resulting In Unplanned Dose Rate Alarms |  | H.11 Challenge the Unknown | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71124.01 | A finding of very-low safety significance, and an associated Non-Cited Violation (NCV) of Technical Specification 5.4.1 was self-revealed when workers violated a radiation work permit (RWP) by entering an area that was outside of the scope of the original
Region: III | Dresden | 9000 | 09/30/2016 10/24/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assess Scope Changes to Corrective Maintenance Activities Affecting Safety-Related Structures, Systems, and Components (SSC) |  | P.2 Evaluation | TE?: N | 05000237 Dresden 2 |  | 71153 | A finding of very low safety significance and associated NCV of TS 5.4.1.a, "Procedures," was self-revealed for the licensee's failure to maintain maintenance procedures appropriate for the circumstances that could affect performance of safety related equ
Region: III | Dresden | 8997 | 07/01/2016 08/04/2016 | 2016009-01 | NRC | FIN | Mitigating Systems | Green | Main Steam Acoustic Safety/Relief Valve Monitoring Channel Calibration Not Performed |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.21N | The inspectors identified a finding of very-low safety significance for the failure to perform a 24-month channel calibration of the Regulatory Guide 1.97 safety/relief valve acoustic monitoring system in accordance with the Technical Requirements Manual.
Region: III | Dresden | 8996 | 06/30/2016 07/25/2016 | 2016002-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement and Maintain Written Procedures Regarding Breathing Air Quality Testing |  | H.1 Resources | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71124.03 | A finding of very-low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 20.1703, was an NRC-identified finding for failure to implement and maintain written procedures regarding breathing air quality that
Region: III | Dresden | 8990 | 03/31/2016 04/29/2016 | 2016001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the 2/3 Emergency Diesel Generator |  | H.9 Training | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," was self-revealed associated with the licensee's failure to assure that the applicable des
Region: III | Dresden | 8983 | 12/31/2015 01/19/2016 | 2015004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Design Control of Secondary Containment Interlock Doors |  | H.14 Conservative Bias | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self-revealed on September 4, 2015, when the integrity of the Secondary Containment for Units 2 and 3 was not maint
Region: III | Dresden | 8980 | 09/30/2015 10/22/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Available Net Positive Suction Head for the Diesel Generator Cooling Water Pumps Following a Dam Failure |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | The inspectors identified a finding of very low safety significance, and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the diesel generator
Region: III | Dresden | 8981 | 09/30/2015 10/22/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Ultimate Heat Sink Surveys in Accordance With Quality Assurance Program |  | H.6 Design Margins | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | The inspectors identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to perform surveys of the UHS in accordance with the Quality Assurance Program. Specifi
Region: III | Dresden | 8982 | 09/30/2015 10/22/2015 | 2015003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Post Protected Pathway Signs |  | H.5 Work Management | TE?: N | 05000249 Dresden 3 |  | 71111.13 | The inspectors identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to implement all necessary prescribed risk manageme
Region: III | Dresden | 8975 | 06/30/2015 08/07/2015 | 2015002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Meet Technical Specification Surveillance Requirements Due to Foreign Material Left in the Unit 2 EDG Starting Circuit (1R13) |  | H.7 Documentation | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.13 | A finding of very-low safety significance (Green) was self-revealed on April 21, 2015 while performing TS Surveillance DOS 6600-12, "Diesel Generator Tests: Endurance and Margin/Full Load Rejection/ECCS [Emergency Core Cooling System]/Hot Restart," in su
Region: III | Dresden | 8976 | 06/30/2015 08/07/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Manipulation of a Test Switch at ESF Bus 23-1 During Surveillance Testing Results in the Inoperability of the 2/3 EDG to Unit 2 |  | H.2 Field Presence | TE?: N | 05000237 Dresden 2 |  | 71111.22 | A finding of very low safety significance (Green), and an associated NCV of TS 5.4.1, "Procedures," was self-revealed on May 19, 2015, when the 2/3 EDG was made inoperable to Unit 2 due to the incorrect manipulation of a test switch by operations personne
Region: III | Dresden | 8977 | 06/30/2015 08/07/2015 | 2015002-03 | Self - Revealed | FIN | Initiating Events | Green | Reactor Scram Due to Feedwater Level Control System Failure with a Reactor Recirculation Pump Runback |  | P.2 Evaluation | TE?: N | 05000237 Dresden 2 |  | 71153 | A finding of very-low safety significance (Green) was self-revealed on January 13, 2015, and again on February 6, 2015, when a loss of power to the Unit 2 feedwater level control (FWLC) system resulted in a reactor scram. The loss in power to the Unit 2
Region: III | Dresden | 8969 | 05/29/2015 07/01/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Procedure Revisions Resulted in Isolation Condenser Unable to Meet Design Basis |  | H.4 Teamwork | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.17T | The inspectors identified a finding of very-low safety significance, and an associated Non-Cited Violation (NCV) of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure tha
Region: III | Dresden | 8974 | 05/29/2015 07/01/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | EDG Usable Fuel Calculations Failed to Consider Appropriate EDG Frequency Variations |  | P.1 Identification | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.17T | The inspectors identified a finding of very-low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to account for increased fuel oil consumption during the development of the Emergenc
Region: III | Dresden | 8968 | 03/31/2015 04/27/2015 | 2015001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | 10 CFR 20.1701; Failure to Implement Effective Radiological Engineering Controls |  | H.5 Work Management | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71124.03 | A finding of very-low safety significance, and an associated NCV of 10 CFR 20.1701 was self-revealed during work activities associated with the failure to effectively implement planned radiological engineering controls during reactor head reassembly that
Region: III | Dresden | 8964 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Unit 3A Low Pressure Coolant Injection (LPCI) Heat Exchanger Supports Returned to Service with Unacceptable Indications |  | H.9 Training | TE?: N | 05000249 Dresden 3 |  | 71111.08G | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR 50.55a(g)(4) was identified by the inspectors for the licensee's failure to maintain American Society of Mechanical Engineers (ASME) Code Class 2 components in ac
Region: III | Dresden | 8966 | 12/31/2014 01/29/2015 | 2014005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Configuration Control in the Unit 3 Containment Pressure Suppression System |  | H.14 Conservative Bias | TE?: N | 05000249 Dresden 3 |  | 71111.2 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 5.4.1, "Procedures," was self-revealed on November 19, 2014, for the licensee's failure to maintain configuration control in the Unit 3 containmen
Region: III | Dresden | 8957 | 09/30/2014 10/23/2014 | 2014004-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform 10 CFR 50.59 Evaluation for Procedure DOP 1300-02 |  | H.6 Design Margins | TE?: Y SL-IV-NCVIV | 05000237 Dresden 2 |  | 71111.15 | The inspectors identified a NCV of 10 CFR 50.59, "Changes, Tests and Experiments," when, on February 10, 2011, the licensee failed to complete a 10 CFR 50.59 evaluation when they revised procedure DOP 1300-02 to change the position of Motor Operated Valve
Region: III | Dresden | 8963 | 09/30/2014 10/23/2014 | 2014004-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71114.05 | The NRC identified a NCV of 10 CFR 50.54(q)(2) associated with 10 CFR 50.47(b)(10) and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the Dresden Nuclear Power Station Emergency Plan as a result of failing to provid
Region: III | Dresden | 8956 | 06/30/2014 07/28/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Appropriate Corrective Action When a Maintenance Rule Performance Goal for the Standby Coolant System Was Not Met |  | H.8 Procedure Adherence | TE?: N | 05000237 Dresden 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and non-cited violation of 10 CFR 50.65(a)(1), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to take corrective action
Region: III | Dresden | 8952 | 05/23/2014 06/16/2014 | 2014008-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Applicability Reviews of Configuration Changes for De-Energizing Safety-Related Valves |  | H.12 Avoid Complacency | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) related to inadequate applicability reviews of operational configuration changes that were implemented as a result of the licensee's Multiple Spurious Operation (MSO) evaluations.
Region: III | Dresden | 8953 | 05/23/2014 06/16/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Seismically Secure Nitrogen Bottles |  | H.5 Work Management | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of Technical Specifications (TS) Section 5.4.1.a, for the licensee's failure to seismically restrain nitrogen bottles located near safety-relate
Region: III | Dresden | 8947 | 03/31/2014 04/17/2014 | 2014002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Secondary Containment Integrity During Outage Demobilization Activities |  | H.11 Challenge the Unknown | TE?: N | 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 5.4.1, "Procedures", was self-revealed on November 28, 2013, when the integrity of the secondary containment for Unit 3 was not maintained when pl
Region: III | Dresden | 8950 | 03/15/2014 05/02/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Incorporate GE Operating Experience into Vendor Manual |  | H.12 Avoid Complacency | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure that operating experience pro
Region: III | Dresden | 8942 | 12/31/2013 11/01/2013 | 2013004-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Update the UFSAR for Reactor Water Cleanup Design Changes |  |  | TE?: Y SL-IV-NCVIV | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | A Severity Level IV NCV of 10 CFR 50.71(e), "Periodic Update of the Final Safety Analysis Report" (USFAR) and an accompanying Green finding were identified by the inspectors for the licensee's failure to update the Updated Final Safety Analysis Report (UF
Region: III | Dresden | 8946 | 12/31/2013 01/23/2014 | 2013005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Lo-Lo Reactor Water Level Indication Received During Maintenance Resulting in Unavailability of the 2/3 Emergency Diesel Generator to Unit 3 |  | H.5 Work Management | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.2 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 5.4.1, "Procedures", was self-revealed on November 17, 2013, when the 2/3 Emergency Diesel Generator (EDG) was inoperable to Unit 3 with an Emerge
Region: III | Dresden | 8925 | 05/30/2013 06/27/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Adequate Voltage Not Assured for Emergency Diesel Generator Air Start Solenoid Valve |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure and verify adequate voltage was available at the air start solenoid associated
Region: III | Dresden | 8932 | 05/30/2013 06/27/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative Sizing Calculation for Target Rock Safety Relief Valve Air Accumulators |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly calculate the minimum air volume and pressure required to actuate the Targe
Region: III | Dresden | 8933 | 05/30/2013 06/27/2013 | 2013007-03 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure Functionality of High Pressure Coolant Injection Steam Suply Valve During an Anticipated Transient Without Scram |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding of very low safety significance concerning motor-operated valve differential pressure calculation with respect to Dresden's anticipated transient without scram (ATWS) analysis. Specifically, the inspectors identified th
Region: III | Dresden | 8934 | 05/30/2013 06/27/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Isolation Condenser Would Perform Its Safety-Related Function Under Design Conditions |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the isolation condenser would be capable of performing its safety function und
Region: III | Dresden | 8923 | 03/31/2013 05/07/2013 | 2013002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Include Adequate Acceptance Criteria in a Surveillance Test |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.01 | The inspectors identified a Finding having very low safety significance for the failure to include acceptance criteria in a surveillance test for equipment that is the sole source of make-up water to the isolation condenser and spent fuel pool for both un
Region: III | Dresden | 8915 | 12/31/2012 01/24/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure To Follow Cold Weather Initiating Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.01 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification 5.4.1.a for the failure to follow an abnormal operating procedure. Specifically, abnormal operating procedure (DOA) 5700-01, "Loss of Heating
Region: III | Dresden | 8916 | 12/31/2012 01/24/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Post Protected Pathway Signs for a Red Risk Path System |  | H.4(b) Procedural Compliance | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(4), Maintenance Rule, was identified by the inspectors for the licensee's failure to implement all necessary prescribed risk management actions during a Unit 3 250 Vdc battery
Region: III | Dresden | 8908 | 06/30/2012 07/25/2012 | 2012003-01 | NRC | FIN | Mitigating Systems | Green | Inspectors Found Unit 3 Containment Cooling Service Water (CCSW) Vault Flood Door Open and Unattended |  |  | TE?: N | 05000249 Dresden 3 |  | 71111.06 | A finding of very low safety significance was identified by the inspectors for leaving the containment cooling service water (CCSW) vault door open and unattended. The licensee immediately closed the door, posted the door as difficult to close, and lubric
Region: III | Dresden | 8909 | 06/30/2012 07/25/2012 | 2012003-02 | Self - Revealed | FIN | Initiating Events | Green | Loss of Lift Station due to Human Performance Error |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance was self-revealed when a human performance error resulted in the loss of the Bus 41 which caused a trip of all circulating water hot canal lift pumps. The licensee performed a rapid down power on both Units 2 and
Region: III | Dresden | 8494 | 04/20/2012 05/23/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Remove Diesel Fire Pump Battery Terminal Corrosion |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specifications for the licensee's failure to adequately implement the diesel fire pump (DFP) battery surveillance procedure. Specifically, the lice
Region: III | Dresden | 8473 | 03/31/2012 05/08/2012 | 2012002-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Ensure the Effectiveness of Packages as required by Department of Transportation (DOT) Regulations |  | P.2(b) Implementing Operating Experience | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | NONE | A finding of very low safety significance was self-revealed following the licensee's failure to appropriately package and transport radioactive material. This finding also resulted in two associated NCVs of 10 CFR 61.56(a)(3) and 10 CFR 71.5(a). The licen
Region: III | Dresden | 8474 | 03/31/2012 05/08/2012 | 2012002-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Ensure Packages Containing Solid Waste Contain as Little Free Standing and Noncorrosive Liquid as Reasonably Achievable |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | NONE | A finding of very low safety significance was self-revealed following the licensee's failure to appropriately package and transport radioactive material. This finding also resulted in two associated Non-Citied Violations (NCVs) of 10 CFR Part 61.56(a)(3)
Region: III | Dresden | 8484 | 03/31/2012 05/08/2012 | 2012002-07 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Work instruction Leads to Failure of Secondary Containment Interlock |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) Section 5.4.1 was self-revealed because the work instructions associated with WO 1450006-01, "D2 SA PM 517 RB/TB INTLK DOOR (2 5850-52) ELECTRICAL
Region: III | Dresden | 8487 | 03/31/2012 05/03/2012 | 2012010-01 | NRC | NCV | Mitigating Systems | Green | Failure of the 125 Vdc Generator Rectifier Set |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated NCV of license condition 2.C.18.b.5 of licensee DPR-19 and 3.AA.b.5 of license DPR-25 when the 125 Vdc Generator Rectifier Set failed an annual surveillance test. Although
Region: III | Dresden | 8467 | 03/27/2012 04/23/2012 | 2012008-01 | NRC | NCV | Initiating Events | Green | Flammable Hydrogen Gas Bottles Installed in the Reactor Building. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.17T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to check the adequacy of design for flammable hydrogen gas bottles in
Region: III | Dresden | 8468 | 03/27/2012 04/23/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Adequate Post Installation and Maintenance Inspections on Standby Liquid Control System Components. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.17T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion X, "Inspection," for the licensee's failure to perform adequate post-installation and post-maintenance inspections on s
Region: III | Dresden | 8462 | 12/31/2011 01/25/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Bus 23 Pot Fuse Drawer Resulting in the Inoperability of the Control Room Emergency Ventilation Air Condition System |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71153 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified on October 24, 2011, when two electrical maintenance technicians performing a c
Region: III | Dresden | 8465 | 12/31/2011 01/25/2012 | 2011005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Control Rod Blade Disengages from Lifting Tool and Drops Over Reactor Core into an Empty Cell |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 |  | 71153 | A finding of very low safety significance and associated NCV of Technical Specification 5.4.1 was self-revealed when a control rod blade (CRB) disengaged from the lifting tool and gravity fell into an empty cell in the reactor core. The immediate actions
Region: III | Dresden | 8453 | 10/17/2011 10/27/2011 | 2011008-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Transient Combustible Program |  | H.1(c) Communication of Decisions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specifications Section 5.4.1.c for the failure to control transient combustible materials in accordance with fire protection program requirements. Specific
Region: III | Dresden | 8454 | 10/17/2011 10/27/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Diesel Fire Pump Battery Terminal Corrosion |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specifications for the licensee's failure to implement the diesel fire pump battery surveillance procedure. Specifically, the licensee failed to id
Region: III | Dresden | 8455 | 10/17/2011 10/27/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Operators Required for Safe Shutdown Were On-Site |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix R, Section III.L., for the licensee's failure to ensure that operators required for safe shutdown were on-site at all times. Specifi
Region: III | Dresden | 8461 | 10/17/2011 10/27/2011 | 2011008-06 | NRC | FIN | Mitigating Systems | Green | Failure to Obtain NRC Approval for Change Adsverse to Safe Shutdown |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) for the failure to obtain NRC approval prior to making a change, which was adverse to safe shutdown. Specifically, the licensee made a change to Administrative Technical Requireme
Region: III | Dresden | 8444 | 09/30/2011 11/07/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Improperly Classifying the Unit 2 and 3 Containment Cooling Service Water (CCSW) Pump Vault Drain Check Valves as Non Safety Related |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.06 | A finding of very low safety significance and associated non cited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," was identified by the inspectors for the reclassification of the Unit 2 and 3 containment cooling service wat
Region: III | Dresden | 8445 | 09/30/2011 11/07/2011 | 2011004-03 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Relay Preventative Maintenance |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.18 | A finding of very low safety significance was self revealed for the failure to follow the preventive maintenance program which resulted in the failure of the Unit 3 303241 52A GE HFA relay. This relay gives a start permissive signal for all three reactor
Region: III | Dresden | 8451 | 09/30/2011 11/07/2011 | 2011004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preventive Maintenance Procedure For Valve 2 2301 29 |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.19 | A finding of very low safety significance and associated non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to have a procedure adequate to ensure quality during the
Region: III | Dresden | 8430 | 06/30/2011 08/04/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Instructions for the Inspection of Safety-related Portions of the Intake Structure |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for licensee's failure to establish adequate instruct
Region: III | Dresden | 8432 | 06/30/2011 08/04/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for Testing Equipment Relied Upon to Mitigate the Consequences of a Lock and Dam Failure |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the inspectors for the licensee's failure to establish adequate acceptance criteria for tes
Region: III | Dresden | 8433 | 06/30/2011 08/04/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Instructions for Coping with a Dresden Lock and Dam Failure |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the inspectors for the licensee's failure to establish adequate instructions for coping wit
Region: III | Dresden | 8434 | 06/30/2011 08/04/2011 | 2011003-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Scoping of a Non-Safety-related Pump Into Maintenance Rule |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | A finding of very low safety significance and associated NCV of 10 CFR Part 50.65(b)(2)(ii), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified by the inspectors for the licensee's failure to adequately
Region: III | Dresden | 8436 | 06/30/2011 08/04/2011 | 2011003-07 | Self - Revealed | NCV | Initiating Events | Green | Change In Unit 2 Reactor Water Level Due To A Failure To Follow Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1 was self-revealed for a Nuclear Station Operator (NSO) failing to follow step G.14.a of procedure DOP 0600-06, "Feedwater Regulating Valve (FWRV)
Region: III | Dresden | 8437 | 06/30/2011 08/04/2011 | 2011003-08 | NRC | NCV | Mitigating Systems | Green | Failure to Place One Channel of the Rod Block Monitor Into Trip |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000249 Dresden 3 |  | 71153 | The inspectors identified a finding of very low safety significance and NCV of Technical Specification 3.2.1.1, Required Action B.1, for the licensee's failure to place one Rod Block Monitor (RBM) channel on Unit 3 in trip within 1 hour as required upon m
Region: III | Dresden | 8439 | 06/23/2011 07/21/2011 | 2010502-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: III | Dresden | 8423 | 03/31/2011 05/09/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Control Room Ventilation Smoke Detector Failure to Perform Post-Maintenance Testing |  | H.3(a) Work Planning | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.04Q | The inspectors identified a finding of very low safety significance and associated NCV of the Dresden Nuclear Power Station Renewed Facility Operating License for the licensee's failure to perform adequate post-maintenance testing on a smoke detector in t
Region: III | Dresden | 8425 | 03/31/2011 05/09/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Surveillance Testing on East Turbine Building Vent HVAC Smoke Detectors |  | H.3(a) Work Planning | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.04Q | The inspectors identified a non-cited violation (NCV) of the Dresden Nuclear Power Station Renewed Facility Operating License having very low safety significance for the licensee's failure to perform adequate testing on four smoke detectors in the east tu
Region: III | Dresden | 8426 | 03/31/2011 05/09/2011 | 2011002-05 | NRC | NCV | Mitigating Systems | Green | Undocumented Technical Basis for change to EOP ATWS Mitigation Strategy |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.11Q | The inspectors identified a finding of very low safety significance and associated NCV of Dresden Technical Specification 5.4.1, for failing to maintain adequate procedures for implementing the emergency operating procedures (EOP). Specifically, the licen
Region: III | Dresden | 8427 | 03/31/2011 05/09/2011 | 2011002-06 | NRC | NCV | Barrier Integrity | Green | Failure to Follow TS 5.5.2 Implementing Procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification (TS) Section 5.5.2, "Primary Coolant Sources Outside Containment," because the licensee was not following procedures which implemented TS 5.5.2. The licensee's corrective actions i
Region: III | Dresden | 8428 | 03/31/2011 05/09/2011 | 2011002-07 | Self - Revealed | FIN | Initiating Events | Green | Dresden 3B Circulating Water Pump Bearing Failure due to Low Oil Level |  | H.4(a) Human Error Prevention | TE?: N | 05000249 Dresden 3 |  | 71153 | A self-revealed finding was identified for the bypass of a circulating water pump lower bearing high temperature alarm without first verifying the instrument reading. Prior to bypassing the alarm, the licensee did not verify if the indication was valid. N
Region: III | Dresden | 8413 | 12/31/2010 02/01/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Robust Indication of Adequate Oil Level in High Pressure Coolant Injection Booster Pump Sight Glasses |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.04Q | The inspectors identified a Non-Cited Violation of Technical Specification 5.4.1 for the licensee's failure to implement the section of the high pressure coolant injection (HPCI) booster pump maintenance procedure that prescribes how to robustly mark the
Region: III | Dresden | 8418 | 12/31/2010 02/01/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Magnetic Particle Examination on the 3/2/1501-20/20-10 U3 LPCI Support in Accordance with Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.08G | A finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to accomplish activities affe
Region: III | Dresden | 8412 | 11/19/2010 12/22/2010 | 2010010-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform an Ultrasound Thickness Measurement of the Drywell liner in accordance with procedures (4OA5.1.b(1)) |  |  | TE?: N | 05000249 Dresden 3 |  | 71003 | A finding of very low safety-significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to accomplish activities affecting quality in accor
Region: III | Dresden | 8410 | 09/30/2010 11/04/2010 | 2010004-03 | NRC | NCV | Barrier Integrity | Green | Installation of Nonconforming Material into a Safety Related System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components" for the installation of a commercially dedicated part for use in a
Region: III | Dresden | 8411 | 09/30/2010 11/04/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Test Procedures to Assess the As-Found Trip Setpoint for Pressure Switches that Satisfy Technical Specification Functions |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to assure that conditions adverse to quality associated with pre-condit
Region: III | Dresden | 8390 | 06/30/2010 07/30/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | LPCI Room Heat up Calculation Deficiencies |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07A | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) related to whether the equipment in the low pressure coolant injection (LPCI) corner rooms would remain within envi
Region: III | Dresden | 8392 | 06/30/2010 07/30/2010 | 2010003-04 | NRC | FIN | Mitigating Systems | Green | Failure to Monitor Unit 3 Drywell Temperature |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | A finding of very low safety significance was identified by the inspectors on May 3, 2010, for the failure to monitor Unit 3 (U3) drywell temperature per commitments made to the NRC within LER 88 22, Supplement 2 to ensure that equipment in the drywell wa
Region: III | Dresden | 8393 | 06/30/2010 07/30/2010 | 2010003-05 | NRC | NCV | Initiating Events | Green | Failure to Provide An Adequate Procedure for Several Instrument Maintenance Surveillance Tests |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.22 | The inspectors identified a NCV of Technical Specification (TS) 5.4.1 for the failure to provide an adequate procedure for the verification of correct installation and restoration of equipment during an instrument maintenance surveillance test in May 2010
Region: III | Dresden | 8399 | 06/30/2010 07/30/2010 | 2010003-06 | Self - Revealed | FIN | Initiating Events | Green | Failure To Perform An Adequate Inspection of Circulating Water Valve 3 4402 C |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | On January 22, 2010, a finding of very low safety significance was self revealed for failure to perform an adequate inspection of the grease condition of the 3 4402 C valve actuator HBC gear box, which was contrary to the requirements of MA AA 723 301,"Pe
Region: III | Dresden | 8400 | 06/30/2010 07/30/2010 | 2010003-07 | Self - Revealed | NCV | Mitigating Systems | Green | 2/3 Emergency Diesel Generator (EDG) Overvoltage during Division I Undervoltage |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance (Green) and associated NCV of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion XI, "Test Control," was self revealed on November 16, 2009, for the failure to perform adequate post modifi
Region: III | Dresden | 8384 | 05/21/2010 07/02/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Heat Exchanger Inspection Procedures Appropriate for the Circumstances |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for the failure to establish inspection procedures that were appropriate for th
Region: III | Dresden | 8385 | 05/21/2010 07/02/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Improper Reclassification of LPCI Pump Mechanical Seals |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," for improperly classifying Low Pressure Coolant Injection (LPCI) pump mechanical seals as non-safety-related. The licensee subsequently concluded th
Region: III | Dresden | 8386 | 05/21/2010 07/02/2010 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Testing to Confirm Acceptable Fast Bus Transfer Time |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, ATest Control,@ for the failure to have an adequate post-maintenance test for circuit breakers to confirm fast bus transfer capability. Specifically, the licensee failed to ensu
Region: III | Dresden | 8377 | 03/31/2010 05/10/2010 | 2010002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Technical Specification 5.5.4 Implementing Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.22 | -The inspectors identified a finding of very low safety significance and associated Non Cited Violation of Technical Specification 5.5.4 for the licensee failing to follow Step I.2.a and b of Procedure DOS 1500 08, "Discharge of Containment Cooling Servic
Region: III | Dresden | 8378 | 03/31/2010 05/10/2010 | 2010002-03 | NRC | FIN | Emergency Preparedness | Green | Failure to Meet Regulatory Commitment to Maintain Contingency Plans for Post-Accident Sampling |  | H.2(d) Facilities & Equipment | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71124.05 | The inspectors identified a finding of very low safety significance for the failure to meet a regulatory commitment to maintain a contingency plan for obtaining highly radioactive samples of reactor coolant, the suppression pool, and drywell atmosphere fo
Region: III | Dresden | 8379 | 03/31/2010 05/10/2010 | 2010002-04 | NRC | NCV | Mitigating Systems | Green | Significance of Potentially Submerged Safety and Non safety-related Low Voltage Power and Control Power Cables |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | The inspectors identified a finding of very low safety significance with an associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, licensee personnel failed to maintain safety related cables in undergr
Region: III | Dresden | 8383 | 03/31/2010 05/10/2010 | 2010002-05 | Self - Revealed | FIN | Initiating Events | Green | Electro Hydraulic Control (EHC) Fluid Leaking From Stop Valve 3-5699-MSV4-FA Resulting in Forced Outage D3F49 |  | P.2(b) Implementing Operating Experience | TE?: N | 05000249 Dresden 3 |  | 71153 | The failure of the Unit 3 Main Turbine Stop Valve (MSV) # 4 fast acting solenoid valve on November 6, 2009, resulted in a self revealed finding of very low safety significance. The licensee failed to use the correct o rings and bolts when replacing the Un
Region: III | Dresden | 8402 | 03/31/2010 05/10/2010 | 2010002-06 | NRC | NCV | MISC | Green | Failure to Record the Identity of Personnel Performing Post-Maintenance Tests - performance deficiency portion. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.18 | A finding of very low safety significance (green0 and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," was identified by the inspectors for the licensee's failure to record the identity of various personnel who pe
Region: III | Dresden | 8345 | 12/31/2009 02/10/2010 | 2009005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Operating Personnel Incorrectly Placed Clearance Tags |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71111.04Q | A finding of very low safety significance and associated NCV of Technical Specification 5.4.1 was self-revealed for the failure to meet the requirements of Clearance Order (CO) 69631 by removing shorting links instead of fuses as required by the CO on Nov
Region: III | Dresden | 8346 | 12/31/2009 02/10/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | NRC Inspector-Identified Control Room Alarm Isolation Valve Out-of-Position |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification 5.4.1 for the licensee failing to follow Dresden procedure DOP 2-1500-M1, "LPCI System Mechanical Checklist," Revision 39. On September 24, 2
Region: III | Dresden | 8347 | 12/31/2009 02/10/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Preconditioning the Unit 2 Emergency Diesel Generator Prior to Performing TS Surveillance Requirements |  | H.3(b) Work Activity Coordination | TE?: N | 05000237 Dresden 2 |  | 71111.19 | The inspectors identified a finding of very low significance and associated NCV of 10 CFR 50 Appendix B, Criterion XI, "Test Control", because the licensee unacceptably preconditioned the Unit 2 Emergency Diesel Generator (EDG) prior to performing Technic
Region: III | Dresden | 8355 | 12/31/2009 02/10/2010 | 2009005-05 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow the master Refueling Procedure During Movement of Fuel Assembly JLU569 |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71111.2 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, was self-revealed for the failure to properly move a fuel assembly to its specified location, in accordance with DFP 0800-01, "Master Refueling Proced
Region: III | Dresden | 8356 | 12/31/2009 02/10/2010 | 2009005-06 | Self - Revealed | NCV | Barrier Integrity | Green | Mispositioning of a Unit 3 Control Rod at Power |  |  | TE?: N | 05000249 Dresden 3 |  | 71111.22 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the mispositioning of a Unit 3 control rod at power. Control rod G-11 was withdrawn on
Region: III | Dresden | 8358 | 12/31/2009 02/10/2010 | 2009005-08 | Self - Revealed | NCV | Initiating Events | Green | Procedural Deficiency Causing a Pressure Pulse Resulting in a Reactor Water Level Low-Low Group 1 Isolcation Signal and Unit 3 Reactor Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000249 Dresden 3 |  | 71153 | A self-revealed finding involving a non-cited violation (NCV) of Technical Specification 5.4.1 was identified on October 3, 2009, due to the licensee's failure to include essential information in DOP 1200-03, "RWCU System Operation with the Reactor at Pre
Region: III | Dresden | 8368 | 12/31/2009 02/10/2010 | 2009005-09 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure a Safety-related Plus was Ordered and installed in the 2/3 Emergency Diesel Generator Turbo Lube Oil "Y" Strainer |  | H.4(b) Procedural Compliance | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion IV, "Procurement Document Control," was self-revealed for the licensee's failure to ensure a safety-related plug was ordered and installed where required
Region: III | Dresden | 8339 | 11/18/2009 12/22/2009 | 2009007-01 | NRC | FIN | Mitigating Systems | Green | Ventilation System One-Time Inspection Results (4OA5.1.b(1)) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 |  | 71003 | A finding of very low safety-significance (Green) was identified by the inspectors for the licensee's failure to adequately evaluate and address an aging effect identified by the ventilation system one-time inspection program in accordance with the licens
Region: III | Dresden | 8340 | 11/18/2009 12/22/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Unit 2 SBLC Tank Thickness Calculation Errors (4OA5.1.b(2)) |  |  | TE?: N | 05000237 Dresden 2 |  | 71003 | A finding of very low safety-significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to accurately translate the design bases for the Standby
Region: III | Dresden | 8341 | 11/18/2009 12/22/2009 | 2009007-03 | NRC | FIN | Mitigating Systems | Green | Failure to Inspect the Non-EQ Electrical Connections Subject to Localized Adverse Environment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000237 Dresden 2 |  | 71003 | A finding of very low safety-significance was identified by the inspectors for the licensee's failure to implement a program in accordance with the license renewal program basis Document B.1.33. Specifically, the licensee failed to develop and implement a
Region: III | Dresden | 8334 | 09/30/2009 11/06/2009 | 2009004-02 | NRC | FIN | Initiating Events | Green | Failure to Identify and Replace CR120A Relays as Recommended by GE SIL 229 Supplement 1 |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | A finding of very low safety significance was identified by NRC Inspectors for the licensee's failure to identify and replace several CR120A relays as recommended by GE SIL 229 Supplement 1. Specifically, the licensee failed to replace several CR120A rela
Region: III | Dresden | 8337 | 09/30/2009 11/06/2009 | 2009004-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Technical Specification 5.5.2 Implementing Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.22 | The inspectors identified several examples of failure to follow the procedures that implemented Technical Specification (TS) 5.5.2, "Primary Coolant Sources Outside Containment." These failures were determined to represent a Green finding and a non cited
Region: III | Dresden | 8330 | 06/30/2009 08/07/2009 | 2009003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Have a Procedure to Sample and Establish Administrative Controls for pH in the Torus |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000249 Dresden 3 |  | 71111.15 | The inspectors identified a finding of very low safety significance involving a Non Cited Violation of Technical Specification 5.4.1 for the failure to include essential information in procedures CY AB 120 310, "Suppression Pool/Torus Chemistry," and CY D
Region: III | Dresden | 8331 | 06/30/2009 08/07/2009 | 2009003-03 | Self - Revealed | NCV | Initiating Events | Green | Instrument Air Isolation Valve Mispositioning on April 26, 2009 |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | A finding of very low safety significance and associated Non Cited Violation of Technical Specification Section 5.4.1 was self revealed when the Unit 2 instrument air system had a significant pressure drop because a non licensed operator failed to follow
Region: III | Dresden | 8322 | 05/22/2009 06/15/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Diesel-Driven Fire Pump Discharge Valve Found Out of Position |  | H.3(b) Work Activity Coordination | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.17T | A finding of very low safety significance and associated non-cited violation of license conditions 2.E and 3.G for Units 2 and 3, respectively, was identified by the inspectors for the failure to restore the Unit 1 diesel-driven fire pump to an operable c
Region: III | Dresden | 8315 | 03/31/2009 05/14/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop a Pre Fire Plan for Fire Zone 18.6 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05Q | The inspectors identified an NCV of the Dresden Nuclear Power Station Renewed Facility Operating License having very low safety significance for the licensee's failure to develop a pre fire plan for Fire Zone 18.6. This issue was entered into the licensee
Region: III | Dresden | 8316 | 03/31/2009 05/14/2009 | 2009002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement and Maintain in Effect All Provision of the Approved Fire Protection Program as described in theUFSAR |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.06 | A self revealed NCV of the Dresden Nuclear Power Station Renewed Facility Operating License having very low safety significance was identified for the licensee's failure to implement and maintain in effect all provisions of the approved Fire Protection Pr
Region: III | Dresden | 8317 | 03/31/2009 05/14/2009 | 2009002-03 | NRC | NCV | Initiating Events | Green | Failure to Ensure the Control of the Design Basis Was Correctly Translated Into Station Procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 |  | 71152 | The inspectors identified a NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control", of very low safety significance, for the failure to ensure that the control of the design basis was correctly translated into station procedures. The procedures use
Region: III | Dresden | 8318 | 03/31/2009 05/14/2009 | 2009002-04 | NRC | NCV | Barrier Integrity | Green | Failure to Take Corrective Actions to Replace a Degraded Valve in a Timely Manner |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000237 Dresden 2 |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action", for the failure to correct degraded safety related equipment in a timely manner. A degraded 4 way solenoid valve for the reactor building ventilation damper 2 5
Region: III | Dresden | 8277 | 03/31/2009 05/14/2009 | 2009002-05 | Self - Revealed | FIN | Barrier Integrity | Green | Operator Performed an Incorrect Response to an Unexpected Alarm in the Control Room |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71153 | On January 13, 2009, a Finding with no violation of regulatory requirements was self revealed when an operator performed an incorrect response to an unexpected alarm in the control room that resulted in a reactor building ventilation isolation and a stand
Region: III | Dresden | 8320 | 03/31/2009 05/14/2009 | 2009002-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Declare Primary Containment Isolation Valve Inoperable and Take Required Actions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000249 Dresden 3 |  | 71153 | A self-revealed NCV of Dresden Station Improved Technical Specification (TS) 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," of very low safety significance was identified for the failure to declare primary containment isolation valve 3 3702 inop
Region: III | Dresden | 8313 | 12/31/2008 02/02/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | LPCI Heat Exchangers' Design Calculation Deficiencies and Discrepancies |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.07T | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the low pressure coolant injection (LPCI) heat exchangers cooling capability during a design basi
Region: III | Dresden | 8312 | 12/31/2008 02/02/2009 | 2008005-02 | NRC | NCV | Initiating Events | Green | Freeze Seal Established Prior to Meeting The Requirements of Procedure MA-AA-736-610 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000249 Dresden 3 |  | 71111.19 | A finding of very low safety significance and associated Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by NRC inspectors on November 12, 2008, when the licensee had declared a free
Region: III | Dresden | 8309 | 09/30/2008 11/13/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Procedure for Several Instrument Maintenance Surveillance Tests |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.22 | The inspectors identified a NCV of Technical Specification (TS) 5.4.1 for the failure to provide an adequate procedure for the verification of correct installation and restoration of equipment during instrument maintenance surveillance tests in June and A
Region: III | Dresden | 8310 | 09/30/2008 11/13/2008 | 2008004-02 | Self - Revealed | FIN | Initiating Events | Green | Repetitive Contaminated Water Spills in the Unit 2 Reactor Building |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 |  | 71152 | A performance deficiency for the spill of contaminated water and the unexpected spread of contamination on multiple occasions was self revealed by additional spills in August 2008. The failure to clear a blockage in the floor drain system in a timely mann
Region: III | Dresden | 8302 | 06/30/2008 08/05/2008 | 2008003-01 | NRC | FIN | Initiating Events | Green | Failure to Control Loose Materials in the Protected Area |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.01 | The inspectors identified a finding of very low safety significance with no associated violation of regulatory requirements for the licensee's failure to control loose materials in the protected area. Specifically, on the morning of May 30, 2008, the insp
Region: III | Dresden | 8303 | 06/30/2008 08/05/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Fire Doors Failed Their Periodic Functional Test |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05Q | The inspectors identified a finding of very low safety significance that involved a Non-cited Violation of the Dresden Nuclear Power Station Renewed Facility Operating License of the Dresden Nuclear Power Station Renewed Operating License Conditions 2.E a
Region: III | Dresden | 8305 | 06/30/2008 08/05/2008 | 2008003-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Verify the Adequacy of Design Information Provided By a Vendor |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152 | A self-revealed finding of very low significance was identified involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to completely verify the adequacy of design information provided by a vendor. T
Region: III | Dresden | 8294 | 03/28/2008 05/09/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Acceptance Criteria for Stem Factor in MOV Testing Did Not Account for Uncertainty |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to include an uncertainty value, to account for test equipment accuracy and lubricant degradation, in the acceptance criteria for the stem factor in
Region: III | Dresden | 8301 | 03/28/2008 05/09/2008 | 2008008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Develop a Pre-Fire Plan for Fire Zone 18.6 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified an NCV for the licensee's failure to develop a pre-fire plan for fire zone 18.6. The finding was a violation of Dresden Nuclear Power Station Renewed Operating License. License conditions 2.E and 3.G for Unit 2 and Unit 3, respec
Region: III | Dresden | 8290 | 02/15/2008 03/26/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Periodic Trip Tests on Thermal Overload Heaters. |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05T | Green. The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." Specifically, the licensee failed to identify and periodically perform the necessary testing on s
Region: III | Dresden | 8273 | 12/31/2007 02/12/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | Failure to perform corrective action to mitigate excessive train unavailability for Auxiliary Electric Equipment Room Heating, Ventilation and Air Conditioning |  | H.3(a) Work Planning | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.12 | The inspectors identified a performance deficiency involving a non-cited violation of 10 CFR 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," Section (a) (1), for the failure to take appropriate corrective act
Region: III | Dresden | 8274 | 12/31/2007 02/12/2008 | 2007005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Take Corrective Actions to Repair Unit 3B Refuel Floor Fuel Pool Area Radiation Monitor in a Timely Manner |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.12 | On May 9, 2007, a performance deficiency involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and adequately correct deficiencies with the Unit 3B Refuel Floor Fuel Pool Ar
Region: III | Dresden | 8276 | 12/31/2007 02/12/2008 | 2007005-04 | Self - Revealed | NCV | Barrier Integrity | Green | Standby Gas Treatment 'A' Train Exhibiting Flow Oscillations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | A performance deficiency involving a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was self-revealed following 2/3A standby gas treatment (SBGT) train flow controller settings and post maintenance testing which did not e
Region: III | Dresden | 8278 | 12/31/2007 02/12/2008 | 2007005-05 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Continuously Sample the Unit 2 and 3 Chimney for Particulate and Iodine Effluents |  | H.3(a) Work Planning | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | NONE | A self-revealed finding of very low safety significance and an associated violation of NRC requirements were identified for the failure to continuously sample the Unit 2 and 3 chimney effluent for particulate and iodine radioactivity. Specifically, for an
Region: III | Dresden | 8279 | 12/31/2007 02/12/2008 | 2007005-06 | Self - Revealed | NCV | Barrier Integrity | Green | Unit 2/3 Standby Gas Treatment Auto-started and a Unit 2 and 3 Reactor Building Ventilation Isolation Occurred |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | On November 9, 2007, a performance deficiency involving a non-cited violation of TS 5.4.1 was self-revealed when a nuclear station operator (NSO) was performing Dresden Operating Procedure (DOP) 0500-03, "Reactor Protection System Power Supply Operation,"
Region: III | Dresden | 8282 | 12/18/2007 01/17/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Failure to meet the EDG Power Factor Testing Requirement |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified an NCV for the failure to meet the requirements contained in SR 3.8.1.15. Specifically, the testing that the licensee performed to meet SR 3.8.1.15 did not test to a power factor as close to the accident load power factor as poss
Region: III | Dresden | 8261 | 09/30/2007 11/05/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Issues with the Operation and Testing of the Isolation Condenser Emergency Make-up Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.06 | The inspectors identified a performance deficiency involving a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very low safety significance for the failure to promptly identify and adequately correct iss
Region: III | Dresden | 8268 | 09/30/2007 11/05/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | High Pressure Coolant Injection System Removed from Service Due to a Steam Leak on the Inlet Drain Pot Drain Piping |  |  | TE?: N | 05000249 Dresden 3 |  | 71153 | A finding involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance was self revealed after the Unit 3 High Pressure Coolant Injection (HPCI) system was removed from service on Marc
Region: III | Dresden | 8258 | 06/12/2007 07/30/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Restore Fire Brigade Equipment to a Ready Status in a Timely Manner after the Performance of a Fire Drill |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05Q | The inspectors identified a Non-Cited Violation (NCV) of the Dresden Nuclear Power Station Renewed Facility Operating License having very low safety significance (Green) for the licensee's failure to restore fire brigade equipment to a ready status in a t
Region: III | Dresden | 8254 | 05/18/2007 07/02/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria in 125 VDC Station Battery Service Test Procedures |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." Specifically, the licensee failed to incorporate the 125 VDC system minimum required voltage value a
Region: III | Dresden | 8255 | 05/18/2007 07/02/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Adequate Control Voltage for 4160 Breaker's Closing Coil was not Assured |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to assure and verify that the minimum available control voltage
Region: III | Dresden | 8256 | 05/18/2007 07/02/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Procedurally Control Regulatory Guide 1.97 Control Board Labeling |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111121 | The inspectors identified a performance deficiency involving a Non-Cited Violation of Technical Specification (TS) 5.4.1 for the licensee's failure to provide procedural controls for the unique identification of Regulatory Guide (RG) 1.97 post-accident in
Region: III | Dresden | 8259 | 05/04/2007 07/30/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment That Led to a Reactor Scram |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71153 | A performance deficiency involving a Non-Cited Violation of 10 CFR 50.65(a)(4) was self-revealed after the Unit 2 reactor scram on May 4, 2007. The licensee failed to adequately assess and manage the risk associated with emergent work. The licensee's root
Region: III | Dresden | 8252 | 03/31/2007 05/07/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform 50.59 Evaluation of Non-Code Conforming Buried HPCI Piping (Section 1R02) |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | NONE | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59(d)(1) for the licensee's failure to document an evaluation which provides the basis for the determination that a change, test, or experiment did not require a license amendm
Region: III | Dresden | 8253 | 03/31/2007 05/07/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | Valves Not Protected in the Division I Torus Pathway as Required by Procedure WC-AA-101 |  | H.3(a) Work Planning | TE?: N | 05000237 Dresden 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a) (4), having very low safety significance associated with inadequate management of risk. On January 16, 2007, the licensee performed preventive maintenance which rendered Division II of th
Region: III | Dresden | 8246 | 12/31/2006 02/01/2007 | 2006011-01 | NRC | NCV | Barrier Integrity | Green | Licensee's Failure to Develop a Pre-fire Plan for Fire Zone 8.2.6.A, Elevation 534' |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.05Q | A performance deficiency involving a non-cited violation of the Dresden Nuclear Power Station Renewed Facility Operating License was identified by the inspectors due to the licensee's failure to develop a pre-fire plan. Specifically, on November 17, 2006,
Region: III | Dresden | 8247 | 12/31/2006 02/01/2007 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with TS 5.5.13 for 125 Vdc Battery Terminal Connection Corrosion and Resistance Measurements |  | H.4(b) Procedural Compliance | TE?: N | 05000237 Dresden 2 |  | 71111.15 | On October 16, 2006, a performance deficiency involving a non-cited violation of TS Section 5.5.13 having very low safety significance was identified by the inspectors for failure to comply with the TS requirement when visible corrosion on the Unit 2 125
Region: III | Dresden | 8250 | 12/31/2006 02/01/2007 | 2006011-05 | Self - Revealed | NCV | Initiating Events | Green | Review of Unit 2/3 Condensate Storage Tank Overflow Event |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000249 Dresden 3 |  | 71153 | A performance deficiency involving a non-cited violation of Technical Specification (TS) 5.4.1, was self revealed on November 20, 2006, when during the Unit 3 hotwell drain down to support Unit 3 startup, operators allowed the 2/3 condensate storage tank
Region: III | Dresden | 8239 | 10/06/2006 11/16/2006 | 2006012-01 | NRC | NCV | Initiating Events | Green | Inappropriate Basis in 10 CFR 50.59 Evaluation for Temporary Modification |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111102 | The inspectors identified a Severity Level IV Non-Cited Violation (NCV) of 10 CFR 50.59 "Changes, Tests, and Experiments," having very low safety significance (Green) for the licensee's failure to perform an adequate safety evaluation review for changes m
Region: III | Dresden | 8241 | 10/06/2006 11/16/2006 | 2006012-03 | NRC | NCV | Mitigating Systems | Green | EQ Binder Failed to Include Conductor Temperature Rise |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7111117B | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" having very low safety significance (Green) for the licensee's failure to evaluate and include the conductor temperature rise for the 5KV cables for the CS and
Region: III | Dresden | 8227 | 09/30/2006 10/30/2006 | 2006010-01 | Self - Revealed | NCV | Mitigating Systems | Green | Mispositioning of Control Rod During Single Notch Timing |  | H.4(a) Human Error Prevention | TE?: N | 05000237 Dresden 2 |  | 71111.22 | On July 30, 2006, a performance deficiency involving a non-cited violation of TS 5.4.1 was self revealed when two nuclear station operators (NSOs) failed to exercise appropriate three-way communication and second verification, resulting in the movement of
Region: III | Dresden | 8232 | 09/30/2006 10/30/2006 | 2006010-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Satisfy Technical Specification LHRA Access Requirements During Entry Into a Steam Sensitive Area at Power |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 7112101 | A self-revealed finding of very low safety significance, and an associated violation of NRC requirements were identified for the failure to satisfy Technical Specification requirements for access into a high radiation area with dose rates in accessible ar
Region: III | Dresden | 8236 | 09/30/2006 10/30/2006 | 2006010-06 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 2 Isolation Condenser Declared Inoperable Due to Inadequate Backfilling of Instrument Sensing Lines |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000237 Dresden 2 |  | 71153 | A self-revealing finding involving a non-cited violation of Technical Specification 5.4.1 was identified on February 1, 2006, due to the licensee's failure to include essential information in DOP 1300-11, "Unit 2 Isolation Condenser Fill and Vent," Revisi
Region: III | Dresden | 8237 | 09/30/2006 10/30/2006 | 2006010-07 | Self - Revealed | NCV | Initiating Events | Green | Failure to Include Adequate Instructions for Fitting Reassembly in Main Steam Isolation Valve Work Package |  |  | TE?: N | 05000237 Dresden 2 |  | 71153 | A performance deficiency involving a non-cited violation of Technical Specification (TS) 5.4.1 was self revealed after the Unit 2 reactor scram on July 4, 2006. The licensee's root cause report determined that the cause of scram was that the Unit 2 inboar
Region: III | Dresden | 8260 | 09/07/2006 07/30/2007 | 2007003-04 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct Issues With the Operation and Testing of the Diesel Driven Pump Used to Respond to External Flooding |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71153 | On September 7, 2006, the inspectors identified a performance deficiency involving a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and adequately correct issues with the operati
Region: III | Dresden | 8221 | 06/29/2006 07/31/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify an Inoperable 3-hour Fire Barrier Wall in the Unit 2 EDG Day Tank Room |  |  | TE?: N | 05000237 Dresden 2 |  | 71111.05Q | On May 1, 2006, the inspectors identified a non-cited violation of Unit 2 Operating License Condition E, Fire Protection Program, for failure to identify and correct a degraded fire barrier wall. The inspectors identified a wall gap in the Unit 2 emergenc
Region: III | Dresden | 8222 | 06/29/2006 07/31/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Unit 2 350 psig Reactor Low Pressure Emergency Core Cooling System Permissive Switch Out-of-tolerance During Surveillance Testing |  |  | TE?: N | 05000237 Dresden 2 |  | 71111.12 | On May 15, 2006, a finding involving a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, was identified by the inspectors. The licensee failed to identify a condition adverse to quality where the Unit 2 350 psig reactor low pressure emergency c
Region: III | Dresden | 8223 | 06/29/2006 07/31/2006 | 2006007-03 | NRC | NCV | Barrier Integrity | Green | Failure to Post Protective Pathway Signs During Unavailability of Torus to Reactor Building Vacuum Breaker |  |  | TE?: N | 05000237 Dresden 2 |  | 71111.13 | On May 15, 2006, the inspectors identified a non-cited violation 10 CFR 50.65 (a) (4), having very low safety significance associated with inadequate management of risk. While working on the Unit 2 1601-20B reactor building to torus vacuum breaker relief
Region: III | Dresden | 8224 | 06/29/2006 07/31/2006 | 2006007-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Perform Procedure Steps in the Proper Sequence by Operations Caused Emergency Safety Feature Systems Actuation |  |  | TE?: N | 05000249 Dresden 3 |  | 71153 | On April 5, 2006, a performance deficiency involving a non-cited violation of TS 5.4.1 was self revealed when an auxiliary nuclear station operator (Aux NSO) and a unit supervisor (US) were performing Dresden Operating Procedure (DOP) 0500-03, "Reactor Pr
Region: III | Dresden | 8225 | 06/29/2006 07/31/2006 | 2006007-05 | Self - Revealed | FIN | Mitigating Systems | Green | Unit 2 High Pressure Coolant Injection (HPCI) System Declared Inoperable |  |  | TE?: N | 05000237 Dresden 2 |  | 71153 | A finding was self-revealed when an instrument maintenance technician shorted a power lead while performing modification work that resulted in the Unit 2 high pressure coolant injection system becoming inoperable for 2 hours and 14 minutes on April 6, 200
Region: III | Dresden | 8226 | 06/29/2006 07/31/2006 | 2006007-06 | NRC | NCV | Mitigating Systems | Green | Standby Liquid Control Valves Installed In The Plant Different than those Assumed in a Design Calculation |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | On May 5, 2006, the inspectors identified a finding involving a non-cited violation of 10 CFR 50.62 associated with a licensee-identified material condition, and having very low safety significance. The licensee identified that the inputs to a design anal
Region: III | Dresden | 8211 | 03/31/2006 05/08/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Weld Inspections by Independent Certified Quality Verification Inspectors |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.13 | On February 19 and March 12, 2006, a performance deficiency involving a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors. The finding involved the licensee's f
Region: III | Dresden | 8212 | 03/31/2006 05/08/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Installation of Various Lighting Fixtures Without Using Plant Modification Process |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71111.15 | On January 27, 2006, a performance deficiency involving a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified by the inspectors. The finding involved the licensee's failure to use the plant modification process, whe
Region: III | Dresden | 8220 | 03/31/2006 05/08/2006 | 2006003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Revision to Work Order Instructions Resulted in the Temporary Loss of Shutdown Cooling |  |  | TE?: N | 05000237 Dresden 2 |  | 71111.2 | On November 6, 2005, a performance deficiency involving a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when a loss of shutdown cooling occurred while maintenance activities were bei
Region: III | Dresden | 8203 | 01/27/2006 03/09/2006 | 2006002-01 | NRC | FIN | Mitigating Systems | Green | Identification of Electromatic Relief Valve (ERV) Degradation |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified a failure to enter discrepancies into the corrective action program that were previously identified in work orders associated with the electromatic relief valves (ERVs) during the 2005 Unit 2 and 2004 Unit 3 refueling outages. Th
Region: III | Dresden | 8208 | 01/27/2006 03/09/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Inadequate Procedure for Surveillance of Remote Shutdown Emergency Lights |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71152B | The inspectors identified an NCV of Technical Specification (TS) 6.8.A.1, which required that written procedures be implemented covering the activities in the applicable procedures recommended by Regulatory Guide 1.33, including procedures for surveillanc
Region: III | Dresden | 8210 | 01/06/2006 04/30/2004 | 2004002-07 | NRC | NCV | Mitigating Systems | Green | Water intrusion in the high pressure coolant injection system steam supply line. | EA Case: 2005232 |  | TE?: N | 05000237 Dresden 2 |  | 7111114 | The NRC identified a NCV for the failure to properly evaluate extended power uprate for its impact on post-scram reactor vessel water level to prevent water intrusion into the HPCI steam supply line. The NRC concluded that EGC implemented extended power u
Region: III | Dresden | 126078 | 12/05/2019 |  |  | LIV |  | Green | A licensee-identified finding and violation of 10 CFR 73.55n(1)(i), Maintenance, Testing and Calibration |  |  | TE?: N | 05000237 Dresden 2 05000249 Dresden 3 |  | 71130.04
Region: III | Duane Arnold | 124844 | 06/30/2019 08/01/2019 | 2019002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Notify Radiation Protection of Change In Work Scope |  | H.4 - Teamwork | TE?: N | 05000331 Duane Arnold | Program & Process | 71124.01 | The inspectors reviewed a self-revealed finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of TS 5.4.1, “Procedures,” when the licensee failed to implement contamination control procedures when machining a contamin
Region: III | Duane Arnold | 125275 | 06/30/2019 08/01/2019 | 2019002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Manage Outage Risk Activities |  | H.5 - Work Management | TE?: N | 05000331 Duane Arnold | Human Performance | 71153 | A self-revealed finding of very low safety significance (i.e., Green) was identified for the licensee’s failure to have appropriately managed risk activity as required by WM-AA-100-1000, Work Activity Risk Management, Revision 16. Specifically, plant per
Region: III | Duane Arnold | 24354 | 06/30/2018 08/03/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Procedural Guidance Resulted in Loss of Scram Function and Failure to Enter Applicable Technical Specification Limiting Condition for Operation |  | H.1 - Resources | TE?: N | 05000331 Duane Arnold |  | 71153 | The inspectors identified a finding of very low safety significance (Green) and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the failure to have procedures appropriate to the circumstance for t
Region: III | Duane Arnold | 24357 | 06/05/2018 07/10/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Environmental Qualification Requirements into Maintenance Procedures/Instructions |  | NPP | TE?: N | 05000331 Duane Arnold |  | 71111.21N | The inspectors identified a finding of very-low safety significance (Green), and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to establish measures to assure that EQ requirements for qualified c
Region: III | Duane Arnold | 23504 | 02/08/2018 03/16/2018 | 2018010-01 | NRC | NCV | Initiating Events | Green | Failure to have Adequate Pre-Fire Plans |  | H.7 - Documentation | TE?: N | 05000331 Duane Arnold |  | 71111.05XT | The inspectors identified a finding of very-low safety significance (Green), and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50.48(c), and National Fire Protection Association (NFPA) 805, Section 3.4.2 “
Region: III | Duane Arnold | 23505 | 02/08/2018 03/16/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Operator Action in the Plant Operating Procedure |  | NPP | TE?: N | 05000331 Duane Arnold |  | 71111.05XT | The inspectors identified a finding of very-low safety significance (Green), and associated NCV of 10 CFR 50.48(c), and NFPA 805, Section 4.2.4.1.6 “Operations Guidance.” Specifically, during the transition process to NFPA 805, performance-based standard
Region: III | Duane Arnold | 22691 | 12/31/2017 01/22/2018 | 2017004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Reactor Water Level within Procedurally Required Level Band Results in Reactor Recirculation Pump Runback. |  | H.4 - Teamwork | TE?: N | 05000331 Duane Arnold |  | 71152 | The inspectors documented a self-revealed finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” due to operations personnel failing to control reactor vessel water le
Region: III | Duane Arnold | 10357 | 06/30/2017 08/02/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION PROGRAM REQUIREMENTS. |  | H.7 Documentation | TE?: N | 05000331 Duane Arnold |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.5.13, "Control Building Envelope (CBE) Habitability Program," for the licensee's failure to implement all TS required elements in t
Region: III | Duane Arnold | 10363 | 05/19/2017 06/30/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE EFFECT OF CREDITING BYPASS LINE AS SAFETY RELATED FLOWPATH |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.21M | A finding of very-low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to designate the functi
Region: III | Duane Arnold | 10364 | 05/19/2017 06/30/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE GAS TRANSPORT THROUGH MODIFIED PIPING CONFIGURATION |  | H.4 Teamwork | TE?: N | 05000331 Duane Arnold |  | 71111.21M | A finding of very-low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to evaluate gas transport through the modified piping configuration. S
Region: III | Duane Arnold | 10349 | 03/31/2017 05/08/2017 | 2017001-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE MAINTENANCE INSTRUCTIONS FOR CONTAINMENT PURGE VALVES LED TO VIOLATION OF TECHNICAL SPECIFICATION 3.6.1.3. |  | H.1 Resources | TE?: N | 05000331 Duane Arnold |  | 71111.12 | A Green finding and an associated NCV of Technical Specification (TS) 3.6.1.3 was self-revealed due to the failure to ensure the outboard containment purge valve was operable when the reactor was placed in Mode 2 on October 30, 2016. Specifically, the lic
Region: III | Duane Arnold | 10350 | 03/31/2017 05/08/2017 | 2017001-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ENTER TECHNICAL SPECIFICATION 3.6.1.3 FOR AN INOPERABLE OUTBOARD CONTAINMENT PURGE VALVE. |  | H.13 Consistent Process | TE?: N | 05000331 Duane Arnold |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.36(c)(2)(i) for the licensee's failure to enter TS 3.6.1.3 for an inoperable outboard drywell purge valve.
Region: III | Duane Arnold | 10355 | 03/31/2017 05/08/2017 | 2017001-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO INCORPORATE ASPECTS OF VENDOR MANUAL INTO SCBA MAINTENANCE PROCEDURE. |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 71124.03 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 20.1703, "Use of Individual Respiratory Protection Equipment," for the licensee's failure to develop and maintain written procedures regarding the maintenance
Region: III | Duane Arnold | 10356 | 03/24/2017 05/03/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO INCLUDE VALVES IN THE INSERVICE TESTING PROGRAM. |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 71152B | The inspectors identified a finding and an associated non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.55a(f)(1) for the licensee's failure to scope in multiple check valves of the main steam isolation valve leakage treatment
Region: III | Duane Arnold | 10348 | 12/31/2016 02/01/2017 | 2016004-01 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO CONTROL EMERGENCY PREPAREDNESS DRILL SCENARIO. |  | H.12 Avoid Complacency | TE?: N | 05000331 Duane Arnold |  | 71114.06 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR 50.54(q)(2) associated with the failure to maintain the effectiveness of an emergency plan that meets the requirements in 10 CFR 50, Appendix E. Specifically, the lic
Region: III | Duane Arnold | 10345 | 12/31/2016 02/01/2017 | 2016004-02 | NRC | NCVIV | Mitigating Systems | Green | INADEQUATE EVALUATION FOR A CHANGE TO THE LOW PRESSURE COOLANT INJECTION ANNUNCIATOR RESPONSE PROCEDURE. |  | H.6 Design Margins | TE?: Y SL-IV-NCVIV | 05000331 Duane Arnold |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated Severity Level IV NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50.59, "Changes, Tests, and Experiments," when licensee personnel failed to p
Region: III | Duane Arnold | 10136 | 09/30/2016 11/01/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY AND EVALUATE A CONDITION ADVERSE TO QUALITY. |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," was identified by the inspectors for the licensee's failure to follow Quality Assurance Program implementing procedure PI-AA-104
Region: III | Duane Arnold | 10137 | 09/30/2016 11/01/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Controls to the DAEC Switchyard Resulting in an Unplanned Technical Specification LCO 3.8.1 Entry and an Unplanned Risk Change from Green to Yellow |  | H.5 Work Management | TE?: N | 05000331 Duane Arnold |  | 71153 | A self-revealed finding of very low safety significance and a non-cited violation (NCV) of Technical Specification (TS) 5.4, "Procedures," was self-revealed due to the licensee's failure to implement a written procedure recommended in Regulatory Guide 1.3
Region: III | Duane Arnold | 10131 | 06/30/2016 08/08/2016 | 2016002-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ACCOMPLISH A SURVEILLANCE TEST PROCEDURE IN ACCORDANCE WITH INSTRUCTIONS RESULTING IN SAFETY SYSTEM INOPERABILITY. |  | H.12 Avoid Complacency | TE?: N | 05000331 Duane Arnold |  | 71111.22 | A self-revealing finding of very low safety significance (Green) and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure
Region: III | Duane Arnold | 10124 | 01/29/2016 03/22/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DOCUMENT REVIEWS PERFORMED IN 50.59 SCREEN FOR NEW ABNORMAL OPERATING PROCEDURE. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.17T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to docume
Region: III | Duane Arnold | 10130 | 01/29/2016 03/22/2016 | 2016007-02 | NRC | NCVIV | Barrier Integrity | Green | FAILURE TO DOCUMENT 50.59 EVALUATION FOR UFSAR CHANGE CONCERNING RADIOLOGICAL DOSE CONSEQUENCE ANALYSIS METHODOLOGY. |  |  | TE?: Y SL-IV-NCVIV | 05000331 Duane Arnold |  | 71111.17T | The inspectors identified a Severity Level IV, NCV of 10 CFR 50.59, "Changes, Tests, and Experiments," having very-low safety significance (Green) for the licensee's failure to document the basis for making a change to Updated Final Safety Analysis Report
Region: III | Duane Arnold | 10112 | 12/31/2015 02/03/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO SCOPE SAFETY RELATED AND NONSAFETY RELATED BREAKER INTO THE MAINTENANCE RULE. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.12 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(1), 10 CFR 50.65(a)(2), and 10 CFR 50.65(b), due to the licensee's failure to scope the load-shed function of safety related and nonsafety related
Region: III | Duane Arnold | 10113 | 12/31/2015 02/03/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DECLARE HIGH PRESSURE COOLANT INJECTION AND REACTOR CORE ISOLATION COOLING INOPERABLE WHEN THE HIGH PRESSURE COOLANT INJECTION AND REACTOR CORE ISOLATION COOLING PUMP SUCTION WAS INOPERABLE |  | H.14 Conservative Bias | TE?: N | 05000331 Duane Arnold |  | 71111.15 | The inspectors identified a finding of very low safety significance, with two examples, and an associated NCV of Technical Specifications (TS) Sections 3.3.5.1, Condition D and 3.3.5.2, Condition D, for failure to initiate required TS action statements 3.
Region: III | Duane Arnold | 10123 | 12/31/2015 02/03/2016 | 2015004-04 | NRC | FIN | Initiating Events | Green | Failure to Follow Temporary Configuration Control Procedure. |  | P.5 Operating Experience | TE?: N | 05000331 Duane Arnold |  | 71111.18 | The inspectors identified a finding of very low safety significance for the licensee's failure to follow procedure EN-AA-205-1102, "Temporary Configuration Changes," Revision 6. Specifically, the licensee constructed a shaft housing enclosure on the "B" c
Region: III | Duane Arnold | 10105 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ACCOMPLISH A PROCEDURE FOR AN ACTIVITY AFFECTING QUALITY IN A MANNER APPROPRIATE TO THE CIRCUMSTANCES. |  | H.14 Conservative Bias | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to iden
Region: III | Duane Arnold | 10106 | 06/30/2015 08/06/2015 | 2015002-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN BREATHING AIR QUALITY REQUIREMENTS FOR SCBAs. |  | H.1 Resources | TE?: N | 05000331 Duane Arnold |  | 71124.03 | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR 20.1703, "Use of Individual Respiratory Protection Equipment," for the licensee's failure to supply breathing air in accordance with manufacturer
Region: III | Duane Arnold | 10090 | 05/01/2015 06/05/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | INAPPROPRIATE DIESEL GENERATOR MAINTENANCE PROCEDURE. |  | P.3 Resolution | TE?: N | 05000331 Duane Arnold |  | 71152B | The inspectors identified a finding of very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to ensure that activities affecting quality were prescribed by documented
Region: III | Duane Arnold | 10089 | 03/31/2015 05/04/2015 | 2015001-01 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO CLASSIFY AND DECLARE A NOTIFICATION OF UNUSUAL EVENT. |  | H.12 Avoid Complacency | TE?: N | 05000331 Duane Arnold |  | 71114.05 | The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) 50.54(q)(2), and 10 CFR 50.47(b)(4) for the failure of the licensee to classify and declare a Notificati
Region: III | Duane Arnold | 10087 | 02/13/2015 03/24/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate the Effects of Vessel Overfill Scenario (Section 1R05.6.b) |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.05XT | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR) 50.48(c), and National Fire Protection Association Standard 805, Section 2.4.3.2 for the licensee's failure t
Region: III | Duane Arnold | 10086 | 01/08/2015 02/19/2015 | 2014011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Coating Strainer Debris Loading Calculation (Section 4OA5.1.d(2)) | EA Case: 2014237 |  | TE?: N | 05000331 Duane Arnold |  | 93812 | -Green. The team identified a finding having very-low safety significance and a Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to account for all unqualified coating debris available for tran
Region: III | Duane Arnold | 10065 | 12/31/2014 02/04/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | THE CONSTRUCTION CODE USED DURING A REPLACEMENT ACTIVITY WAS NOT RECONCILED WITH THE OWNER'S REQUIREMENTS. |  | H.8 Procedure Adherence | TE?: N | 05000331 Duane Arnold |  | 71111.08G | A finding of very low safety significance (Green) and an associated non-cited violation of Title 10 of the Code of Federal Regulations, Section 50.55a, "Codes and Standards," was identified by the inspectors for the failure to reconcile the construction c
Region: III | Duane Arnold | 10066 | 12/31/2014 02/04/2015 | 2014005-02 | NRC | NCV | Initiating Events | Green | LIQUID PENETRANT TESTING PROCEDURES WERE NOT QUALIFIED FOR THEIR FULL APPLICABILITY RANGE. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.08G | A finding of very low safety significance (Green) and an associated non-cited violation of Title 10 of the Code of Federal Regulation, Part 50, Appendix B, Criterion IX, "Control of Special Processes," was identified by the inspectors for the failure to p
Region: III | Duane Arnold | 10067 | 12/31/2014 02/04/2015 | 2014005-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO EVALUATE MAINTENANCE ACTIVITIES FOR PRECONDITIONING. |  | H.5 Work Management | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.4.1.a, "Procedures," was identified by the inspectors for the licensee's failure to maintain maintenance planning procedures appropriate for the c
Region: III | Duane Arnold | 10073 | 12/31/2014 02/04/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ACCOMPLISH PROCEDURE FOR LEAKING PIPE SNUBBER. |  | H.13 Consistent Process | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's
Region: III | Duane Arnold | 10074 | 12/31/2014 02/04/2015 | 2014005-05 | NRC | NCV | Barrier Integrity | Green | INADEQUATE CONTAINMENT ISOLATION VALVE LEAK TIGHTNESS TEST PROCEDURE. |  | H.1 Resources | TE?: N | 05000331 Duane Arnold |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulation, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure
Region: III | Duane Arnold | 10075 | 12/31/2014 02/04/2015 | 2014005-06 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO DETERMINE DOSE RATES PRIOR TO ENTRY INTO A HIGH RADIATION AREA. |  | H.11 Challenge the Unknown | TE?: N | 05000331 Duane Arnold |  | 71124.01 | . A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.7.1.e was identified by the inspectors following entry into the fuel pool heat exchanger room which was a high radiation area (HRA). The inspect
Region: III | Duane Arnold | 10082 | 12/31/2014 02/04/2015 | 2014005-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | INEFFECTIVE RADIOLOGICAL ENGINEERING CONTROLS RESULTED IN UNPLANNED AND UNINTENDED RADIOLOGICAL INTAKES TO WORKERS. |  | P.5 Operating Experience | TE?: N | 05000331 Duane Arnold |  | 71124.03 | A finding of very-low-safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulation, Section 20.1701 was self-revealed during work activities associated with the failure to implement effective radiological enginee
Region: III | Duane Arnold | 10083 | 12/31/2014 02/04/2015 | 2014005-08 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE SEVERAL SAFETY RELATED RELAYS INSTALLED BEYOND THEIR DESIGN LIFE. |  | P.1 Identification | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's
Region: III | Duane Arnold | 10084 | 12/31/2014 02/04/2015 | 2014005-09 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TEST OR EVALUATE THE SEISMIC CRITICAL CHARACTERISTIC FOR A COMMERCIAL GRADE CIRCUIT BREAKER. |  |  | TE?: N | 05000331 Duane Arnold |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify commercial
Region: III | Duane Arnold | 10061 | 09/30/2014 11/03/2014 | 2014004-01 | NRC | FIN | MISC | Green | FAILURE TO PERFORM CRITICAL EQUIPMENT FAILURE EVALUATIONS. |  | P.1 Identification | TE?: N | 05000331 Duane Arnold |  | 71111.05Q | A finding of very low safety significance, with three examples, and no associated violation was identified by the inspectors for the licensee's failure to accomplish procedure ER-AA-204-2005, "Critical Equipment Failure Evaluation," Revision 5. Specifical
Region: III | Duane Arnold | 10051 | 09/30/2014 11/03/2014 | 2014004-02 | Self - Revealed | NCV | Mitigating Systems | Green | HYDRAULIC CONTROL UNIT CONFIGURATION CONTROL ERROR. |  | H.5 Work Management | TE?: N | 05000331 Duane Arnold |  | 71111.13 | A finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to accomplish procedure OP-AA-101-1000, "Clear
Region: III | Duane Arnold | 10060 | 09/30/2014 11/03/2014 | 2014004-03 | NRC | FIN | Barrier Integrity | Green | FAILURE TO PERFORM CAUSAL EVALUATIONS FOR "A" STANDBY FILTER UNIT ISSUES. |  | H.13 Consistent Process | TE?: N | 05000331 Duane Arnold |  | 71111.19 | A finding of very low safety significance with no associated violation was identified by the inspectors for the licensee's failure to accomplish procedure PI-AA-204, "Condition Identification and Screening Process," Revision 24. Specifically, on September
Region: III | Duane Arnold | 10038 | 09/03/2014 09/19/2014 | 2014010-01 | NRC | VIO | Mitigating Systems | Green | FAILURE TO REMOVE WATER FROM CONDUITS CONTAINING SAFETY-RELATED CABLES. |  | H.6 Design Margins | TE?: N | 05000331 Duane Arnold |  | 71152 | The inspectors identified a finding of very low safety significance and an associated cited violation of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," where the licensee failed to correct a condition
Region: III | Duane Arnold | 10044 | 08/15/2014 09/26/2014 | 2014008-01 | NRC | NCV | Initiating Events | Green | Failure to Verify Design Adequacy of Loss of Voltage Relay Setting. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure the Loss of Voltage Relay trip settings were properly establ
Region: III | Duane Arnold | 10045 | 08/15/2014 09/26/2014 | 2014008-02 | NRC | FIN | Initiating Events | Green | Failure to Verify Startup Transformer Neutral Grounding Resistor Design Assumption. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding having very low safety significance (Green) in that, the licensee did not adequately ensure the operation of the Startup Transformer Neutral Grounding Resistors was within the design assumptions used in the calculation
Region: III | Duane Arnold | 10046 | 08/15/2014 09/26/2014 | 2014008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Include Minimum Required System Voltage as an Acceptance Criterion in the 125 Vdc Station Battery Surveillances Test Procedures. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to have adequate acceptance criteria in the station battery surveillance
Region: III | Duane Arnold | 10047 | 08/15/2014 09/26/2014 | 2014008-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to fully Incorporate the Sequential Loading Relay Functions into the UFSAR. |  |  | TE?: Y SL-IV-NCVIV | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a Severity Level IV NCV of Title 10 CFR 50.71(e), "Maintenance of Record, Making of Reports," and an associated finding of very low safety significance (Green) for the licensee's failure to maintain up-to-date the Updated Final S
Region: III | Duane Arnold | 10050 | 08/15/2014 09/26/2014 | 2014008-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Flow Balancing ESW System. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide adequate procedures for flow balancing of th
Region: III | Duane Arnold | 10023 | 07/11/2014 08/29/2014 | 2014009-01 | NRC | NCV | Mitigating Systems | Green | Inadequately Performed Drawing Revision Related to CAPR |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 95002 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that a safety-related drawing for the High Pressure Cool
Region: III | Duane Arnold | 10029 | 07/11/2014 08/29/2014 | 2014009-02 | NRC | NCV | Mitigating Systems | Green | Incomplete Corrective Actions To Prevent Recurrence |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 95002 | The inspectors identified a finding of very low significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving multiple examples where the licensee failed to ensure tha
Region: III | Duane Arnold | 10030 | 07/11/2014 08/29/2014 | 2014009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish EFR Attributes to Assess the Effectiveness of Corrective Actions |  | H.8 Procedure Adherence | TE?: N | 05000331 Duane Arnold |  | 95002 | The inspectors identified a finding of very low safety significance (Green)and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V,"Instructions, Procedures, and Drawings," for the failure to ensure the effectivenessreview (EFR) a
Region: III | Duane Arnold | 10014 | 06/30/2014 08/14/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ACCOMPLISH PROCEDURE FOR REPETITIVE MALFUNCTIONS OF REFUEL FLOOR RADIATION MONITOR. |  | H.13 Consistent Process | TE?: N | 05000331 Duane Arnold |  | 71111.12 | A finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to accomplish procedure EN-AA-2
Region: III | Duane Arnold | 10015 | 06/30/2014 08/14/2014 | 2014003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO ESTABLISH FIRE PATROLS AS COMPENSATORY ACTIONS IN ACCORDANCE WITH THE FIRE PROTECTION PROGRAM. |  | H.13 Consistent Process | TE?: N | 05000331 Duane Arnold |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated non-citied violation of Duane Arnold Energy Center (DAEC) Renewed Operating License Condition 2.C.(3), for the failure to implement compensatory measures for non-fu
Region: III | Duane Arnold | 10021 | 06/30/2014 08/14/2014 | 2014003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PRESCRIBE WORK ORDER PLANNING PROCEDURE APPROPRIATE TO THE CIRCUMSTANCES. |  | P.2 Evaluation | TE?: N | 05000331 Duane Arnold |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to prescribe a procedure appropriate to the cir
Region: III | Duane Arnold | 10012 | 10/30/2013 12/05/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Failed to Establish Measures for the Selection and Review for the Suitability of Safety-Related Cables. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71111.17T | he inspectors identified a finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," where the licensee failed to establish measures for the selectio
Region: III | Duane Arnold | 10013 | 10/30/2013 12/05/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Failed to Ensure the SBDG Power Cables Were Not Submerged. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality following discovery of water
Region: III | Duane Arnold | 10007 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | EXTENT OF CONDITION NOT PROPERLY EVALUATED. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71111.12 | A finding of very low safety significance and associated non-citied violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to accomplish safety-rela
Region: III | Duane Arnold | 10011 | 09/30/2013 11/14/2013 | 2013004-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO REPORT CHANNEL CHECKS. |  | P.1(b) Trend Performance CAP | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to prescribe a procedure with appropriate qualit
Region: III | Duane Arnold | 9997 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE OPERABILITY OF LOW PRESSURE COOLANT INJECTION FOLLOWING A POSTULATED LOCA IN MODE 3. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000331 Duane Arnold |  | NONE | A finding of very low safety significance (Green) and associated non-citied violation 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure the low pressure coolant injection (LPCI) mode of
Region: III | Duane Arnold | 9998 | 03/31/2013 05/09/2013 | 2013002-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO IMPLEMENT AND MAINTAIN PROCEDURES REGARDING BREATHING AIR QUALITY. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71124.03 | A finding of very low safety significance and associated non-cited violation of 10 CFR 20.1703 was identified by the inspectors on January 18, 2013, for the licensee's failure to implement and maintain written procedures regarding breathing air quality
Region: III | Duane Arnold | 10001 | 03/31/2013 05/09/2013 | 2013002-04 | Self - Revealed | NCV | Mitigating Systems | Green | CORRECTIVE ACTIONS ASSOCIATED WITH POTENTIAL CABLE SUBMERGENCE IMPROPERLY CLOSED. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance (Green) and associated non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on October 12, 2012, for the licensee's failure to meet corrective act
Region: III | Duane Arnold | 10002 | 03/31/2013 05/09/2013 | 2013002-05 | NRC | NCV | Barrier Integrity | Green | FAILURE TO CONDUCT ADEQUATE POST-MAINTENANCE TESTING. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to conduct post maintenance testing in accordance with proced
Region: III | Duane Arnold | 10006 | 03/31/2013 05/09/2013 | 2013002-06 | Self - Revealed | NCV | Initiating Events | Green | AVERAGE POWER RANGE MONITOR CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated non-citied violation of Technical Specification (TS) 3.3.1.1, "Reactor Protection System (RPS) Instrumentation," Required Action A, was self-revealed on December 1, 2012, for the licensee's failure
Region: III | Duane Arnold | 9996 | 03/31/2013 04/02/2013 | 2013007-01 | NRC | NCV | Barrier Integrity | Green | FUEL POOL RADIATION MONITOR CORRECTIVE ACTIONS. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | 71152B | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for two examples of the failure to follow procedures assoc
Region: III | Duane Arnold | 9981 | 12/31/2012 01/30/2013 | 2012005-01 | NRC | NCV | Public Radiation Safety | Green | LACK OF PROCEDURE LEADS TO OVER FILLING CONDENSATE STORAGE OVERFLOW TANK. |  | H.3(a) Work Planning | TE?: N | 05000331 Duane Arnold |  | 71111.13 | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified by the inspectors for the licensee's failure to establish a procedure for filling the condensate storage tanks (CSTs) from mul
Region: III | Duane Arnold | 9982 | 12/31/2012 01/30/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | DEGRADED/NON-CONFORMING CONDITIONS NOT PROPERLY EVALUATED. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors on October 17, 2012, for the licensee's failure to accomplish procedure EN-AA-20
Region: III | Duane Arnold | 9989 | 12/31/2012 01/30/2013 | 2012005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO MAKE SURVEYS TO EVALUATE THE POTENTIAL RADIOLOGICAL HAZARDS IN THE TORUS. |  | H.4(b) Procedural Compliance | TE?: N | 05000331 Duane Arnold |  | 71124.01 | A finding of very low safety significance and associated NCV of 10 CFR 20.1501 was self-revealed on October 16, 2012, for the licensee's failure to make surveys to evaluate the potential radiological hazards during work inside the torus. Specifically, ten
Region: III | Duane Arnold | 9990 | 12/31/2012 01/30/2013 | 2012005-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO ACCOMPLISH SAFETY/RELIEF VALVE TEST INSTRUCTIONS. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on October 24, 2012, for the licensee's failure to accomplish instructions for functional testi
Region: III | Duane Arnold | 9976 | 09/30/2012 10/25/2012 | 2012004-01 | Self - Revealed | NCV | Mitigating Systems | Green | DIESEL FIRE PUMP OVERHEATING DUE TO INADEQUATE TEST PROCEDURE. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000331 Duane Arnold |  | 71111.12 | A finding of very low safety significance and associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1.d, Fire Protection Program Implementation, was self-revealed on June 24, 2012, for the failure of the licensee to test the diesel fire
Region: III | Duane Arnold | 9975 | 06/30/2012 08/02/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | LACK OF PROCEDURES FOR MONITORING THE PERFORMANCE OF RHRSW PUMP MOTOR COOLING COILS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71111.07T | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to prescribe a procedure for activities affecting quality. Specifi
Region: III | Duane Arnold | 9974 | 06/30/2012 08/02/2012 | 2012003-02 | NRC | NCV | Barrier Integrity | Green | INADEQUATE TESTING FOLLOWING MAINTENANCE ON SECONDARY CONTAINMENT ISOLATION DAMPERS. |  | H.3(a) Work Planning | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors on May 31, 2012, for the licensee's failure to conduct post-maintenance tes
Region: III | Duane Arnold | 9963 | 03/31/2012 05/10/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | LACK OF ACCEPTANCE CRITERIA WITHIN EMERGENCY CORE COOLING SYSTEM SURVEILLANCE PROCEDURE. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 71111.22 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the inspectors on February 2, 2012, for the licensee's failure to prescribe a proce
Region: III | Duane Arnold | 9964 | 03/31/2012 05/10/2012 | 2012002-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO PROPERLY LABEL AND MAINTAIN LABELS ON CONTAINERS IN THE RADIOACTIVE WASTE FACILITY. |  | P.3(a) Self-Assessment | TE?: N | 05000331 Duane Arnold |  | 71124.08 | A finding of very low safety significance and associated NCV of 10 CFR 20.1904(a) was identified by the inspectors on January 31, 2012, due to the licensee's failure to label several containers holding radioactive material in the radioactive waste facilit
Region: III | Duane Arnold | 9965 | 03/31/2012 05/10/2012 | 2012002-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN TYPE A CONTAINER DESIGN TESTS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71124.08 | A finding of very low safety significance and associated NCV of 10 CFR 71.5 was identified by the inspectors on February 2, 2012, due to the licensee's failure to maintain a licensed material shipment on file for at least one year after the latest shipmen
Region: III | Duane Arnold | 9968 | 03/31/2012 05/10/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | BATTERY CONDITIONS ADVERSE TO QUALITY NOT PROMPTLY IDENTIFIED. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors on January 23, 2012, for the licensee's failure to promptly identify and correct safety relate
Region: III | Duane Arnold | 9969 | 03/31/2012 05/10/2012 | 2012002-05 | NRC | NCV | Barrier Integrity | Green | SECONDARY CONTAINMENT AIRLOCK DOOR INTERLOCK SYSTEM CONDITIONS ADVERSE TO QUALITY NOT PROMPTLY CORRECTED. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors on February 21, 2012, for the licensee's failure to promptly correct secondary containment (SC
Region: III | Duane Arnold | 9970 | 03/31/2012 05/10/2012 | 2012002-06 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CAUSAL EVALUATION AND CORRECTIVE ACTIONS FOR LOSS OF RHR SYSTEM LPCI SAFETY FUNCTION DUE TO INOPERABLE ECCS INSTRUMENTATION. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" was identified by the inspectors on March 7, 2012, following review of apparent cause evaluation (ACE) 01720033 associated with
Region: III | Duane Arnold | 9960 | 02/10/2012 03/06/2012 | 2012007-01 | NRC | NCV | Initiating Events | Green | Flammable Gas Bottles Installed in the Reactor Building (Section 1R05.11b) |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to check the adequacy of design for flammable gas b
Region: III | Duane Arnold | 9958 | 12/31/2011 01/31/2012 | 2011005-02 | Self - Revealed | NCV | Initiating Events | Green | CANCELLATION OF RIVER SURVEY WORK ORDER CAUSES INOPERABILITY OF RIVER WATER SYSTEM. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed on August 11, 2011, when both river water supply subsystems were rendered inoperable follo
Region: III | Duane Arnold | 9959 | 12/31/2011 01/31/2012 | 2011005-03 | Self - Revealed | NCV | Barrier Integrity | Green | PROCEDURAL NON-COMPLIANCE RESULTS IN REACTOR BUILDING CRANE COLLIDING WITH ISFSI INSPECTION STAND. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed on October 31, 2011, when operators failed to follow Operating Instruction 999, "Reactor B
Region: III | Duane Arnold | 9771 | 09/30/2011 10/21/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | DEGRADED OR NON-CONFORMING CONDITIONS NOT PROPERLY EVALUATED. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure on two occasions to follow procedure EN AA 203 1
Region: III | Duane Arnold | 9953 | 09/30/2011 10/21/2011 | 2011004-02 | Self - Revealed | NCV | Barrier Integrity | Green | MISPLACED SPENT FUEL ASSEMBLY IN SPENT FUEL POOL. |  | H.4(a) Human Error Prevention | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed on August 16, 2011, for the failure of the licensee to place a spent fuel assembly in its
Region: III | Duane Arnold | 9770 | 06/30/2011 08/02/2011 | 2011003-01 | Self - Revealed | NCV | Barrier Integrity | Green | WORK INSTRUCTIONS DID NOT INCLUDE REACTIVITY IMPACT EVALUATION FOR PREVENTATIVE MAINTENANCE ACTIVITY. |  | H.3(a) Work Planning | TE?: N | 05000331 Duane Arnold |  | 71111.19 | .A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when opening MO 1044 (main steam line drain orifice valve) to conduct preventive maintena
Region: III | Duane Arnold | 9761 | 04/28/2011 05/18/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Sufficient Thrust Margins for the 480 VAC Safety-Related MOVs. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to ensure sufficient thrust margins for 480 VAC
Region: III | Duane Arnold | 9762 | 04/28/2011 05/18/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Test Eight Valves in Accordance with the IST Program. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of Technical Specification 5.5.6, "Inservice Testing Program," for the failure to perform the required testing in accordance with the American S
Region: III | Duane Arnold | 9763 | 04/28/2011 05/18/2011 | 2011009-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Evaluation of RCIC Operation during an SBO. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) in that, the licensee did not adequately ensure the operation of the reactor core isolation cooling (RCIC) system was within the capability of the 125 VDC station batteries under
Region: III | Duane Arnold | 9756 | 03/31/2011 05/11/2011 | 2011002-01 | Self - Revealed | NCV | Barrier Integrity | Green | OPERATING INSTRUCTION DID NOT INCLUDE ADEQUATE CRITERIA PRIOR TO REMOVING PLANT PROCESS COMPUTER FROM SERVICE. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000331 Duane Arnold |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed following restoration of the plant process computer (PPC) from a planned maintenance activ
Region: III | Duane Arnold | 9757 | 03/31/2011 05/11/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE FIRE PATROLS IN AREAS CONTAINING SAFETY RELATED EQUIPMENT. |  | H.4(b) Procedural Compliance | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specification 5.4, "Procedures," was identified by the inspectors for the licensee's failure to conduct fire watch patrols in accordance with Attachment 7 of Administrative Control
Region: III | Duane Arnold | 9750 | 12/31/2010 02/01/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY WATER INTRUSION INTO CABLE VAULTS CONTAINING SAFETY RELATED CABLES. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure to promptly identify and correct a condition adverse to quality. Speci
Region: III | Duane Arnold | 9745 | 12/31/2010 02/01/2011 | 2010005-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEUDRE RESULTS IN A LOSS OF SHUTDOWN COOLING. |  |  | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated non-cited violation of Technical Specification Section 5.4.1.a was self revealed because procedure "OI 358, Reactor Protection System, Revision 58" was inadequate. Specifically, while transferring p
Region: III | Duane Arnold | 9754 | 12/31/2010 02/01/2011 | 2010005-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO COMPLY WITH REQUIREMENTS OF RWP. |  | H.4(b) Procedural Compliance | TE?: N | 05000331 Duane Arnold |  | 71124.01 | A finding of very low safety significance and an associated Non-Cited-Violation (NCV) of Technical Specification 5.4.1(a) was identified by the inspectors for the failure to implement adequate written procedures regarding the radiation safety program. Spe
Region: III | Duane Arnold | 9742 | 10/01/2010 11/08/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENT 3.8.1.6. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 3.8.1 for the licensee failing to perform TS Surveillance Requirement (SR) 3.8.1.6, which verifies the fuel oil transfer system operates
Region: III | Duane Arnold | 9743 | 09/30/2010 11/12/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | SURVEILLANCE TEST PROCEDURE DID NOT INCLUDE APPROPRIATE ACCEPTANCE CRITERA. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000331 Duane Arnold |  | 71111.22 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee?s failure to include appropriate acceptance criteria withi
Region: III | Duane Arnold | 9744 | 09/30/2010 11/12/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | CONDITION ADVERSE TO QUALITY NOT PROMPTLY IDENTIFIED AND CORRECTED. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 71111.22 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee?s failure to promptly identify and correct a condition adverse to quality on
Region: III | Duane Arnold | 9747 | 09/30/2010 11/12/2010 | 2010004-04 | NRC | FIN | Mitigating Systems | Green | ANSI STANDARDS FOR LICENSED OPERATORS NOT MET. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000331 Duane Arnold |  | 71111.11B | A non-cited violation (NCV) of 10 CFR 50.9, "Completeness and Accuracy of Information," was identified due to the submittal of inaccurate medical information for licensed operators. The submittals to the NRC were inaccurate because they certified that the
Region: III | Duane Arnold | 9739 | 06/30/2010 08/09/2010 | 2010003-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW THE PROCEDURES FOR PERFORMING OPERABILITY DETERMINATIONS. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure of the licensee to follow procedure EN-AA-203-1001, "Operab
Region: III | Duane Arnold | 9740 | 06/30/2010 08/09/2010 | 2010003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO ADEQUATELY DEFINE REQUIREMENTS AND PRESCRIBE A PROCEDURE APPROPRIATE FOR PLANT CONDITIONS. |  | P.1(b) Trend Performance CAP | TE?: N | 05000331 Duane Arnold |  | 71111.18 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to prescribe a procedure appropr
Region: III | Duane Arnold | 9734 | 06/09/2010 06/17/2010 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE TEH PAST OPERABILITY OF THE 'B' CONTROL BUILDING CHILLER CONDENSER. |  | P.3(a) Self-Assessment | TE?: N | 05000331 Duane Arnold |  | 71111.07T | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very- low-safety significance for the failure to evaluate the past operability of the 'B' control building chiller condenser follo
Region: III | Duane Arnold | 9735 | 06/09/2010 06/17/2010 | 2010008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO UPDATE THE UFSAR TO REFLECT REQUIRED COOLING TO THE RHR PUMP SEALS. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.07T | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very-low-safety significance for the failure to take corrective actions in response to a previous NCV concerning the residual heat removal pump seal
Region: III | Duane Arnold | 9738 | 06/09/2010 06/17/2010 | 2010008-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THE OPERABILITY OF LPCI IN MODE 3. |  |  | TE?: N | 05000331 Duane Arnold |  | 2515/177 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very-low-safety significance for the failure to correct the lack of barriers to prevent low pressure core injection (LPCI) from becom
Region: III | Duane Arnold | 9730 | 03/31/2010 05/14/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | INADEQUATE EVALUATIONS FOR CRANE AND SPECIAL LIFTING DEVICES. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.2 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for deficiencies in the design documents for the reactor building crane and the special lifting d
Region: III | Duane Arnold | 9731 | 03/31/2010 05/14/2010 | 2010002-02 | NRC | FIN | Mitigating Systems | Green | LIFT HEIGHT ASSUMPTIONS IN DROP LOAD ANALYSES NOT REFLECTED IN RIGGING PROCEDURES. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71111.2 | A finding of very low safety significance was identified by the inspectors for deficiencies in the design documents for failure to translate the lift height assumptions used in drop load evaluations into field instructions in appropriate rigging procedure
Region: III | Duane Arnold | 9732 | 03/31/2010 05/14/2010 | 2010002-03 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO CONDUCT AN ADEQUATE CRITIQUE FOR THE MAY 20, 2009, DRILL. |  | P.3(a) Self-Assessment | TE?: N | 05000331 Duane Arnold |  | NONE | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix E, Section IV.F.2.g, and of the emergency planning standard 10 CFR 50.47(b)(14) was identified by the inspectors for the failure of the critique to identify a plannin
Region: III | Duane Arnold | 9733 | 03/31/2010 05/14/2010 | 2010002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | AN INTERNAL CONTAMINATION OCCURRED WHILE CLEANING RPV STUDS AND WASHERS ON THE REFUEL FLOOR AT DUANE ARNOLD. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | NONE | A self revealed finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1(a) was identified for failure to establish and implement a procedure for performing decontamination activities associated with a potentially s
Region: III | Duane Arnold | 9719 | 12/31/2009 02/03/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | UNQUALIFIED SAFETY RELATED CABLES USED IN A SUBMERGED ENVIRONMENT. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the NRC for the failure to maintain 'A' Emergency Service Water (ESW) safety related cables in an environment for whi
Region: III | Duane Arnold | 9725 | 12/31/2009 02/03/2010 | 2009005-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW SURVEILLANCE TEST PROCEDURE RESULTS IN AUTOMATIC REACTOR SCRAM. |  | H.4(a) Human Error Prevention | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when Instrumentation and Controls (I&C) Technicians failed to fully shut an instrument isolatio
Region: III | Duane Arnold | 9726 | 12/31/2009 02/03/2010 | 2009005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION AND DIVING SURVEY REQUIREMENTS DURING WORK IN THE TORUS RESULTED IN UNNECESSARY RADIATION EXPOSURE. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 7112101 | An NRC-identified finding of very low safety significance and an associated Non Cited Violation (NCV) of Technical Specification 5.4.1(a) was identified for the failure to comply with the requirements of the "Diving Operation within Radiological Areas" pr
Region: III | Duane Arnold | 9729 | 12/15/2009 01/28/2010 | 2009013-01 | NRC | NCV | Mitigating Systems | Green | Failure To Implement Licensee Procedure PI-AA-205, "Condition Evaluation and Corrective Action" (02.03.f) | EA Case: 2009083 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 95001 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the inspector for the licensee's failure to implement the requirements of PI-AA-205, "Condition
Region: III | Duane Arnold | 9712 | 10/06/2009 10/29/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Address an Adverse Trend in Performing Required Fire Watches |  | P.1(b) Trend Performance CAP | TE?: N | 05000331 Duane Arnold |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation (NCV) of Technical Specifications, Paragraph 5.4.1.d, for the failure to identify an adverse trend in performing fire watches required as compensatory m
Region: III | Duane Arnold | 9713 | 09/30/2009 11/09/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN IMMEDIATE OPERABILITY DETERMINATION FOR THE 'B' STANDBY DIESEL GENERATOR. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for a failure of the Shift Manager to perform an Immediate Operability Determina
Region: III | Duane Arnold | 9717 | 09/30/2009 11/09/2009 | 2009004-02 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO MAINTAIN EAL SCHEME FOR RIVER LOW LEVEL. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71114.05 | A finding of very low safety significance and associated NCV of the emergency planning standard 10 CFR 50.47(b)(4) was identified by the inspectors. The finding involved an inadequate threshold for river water level indentified in the emergency classifica
Region: III | Duane Arnold | 9707 | 06/30/2009 08/05/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY IDENTIFY AND CORRECTA NONCONFORMING CONDITION ON A HPCI SUPPRESSION POOL SUCTION LINE SEISMIC RESTRAINT. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 71111.04Q | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for a failure of the licensee to promptly identify and correct a condition adverse to quality
Region: III | Duane Arnold | 9710 | 06/30/2009 08/05/2009 | 2009003-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE SURVEILLANCE TEST PROCEDURE REVISION RESULTS IN A PLANT SCRAM. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when Instrument and Controls (I&C) Technicians lifted a lead on a reactor water level recorder
Region: III | Duane Arnold | 9705 | 05/22/2009 06/26/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY IDENTIFY AND EVALUATE THE DEGRADED CONDITION ASSOCIATED WITH THE 'D' RWS PUMP MOUNTING BASE BOLTED CONNECTORS. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 71152B | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for a failure of the licensee to promptly identify and correct a condition adv
Region: III | Duane Arnold | 9695 | 03/31/2009 05/12/2009 | 2009002-02 | Self - Revealed | FIN | Initiating Events | Green | COOLING TOWER RISER BREAK LEADS TO MANUAL REACTOR SCRAM. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance was self revealed when the Operators exceeded the operational limit of the cooling tower riser by failing to secure one of the two running circulating water pumps prior to securing flow to the 'A' cooling tower. T
Region: III | Duane Arnold | 9702 | 03/31/2009 05/12/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM REQUIRED ACTIONS FOR EXISTING LCO CONDITIONS DURING IN-VESSEL FUEL MOVEMENTS. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated non-cited violation of Technical Specifications (TSs) was identified by the inspectors for the operators failing to perform required actions for existing limiting condition for operation (LCO) condi
Region: III | Duane Arnold | 9704 | 03/31/2009 05/12/2009 | 2009002-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO CONSIDER DESIGN BASIS LOAD IN EVALUATION FOR CONTINUED OPERATION. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to verify the adequacy of the methodology and design inputs used to support licen
Region: III | Duane Arnold | 9691 | 12/31/2008 02/06/2009 | 2008005-01 | NRC | NCV | Barrier Integrity | Green | HPCI STEAM EXHAUST VACUUM BREAKER PIPING CONFIGURATION NOT IN CONFORMANCE WITH PIPING DESIGN BASIS ANALYSIS OF RECORD. |  |  | TE?: N | 05000331 Duane Arnold |  | NONE | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspector for the failure of the high pressure coolant injection vacuum breaker piping configuration to be i
Region: III | Duane Arnold | 9664 | 09/30/2008 04/27/2007 | 2007002-06 | NRC | URI | Occupational Radiation Safety | Green | CONTRACTOR/SUPERVISOR MOVING REACTOR CAVITY LIGHTS FROM THE SPENT FUEL POOL TO THE REACTOR CAVITY WITHOUT NOTIFYING THE HEALTH PHYSICS TECHNICIAN. |  |  | TE?: N | 05000331 Duane Arnold |  | 7112102 | DAEC TS 5.4.1 provides, in part, that written procedures shall be established, implemented, and maintained covering the applicable procedures recommended in Regulatory Guide 1.33 Revision 2, Appendix A, February 1978. Section 2 of Appendix A to Regulatory
Region: III | Duane Arnold | 9687 | 09/30/2008 11/04/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE ASSESSMENT OF ECCS ROOM COOLER FAN MOTOR BEARING NONCONFORMING CONDITION. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and associated NCV of Technical Specification (TS) Section 5.4.1.a, associated with Regulatory Guide 1.33, Revision 2, Appendix A, Section 9, was identified by the inspectors when the licensee failed to adequately
Region: III | Duane Arnold | 9688 | 09/30/2008 11/04/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM A TS SURVEILLANCE REQUIREMENT FOR THE HPCI SYSTEM WITHIN THE SPECIFIED FREQUENCY. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000331 Duane Arnold |  | 71111.18 | A finding of very low safety significance and associated NCV of 10 CFR 50 Appendix B, Criterion III, "Design Control" was identified by the inspectors for the licensee's failure to assure that applicable regulatory requirements and design basis were corre
Region: III | Duane Arnold | 9683 | 03/31/2008 05/02/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PROPERLY ADMINISTER AND DOCUMENT OVERTIME LIMITS, REQUIREMENTS, AND DEVIATIONS. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance, and an associated NCV of Technical Specification (TS) 5.2.2.e, Administrative Controls, Organization, Unit Staff, was identified by the inspectors for the licensee's failure to follow the Administrative Control P
Region: III | Duane Arnold | 9684 | 03/14/2008 04/24/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations/Analyses for Essential 4160 VAC Circuit Breaker Close/Open Coils (1R21.3.b.(1)) |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to assure and verify that adequate control voltage was available for the
Region: III | Duane Arnold | 9685 | 03/14/2008 04/24/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations/Analyses and Testing for TOLs on Safety-Related MOVs (1R21.3.b.(2)) |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to assure that thermal overload relays (TOLs) on safety-related motor-ope
Region: III | Duane Arnold | 9686 | 03/14/2008 04/24/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Test Reactor Protection System Key Lock Bypass Switches (1R21.6.b.(1)) |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the failure to test reactor protection system (RPS) key locked bypass switches. The lice
Region: III | Duane Arnold | 9681 | 12/31/2007 02/08/2008 | 2007005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO ADEQUATELY SURVEY RESULTING IN UNPOSTED, UNCONTROLLED HIGH RADIATION AREA. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 7112102 | A self-revealed finding of very low safety significance and an associated Non¡Cited Violation (NCV) of Title 10 CFR 20.1501 were identified for failure to adequately survey and evaluate the magnitude and extent of radiation levels to ensure that high radi
Region: III | Duane Arnold | 9654 | 10/19/2007 11/21/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | DROP LOAD EVALUATION FOR STUD TENSIONER. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111102 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance for the failure to translate the design bases into procedures and instructions. Specifically, the lift height limit a
Region: III | Duane Arnold | 9674 | 10/19/2007 11/21/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ACCOUNT FOR DELAYS IN ECCS MOVS DUE TO VOLTAGE DIPS DURING LOAD SEQUENCING. |  |  | TE?: N | 05000331 Duane Arnold |  | 7111102 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance. Specifically, MOV stroke time delays which result from Emergency Diesel Generator (EDG) voltage drops during load se
Region: III | Duane Arnold | 9675 | 10/19/2007 11/21/2007 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO INITIATE A CORRECTIVE ACTION DOCUMENT FOR DEGRADING CABLING. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000331 Duane Arnold |  | 7111117B | The inspections identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," that was of very low safety significance. Specifically, the licensee found safety related cable 1S0104-E to be severely degraded due to
Region: III | Duane Arnold | 9670 | 09/30/2007 10/31/2007 | 2007004-01 | NRC | NCV | Initiating Events | Green | INADEQUATE RECIRCULATION RISER WELD EXAMINATION (NOZZLE N2F). |  |  | TE?: N | 05000331 Duane Arnold |  | NONE | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V for the licensee's failure to follow an ultrasonic examination procedure used to examine recirculation riser safe-end to nozzle weld RRF-F002. Specifically, t
Region: III | Duane Arnold | 9671 | 09/30/2007 10/31/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY USE ERROR PREVENTION TOOLS RESULTS IN A LOSS OF SAFETY FUNCTION BY INSTALLING A RELAY JUMPER ON THE INCORRECT RELAY. |  | H.4(a) Human Error Prevention | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and an associated NCV of TS 5.4.1a, associated with Regulatory Guide 1.33, Revision 2, Appendix A, Section 8 were identified through a self-revealing event when the licensee failed to properly implement procedures
Region: III | Duane Arnold | 9678 | 09/30/2007 10/31/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Calculations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71153 | Green. The inspectors identified a finding having very low safety significance and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to verify the adequacy of design calcula
Region: III | Duane Arnold | 9665 | 06/30/2007 08/07/2007 | 2007003-01 | Self - Revealed | NCV | Mitigating Systems | Green | LIFTING OF HPCI DISCHARGE RELIEF VALVE DURING PLANNED SURVEILLANCE TESTING. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR 50 Appendix B, Criterion 3, was self-revealed when PSV2302, the HPCI discharge pressure relief valve, stuck open during planned testing of the High Pressure Co
Region: III | Duane Arnold | 9666 | 06/30/2007 08/07/2007 | 2007003-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IMPLEMENT THE APPROPRIATE PROCEDURAL CONTROLS PRIOR TO USING NYLON ROPE TO SECURE UNDERWATER LIGHTS IN THE SPENT FUEL POOL. |  | H.4(b) Procedural Compliance | TE?: N | 05000331 Duane Arnold |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50 Appendix B, Criterion 5, when licensee staff failed to implement the appropriate controls to properly store underwater lights in the spent fuel pool. Th
Region: III | Duane Arnold | 9667 | 06/30/2007 08/07/2007 | 2007003-04 | Self - Revealed | NCV | Mitigating Systems | Green | TS ALLOWED OUTAGE TIME EXCEEDED FOR INOPERABLE EDGs. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 3.8.1.b, Electrical Power Systems, AC Sources-Operating, was self-revealed when a leak was discovered coming from the lube oil filter (LOF) cover on the 'B' Em
Region: III | Duane Arnold | 9669 | 06/30/2007 08/07/2007 | 2007003-05 | Self - Revealed | FIN | Initiating Events | Green | OPERATORS FAILED TO CONTROL A CRITICAL PARAMETER AND RECEIVED A SUBSEQUENT AUTOMATIC SCRAM SIGNAL. |  |  | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance was self-revealed regarding the failure of the control room crew to establish control of a critical parameter, Reactor Pressure Vessel (RPV) level, in a timely manner during the feedwater recovery efforts followin
Region: III | Duane Arnold | 9653 | 03/31/2007 04/27/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM QUALIFIED UT REACTOR VESSEL SHELL WELDS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71111.08G | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR 50.55a(g)4 for failure to complete a Code qualified volumetric examination of the reactor vessel shell welds during the previous refueling outage No.19. Specifically, the licensee used a long
Region: III | Duane Arnold | 9655 | 03/31/2007 04/27/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | UNQUALIFIED MAIN STEAM SAFETY RELIEF VALVE WELD REPAIR. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000331 Duane Arnold |  | 71111.08G | The inspectors identified a NCV of 10 CFR 50.55a(g)4 for failure to complete Code qualified weld repairs for the main steam safety relief valve PSV-4401. Specifically, the weld procedures for this repair were not qualified by performing tensile and guided
Region: III | Duane Arnold | 9656 | 03/31/2007 04/27/2007 | 2007002-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO INCLUDE ACCEPTANCE CRITERIA IN TROUBLESHOOTING INSTRUCTION FORM FOR CONTROL BUILDING STANDBY FILTER UNIT TESTING. |  | H.3(b) Work Activity Coordination | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion 5, was identified by the inspectors when engineering and operations personnel failed to include acceptance criteria in a Troubleshooting Instruction Form (
Region: III | Duane Arnold | 9657 | 03/31/2007 04/27/2007 | 2007002-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | WORKERS INAPPROPRIATELY ENTERED A HIGH RADIATION AREA. |  | H.4(a) Human Error Prevention | TE?: N | 05000331 Duane Arnold |  | 7112101 | A self-revealed finding of very low safety significance and an associated NCV of TS 5.7.1 were identified for the failure to satisfy TS requirements for worker access into a high radiation area with dose rates in accessible areas between 100 and 1000 mrem
Region: III | Duane Arnold | 9661 | 03/31/2007 04/27/2007 | 2007002-07 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TAKE PROMPT CORRECTIVE ACTION TO CORRECT AN OPERABLE BUT NONCONFORMING CONDITION ON THE EMERGENCY DIESEL GENERATORS. |  |  | TE?: N | 05000331 Duane Arnold |  | 71152 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion 16, was identified by the inspectors for failure to take prompt corrective action to repair an operable but nonconforming condition on the 'A' and 'B' Emer
Region: III | Duane Arnold | 9662 | 03/31/2007 04/27/2007 | 2007002-08 | Self - Revealed | NCV | Initiating Events | Green | UNPLANNED REACTOR PROTECTION SYSTEM AUTOMATIC SCRAM DUE TO INADEQUATE PROCEDURE. |  | H.4(a) Human Error Prevention | TE?: N | 05000331 Duane Arnold |  | 71153 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion 5, was self-revealed when an unplanned RPS reactor scram occurred during surveillance testing due to a scram discharge volume (SDV) high level. On March 2,
Region: III | Duane Arnold | 9650 | 02/11/2007 03/02/2007 | 2006008-01 | NRC | NCV | Mitigating Systems | Green | Recorded Pressure above Design Limits Not Entered into Corrective Action System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" having very low safety significance (Green). Specifically, the licensee failed to identify and correct a condition adverse to quality regardi
Region: III | Duane Arnold | 9651 | 02/11/2007 03/02/2007 | 2006008-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative Analysis Methodology |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000331 Duane Arnold |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green). Specifically, the licensee's calculation to show that the existing feedwater piping system configu
Region: III | Duane Arnold | 9648 | 12/31/2006 01/24/2007 | 2006005-01 | NRC | FIN | Mitigating Systems | Green | CREW PERFORMANCE ON THE DYNAMIC SCENARIO PORTION OF THE 2006 FACILITY-ADMINISTERED ANNUAL REQUALIFICATION EXAMINATION OPERATING TEST. |  | H.1(c) Communication of Decisions | TE?: N | 05000331 Duane Arnold |  | NONE | A finding of very low safety significance was identified. The finding was associated with unsatisfactory operating crew performance on the simulator during facility-administered licensed annual operator requalification examinations. Of the ten crews evalu
Region: III | Duane Arnold | 9631 | 06/30/2006 07/19/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE RISK ASSESSMENT. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.13 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to conduct an adequate risk assessment of the Standby Liquid Control System (SLCS) which was removed from service for scheduled surveillances December 1,
Region: III | Duane Arnold | 9614 | 04/21/2006 06/05/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | Calculation Deficiency for Potential Vortexing in CST |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the calculation of low level setpoints for the CST. Specifically, the licensee did not include a quan
Region: III | Duane Arnold | 9615 | 04/21/2006 06/05/2006 | 2006007-02 | NRC | NCV | Barrier Integrity | Green | RCIC Pump Suction Valves Automatic Control Logic |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the control logic of reactor core isolation cooling (RCIC) pump suction valves MO-2516 and MO-2
Region: III | Duane Arnold | 9620 | 04/21/2006 06/05/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Torquing of 250Vdc, 125Vdc and 48Vdc Batteries Electrical Connections |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving licensee's failure to ensure that the torque values specified in the maintenance procedure for safety
Region: III | Duane Arnold | 9621 | 04/21/2006 06/05/2006 | 2006007-04 | NRC | NCV | Mitigating Systems | Green | Electrical Components Downgraded from SR to NSR Without Appropriate Isolation Devices |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," having very low safety significance for failure to ensure that proper design control was maintained. Specifically, the licensee failed to perform a compr
Region: III | Duane Arnold | 9622 | 04/21/2006 06/05/2006 | 2006007-05 | NRC | NCV | Mitigating Systems | Green | UFSAR Table 8.2-1 Had No Documented Basis |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, Design Control, having a very low safety significance pertaining to lack of design basis for the values listed in Updated Final Safety Analysis Report Table 8.1-2. The
Region: III | Duane Arnold | 9623 | 04/21/2006 06/05/2006 | 2006007-06 | NRC | NCV | Mitigating Systems | Green | Non-Safety Related Charger Used to Charge a Cell of a 125Vdc SR Battery Without Electrical Isolation |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of TS 5.4.1a, "Procedures," having a very low safety significance pertaining to licensee's failure to establish and use an appropriate procedure for charging a single cell of a safety related battery. A portable
Region: III | Duane Arnold | 9625 | 04/21/2006 06/05/2006 | 2006007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Testing Program for Molded Case Circuit Breakers (MCCBs) |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance for failure to implement a testing program to ensure that the installed safety related and important-to-safety mol
Region: III | Duane Arnold | 9630 | 04/21/2006 06/05/2006 | 2006007-09 | NRC | NCV | Mitigating Systems | Green | Simulation of Operator response to an SBO event |  |  | TE?: N | 05000331 Duane Arnold |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for failing to maintain adequate procedures to establish alternate ventilation within a m
Region: III | Duane Arnold | 9610 | 03/31/2006 04/27/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE PROPER DESIGN CONTROL WAS MAINTAINED WITH THE SBDG. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance was identified by the inspectors for the failure to ensure proper design control was maintained during loading of the standby diesel generators (SBDG). The licensee entered this issue into their corrective action
Region: III | Duane Arnold | 9611 | 03/31/2006 04/27/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE PROPER DESIGN CONTROL WAS MAINTAINED WITH THE FEEDWATER PIPING HANGERS. |  |  | TE?: N | 05000331 Duane Arnold |  | 71111.15 | A finding of very low safety significance was identified by the inspectors for the failure to ensure proper design control was maintained with feedwater piping hangers DBD-4-H57A and DBD-4-H50A. The primary cause of this finding was related to the cross-c
Region: III | Duane Arnold | 9613 | 03/31/2006 04/27/2006 | 2006002-04 | NRC | FIN | Public Radiation Safety | Green | FAILURE TO MEET INDUSTRY STANDARDS FOR THE UNCONDITIONAL RELEASE OF BULK AGGREGATE LIQUID AND SOLID MATERIALS. |  |  | TE?: N | 05000331 Duane Arnold |  | 7112201 | An inspector-identified finding of very low safety significance was identified for the failure to meet the industry standard of using the environmental Lower Limit of Detection (LLD) when surveying, and analyzing bulk aggregate and liquid materials prior
Region: III | Fermi | 126150 | 12/31/2019 02/07/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to have Appropriate Instructions for Determining the Average Sediment Depth in the Residual Heat Removal Complex Reservoir |  | H.13 - Consistent Process | TE?: N | 05000341 Fermi 2 | Procedure Quality | 71111.07T | A finding of very low safety significance (Green) and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulation (CFR), Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings”, was identified by the inspectors due t
Region: III | Fermi | 126398 | 12/31/2019 02/07/2020 | 2019004-02 | Self - Revealed | FIN | Barrier Integrity | Green | Inadequate Relay Replacement Frequency Causes Momentary Loss of Secondary Containment Vacuum |  | NPP | TE?: N | 05000341 Fermi 2 | SSC and Barrier Performance | 71111.12 | A self-revealed Green finding was identified when the licensee failed to follow site procedure MES51, "Preventative Maintenance Program." Specifically, the licensee failed to replace a relay within the vendor recommended interval due to an inappropriate a
Region: III | Fermi | 125514 | 09/30/2019 11/06/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Datum Used to Assess Lake Levels |  | NPP | TE?: N | 05000341 Fermi 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance (i.e., Green) and an associated Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," when licensee personnel failed to have appropriate measures in place t
Region: III | Fermi | 125712 | 09/30/2019 11/06/2019 | 2019003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Response to an Out-of-Service Diesel Fire Pump |  | H.5 - Work Management | TE?: N | 05000341 Fermi 2 | Protection Against External Factors | 71111.18 | A self-revealed finding of very low safety significance (i.e., Green) and an associated Non-Cited Violation (NCV) of Fermi License Condition 2.C.(9) was identified when licensee personnel failed to take appropriate actions in response to an out-of-service
Region: III | Fermi | 125704 | 09/30/2019 11/06/2019 | 2019003-03 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Properly Pre-Plan Work in Accordance with the Work Control Conduct Manual |  | H.7 - Documentation | TE?: N | 05000341 Fermi 2 | SSC and Barrier Performance | 71153 | A self-revealed finding of very low safety significance (i.e., Green) was identified when the licensee failed to properly pre-plan maintenance activities on the Feedwater Distributed Control System in accordance with the Work Control Conduct Manual. This
Region: III | Fermi | 125038 | 07/10/2019 07/29/2019 | 2019012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Acceptance Limits Contained in High Pressure Coolant Injection Design Documents into Test Procedure |  | H.8 - Procedure Adherence | TE?: N | 05000341 Fermi 2 |  | 71111.21M | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50 Appendix B, Criterion XI, “Test Control,” for the licensee’s failure to i
Region: III | Fermi | 125078 | 07/10/2019 07/29/2019 | 2019012-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Motor-Operated Valve Output Torque Capacity Methodology |  | NPP | TE?: N | 05000341 Fermi 2 | Design Control | 71111.21M | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, “Design Control,” for the licensee's failure to
Region: III | Fermi | 125162 | 06/30/2019 07/26/2019 | 2019002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Verify the Adequacy of the Design of the Reactor Building to Suppression Chamber Vacuum Breakers |  | NPP | TE?: N | 05000341 Fermi 2 | Design Control | 71153 | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors when the licensee failed to verify the adequacy of the design of the reactor
Region: III | Fermi | 124702 | 03/31/2019 05/09/2019 | 2019001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Secondary Containment Rendered Inoperable Due to Improper Operation of Airlock Doors |  | H.12 - Avoid Complacency | TE?: N | 05000341 Fermi 2 | Human Performance | 71111.12 | A self-revealed finding of very low safety significance (i.e., Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when workers failed to operate secondary containment airlock doors
Region: III | Fermi | 124750 | 03/31/2019 05/09/2019 | 2019001-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Evaluate the Operability and Functionality Impacts of Various Systems and Components Following a Trip of Division 1 24/48 Volt Direct Current Battery Charger 2IA-2 |  | H.11 - Challenge the Unknown | TE?: N | 05000341 Fermi 2 |  | 71111.15 | A finding of very low safety significance (i.e., Green) was identified by the inspectors for the licensee’s failure to adequately evaluate the operability and functionality of various structures, systems, and components (SSCs) following a trip of Division
Region: III | Fermi | 124443 | 03/31/2019 05/09/2019 | 2019001-03 | NRC | NCV | Mitigating Systems | Green | Torus Coating Work Not Covered Under Work Hour Rules |  | H.7 - Documentation | TE?: N | 05000341 Fermi 2 | Equipment Performance | 71111.2 | A finding of very low safety significance (i.e., Green) and an associated NCV of 10 CFR 26.205(c) and (d) was identified by the inspectors when the licensee failed to appropriately schedule and control the work hours of eight workers that performed or dir
Region: III | Fermi | 25946 | 12/31/2018 02/13/2019 | 2018004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Rigging and Lifting Practices Result in Damage to Division 2 Residual Heat Removal Structures and Components |  | H.12 - Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71111.13 | A finding of very low safety significance was self-revealed for the licensee’s failure to follow site standards and procedures for safe rigging and handling practices while lifting the division 2 residual heat removal service water outlet flow control val
Region: III | Fermi | 25949 | 12/31/2018 02/13/2019 | 2018004-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Obtain Radiological Briefing Prior to Entry Into a High Radiation Area |  | H.4 - Teamwork | TE?: N | 05000341 Fermi 2 |  | 71124.01 | A self-revealed Green finding and associated Non-Cited Violation (NCV) of Technical Specification (TS) 5.4.1, Procedures, and TS 5.7.1, High Radiation Areas (HRAs), was identified when radiation workers violated Radiation Work Permit (RWP) requirements by
Region: III | Fermi | 25950 | 12/31/2018 02/13/2019 | 2018004-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Establish Radiological Conditions For Locked High Radiation Area Entry |  | H.10 - Bases for Decisions | TE?: N | 05000341 Fermi 2 |  | 71124.01 | A self-revealed Green finding and associated NCV of TS 5.7.2, High Radiation Areas, was identified when RP staff allowed workers to enter an area of a Locked High Radiation Area (LHRA) where radiological conditions had not been established. RP staff
Region: III | Fermi | 25951 | 12/31/2018 02/13/2019 | 2018004-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of Design of the 4160 Volt Safety Bus 64B, 64C, 65E, and 65F Degraded Voltage Protection Schemes |  | NPP | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance and associated non-cited violations of 10 CFR Part 50, Appendix B, Criterion III, “Design Control”; Technical Specification (TS) 3.3.8.1 “Loss of Power (LOP) Instrumentation; TS 3.5.1 “ECCS – Operating”; and TS 3.
Region: III | Fermi | 25952 | 12/31/2018 02/13/2019 | 2018004-07 | Self - Revealed | FIN | Initiating Events | Green | Rainwater Intrusion into Degraded Metal-Clad Enclosure for Bus 1-2B Results in Partial Loss of Offsite Power, Reactor Scram, and Emergency Core Cooling System Initiation |  | H.12 - Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance was self-revealed on April 14, 2018 when rainwater intrusion into a degraded, metal-clad enclosure for Bus 1-2B switchgear in the Division 1 (120 kilo-volt) switchyard caused a partial loss of offsite power, subse
Region: III | Fermi | 24679 | 09/30/2018 11/08/2018 | 2018003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Apply Torque Values Described in Maintenance Procedure for Flexible Couplings on Emergency Diesel Generator 12 |  | P.3 - Resolution | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated non-cited violation of Technical Specification 5.4.1.a was self-revealed when plant operators discovered a pencil-thick lube oil leak coming from a flexible coupling on emergency diesel generato
Region: III | Fermi | 24680 | 09/30/2018 11/08/2018 | 2018003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure Electrolytic Capacitors Installed in the Plant Did Not Have Expired Shelf Lives |  | H.7 - Documentation | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated non-cited violation of 10 CFR 50, Appendix B, Criterion VIII, “Identification and Control of Materials, Parts, and Components” was self-revealed when the reactor water cleanup system inlet flow
Region: III | Fermi | 24351 | 06/30/2018 08/14/2018 | 2018002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Document a Condition Assessment Resolution Document for Reactor Recirculation Motor-Generator Set 'A' Brush Gear Sparking |  | H.14 - Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 71111.11Q | A self-revealed Green finding was identified for failure to document a Condition Assessment Resolution Document (CARD) for 5-inch rooster tail sparking on reactor recirculation motor generator set ‘A’ brush gear, which ultimately resulted in a manual reci
Region: III | Fermi | 24352 | 06/30/2018 08/14/2018 | 2018002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Preventative Maintenance in Residual Heat Removal Service Water System Outlet Flow Control Valves Results in Lower Bonnet (Backseat) Bushing Failure |  | P.2 - Evaluation | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A self-revealed Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings” were identified for the licensee’s failure to ensure activities affecting quality were prescribed in a manner consistent
Region: III | Fermi | 24366 | 06/30/2018 08/14/2018 | 2018002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate the Operability of Emergency Diesel Generator 11 |  | P.2 - Evaluation | TE?: N | 05000341 Fermi 2 |  | 71111.15 | A finding of very low safety significance was self-revealed for the licensee’s failure to adequately evaluate the operability of a condition adverse to quality identified on Emergency Diesel Generator 11. Specifically, a lube oil leak was evaluated as hav
Region: III | Fermi | 24367 | 06/30/2018 08/14/2018 | 2018002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality on Division 2 Residual Heat Removal |  | H.11 - Challenge the Unknown | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed TBD finding and an apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” and TS 3.7.1 “Residual Heat Removal Service Water (RHRSW) System”, were self-revealed for the licensee’s failure to identify a conditi
Region: III | Fermi | 25932 | 03/31/2018 05/10/2018 | 2018001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Incorporate Vendor Recommendations into Maintenance Instructions on the Division 1 Control Complex Heating Ventilation and Air Conditioning Supply Fan Motor |  | H.7 - Documentation | TE?: N | 05000341 Fermi 2 |  | 71111.19 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was self-revealed for the licensee’s failure to include instructions for maintenance on the
Region: III | Fermi | 23155 | 02/02/2018 02/02/2018 | 2017004-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Fit Testing on Self-Contained Breathing Apparatus Respirators |  | H.14 - Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 71124.03 | A finding of very-low safety significance (Green) and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations (CFR), Part 20.1703(c)(6) was identified by the inspectors for the licensee’s failure to perform fit testing for the se
Region: III | Fermi | 21664 | 09/30/2017 11/13/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Technical Specification Allowed Outage Time Exceeded for Electrical Power Distribution Systems Due to Auxiliary Equipment Out of Service |  | H.1 - Resources | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a Non-Cited Violation (NCV) of Technical Specification (TS) 3.8.7 "Distribution Systems – Operating," for the licensee’s failure to either restore inoperable Division 1 and Division 2 AC electrical power distribution subsystems t
Region: III | Fermi | 21675 | 09/14/2017 10/26/2017 | 2017407-01 | NRC | NCV | Mitigating Systems | Green | Challenges Implementing Offsite Notifications |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | The inspectors identified a finding of very-low safety significance (Green) and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50.54(hh)(1) for the licensee’s failure to implement and maintain procedures that describe
Region: III | Fermi | 27658 | 06/30/2017 08/09/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Maintenance on EDG 14 |  | H.7 Documentation | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when plant operators were not able to shut down emergency diesel generator
Region: III | Fermi | 27661 | 06/30/2017 08/09/2017 | 2017002-02 | NRC | NCV | Barrier Integrity | Green | Unacceptable Preconditioning of High Pressure Coolant Injection System Air Operated Valve Prior to Stroke Time Test Measurement |  | P.3 Resolution | TE?: N | 05000341 Fermi 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to establish an adequate procedure to perform r
Region: III | Fermi | 27662 | 06/23/2017 08/01/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Design Deficiency that Mis-Quantified Unidentified Leakage |  |  | TE?: N | 05000341 Fermi 2 |  | 71152B | The inspectors identified a finding of very low safety significance with an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to correct a design de
Region: III | Fermi | 27666 | 06/15/2017 07/20/2017 | 2017010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Internal Heat Rise for Protective Devices Settings (Section 1R21.3.b(1)) |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.21N | Green. The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that
Region: III | Fermi | 27667 | 06/15/2017 07/20/2017 | 2017010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Calculate the Post Accident Operating Time (Section 1R21.3.b(2)) |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.21N | Green. The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR 50.49, Paragraph (e) (1), "Environmental Qualification of Electrical Equipment Important to Safety for Nuclear Power Plants," for the licens
Region: III | Fermi | 27668 | 06/15/2017 07/20/2017 | 2017010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Environmental Qualification Requirements into Maintenance Procedures (Section 1R21.3.b(3)) |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.21N | Green. The inspectors identified a finding of very-low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to translate Environmental Qualification Requirements into Maintenance Proced
Region: III | Fermi | 27643 | 03/31/2017 05/01/2017 | 2017001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Maintenance on Emergency Diesel Generator 14 |  | H.7 Documentation | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when plant operators discovered a thick white smoke plume coming from the e
Region: III | Fermi | 27644 | 03/31/2017 05/01/2017 | 2017001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Standby Liquid Control Storage Tank Boron Concentration |  | H.1 Resources | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of TS 3.1.7, "Standby Liquid Control (SLC) System," was self-revealed when the licensee measured the boron concentration in the SLC storage tank and discovered the concentrat
Region: III | Fermi | 27631 | 12/31/2016 01/30/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Maintenance on Flexible Couplings for EDGs |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when plant operators discovered an oil
Region: III | Fermi | 27639 | 12/31/2016 01/30/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Interpret and Implement TS Requirements for LOP Instrumentation and AC Electrical Power Functions |  | H.9 Training | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated NCV of TS 3.3.8.1, "Loss of Power (LOP) Instrumentation," and TS 3.8.1, AC [Alternating Current] Sources - Operating." The licensee failed to satisfy applicable action
Region: III | Fermi | 27641 | 12/31/2016 01/30/2017 | 2016004-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Testing of SGTS Filters |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated NCV of TS 5.5.7, "Ventilation Filter Testing Program." The licensee failed to perform testing of the standby gas treatment system (SGTS) high-efficiency particulate air
Region: III | Fermi | 27642 | 12/31/2016 01/30/2017 | 2016004-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Lock an Area Meeting Locked High Radiation Area Conditions |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | NONE | A finding of very low safety significance with an associated NCV of TS 5.7.2, "High Radiation Area," was self-revealed when a locked high radiation area (LHRA) was found to be unlocked. The licensee immediately locked the LHRA and performed follow-up surv
Region: III | Fermi | 27585 | 09/30/2016 11/14/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination for Division 1 RPV Reference Leg Backfill System Not Providing Adequate Flow |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to complete an operability determination
Region: III | Fermi | 27591 | 09/30/2016 11/14/2016 | 2016003-03 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures During Concrete Placement of Flexible Storage Facility Buildings |  | H.8 Procedure Adherence | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified a finding of very low safety significance when licensee personnel failed to follow the applicable procedure and design specification during concrete placement for installation of Diverse and Flexible Coping Strategies (FLEX) Buil
Region: III | Fermi | 27592 | 09/28/2016 11/10/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Addressing Non Functional MDCT Fan Motor Brake System (Section 1R21.3.b(1)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee failure t
Region: III | Fermi | 27593 | 09/28/2016 11/10/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Voltage Supplied to Transformer #64 Load Tap Changer (Section 1R21.3.b(2)) |  | P.6 Self Assessment | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the voltage supplied to the transformer #64 load t
Region: III | Fermi | 27599 | 09/28/2016 11/10/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Ability to Manually Throttle Safety-Related MOVs during a DBA (Section 1R21.3.b(3)) |  | H.4 Teamwork | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the capability to manually throttle safety-related motor-operated
Region: III | Fermi | 27600 | 09/28/2016 11/10/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Test the EDG Capability to Start and Accelerate All of the Sequenced Loads Within the Applicable Limits (Section 1R21.3.b(4)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to periodically test the emergency diesel generator (EDG) capacity to start and
Region: III | Fermi | 27601 | 09/28/2016 11/10/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Leak Test All Division 2 NIAS Boundary Isolation Valves (Section 1R21.3.b(5)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to leak test all Division 2 non-interruptible control air system (NI
Region: III | Fermi | 27607 | 09/28/2016 11/10/2016 | 2016007-06 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure that the MSIVs Would Close Within the TS Required Timeframe and as Described in the UFSAR (Section 1R21.3.b(6)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that the main steam isolation valves (MSIVs) would clo
Region: III | Fermi | 27608 | 09/28/2016 11/10/2016 | 2016007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Protective Devices for the Loads Required at the Beginning of a LOCA Would Not Trip Under Degraded Voltage Conditions (Section 1R21.4.b(1)) |  | P.6 Self Assessment | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that the protective devices for the loads required at t
Region: III | Fermi | 27609 | 09/28/2016 11/10/2016 | 2016007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Containment Debris Inspections Acceptance Criteria (Section 1R21.4.b(2)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish procedures that were appropria
Region: III | Fermi | 27612 | 09/28/2016 11/10/2016 | 2016007-09 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Acceptability of Drywell Coatings with Respect to Potential ECCS Suction Strainer Blockage (Section 1R21.4.b(3)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate the acceptability of drywell coatings with respect to
Region: III | Fermi | 27613 | 09/28/2016 11/10/2016 | 2016007-10 | NRC | NCV | Mitigating Systems | Green | Non Conservative ECCS Suction Strainer Min-K Combined Generation and Transport Factors (Section 1R21.4.b(4)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to use the min-K insulation debris generation and transport fact
Region: III | Fermi | 27614 | 09/28/2016 11/10/2016 | 2016007-11 | NRC | NCV | Mitigating Systems | Green | Failure to Apply Design Control Measures to a Design Change Associated with NIAS Accumulator Capability (Section 1R21.5.b(1)) |  | H.6 Design Margins | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green: The team identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to apply design control measures to a design change associated w
Region: III | Fermi | 27620 | 09/28/2016 11/10/2016 | 2016007-12 | NRC | NCV | Mitigating Systems | Green | Failure to Identify an Out-of-Specification Pressure Reading on the Nitrogen Supply to the "A" MDCT Fan Motor Brake System (Section 4OA2.1.b(1)) |  | H.4 Teamwork | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify that the 'A' MDCT fan motor brake system 100 psi n
Region: III | Fermi | 27621 | 09/28/2016 11/10/2016 | 2016007-13 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a CAQ Associated with Over-Dutied 480V Safety-Related Switchgear Breakers (Section 4OA2.1.b(2)) |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify that over-dutied 480V safety-related switchgear br
Region: III | Fermi | 27622 | 09/28/2016 11/10/2016 | 2016007-14 | NRC | NCV | Barrier Integrity | Green | Failure to Identify that an Inadequate Minimum MSIV Accumulator Air Pressure Setpoint Was CAQ (Section 4OA2.1.b(3)) |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify that an inadequate minimum MSIV accumulator air pr
Region: III | Fermi | 27629 | 09/28/2016 11/10/2016 | 2016007-15 | NRC | NCV | Mitigating Systems | Green | Failure to Identify that a Non-Conservative Min-K Insulation Volume Calculation Error Was Nonconforming to the ECCS Suction Strainer Licensing Basis (Section 4OA2.1.b(4)) |  | H.14 Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify that a non-conservative min-K insulation volume ca
Region: III | Fermi | 27630 | 09/28/2016 11/10/2016 | 2016007-16 | NRC | NCV | Mitigating Systems | Green | Failure to Timely Identify, Document, and Evaluate Conditions that Challenge Operability (Section 4OA2.1.b(5)) |  | H.13 Consistent Process | TE?: N | 05000341 Fermi 2 |  | 7111121 | Green. The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to timely identify, document, and evaluate
Region: III | Fermi | 27578 | 06/30/2016 08/04/2016 | 2016002-01 | NRC | NCV | Initiating Events | Green | Failure to Control Combustible Materials |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4, "Procedures." During fire protection walkdowns in safety-related and risk-significant areas of the plant, the i
Region: III | Fermi | 27579 | 06/30/2016 08/04/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Procedure Used for Measuring and Determining Average Silt Levels in the Service Water Reservoir |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.07T | The inspectors identified a finding of very-low safety significance with an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have a procedure that prescribed instructio
Region: III | Fermi | 27581 | 06/30/2016 08/04/2016 | 2016002-04 | NRC | NCV | MISC | Green | Failure to Control the Work Hours of Covered Workers |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 26.205(c) and (d). The licensee failed to schedule and control the work hours of two maintenance craftsmen performing work covered under 1
Region: III | Fermi | 27582 | 06/30/2016 08/04/2016 | 2016002-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Use Correct Material in a Feedwater Heater Level Control Valve Resulted in a Loss of Feedwater Heater Drains and a Reactor Recirculation System Runback |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance was self-revealed when a reactor recirculation system runback occurred during power ascension due to a loss of feedwater heater drains caused by a feedwater heater level control valve malfunction. The control valv
Region: III | Fermi | 27583 | 06/30/2016 08/04/2016 | 2016002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Adequate Preventive Maintenance on Spare Terminals in Safety-Related Motor Control Centers |  |  | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the Division 1 low pressure coolant injection (LPCI) outboard injectio
Region: III | Fermi | 26377 | 03/31/2016 05/09/2016 | 2016001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure of the Plant-Referenced Simulator to Demonstrate Expected Plant Response for Safety Relief Valves |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.11Q | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 55.46(c), "Plant-Referenced Simulators," was self-revealed. The licensee failed to ensure the plant-referenced simulator demonstrated expected plant response to nor
Region: III | Fermi | 26378 | 03/31/2016 05/09/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Interpret and Implement TS Requirements for RPS Trip Functions |  | H.14 Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4, "Procedures." Specifically, the licensee failed to enter TS 3.3.1.1, Condition C when the high pressure stop va
Region: III | Fermi | 27566 | 03/31/2016 05/09/2016 | 2016001-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Incorporate Operating Experience into Preventive Maintenance Activities Associated with the TBCCW System |  | P.4 Trending | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was self-revealed when the failure of a tube inside the east turbine
Region: III | Fermi | 27568 | 03/31/2016 05/09/2016 | 2016001-06 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Requirements of the RHRHVAC System into Procedures |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to demonstrate the residual heat removal heating, venti
Region: III | Fermi | 27573 | 03/31/2016 05/09/2016 | 2016001-07 | NRC | NCV | Barrier Integrity | Green | Inadequate Test Criteria in SGTS Flow/Heater Operability Surveillance Test |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings." Specifically, the licensee failed to include appropriate quantitativ
Region: III | Fermi | 27574 | 03/31/2016 05/09/2016 | 2016001-08 | NRC | FIN | MISC | Green | Failure to Follow Apparent Cause Evaluation Procedure |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified a finding of very low safety significance for the licensee's failure to implement its procedure standards when performing an apparent cause evaluation for a condition adverse to quality. Specifically, the inspectors determined th
Region: III | Fermi | 27575 | 03/31/2016 05/09/2016 | 2016001-09 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Reactor Water Low Level Reactor Protection System Actuation Due to Operator Error |  | H.1 Resources | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification 5.4, "Procedures," was self-revealed when a valid automatic reactor scram signal and isolation signal for multiple primary containment isolation va
Region: III | Fermi | 26372 | 12/31/2015 02/10/2016 | 2015004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Satisfy Technical Specification Requirements During an Unplanned Operation with the Potential to Drain the Reactor Vessel |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71111.2 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 3.0.4 was self-revealed on October 4, 2015, when the licensee inadvertently entered an operation with the potential to drain the reactor vesse
Region: III | Fermi | 26374 | 12/18/2015 01/29/2016 | 2015007-01 | NRC | FIN | Initiating Events | Green | Failure to Comply with ASME B30.16 for Planned Engineered Lifts |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 71152B | The inspectors identified a finding of very low safety significance for the licensee's failure to meet American Society of Mechanical Engineers (ASME) Code requirements to perform planned engineering lifts of loads that exceeded a hoist's rated capacity.
Region: III | Fermi | 26348 | 09/30/2015 11/05/2015 | 2015003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate Operating Experience Into Preventive Maintenance Activities Associated With RPS Timing Relays |  | H.6 Design Margins | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was self-revealed on May 24, 2015, when the failure of a reactor prot
Region: III | Fermi | 26357 | 09/30/2015 11/05/2015 | 2015003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Correct Classification and Preventative Maintenance for Reactor Recirculation Pump Flow Switches |  | P.1 Identification | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was self revealed on March 19, 2015, when the reactor recirculation p
Region: III | Fermi | 26358 | 09/30/2015 11/05/2015 | 2015003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Preventative Maintenance on Safety-Related Auxiliary Trip Unit Relays for the Spent Fuel Pool Ventilation Exhaust Radiation Monitors |  | P.5 Operating Experience | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification 5.4, "Procedures," was self-revealed on May 16, 2015, when the failure of an auxiliary trip unit relay for the Division 2 spent fuel pool ventilati
Region: III | Fermi | 26367 | 09/30/2015 11/05/2015 | 2015003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Procedures to Respond to Thermal-Hydraulic Instabilities |  |  | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self-revealed on March 19, 2015, when the reactor automatically scrammed due to an automat
Region: III | Fermi | 26368 | 09/30/2015 11/05/2015 | 2015003-06 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Adequately Assess Plant Impact for Post-Maintenance Testing on RBHVAC |  | H.13 Consistent Process | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance was self-revealed on July 7, 2015, during post maintenance testing of the Reactor Building heating, ventilation, and air conditioning (RBHVAC) system when reverse rotation of the center exhaust fan pressurized sec
Region: III | Fermi | 26346 | 06/30/2015 07/31/2015 | 2015002-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Self-Contained Breathing Apparatus Respirators |  |  | TE?: N | 05000341 Fermi 2 |  | 71124.03 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR 20.1703(c)(4)(vii) for the licensee's failure to implement and maintain procedures for its Mine Safety Appliance (MSA) Ultralite« Self Contain
Region: III | Fermi | 26332 | 03/31/2015 05/11/2015 | 2015001-01 | NRC | FIN | Mitigating Systems | Green | Failure to Correct a Nonconforming Condition Adversely Affecting Plant Safety With the Reactor Building Steam Tunnel Floor Drain |  | H.2 Field Presence | TE?: N | 05000341 Fermi 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance for the licensee's failure to correct, as specified in a plant procedure, a nonconforming condition adversely affecting plant safety. On January 24, 2012, the licensee identified the Reac
Region: III | Fermi | 26333 | 03/31/2015 05/11/2015 | 2015001-02 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Functionality Assessments for Degraded and Nonconforming Plant Conditions |  | H.1 Resources | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance for the licensee's failure to follow its procedural guidance to assess the effects of degraded and nonconforming conditions involving plant structures, systems, or components (SSCs) not s
Region: III | Fermi | 26335 | 03/31/2015 05/11/2015 | 2015001-04 | Self - Revealed | NCV | Mitigating Systems | Green | Operation Above the Licensed Thermal Power Limit |  | H.8 Procedure Adherence | TE?: N | 05000341 Fermi 2 |  | 71153 | A finding of very low safety significance with an associated Non-Cited Violation of the Fermi 2 Facility Operating License (NPF-43), Condition 2.C (1), "Maximum Power Level," was self-revealed on March 10, 2015. Licensed reactor operators in the Control R
Region: III | Fermi | 26337 | 03/09/2015 03/31/2015 | 2015008-01 | NRC | NCV | Barrier Integrity | Green | Failure to Translate TS 3.7.4 Requirements Correctly into Plant Procedures (Section 1R17.1.b.(1)) |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a finding of very-low safety significance, and an associated Non-Cited Violation of Title 10, Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure instructions in
Region: III | Fermi | 26338 | 03/09/2015 03/31/2015 | 2015008-02 | NRC | NCV | Initiating Events | Green | Temporary Change Notice Administrative Conduct Manual MGA04 Deficiency (Section 1R17.1.b.(2)) |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a finding of very-low safety significance and an associated Non-Cited Violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to have adequate procedural guidance when performing Temporary Change No
Region: III | Fermi | 26340 | 03/09/2015 03/31/2015 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Test the Electrical Characteristics for Control Power Transformers to Verify the Degraded Voltage Calculations Results (Section 1R17.2.b(1)) |  | H.14 Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a finding of very-low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that design parameters for Structures, Systems,
Region: III | Fermi | 26319 | 12/31/2014 01/28/2015 | 2014005-01 | NRC | FIN | Initiating Events | Green | Potential Missile Hazards from Unrestrained Equipment near the 345-Kilovolt and 120-Kilovolt Switchyards |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance for the licensee's failure to adequately control loose materials near the 345-kilovolt and 120-kilovolt switchyards. Specifically, on September 10, 2014, the inspectors identified numerou
Region: III | Fermi | 26320 | 12/31/2014 01/28/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination for Partially Submerged EDG Cables |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to complete an operability determination
Region: III | Fermi | 26321 | 12/31/2014 01/28/2015 | 2014005-04 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA During RF-16. |  | H.2 Field Presence | TE?: N | 05000341 Fermi 2 |  | 71124.02 | A finding of very low safety significance was self-revealed due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee's Radiological Work Planning and Work Control Program. Specifica
Region: III | Fermi | 26310 | 09/30/2014 10/30/2014 | 2014004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Incorporate Operating Experience into Preventive Maintenance Activities |  | P.5 Operating Experience | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was self-revealed on March 18, 2014, when the failure of a reactor pr
Region: III | Fermi | 26316 | 09/30/2014 10/30/2014 | 2014004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality on EDG 11 |  | H.5 Work Management | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was self-revealed on March 20, 2014, when operators manually shut down emergency diesel generator (EDG) 11 while
Region: III | Fermi | 26317 | 09/12/2014 10/20/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Valve Location in Procedure |  | P.3 Resolution | TE?: N | 05000341 Fermi 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specifications (TS) Section 5.4.1.a for the licensee's failure to maintain Procedure 20.000.23, "High RPV [Reactor Pressure Vessel] Water Level" to
Region: III | Fermi | 26301 | 06/30/2014 07/25/2014 | 2014003-01 | NRC | FIN | Mitigating Systems | Green | Incorrect Application of TSSR 3.0.3 to Never-Performed Battery Surveillances |  | H.14 Conservative Bias | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance. Upon discovery that surveillance testing procedures for safety-related batteries had not fully satisfied the applicable Technical Specification Surveillance Requirements (TSSRs), the lic
Region: III | Fermi | 26302 | 06/30/2014 07/25/2014 | 2014003-02 | NRC | NCV | Occupational Radiation Safety | Green | Disabled Respirator Safety Feature |  | H.7 Documentation | TE?: N | 05000341 Fermi 2 |  | NONE | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 20.1703(c)(4)(vii) for defeating a safety feature for the Mururoa V4 MTH2 air-supplied suit (Delta Suit) Respirator, i.e., placement of ta
Region: III | Fermi | 26308 | 06/30/2014 07/25/2014 | 2014003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Mis-Positioned Control Switch Inadvertently Rendered the Division 2 EECW System and Supported Systems Inoperable |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification 5.4.1.a was self-revealed on February 6, 2014, when the Division 2 emergency equipment cooling water (EECW) system and its supported systems were i
Region: III | Fermi | 26296 | 03/31/2014 04/24/2014 | 2014002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Perform Appropriate Preventive Maintenance on Reactor Building Heating, Ventilation, and Air Conditioning Components |  | P.4 Trending | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.65(a)(2) was self-revealed on November 24, 2013, for the licensee's failure to demonstrate that the performance of the temperature switches, steam traps, and dra
Region: III | Fermi | 26297 | 03/31/2014 04/24/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control the Work Hours of a Covered Worker |  | H.1 Resources | TE?: N | 05000341 Fermi 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 26.205(c) and (d) for the licensee's failure to schedule and control the work hours of a covered worker directing and performing surveilla
Region: III | Fermi | 26298 | 03/31/2014 04/24/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | Unacceptable Preconditioning of High Pressure Coolant Injection System Air Operated Valve Prior to Stroke Time Test Measurement |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." The licensee failed to establish an adequate procedure to perform r
Region: III | Fermi | 26299 | 03/31/2014 04/24/2014 | 2014002-04 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Inservice Testing of High Pressure Coolant Injection and Reactor Core Isolation Cooling System Valves |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50.55a. The licensee failed to perform required inservice testing of high pressure coolant injection and reactor core isolation cooling tu
Region: III | Fermi | 26271 | 12/31/2013 01/27/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | RHR Pump Seal Cooler Test Was Not Adequately Implemented |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to demonstrate the cooling capability of the residual heat removal pump
Region: III | Fermi | 26272 | 12/31/2013 01/27/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Acceptance Criteria for UHS Level and Temperature Did Not Consider Instrument Uncertainties |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to include appropriate acceptance criteria for
Region: III | Fermi | 26284 | 12/31/2013 01/27/2014 | 2013005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correctly Connect Thermocouple Wiring During Maintenance Resulted in Inoperable Reactor Core Isolation Cooling System Isolation Instrumentation |  | H.12 Avoid Complacency | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance with an associated Non-Cited Violation of Technical Specification (TS) 5.4.1.a was self-revealed on August 30, 2013, when the Division 1 Reactor Core Isolation Cooling (RCIC) Equipment Room temperature input to th
Region: III | Fermi | 26286 | 12/31/2013 01/27/2014 | 2013005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Nonconforming Materials Used in EDG Air Coolant Piping System |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," was self-revealed on August 9, 2013, when operators had to manually shut down emergen
Region: III | Fermi | 26265 | 09/06/2013 10/29/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Battery Rack Configuration Not in Accordance with Design Basis |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure the battery rack end rail configuration for battery 2P-29 was
Region: III | Fermi | 26266 | 09/06/2013 10/29/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Design Loads for ECCS Suction Strainer Modification Not in Conformance with Design Basis Plant Unique Analysis Report |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to establish measures to assure the design basis was correctly translate
Region: III | Fermi | 26267 | 09/06/2013 10/29/2013 | 2013008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Non-Conservative Technical Specification |  | H.13 Consistent Process | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to ensure a non-conservative battery technical specification (TS) was
Region: III | Fermi | 26231 | 09/06/2013 10/29/2013 | 2013008-04 | NRC | NCV | Mitigating Systems | Green | Untimely Resolution of Non-Conservative Battery Technical Specification |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | he inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly translate the requirements of IEEE 450-1972 into TS surveill
Region: III | Fermi | 26270 | 09/06/2013 10/29/2013 | 2013008-05 | NRC | NCV | Mitigating Systems | Green | Battery Testing Not in Conformance with Design Standard |  | P.2 Evaluation | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to translate the design standard requirements for battery test periodici
Region: III | Fermi | 26259 | 06/30/2013 07/29/2013 | 2013003-01 | NRC | FIN | Initiating Events | Green | Not Following AQP and NPOA for Switchyard Modifications |  | H.3(b) Work Activity Coordination | TE?: N | 05000341 Fermi 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance for the licensee's failure to follow the augmented quality program (AQP), nuclear plant operating agreement (NPOA), and Updated Final Safety Analysis Report (UFSAR) for plant modification
Region: III | Fermi | 26261 | 06/30/2013 07/29/2013 | 2013003-03 | NRC | FIN | Initiating Events | Green | Failure to Maintain Configuration Control during Plant Operation |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified a finding of very low safety significance for the licensure's failure to maintain configuration control during plant operations. Specifically, the inspectors identified multiple instances concerning the improper storage of equipm
Region: III | Fermi | 26264 | 06/14/2013 07/17/2013 | 2013009-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Foreign Material Exclusion Procedure Requirements Adversely Affected the Reliability of the Main Turbine Generator and Caused a Reactor Scram |  |  | TE?: N | 05000341 Fermi 2 |  | 95001 | A finding of very low safety significance was self-revealed from an event that resulted in a reactor scram. The licensee failed to correctly implement its foreign material exclusion procedure following a reactor scram on September 30, 2009. The scram was
Region: III | Fermi | 26253 | 12/31/2012 01/28/2013 | 2012005-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure of E4150F002 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance was self-revealed for failing to adequately inspect and identify, and then correct severe degradation of the motor operator for E4150F002 [HPCI turbine steam supply inboard containment isolation valve], which fail
Region: III | Fermi | 26256 | 12/31/2012 01/28/2013 | 2012005-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Implementation of Overhaul Post-Maintenance Testing and Operation of South Reactor Feed Pump Turbine |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed finding of very low safety significance and associated NCV of Technical Specification 5.4.1.a was identified for the licensee's failure to establish and implement procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, Feb
Region: III | Fermi | 26245 | 09/30/2012 10/31/2012 | 2012004-01 | NRC | NCV | Initiating Events | Green | Inspection Procedure for Reactor Pressure Vessel Head Strongback and Steam Dryer/Separator Lifting Device Omitted Testing Requirements |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified by the NRC inspectors. Specifically, the licensee failed to perform dimensional testing of
Region: III | Fermi | 26246 | 09/30/2012 10/31/2012 | 2012004-02 | NRC | NCV | Initiating Events | Green | Inadequate Evaluation of Steam Dryer/Steam Separator Lifting Device |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the NRC inspectors for the failure to ensure the adequacy of the steam dryer/steam separator lifting device d
Region: III | Fermi | 26247 | 09/30/2012 10/31/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform ASME Inservice Testing Comprehensive Pump Test |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance and an associated NCV of 10 CFR 50.55a(f), "Inservice testing requirements," and 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," was identified by the NRC inspectors. Specifically
Region: III | Fermi | 26248 | 09/30/2012 10/31/2012 | 2012004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Control Rod 10-35 to Fully Scram during Scram Time Testing |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR 50 Appendix B, Section V, "Instructions, Procedures, and Drawings," was identified for the failure to adequately prevent foreign material from entering the hydraulic c
Region: III | Fermi | 26235 | 06/30/2012 08/06/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Energizing Bus 65E with Ground Truck Installed and Subsequent Loss of Shutdown Cooling |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed Green finding and associated NCV of 10 CFR 50 Appendix B, Section V, "Instructions, Procedures, and Drawings," for failure to follow procedureswhen the licensee energized a safety-related electrical bus with a ground truck installed in bus
Region: III | Fermi | 26244 | 06/30/2012 08/06/2012 | 2012003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Monitor Reactor Pressure during Reactor Pressure Vessel Hydrostatic Test |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed Green finding and associated NCV of Technical Specification (TS) 5.4.1.a was identified for the licensee's failure to establish and implement procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifica
Region: III | Fermi | 26230 | 02/03/2012 03/06/2012 | 2012007-01 | NRC | NCV | Initiating Events | Green | Inadequate Safety Evaluation for the Online Noble Chemical Metal Process |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a Severity Level IV, Non-Cited Violation (NCV) of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated (Green) finding for the licensee's failure to provide an adequate written safety evaluation to demonstrate
Region: III | Fermi | 26232 | 02/03/2012 03/06/2012 | 2012007-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Safety Evaluation for the Online Noble Chemical Metal Process |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a condition adverse to quality. Specifically, t
Region: III | Fermi | 26233 | 02/03/2012 03/06/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify EDG's Neutral Grounding Resistor Exceeded its Design Values |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a condition adverse to quality. Specifically, t
Region: III | Fermi | 26228 | 12/31/2011 01/30/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DEVELOP APPROPRIATE CORRECTIVE ACTIONS FOR A MAINTENANCE RULE (a)(1) MONITORED SYSTEM |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71111.12 | The NRC inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65 for failure to develop appropriate corrective actions for an (a)(1) monitored system. The licensee failed to determine the cause of repeated SS 1
Region: III | Fermi | 26229 | 12/31/2011 01/30/2012 | 2011005-02 | Self - Revealed | FIN | Barrier Integrity | Green | PLACING A FUEL BUNDLE IN THE WRONG CELL DURING FUEL SHUFFLE |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71152 | A self-revealed finding of very low safety significance (Green) was identified by the inspectors for placing a fuel bundle in the wrong cell during a fuel shuffle in the spent fuel pool. The error was noted later in the fuel shuffle when another bundle wa
Region: III | Fermi | 26223 | 09/30/2011 10/26/2011 | 2011004-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Maintain Separation of Metal Containers and Combustible Radwaste |  | H.3(b) Work Activity Coordination | TE?: N | 05000341 Fermi 2 |  | 71111.05Q | A finding of very low safety significance and an associated NCV of the Fermi 2 Facility Operating License Condition 2.C(9),for the fire protection program, was identified by the inspectors for the licensee's failure to ensure combustible radwaste was not
Region: III | Fermi | 26220 | 06/30/2011 08/01/2011 | 2011003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | ENTRY TO A HIGH RADIATION AREA ON THE WRONG RADIATION WORK PERMIT |  |  | TE?: N | 05000341 Fermi 2 |  | 71124.01 | A finding of very low safety significance (Green) was self revealed when two radiation workers entered a high radiation area without proper authorization. This issue was an NCV of licensee Technical Specification 5.4.1, Procedures. Specifically, radiation
Region: III | Fermi | 26221 | 06/30/2011 08/01/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | SPENT FUEL CASK LAY-DOWN AREAS DID NOT MEET SEISMIC CATEGORY I REQUIREMENTS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | NONE | A finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for failure to provide adequate design control measures for
Region: III | Fermi | 26217 | 04/29/2011 06/07/2011 | 2011009-01 | NRC | NCV | Initiating Events | Green | Unauthorized Transient Combustibles |  | H.3(a) Work Planning | TE?: N | 05000341 Fermi 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of License Condition 2.C(9) for the licensee's failure to control transient combustibles in accordance with the fire protection program requirements. Specifical
Region: III | Fermi | 26216 | 04/29/2011 06/07/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Detection in Emergency Diesel Generator Rooms |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of License Condition 2.C(9) for the licensee's failure to install heat detectors at the ceiling in the emergency diesel generator (EDG) rooms. Specifically, the
Region: III | Fermi | 26215 | 04/29/2011 06/07/2011 | 2011009-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures to Control the Plant from the Dedicated Shutdown Panel |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of License Condition 2.C(9) for the failure to implement procedures which would ensure that reactor vessel water level would be maintained above the top of the
Region: III | Fermi | 26214 | 04/29/2011 06/07/2011 | 2011012-01 | NRC | FIN | Barrier Integrity | Green | Failure to Store B.5.b Equipment Appropriately |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000341 Fermi 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) associated with the licensee's failure to store B.5.b equipment appropriately. Specifically, the failure to store hose used for B.5.b strategies consistent with the manufacturer's
Region: III | Fermi | 26211 | 03/31/2011 05/02/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Evaluate the Failure of H2O2 Sampling Pump Trips during Caligration |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71111.12 | The inspectors identified a finding and associated NCV of Technical Specification 5.4.1 for failure follow their Conduct Manual MES 43, "Instrument Calibration Specification Sheets (ICSS)," as established in Regulatory Guide 1.33, Appendix A.10, to ensure
Region: III | Fermi | 26212 | 03/31/2011 05/02/2011 | 2011002-02 | NRC | NCV | Initiating Events | Green | Design Control Measures Failed to Ensure Adequacy of the Design Relating to the Reactor Building Crane Support Structure and Reactor Building Superstructure |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.2 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure the adequacy of the design for the reactor building crane support struc
Region: III | Fermi | 26213 | 03/31/2011 05/02/2011 | 2011002-03 | Self - Revealed | FIN | Initiating Events | Green | Reactor Scram due to Loss of Vacuum |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance (Green) for failure to evaluate and incorporate the operating experience received from the Boiling Water Reactors Owners Group (BWROG) Off Gas committee was self revealed when Fermi 2 experienced a reactor scram d
Region: III | Fermi | 26206 | 12/31/2010 02/03/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | Plastic Face Shield Lost in the Reactor Cavity |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000341 Fermi 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified by the inspectors for the licensee's failure to follow procedures and review the accident anal
Region: III | Fermi | 26210 | 12/31/2010 02/03/2011 | 2010005-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure of Condensate Filter Demineralizer 'D' Main Drain Valve |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000341 Fermi 2 |  | 71153 | A self revealed finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.5.4.c, Radiation Effluent Controls Program, were self-revealed for failure to monitor an effluent release path when the condensate filter
Region: III | Fermi | 26205 | 09/30/2010 10/20/2010 | 2010004-01 | NRC | URI | Mitigating Systems | Green | Inadequate procedures to control the plant from the dedicated shutdown panel |  |  | TE?: N | 05000341 Fermi 2 |  | NONE
Region: III | Fermi | 26202 | 06/30/2010 07/30/2010 | 2010003-01 | NRC | FIN | Initiating Events | Green | Failure to Adequately Control Loose Materials near the Switchyard |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000341 Fermi 2 |  | 71111.01 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to adequately control loose materials next to the 345kV switchyard. Specifically, the inspectors identified tarps next to the switchyard fence. Once this
Region: III | Fermi | 26187 | 04/05/2010 04/30/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations for Availability of 120kV System Offsite Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding having very low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to perform adequate calculations to ensure the availability of offsit
Region: III | Fermi | 26188 | 04/05/2010 04/30/2010 | 2010006-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Motor Starting Voltage Calculations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) with an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failing to perform proper motor starting studies to demonstrate that motors would succes
Region: III | Fermi | 26195 | 04/05/2010 04/30/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Controlling Availability of 120kV System Voltage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding having very low safety significance (Green) with an associated NCV of Technical Specifications 5.4.1.a, "Procedures" for the licensee's failure to translate the design requirements for the availability of the 120kV offs
Region: III | Fermi | 26196 | 04/05/2010 04/30/2010 | 2010006-04 | NRC | NCV | Initiating Events | Green | Failure to include Turbine Building Heating Ventilation and Air Conditioning Fans in the Scope of the Maintenance Rule Program. |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding having very low safety significance with an Non-Cited Violation (NCV) of 10 CFR 50.65(b)(2)(iii), for the licensee's failure to include turbine building heating ventilation and air conditioning (TBHVAC) fans in the scop
Region: III | Fermi | 26197 | 04/05/2010 04/30/2010 | 2010006-05 | NRC | NCV | Mitigating Systems | Green | Adequate Calculation for DC Short Circuit Analysis |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 7111121 | . The inspectors identified a finding having very low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to accurately account for the cable resistance for the reactor core
Region: III | Fermi | 26198 | 04/05/2010 04/30/2010 | 2010006-06 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Evaluate Industry Operating Experience for Applicability to Fermi 2 |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) for the licensee's failure to adhere to operating experience program procedural requirements. Specifically, the inspectors identified three instances where the licensee failed to
Region: III | Fermi | 26201 | 04/05/2010 04/30/2010 | 2010006-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations for Backfit Modifications |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 7111121 | . The inspectors identified a finding of very low safety significance (Green) with an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance with two examples, for failing to perform adequate ele
Region: III | Fermi | 26186 | 12/31/2009 02/02/2010 | 2009005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Adhere to Self-Imposed Maintenance Rule Procedural Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 71111.12 | A finding of very low safety significance (Green) was identified by the inspectors for the licensee's failure to adhere to self-imposed maintenance rule procedural requirements. Contrary to maintenance rule monitoring requirements, while performing a main
Region: III | Fermi | 26175 | 06/30/2009 08/05/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Completely Disassemble and Remove Scaffold from the Steam Tunnel |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V (Procedures), for the failure to follow procedures. The licensee partially dismantled a scaffold and left the remaining scaffold p
Region: III | Fermi | 26169 | 06/30/2009 08/05/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Dedicate a Commercial Grade Item for Safety-Related Use |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A Green self-revealing finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," was identified for the failure to adequately dedicate a commercial grade i
Region: III | Fermi | 26174 | 06/30/2009 08/05/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Control Potential Debris Source Term in Primary Containment |  |  | TE?: N | 05000341 Fermi 2 |  | 71153 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III (Design Control), for the failure to control debris source term inside the drywell. The licensee installed ty wraps inside the d
Region: III | Fermi | 13753 | 03/31/2009 05/13/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedural Controls Over Construction of Storage Racks and Storage Areas |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000341 Fermi 2 |  | 71111.18 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to include criteria in procedures for evaluation o
Region: III | Fermi | 13754 | 03/31/2009 05/13/2009 | 2009002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Core Spray Pump Motor Oil Leak Not Promptly Identified and Corrected |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was self-revealed for the failure to promptly identify and correct an oil leak that subsequently rendered a safety-r
Region: III | Fermi | 13741 | 12/31/2008 01/30/2009 | 2008005-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Heat Exchanger Inspection Frequency |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.07A | A finding of very low safety significance was identified by the inspectors for the failure to test and/or inspect the safety-related non-interruptible air supply (NIAS) control air compressor (CAC) aftercoolers in accordance with Generic Letter (GL) 89-13
Region: III | Fermi | 13742 | 12/31/2008 01/30/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Control Air Compressor Capacity Test Program |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.22 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the failure to perform adequate testing for both the Division 1 and 2 CACs. Specifically, the
Region: III | Fermi | 13752 | 12/31/2008 01/30/2009 | 2008005-03 | NRC | VIO | Mitigating Systems | Green | Backfit-Inadequate Degraded Voltage Protection Scheme |  |  | TE?: N | 05000341 Fermi 2 |  | NONE | As documented in Inspection Report 05000341/2008008, the inspectors identified a concern with respect to the adequacy of the degraded voltage protection scheme. In correspondence dated June 11, 1981, the licensee described the time delay settings for the
Region: III | Fermi | 13737 | 09/30/2008 11/12/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Install Smoke Detectors in the Reactor Building, First Floor, Beam Pockets. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000341 Fermi 2 |  | 71111.05Q | The inspectors identified an NCV of Condition 2.C.(9) of the Fermi-2 Facility Operating License NPF-43 for the failure to have adequate fire detection installed in the reactor building first floor in accordance with the applicable National Fire Protection
Region: III | Fermi | 13739 | 09/30/2008 11/12/2008 | 2008004-02 | NRC | FIN | Initiating Events | Green | Failure to Adequately Control Loose Materials in the Switchyard. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71111.13 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to adequately control loose materials in the 345kV switchyard. Specifically, the inspectors identified a wooden pallet and multiple wooden boards, stanch
Region: III | Fermi | 13734 | 06/30/2008 08/14/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Maintain Plant Flooding and Pipe Break Design Basis Requirements |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.06 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure the design basis flooding and pipe break criteria were properly incorporated
Region: III | Fermi | 13735 | 06/30/2008 08/14/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Maintain Configuration Control of Pipe Spray Shrouds |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 71111.06 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure the configuration of spray shrouds was properly controlled. The inspectors i
Region: III | Fermi | 13736 | 06/30/2008 08/14/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Undocumented Technical Basis for Change to EOP ATWS Mitigation Strategy |  |  | TE?: N | 05000341 Fermi 2 |  | NONE | . The inspectors identified a finding of very low safety significance and associated NCV of Fermi Unit 2 Technical Specification (TS) 5.4.1, for failing to maintain adequate procedures for implementing the emergency operating procedures (EOPs). Specifical
Region: III | Fermi | 13723 | 05/08/2008 06/20/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Air Supply Tubing for Safe Shutdown Valves Free of Fire Damage |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of the Fermi 2 Facility Operating License Condition 2.C(9),for the fire protection program, was identified by the inspectors for the licensee failure to ensure that one
Region: III | Fermi | 13724 | 05/08/2008 06/20/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | High Pressure Coolant Injection Room Sprinkler System Failed to Protect Against Hazard |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | A finding of very low safety significance and an associated NCV of the Fermi 2 Facility Operating License Condition 2.C(9), for the fire protection program, was identified by the inspectors for the failure to ensure the adequacy of a sprinkler system in F
Region: III | Fermi | 13725 | 05/08/2008 06/20/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Reactor Core Isolation Cooling Room Sprinkler System Improperly Installed |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000341 Fermi 2 |  | 71111.05T | A finding of very low safety significance and an associated NCV of the Fermi 2 Facility Operating License Condition 2.C(9), for the fire protection program, was identified by the inspectors for the failure to install sprinkler system in accordance with th
Region: III | Fermi | 13726 | 05/08/2008 06/20/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | Lack of Basis for Diesel Fire Pump Temperature De-Rating |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | A finding of very low safety significance and an associated NCV of the Fermi 2 Facility Operating License condition 2.C(9), for the fire protection program, was identified by the inspectors for the failure to provide a design basis for the general service
Region: III | Fermi | 13732 | 05/08/2008 06/20/2008 | 2008006-05 | NRC | NCV | Mitigating Systems | Green | Alternate Shutdown Procedure Failed to Identify Time-Critical Steps |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05T | A finding of very low safety significance and an associated NCV of the Fermi 2 Facility Operating License Condition 2.C(9), for the fire protection program, was identified by the inspectors for the failure to have adequate shutdown procedure in the event
Region: III | Fermi | 13719 | 03/31/2008 05/13/2008 | 2008002-01 | NRC | URI | Mitigating Systems | Green | Failure to Perform Adequate Evaluation for Penetrations in Reactor and Auxiliary Building Walls |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.01
Region: III | Fermi | 13720 | 03/31/2008 05/13/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Control High Pressure Gas Cylinders in Proximity to Safety-Related Equipment |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, was identified by the inspectors for the failure to properly control high pressure gas cylinders in proximity to safety-related equipment. The inspe
Region: III | Fermi | 13721 | 03/31/2008 05/13/2008 | 2008002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Perform a Proper Engineering Evaluation on Replacing the Torus-to-Reactor Building Vacuum Breaker Differential Pressure Switches |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 71111.15 | A self-revealing finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the failure to perform a proper engineering evaluation. The licensee replaced both differential press
Region: III | Fermi | 13722 | 03/31/2008 05/13/2008 | 2008002-04 | NRC | NCV | Barrier Integrity | Green | Licensee Procedures Failed to Contain Adequate Controls to Prevent Materials Stored on the Refuel Floor from Becoming Missiles During a Tornado Strike |  |  | TE?: N | 05000341 Fermi 2 |  | 71152 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified by the inspectors for the failure to maintain adequate procedures. Licensee procedures failed to contain adequate controls to prevent m
Region: III | Fermi | 13707 | 12/31/2007 02/13/2008 | 2007006-01 | NRC | NCV | Initiating Events | Green | Failure to Expand Scope of Pipe Support Hanger Examinations |  | H.3(b) Work Activity Coordination | TE?: N | 05000341 Fermi 2 |  | 71111.08G | The inspectors identified a Green NCV of 10 CFR 50.55a(b)5 for failure to perform additional pipe support examinations required by the American Society of Mechanical Engineers Code following adjustments to spring can settings on reactor water cleanup syst
Region: III | Fermi | 13709 | 12/31/2007 02/13/2008 | 2007006-03 | NRC | FIN | Mitigating Systems | Green | High Failure Rate on Licensed Operator Requalification Examination |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.11B | A finding of very low safety significance was identified by the inspectors. The inspectors identified a performance deficiency based on licensed operators' failure to pass an NRC comprehensive biennial written examination. Of the 48 licensed operators eva
Region: III | Fermi | 13710 | 12/31/2007 02/13/2008 | 2007006-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Work Planning for Shield Block Wall Removal |  | H.3(a) Work Planning | TE?: N | 05000341 Fermi 2 |  | 71111.13 | A self-revealed NCV of 10 CFR 50.65(a)(4) was identified for the failure to adequately assess the increased risk associated with the removal of shield blocks in the turbine building. After the licensee removed the shield blocks, the airflow in the turbine
Region: III | Fermi | 13711 | 12/31/2007 02/13/2008 | 2007006-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control of the Reactor Core Isolation Cooling Pump |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.19 | A self-revealed NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the failure to properly maintain design control of the reactor core isolation cooling pump. The licensee replaced all four pump impellers in 1996 but failed
Region: III | Fermi | 13712 | 12/31/2007 02/13/2008 | 2007006-06 | Self - Revealed | FIN | Initiating Events | Green | Transient During Testing of #5 Low Pressure Stop Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 71111.19 | A self-revealed finding was identified for the failure to operate the plant in accordance with the documented instructions while performing a maintenance activity on the number 5 low pressure stop valve, which resulted in an unplanned power transient caus
Region: III | Fermi | 13714 | 12/31/2007 02/13/2008 | 2007006-08 | Self - Revealed | NCV | Occupational Radiation Safety | Green | An HRA was entered without adequate awareness of radiological conditions and without an RWP that allowed HRA entry. |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 7112101 | A self-revealed finding of very low safety significance and an associated NCV of regulatory requirements was identified for workers entering a high radiation area without an adequate awareness of radiological conditions and without performing work using a
Region: III | Fermi | 13717 | 12/31/2007 02/13/2008 | 2007006-09 | Self - Revealed | NCV | Initiating Events | Green | Improper Valve Operation Caused Reactor Scram |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed NCV of Technical Specification 5.4.1.a was identified for the failure to perform a maintenance activity in accordance with the documented instructions which resulted in an unplanned scram from nine percent power. During a maintenance taggi
Region: III | Fermi | 13718 | 12/31/2007 02/13/2008 | 2007006-10 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent RPS Undervoltage Trip |  |  | TE?: N | 05000341 Fermi 2 |  | 71153 | A self-revealed NCV of 10 CFR 50.65(a)(4) was identified for the failure to appropriately assess the risk associated with removing the Reactor Protection System (RPS) from its normal power source. During refueling outage 12, the licensee placed RPS 'B' on
Region: III | Fermi | 13701 | 10/19/2007 12/03/2007 | 2007010-01 | NRC | NCV | Mitigating Systems | Green | Procedures Not Appropriate to the Circumstances for Evaluating Poetntial Tampering |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 93812 | Green: The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to establish a cond
Region: III | Fermi | 13702 | 10/19/2007 12/03/2007 | 2007010-02 | NRC | NCV | Mitigating Systems | Green | Procedures Not Appropriate to the Circumstances for SRV Insulation Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 93812 | Green: The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to establish procedures appropriate to th
Region: III | Fermi | 13703 | 10/19/2007 12/03/2007 | 2007010-03 | NRC | NCV | Mitigating Systems | Green | Design Specification Not Adhered to for Installation of Pop Rivets to Join SRV Thermal Shield Sections |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 93812 | Green: The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure that the design specifications for SRV tailpipe insulation were corr
Region: III | Fermi | 13704 | 10/19/2007 12/03/2007 | 2007010-04 | NRC | FIN | Emergency Preparedness | Green | Late NOUE Classification |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 93812 | Green: The inspectors identified a finding of very low safety significance involving failure to follow the requirements of the Fermi 2 Radiological Emergency Response Preparedness (RERP) Plan during a Notice of Unusual Event (NOUE) level event on October
Region: III | Fermi | 13706 | 10/19/2007 12/03/2007 | 2007010-06 | NRC | FIN | MISC | Green | Delayed Security Response |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 93812 | Green: The inspectors identified a finding of very low security significance when licensee personnel failed to follow an NRC approved safeguards contingency plan for responding to threats, thefts, and radiological sabotage related to nuclear facilities in
Region: III | Fermi | 13698 | 09/30/2007 11/02/2007 | 2007005-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Preventive Maintenance Deferral Evaluations |  | H.4(b) Procedural Compliance | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," for the failure to follow procedural requirements for evaluating a preventive maintenance deferral for a main steam line drain valve. The inadequate deferral evaluation
Region: III | Fermi | 13700 | 09/14/2007 10/26/2007 | 2007007-01 | NRC | FIN | Initiating Events | Green | failure to maintain adequate maintenance procedures to clean the '2B' Main Unit Transformer |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 71152B | A finding involving the failure to maintain adequate maintenance procedures to clean the '2B' Main Unit Transformer was self-revealed during an event. The procedure did not contain adequate controls over the removal of the cooling fans from service with t
Region: III | Fermi | 13691 | 09/06/2007 09/11/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | EDG Cable Design Deficiency |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving inadequate cable design. Specifically, the inspectors identified that the licensee failed to implement li
Region: III | Fermi | 13692 | 09/06/2007 09/11/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | HPCI Vortex and NPSHA Calculations Were Not Based on Maximum System Flow Rate |  |  | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving the available Net Positive Suction Head (NPSHA) and vortex calculation for the high pressure core injecti
Region: III | Fermi | 13693 | 09/06/2007 09/11/2007 | 2007003-03 | NRC | NCV | Mitigating Systems | Green | HPCI Pump IST Acceptance Criterion Was Not Conservative with Respect with the System Performance Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 7111121 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving a non-conservative acceptance criteria used to verify that high pressure core injection (HPCI) pump could
Region: III | Fermi | 13683 | 06/30/2007 08/10/2007 | 2007004-01 | NRC | FIN | Initiating Events | Green | Failure to Control Transient Combustibles |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000341 Fermi 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance after the inspectors observed numerous fire hazards during a walkdown of several non-safety-related buildings located inside the protected area and the 120 kilovolt (kV) switchyard. These
Region: III | Fermi | 13684 | 06/30/2007 08/10/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Restoration of Drywell Following SBO Event Does Not Control Rate of Heat Addition to EECW and No Analyses Were Performed for Potential Two Phase Flow and Water Hammer |  |  | TE?: N | 05000341 Fermi 2 |  | 7111107B | The inspectors identified a finding of very low safety significance involving an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control." The inspectors determined the licensee did not have analyses or adequate procedural guidance to ensure the emer
Region: III | Fermi | 13685 | 06/30/2007 08/10/2007 | 2007004-03 | NRC | NCV | Barrier Integrity | Green | Residual Heat Removal/Feedwater Injection Check Valves Inadequate Goal Monitoring in 10 CFR 50.65(a)(1) Status |  | P.2(b) Implementing Operating Experience | TE?: N | 05000341 Fermi 2 |  | 71111.12 | The inspectors identified an NCV of paragraph (a)(1) of 10 CFR 50.65, "Maintenance Rule," for the failure to monitor the performance of the feedwater and residual heat removal injection check valve component class against licensee-established goals when t
Region: III | Fermi | 13686 | 06/30/2007 08/10/2007 | 2007004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Install RCIC Mechanical Seal |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000341 Fermi 2 |  | 71111.15 | An NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," for the failure to maintain adequate maintenance procedures to install the outboard mechanical seal for the reactor core isolation cooling pump was self-revealed when the seal failed. The procedu
Region: III | Fermi | 13687 | 06/30/2007 08/10/2007 | 2007004-05 | NRC | NCV | Barrier Integrity | Green | Failure to Perform an Adequate Root-Cause Evaluation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to identify the cause and take appropriate corrective actions for a significant condition adverse to quality. The licensee failed to perform an
Region: III | Fermi | 13677 | 03/31/2007 05/04/2007 | 2007002-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform a Complete Calibration of the Containment High Range Area Radiation Monitor |  |  | TE?: N | 05000341 Fermi 2 |  | 7112103 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of NRC requirements for the failure to maintain adequate procedures for the calibration of the containment high range area radiation monitors (
Region: III | Fermi | 13678 | 03/31/2007 05/04/2007 | 2007002-02 | NRC | FIN | Emergency Preparedness | Green | Inadequate Verification of Alternate Emergency Operations Facility Readiness |  |  | TE?: N | 05000341 Fermi 2 |  | 71153 | The inspectors identified a finding associated with the failure to verify adequate compensatory measures were in place while the Emergency Operations Facility (EOF) was unavailable. The licensee removed the EOF from service for remodeling and planned to u
Region: III | Fermi | 13674 | 12/31/2006 01/29/2007 | 2006005-01 | Self - Revealed | NCV | Mitigating Systems | Green | EDG-14 Fast Start, Slow Start and Run, and Load Reject |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 71111.22 | A self-revealed NCV was identified for failure to comply with 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when an operator failed to properly follow procedures. As a result, an operator inadvertently caused a generator ov
Region: III | Fermi | 13675 | 12/31/2006 01/29/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Inappropriate Use of Risk in Operability Evaluations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000341 Fermi 2 |  | NONE | The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to adequately control the design of the plant when thermal insulation was removed from piping in the reactor building at power without a proper ope
Region: III | Fermi | 13669 | 09/30/2006 11/03/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Temperatures in Dedicated Shutdown Panel Area - Balance of Plant Switchgear Room |  |  | TE?: N | 05000341 Fermi 2 |  | NONE | The inspectors identified an NCV of License Condition 2.C.(9) having very low safety significance for the licensee's failure to ensure that alternative shutdown capability would accommodate post-fire conditions for 72 hours where offsite power is not avai
Region: III | Fermi | 13670 | 09/30/2006 11/03/2006 | 2006004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Entrance to an High Radiation Area by Issuance of an Radiation Work Permit |  | H.4(a) Human Error Prevention | TE?: N | 05000341 Fermi 2 |  | 7112101 | A self-revealed finding of very low safety significance and associated NCV of Technical Specification (TS) 5.7.1 was identified when a radiation worker entered a posted high radiation area without being on the designated radiation work permit task for thi
Region: III | Fermi | 13671 | 09/29/2006 11/07/2006 | 2006015-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Emergency Diesel Generator Surveillance Test Procedures |  |  | TE?: N | 05000341 Fermi 2 |  | 93812 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of Technical Specification (TS) 5.4, "Procedures," for the licensee's failure to maintain surveillance test procedures for the Division 1 Emergency D
Region: III | Fermi | 13672 | 09/29/2006 11/07/2006 | 2006015-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control Design Change Leading to Undersized Control Power Transformers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 93812 | The inspectors identified a finding and an associated NCV of 10 CFR Part 50, Appendix "B," Criterion III (Design Control) for the failure to adequately review the suitability of the design of 480 Volt breakers used for all four emergency diesel generator
Region: III | Fermi | 13661 | 06/30/2006 08/02/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Unauthorized Transient Combustibles in Safety-Related Areas |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71111.05Q | The inspectors identified a non-cited violation of license condition 2.C(9) due to the presence of unauthorized transient combustible materials in the residual heat removal complex. An office chair and a plastic trash bin half filled with paper were secur
Region: III | Fermi | 13662 | 06/30/2006 08/02/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Improper Storage of Chemicals Affecting Fire Fighting Response |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.05A | The inspectors identified a non-cited violation of license condition 2.C(9), for the failure to appropriately store chemicals in accordance with the fire hazards analysis. The licensee failed to evaluate the fire fighting response guidelines in NFPA-49 fo
Region: III | Fermi | 13664 | 06/30/2006 08/02/2006 | 2006003-03 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Risk Assessment |  | H.3(b) Work Activity Coordination | TE?: N | 05000341 Fermi 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4) for the failure to perform an adequate risk assessment for the Division I battery load test. The licensee failed to consider the effect the test would have on the temperature in the rea
Region: III | Fermi | 13665 | 06/30/2006 08/02/2006 | 2006003-04 | NRC | NCV | Mitigating Systems | Green | Improper Evaluation of Standby Liquid Control Operability During Tank Sparging |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 3.1.5.a.2, Amendment 38, for the standby liquid control (SLC) system being inoperable for longer than the allowed time without the plant being placed in hot shutdown. The licensee
Region: III | Fermi | 13667 | 06/30/2006 08/02/2006 | 2006003-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Inadequate Design Control for Venting the Reactor Pressure Vessel Head |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.2 | A self-revealed NCV was identified for the licensee's failure to comply with Technical Specification 5.4.1.a, written procedures shall be established, implemented, and maintained covering applicable procedures recommended in Regulatory Guide 1.33. The lic
Region: III | Fermi | 13658 | 03/31/2006 05/08/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure of Breaker to Open |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71111.19 | The inspectors identified a finding of very low significance associated with a Non-Cited Violation (NCV) of 10CFR50, Appendix B, Criterion XVI (Corrective Action) for the failure to identify and correct a condition adverse to quality related to the emerge
Region: III | Fermi | 13659 | 03/31/2006 05/08/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Control of Cables and Wiring in the Power Block |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 7111123 | The inspectors identified a finding of very low significance (Green) associated with a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to adequately control cabling for cameras, vibration monitoring, and tele
Region: III | Fermi | 13660 | 03/31/2006 05/08/2006 | 2006002-03 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustibles |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000341 Fermi 2 |  | 71152 | The inspectors identified a finding of very low significance (Green) associated with a Non-Cited Violation of license condition 2.C(9) for the failure to appropriately control transient combustibles on multiple occasions. Personnel left aerosol cans conta
Region: III | Fermi | 125036 | 07/29/2019 |  |  | LIV |  | Green | Failure to Establish Measures to Promptly Correct Inadequate Vortexing Protection for Pumps Aligned to the Condensate Storage Tank |  |  | TE?: N | 05000341 Fermi 2 |  | 71111.21M
Region: III | Kewaunee | 32975 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Ultimate Heat Sink Water Level |  |  | TE?: N | 05000305 Kewaunee |  | 71111.04Q | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that appropriate quality standards were specified and included
Region: III | Kewaunee | 32976 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment For Degraded Equipment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.13 | The inspectors identified a finding of very low safety significance and associated non-citied violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," Paragraph (a)(4), for the failure to properly
Region: III | Kewaunee | 32977 | 03/31/2013 05/14/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Fire Detection and Fixed Fire Suppression in a III.G.3 Area |  |  | TE?: N | 05000305 Kewaunee |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix R, Section III.G.3, "Fire Protection Program for Nuclear Power Facilities Operating Prior to January 1, 1979," for the lice
Region: III | Kewaunee | 32955 | 12/31/2012 02/08/2013 | 2012005-01 | NRC | NCV | Emergency Preparedness | Green | EAL Table Utilizes 1955 IGLD for Emergency Event Classification |  |  | TE?: N | 05000305 Kewaunee |  | 71111.01 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.54(q), "Emergency Plans," for failing to follow and maintain the effectiveness of an emergency plan that met the requirements of emergency planning standar
Region: III | Kewaunee | 32960 | 12/31/2012 02/08/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Starting Air System Quality Classification Error |  | H.3(b) Work Activity Coordination | TE?: N | 05000305 Kewaunee |  | 71111.04Q | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that appropriate quality standards were specified and in
Region: III | Kewaunee | 32962 | 12/31/2012 02/08/2013 | 2012005-04 | NRC | FIN | Barrier Integrity | Green | Removal of Refueling Procedure Requirement for Spent Fuel Pool cooling Without Prior NRC Approval |  |  | TE?: N | 05000305 Kewaunee |  | 71111.04Q
Region: III | Kewaunee | 32968 | 12/31/2012 02/08/2013 | 2012005-06 | NRC | NCV | Emergency Preparedness | Green | CO2 Detection instrumentation Unavailable For Emergency Event Classification |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000305 Kewaunee |  | 71114.05 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.54(q) "Emergency Plans," for failing to follow and maintain an emergency plan that met the requirements of emergency planning standard 10 CFR 50.47(b)(4).
Region: III | Kewaunee | 32942 | 11/02/2012 12/21/2012 | 2012009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with the Safety-related 125 Vdc Battery Service Test Procedures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to establish measures to assure that conditions a
Region: III | Kewaunee | 32943 | 11/02/2012 12/21/2012 | 2012009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Four CC System Manual Valves Were in the Correct Position as Required by ITS, SR 3.7.7.1 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of Improved Technical Specifications (ITS), Surveillance Requirement (SR) 3.7.7.1 because the licensee failed to ensure four component cooling
Region: III | Kewaunee | 32944 | 11/02/2012 12/21/2012 | 2012009-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Voltage Calculations for Motor Operated Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the design basis was correctly transl
Region: III | Kewaunee | 32948 | 11/02/2012 12/21/2012 | 2012009-04 | NRC | NCV | Mitigating Systems | Green | Failed to Consider Multiple Failures in ES 1.3, "Transfer to Containment Sump Recirculation" as Required by ITS, Section 5.4.1b) |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of Improved Technical Specification (ITS), Section 5.4.1b because Procedure EOP ES-1.3, "Transfer to Containment Sump Recirculation," Revision
Region: III | Kewaunee | 32949 | 11/02/2012 12/21/2012 | 2012009-05 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Correct Criterion Used for Time Critical Operator Actions to Prevent a Steam Generator Overfill |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure consistent criterion was used in OP KW ORT
Region: III | Kewaunee | 31921 | 09/30/2012 11/05/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment During Heavy Lift Over Service Water System |  | H.3(a) Work Planning | TE?: N | 05000305 Kewaunee |  | 71111.13 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.65,"Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," paragraph (a)(4), for the failure to properly assess and manage
Region: III | Kewaunee | 31924 | 09/30/2012 11/05/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Degradation Evaluation Of Leaking Refueling Water Storage Tank |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000305 Kewaunee |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to adequately evaluate a through wall flaw in the refueling water storage tan
Region: III | Kewaunee | 31926 | 09/30/2012 11/05/2012 | 2012004-04 | NRC | NCV | Occupational Radiation Safety | Green | Effective Dose Equivalent Determination (Section 2RS4) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 20.1201(c) for the failure to accurately assess occupational dose specific to effective dose equivalent for external exposure (EDEex) determinations. The i
Region: III | Kewaunee | 31920 | 09/28/2012 11/01/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Battery Rack Configuration Not In Accordance With Design Basis |  |  | TE?: N | 05000305 Kewaunee |  | 71152B | The inspectors identified a finding of very low safety significance (Green) and an associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because the licensee failed to ensure that the configuration of the safeguar
Region: III | Kewaunee | 31912 | 06/30/2012 08/09/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure To Utilize Work Order For Temporary Weld Repair On ASME Code, Class 2 Piping |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 71111.18 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to accomplish Temporary Modification (TMOD) 2012-11
Region: III | Kewaunee | 31913 | 06/30/2012 08/09/2012 | 2012003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Loose Cable Clamp Caused Loaded Spent Fuel Upender To Unintentionally Lower |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000305 Kewaunee |  | 71111.2 | A finding of very low safety significance (Green) and associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," was self-revealed because procedure MCM-FH-001, "Repair of the Fuel Transfer System," was inadequate. Specifica
Region: III | Kewaunee | 31914 | 06/30/2012 08/09/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure To Provide Adequate Suppression In Cable Spreading Area |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix R, Section III.G.3, for the licensee's failure to provide adequate fire suppression coverage for fire zone AX-
Region: III | Kewaunee | 31904 | 03/31/2012 05/10/2012 | 2012002-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Post-Maintenance Test Of Motor Replacements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.19 | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," which required, in part, that written procedures shall be implemented covering the applicable
Region: III | Kewaunee | 31905 | 03/31/2012 05/10/2012 | 2012002-05 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure For Technical Specification Surveillance |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have appropriate procedures to
Region: III | Kewaunee | 31885 | 12/31/2011 02/06/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Unanalyzed Flood Source From Technical Support Center Building |  |  | TE?: N | 05000305 Kewaunee |  | 71111.06 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to identify and analyze a potential flooding source that was with
Region: III | Kewaunee | 31889 | 12/31/2011 02/06/2012 | 2011005-03 | Self - Revealed | FIN | Mitigating Systems | Green | Two Of Six Operating Crew Failures On The Simulator Operational Evaluation Portion Of The 2011 Annual Requalification Operating Test |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000305 Kewaunee |  | 71111.11A | A self-revealed finding associated with operating crew performance on the simulator during a licensee-administered requalification examination was identified. Two of the six crews evaluated during the annual operating tests failed to pass their simulator
Region: III | Kewaunee | 31890 | 12/31/2011 02/06/2012 | 2011005-04 | NRC | FIN | Mitigating Systems | Green | Inadequate Operability Determination Of Control Room Air Conditioning System Components |  | H.1(c) Communication of Decisions | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance was identified by the inspectors for the failure to adequately assess operability of the Control Room Air Conditioning Component (ACC) dampers, ACC-15 and ACC-16, in Operability Determination (OD) 456, Revision 0,
Region: III | Kewaunee | 31900 | 12/31/2011 02/06/2012 | 2011005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Unanticipated Closure Of Emergency Diesel Generator B Output Breaker |  | H.4(a) Human Error Prevention | TE?: N | 05000305 Kewaunee |  | 71111.19 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to implement a procedure for an activity affecting quality
Region: III | Kewaunee | 31901 | 12/31/2011 02/06/2012 | 2011005-06 | NRC | NCV | Emergency Preparedness | Green | Incorrect Assumptions Used In The Development Of Emergency Action Level Thresholds |  |  | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance and associated non-cited violation of 10 CFR 50.54(q) was identified by the NRC for failing to maintain emergency plans that meet the requirements of emergency planning standard 10 CFR 50.47(b)(4). The inspectors
Region: III | Kewaunee | 31903 | 12/31/2011 02/06/2012 | 2011005-08 | NRC | NCV | Initiating Events | Green | Procedures For Reduced Inventory Operations Were Not Appropriate To Preclude Air Entrainment |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000305 Kewaunee |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish procedures for reduced inventory oper
Region: III | Kewaunee | 31873 | 10/07/2011 11/14/2011 | 2011008-01 | NRC | NCV | Initiating Events | Green | Flammable Gas Bottles Installed and/or Stored in the Auxiliary Building |  |  | TE?: N | 05000305 Kewaunee |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to check the adequacy of design for flammable gas b
Region: III | Kewaunee | 31874 | 09/30/2011 11/09/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure To Maintain Fire Barrier And Automatic Fire Suppression |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.05Q | A finding of very low safety significance and associated non-cited violation of license condition 2.C(3) of the Kewaunee Power Station Renewed Operating License was identified by inspectors for the failure to have a self-closing fire door that closed and
Region: III | Kewaunee | 31876 | 09/30/2011 11/09/2011 | 2011004-03 | NRC | NCV | Initiating Events | Green | Repetitive Molded Case Circuit Breaker Failures |  | H.3(b) Work Activity Coordination | TE?: N | 05000305 Kewaunee |  | 71111.12 | A finding of very low significance and associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR) 50.65(a)(3) was identified by the inspectors for the failure to incorporate industry operating experience into preventive maintenanc
Region: III | Kewaunee | 31882 | 09/30/2011 11/09/2011 | 2011004-05 | NRC | NCV | Mitigating Systems | Green | Misapplication Of Technical Specification 3.1.6 Applicability Note |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 71111.22 | A finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 3.1.6, "Control Bank Insertion Limits," was identified by the inspectors for the failure to comply with TS action condition 3.1.6.A due to incorre
Region: III | Kewaunee | 31883 | 09/30/2011 11/09/2011 | 2011004-06 | Self - Revealed | NCV | Mitigating Systems | Green | Incorrect Transformer Load Tap Changer Setting Causes Inoperable Offsite Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance and associated non-cited violation of Technical Specification 3.8.1 was self revealed for the failure to maintain a switchyard transformer load tap changer (LTC) at the appropriate setting for the predicted post t
Region: III | Kewaunee | 31864 | 06/30/2011 07/28/2011 | 2011003-01 | Self - Revealed | FIN | Mitigating Systems | Green | Technical Support Center Diesel Generator Output Breaker Fails To Close |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000305 Kewaunee |  | 71111.12 | A finding of very low safety significance was self revealed for the failure to perform adequate preventive maintenance on latching relay VR1/B46, a relay required for closure of the technical support center (TSC) diesel generator's (DG's) output breaker a
Region: III | Kewaunee | 31865 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Operability Determination Of A Heat Exchanger Leak On Emergency Diesel Generator A |  | H.1(c) Communication of Decisions | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance was identified by the inspectors for the failure to adequately assess operability of the service water system in operability determination 413, "EDG A Jacket Water Expansion Tank Overflow," in accordance with site
Region: III | Kewaunee | 31870 | 06/30/2011 07/28/2011 | 2011003-03 | NRC | NCV | Barrier Integrity | Green | Failed Standoffs Result In An Inoperable Train of Shield Building Ventilation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by inspectors for the failure to have and follow adequate procedures for eval
Region: III | Kewaunee | 31872 | 06/30/2011 07/28/2011 | 2011003-05 | NRC | FIN | Mitigating Systems | Green | Failure To Review And Update Severe Accident Management Guidelines In Accordance With An Established Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to perform reviews and update the Severe Accident Management Guidelines (SAMGs) in accordance with the licensee's nuclear administrative directives (NADs
Region: III | Kewaunee | 31859 | 03/31/2011 04/26/2011 | 2011002-01 | NRC | NCV | Initiating Events | Green | Misapplication Of Code Acceptance Criteria For Weld Flaws |  | H.4(a) Human Error Prevention | TE?: N | 05000305 Kewaunee |  | 71111.08P | A finding of very low safety-significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," was identified by the inspectors on March 3, 2011, for the licensee's failure to establish a pr
Region: III | Kewaunee | 31860 | 03/31/2011 04/26/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions Results In Potential Orange Path |  | H.3(a) Work Planning | TE?: N | 05000305 Kewaunee |  | 71111.13 | A finding of very low safety-significance and associated non-cited violation (NCV) of Technical Specification 5.4.1, "Procedures," was identified by the inspectors for the failure to implement procedures for shutdown operations involving shutdown operatio
Region: III | Kewaunee | 31861 | 03/31/2011 04/26/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Unintended Voiding Of The Reactor Vessel Closure Head |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.2 | A finding of very low safety-significance and associated non-cited violation (NCV) of Technical Specification 5.4.1, "Procedures," was identified by the inspectors for the failure to establish, implement, and maintain procedures for shutdown operations in
Region: III | Kewaunee | 31862 | 03/31/2011 04/26/2011 | 2011002-04 | Self - Revealed | FIN | Initiating Events | Green | Partial Loss Of Offsite Power Caused By Less Than Adequate Interface And Oversight Of Switchyard Modification Work |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety-significance was self-revealed for the failure to adequately control relay testing for switchyard breaker installations under Design Change WO KW100691871. Specifically, on March 10, 2011, Dominion Electrical Transmission tech
Region: III | Kewaunee | 31844 | 12/31/2010 02/04/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Containment Fan Coil Unit Acceptance Criteria |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.07A | A finding of very low safety significance and associated non cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to correctly translate the applicable regulatory requiremen
Region: III | Kewaunee | 31845 | 12/31/2010 02/04/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of Safety-Related Pressure Switches |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low significance and associated non cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings", was identified by the inspectors for the failure to develop and implement an adequate surveillance
Region: III | Kewaunee | 31852 | 12/31/2010 02/04/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Inappropriate Isolation of the Safety Injection Pump Minimum Flow Recirculation Lines |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 71111.22 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for multiple inadequate procedures, which directed cl
Region: III | Kewaunee | 31853 | 12/31/2010 02/04/2011 | 2010005-04 | Self - Revealed | NCV | Initiating Events | Green | Failure To Follow Red Channel Instrument Test Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.22 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when a nuclear control operator (NCO) failed to perform a procedure
Region: III | Kewaunee | 31826 | 09/30/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Operating Procedure |  |  | TE?: N | 05000305 Kewaunee |  | 71111.04Q | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to have an adequate emerge
Region: III | Kewaunee | 31831 | 09/30/2010 11/03/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Barrier Control Procedures Result In Exposed Service Water Pumps |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000305 Kewaunee |  | 71111.12 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to have adequate procedures to addres
Region: III | Kewaunee | 31839 | 09/30/2010 11/03/2010 | 2010004-04 | NRC | FIN | Mitigating Systems | Green | Performance Deficiency Associated With SLIV NCV - Replace of Automatic Actions With an Operator Manual Action Without Prior NRC Approval |  |  | TE?: N | 05000305 Kewaunee |  | 71111.18 | A Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," was identified by the inspectors for the failure to document an evaluation that provided a basis for the determination that the changes implemented in DCR 3163 and Emergency
Region: III | Kewaunee | 31838 | 09/30/2010 11/03/2010 | 2010004-05 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area (HRA) |  | H.3(b) Work Activity Coordination | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification 6.13 was identified by the inspectors after a worker entered a high radiation area on October 15, 2009. Radiation protection did not authorize
Region: III | Kewaunee | 31819 | 09/07/2010 09/30/2010 | 2010502-02 | NRC | FIN | Emergency Preparedness | Green | Changes Made to Emergency Action Level (EAL) Technical Bases that Decreased the Effectiveness |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 71114.04 | The inspector identified a Green finding associated with 10 CFR 50.47(b)(2) because the licensee failed to obtain prior NRC approval for a change made to its emergency plan that decreased the effectiveness of the plan. Specifically, the licensee changed w
Region: III | Kewaunee | 31820 | 09/03/2010 10/14/2010 | 2010006-01 | NRC | NCV | Barrier Integrity | Green | Failure to Correct the Classification of a Containment Isolation Valve |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71152B | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the failure to correct a condition adverse to quality. Specifically, the l
Region: III | Kewaunee | 31825 | 09/03/2010 10/14/2010 | 2010006-03 | NRC | FIN | Barrier Integrity | Green | Failure to Update the Updated Safety Analysis Report to Include Containment Penetration Leakage Testing Information |  |  | TE?: N | 05000305 Kewaunee |  | 71152B | The inspectors identified a finding associated with a traditional enforcement Severity Level IV, non-cited violation of 10 CFR 50.71(e), "Maintenance of Records, Making of Reports," having very low safety significance. The resulting changes were evaluated
Region: III | Kewaunee | 31817 | 06/30/2010 07/21/2010 | 2010003-01 | NRC | FIN | Mitigating Systems | Green | Inappropriate Use of a Probabilistic Methodology in an Operability Determination |  |  | TE?: N | 05000305 Kewaunee |  | 71111.01 | A finding of very low safety significance was identified by the inspectors for an inadequate operability determination performed for the emergency diesel generators. Specifically, the licensee used TORMIS, a computer code and probabilistic-based methodolo
Region: III | Kewaunee | 31812 | 03/31/2010 05/12/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Curve Was Incorporated Into Calibration Surveillance Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety-significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for inadequate surveillance calibration procedures. Spec
Region: III | Kewaunee | 31813 | 03/31/2010 05/12/2010 | 2010002-02 | Self - Revealed | NCV | Initiating Events | Green | Fuel Loading Occurs With Boron Concentration Below Required Minimum |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance and associated Non-Cited Violation of Technical Specification 3.8.a.5 was self-revealed when the licensee loaded fuel into the reactor with reactor coolant system boron sample results less than the minimum boron
Region: III | Kewaunee | 31814 | 03/31/2010 05/12/2010 | 2010002-03 | Self - Revealed | NCV | Initiating Events | Green | Incorrect Settings On Differential Relay Results In Loss Of Tertiary Auxiliary Transformer |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self-revealed for the failure to establish adequate measures to identify and control design interfaces and
Region: III | Kewaunee | 31807 | 02/12/2010 03/12/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Calculation Methodology Did Not Represent Actual Plant Equipment Configuration |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 71111.17T | A finding of very low safety-significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to assure that the calculation methodology represented the actual plan
Region: III | Kewaunee | 31798 | 12/31/2009 02/08/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure To Perform Dye Penetrant Examinations Of The Full Code Required Exam Surfaces |  | H.4(a) Human Error Prevention | TE?: N | 05000305 Kewaunee |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50.55a(g)(4) for the failure to perform dye penetrant examinations of the full required exam surface on safety injection (SI) gas collectio
Region: III | Kewaunee | 31800 | 12/31/2009 02/08/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Latching Pawl On Safety-Related Bus Tie Breakers Fails To Engage Due To Grease Hardening |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct deficiencies that had caused 4160
Region: III | Kewaunee | 31803 | 12/31/2009 02/08/2010 | 2009005-06 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Work Instructions Lead to Component Cooling Water Relief Valve Lift And Surge Tank Level Drop |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000305 Kewaunee |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to have adequate work instructions in place during the iso
Region: III | Kewaunee | 31804 | 12/31/2009 02/08/2010 | 2009005-07 | Self - Revealed | NCV | Initiating Events | Green | Procedure Inadequacy Results In The Tertiary Auxiliary Transformer Breaker Reopening After Alignment To The Bus |  | H.4(a) Human Error Prevention | TE?: N | 05000305 Kewaunee |  | 71111.22 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to have adequate procedures to ensure that step
Region: III | Kewaunee | 31782 | 09/30/2009 11/13/2009 | 2009004-02 | NRC | NCV | Barrier Integrity | Green | Containment Isolation Valve Inoperable With No Technical Specification Action requirement Entry |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.19 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to have adequate procedures that
Region: III | Kewaunee | 31787 | 09/30/2009 11/13/2009 | 2009004-03 | NRC | NCV | Initiating Events | Green | Failure To Adequately Analyze The Automatic Fast Transfer Feature That Allowed Operation With Both 4.16-kiloVolt Safety-Related Buses 1-5 And 1-6 Connected To The Reserve Auxiliary Transformer |  |  | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety-significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to perform a power system analysis calculation that would have id
Region: III | Kewaunee | 31789 | 09/30/2009 11/13/2009 | 2009004-05 | NRC | NCV | Initiating Events | Green | Inadequate Design Analysis For 105-Ton Transfer Cask Lifting Beam |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance and associated Non-Cited Violation of Title 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to provide an adequate s
Region: III | Kewaunee | 31772 | 08/20/2009 09/29/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Improper Application of 440Vac Rated Motors |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety-significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control," for the failure to ensure the proper application of safety-related 440Vac motors. Specifically, eight 440
Region: III | Kewaunee | 31773 | 08/20/2009 09/29/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Inaccurate Minimum Low Head Safety Injection Flow Specified in Emergency Operating Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety-significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to specify the appropriate quantitative acceptance criterion to as
Region: III | Kewaunee | 31778 | 08/20/2009 09/29/2009 | 2009006-03 | NRC | NCV | Barrier Integrity | Green | Non-Conservative Main Steam Line Break Analysis |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control," for the failure to correctly translate the design bases for the maximum steam generator narrow range leve
Region: III | Kewaunee | 31780 | 08/20/2009 09/29/2009 | 2009006-05 | NRC | NCV | Mitigating Systems | Green | Inadequate procedure for a Battery Room Flooding Event. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 7111121 | A finding of very low safety significance and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to provide adequate procedural direct
Region: III | Kewaunee | 31760 | 06/30/2009 08/05/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure That Motor Control Circuit Control Circuits Have Adequate Voltage To Operate During Design Basis Accident Conditions |  |  | TE?: N | 05000305 Kewaunee |  | NONE | . A finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," were identified by the inspectors for the failure to verify that motor control center (MCC) control c
Region: III | Kewaunee | 31763 | 06/30/2009 08/05/2009 | 2009003-04 | NRC | NCV | Emergency Preparedness | Green | Seismic Monitoring System Repeatedly Fails Surveillance |  | P.1(b) Trend Performance CAP | TE?: N | 05000305 Kewaunee |  | 71111.22 | A finding of very low safety significance (Green) and an associated Non-Cited Violation were identified by the inspectors for the licensee's failure to maintain radiation monitoring instrumentation operable that was required by its emergency plans to meet
Region: III | Kewaunee | 31764 | 06/30/2009 08/05/2009 | 2009003-05 | NRC | NCV | Public Radiation Safety | Green | Inadequate Calibration Of Radiation Monitor R-19 |  |  | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance (Green) and an associated Non-Cited Violation of Technical Specification 4.1 were identified by the inspectors for the licensee's calibration practices for process radiation instrument R-19 that did not qualify as
Region: III | Kewaunee | 31765 | 06/30/2009 08/05/2009 | 2009003-06 | NRC | NCV | Barrier Integrity | Green | Failed Backdraft Damper Renders Containment Fan Coil Unit Inoperable |  | P.2(b) Implementing Operating Experience | TE?: N | 05000305 Kewaunee |  | 71153 | . A finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were self revealed for the licensee's failure to maintain adequate procedures f
Region: III | Kewaunee | 31766 | 06/30/2009 08/05/2009 | 2009003-07 | NRC | FIN | Barrier Integrity | Green | Failure To Update Procedures As Required By Commitments |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance (Green) was identified by the inspectors for the licensee's failure to update procedures as required by NRC commitments. Specifically, a procedure for fuel oil sampling and a procedure for steam generator tube ins
Region: III | Kewaunee | 31748 | 03/31/2009 05/08/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Potential Debris Sources Could Clog A Drain Credited During Internal Floods |  |  | TE?: N | 05000305 Kewaunee |  | 71111.06 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to translate the flooding design basis into specifications, proce
Region: III | Kewaunee | 31750 | 03/31/2009 05/08/2009 | 2009002-03 | NRC | NCV | Initiating Events | Green | Inappropriate Application Of A Dedicated Operator During A Component Cooling Water Surveillance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.13 | A finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR 50.65(a)(4) was identified by the inspectors for the failure to properly assess risk that resulted from risk significant maintenance being performed on the comp
Region: III | Kewaunee | 31754 | 03/31/2009 05/08/2009 | 2009002-07 | NRC | NCV | Mitigating Systems | Green | Siphon Line Which Interconnected Two Diesel Generator Emergency Fuel Oil Storage Tanks Was Not Functioning as Designed |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance (Green) and associated Severity Level IV, Non-Cited Violation of 10 CFR 50.59 was identified by the inspectors while reviewing Unresolved Item 05000305/2008003-03, "Siphon Line Which Interconnected Two Diesel Gene
Region: III | Kewaunee | 31755 | 03/31/2009 05/08/2009 | 2009002-08 | NRC | NCV | Barrier Integrity | Green | Steam Exclusion Door Failure Results In Multiple Safety Systems Being Declared Inoperable |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to follow the corrective action program proc
Region: III | Kewaunee | 31745 | 12/31/2008 02/10/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Room Cooling Fan Testing Deficienceies |  |  | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance and an associated NCV of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to verify the ventilation flow rate for the emergency diesel gener
Region: III | Kewaunee | 31746 | 12/31/2008 02/10/2009 | 2008005-03 | NRC | NCV | Initiating Events | Green | Failure to Transfer Turbine Valve Testing Requirements into the USAR |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance and associated Severity Level IV Non-Cited Violation of 10 CFR 50.71, "Maintenance of records, making of reports," was identified by the inspectors for the licensee's failure to adequately update the Kewaunee Powe
Region: III | Kewaunee | 31737 | 09/30/2008 11/10/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Operability Evaluation for Degraded Gauge Pedestals Failed to Adequately Evaluate Degraded Conditions Per Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors during a review of an operability evaluation for degraded con
Region: III | Kewaunee | 31738 | 09/30/2008 11/10/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a 10 CFR Part 50.59 Screening for Alteration During Maintenance that Existed for More Than 90 Days |  | H.3(a) Work Planning | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance and an associated Severity Level IV, Non-Cited Violation of 10 CFR 50.59 was identified by the inspectors for a failure to perform a 50.59 screening for an alteration during maintenance that existed for more than
Region: III | Kewaunee | 31741 | 09/30/2008 11/10/2008 | 2008004-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure Results in Unplanned Control Rod Motion |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when control rods automatically stepped inward unexpectedly. Ultimately
Region: III | Kewaunee | 30853 | 06/30/2008 08/08/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | Failure to Follow the Provisions of General Nuclear Procedure, GNP-12.06.01, "Hot and Cold Weather Operations" |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.01 | A finding of very low safety significance (Green) and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors following an inspection of licensee preparations for adverse
Region: III | Kewaunee | 30849 | 03/31/2008 05/14/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Scaffolding in Close Proximity to Multiple Safety-Related Systems Affects Operability |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71111.04Q | A finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to install scaffoldin
Region: III | Kewaunee | 30850 | 03/31/2008 05/14/2008 | 2008002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow the Provisions of Corrective Action Procedure PI-KW-200 Following Surveillance Testing of Containment Isolation Valve LOCA-31 |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.19 | A finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors following surveillance testing of containment is
Region: III | Kewaunee | 30835 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Characterize and Manage Risk in Accordance with Maintenance Rule With the Turbine-Driven Auxiliary Feedwater Pump in Pull-to-Lock |  |  | TE?: N | 05000305 Kewaunee |  | 71111.13 | A finding of very low safety significance and an associated Non Cited Violation (NCV) of 10 CFR 50.65(a)(4), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," was identified by the inspectors during startup of the rea
Region: III | Kewaunee | 30836 | 12/31/2007 02/11/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Solenoid Valve Not Installed Properly |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the "B" turbine building service water header isolation valve failed to
Region: III | Kewaunee | 30839 | 12/31/2007 02/11/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Post-Maintenance Testing of Steam Traps in the Turbine-Driven Auxiliary Feedwater Pump System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.19 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors during observation of a post-maintenance test on a steam trap
Region: III | Kewaunee | 30840 | 12/31/2007 02/11/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Seismic Storage Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors during a review of procedures related to the control and stor
Region: III | Kewaunee | 30827 | 12/19/2007 02/01/2008 | 2007011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition Review for Fuel Leak. |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," of very low safety significance, for failure by the licensee to follow procedural requirements for performing an adequate exte
Region: III | Kewaunee | 30833 | 12/19/2007 02/01/2008 | 2007011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Corrective Action Documents for Multiple Leaks in the Plant |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 95002 | The inspections identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," of very low safety significance. Specifically, the licensee failed to initiate corrective action documents in accordance with
Region: III | Kewaunee | 30834 | 12/19/2007 02/01/2008 | 2007011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Update the Updated Safety Analysis Report with Safety Analysis for Pressure Locking of Containment Sump Isolation Valves |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The inspectors identified a non cited violation of 10 CFR 50.71, of very low safety significance, for the licensee's failure to update the Updated Safety Analysis Report (USAR). Specifically, the licensee failed to update the USAR to fully reflect the res
Region: III | Kewaunee | 30842 | 12/19/2007 02/01/2008 | 2007011-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition Review of BF-66 Relays |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The inspectors identified a non cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," of very low safety significance, for failure by the licensee to follow procedural requirements for performing an adequate exte
Region: III | Kewaunee | 30820 | 09/30/2007 11/02/2007 | 2007004-02 | NRC | NCV | Initiating Events | Green | Failure to Implement Maintenance Rule (a)(1) in Corrective Actions on the "G" Instrument Air Compressor |  |  | TE?: N | 05000305 Kewaunee |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50.65(a)(1), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants." Specifically, as of August 25, 2007, t
Region: III | Kewaunee | 30824 | 09/30/2007 11/02/2007 | 2007004-03 | NRC | NCV | Barrier Integrity | Green | Preconditioning of Safety-Related Motor-Operated Valves Prior to Performance of Technical Specification Required Surveillance Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," during plant preparations to perform Surveillance Procedure SP-
Region: III | Kewaunee | 30818 | 06/30/2007 08/14/2007 | 2007003-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure for Surveillance Testing of Auxiliary Building Special Ventilation Zone |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.22 | The inspectors identified a finding having very low safety significance and an associated non-cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," while reviewing surveillance testing procedures for the auxiliar
Region: III | Kewaunee | 30808 | 05/18/2007 06/29/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Procedure Non-Compliance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | NONE | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to adequately implement procedure DNAP-1604, "Cause Evaluation Program," and the Cause Evaluation Handbook during investigat
Region: III | Kewaunee | 30785 | 04/17/2007 06/01/2007 | 2007006-01 | NRC | NCV | Initiating Events | Green | No Analysis or Procedures to Establish Operability of the Tertiary Auxiliary Transformer Source |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to evaluate the capability of the 345 kV offsite power supply when iso
Region: III | Kewaunee | 30786 | 04/17/2007 06/01/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | No Motor Starting Analyses for Offsite Power Supply |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to perform motor starting studies to demonstrate that motors would suc
Region: III | Kewaunee | 30789 | 04/17/2007 06/01/2007 | 2007006-05 | NRC | NCV | Mitigating Systems | Green | Increased Cable Resistance Due to Accident Temperatures |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to consider the effects of accident temperatures on cable resistance i
Region: III | Kewaunee | 30753 | 04/17/2007 06/01/2007 | 2007006-07 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate 125-Volt Direct Current Breaker Interrupting Short Circuit Current Capability |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to ensure that four of the 125-Volt Direct Current (DC) circuit
Region: III | Kewaunee | 30795 | 04/17/2007 06/01/2007 | 2007006-08 | NRC | NCV | Mitigating Systems | Green | Failure to Use Actual Minimum Voltage Value in 125-Volt Direct Current Voltage Drop Calculation |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to use correct design input data into the 125-Volt Direct Curre
Region: III | Kewaunee | 30796 | 04/17/2007 06/01/2007 | 2007006-09 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria in 125-Volt Direct Current Station Battery Load Tests Procedures |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings." Specifically, the licensee failed to include the acceptable minimum battery
Region: III | Kewaunee | 30797 | 04/17/2007 06/01/2007 | 2007006-10 | NRC | NCV | Mitigating Systems | Green | Adequate Control Voltage for 4160-Volt Breaker's Closing Coil Was Not Assured |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to assure that the minimum available control voltage at the 416
Region: III | Kewaunee | 30798 | 04/17/2007 06/01/2007 | 2007006-11 | NRC | NCV | Mitigating Systems | Green | Safeguard Battery Load Profile Did Not Include Loss of Offsite Power/Loss of Coolant Accident Loads |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" having very low safety significance for the licensee's failure to assure that safeguard battery loads profile was adequate to meet all Updated Safety Analysis
Region: III | Kewaunee | 30799 | 04/17/2007 06/01/2007 | 2007006-12 | NRC | NCV | Mitigating Systems | Green | Electrolytic Capacitors in Spare Safeguard Battery Charger Not Periodically Energized |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." Specifically, the licensee failed to incorporate previously identified vendor recommendation t
Region: III | Kewaunee | 30781 | 04/17/2007 06/01/2007 | 2007006-13 | NRC | NCV | Mitigating Systems | Green | Diesel Loading Calculations Non-Conservative |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to properly account for all loads on the diesel generators. Upon disco
Region: III | Kewaunee | 30800 | 04/17/2007 06/01/2007 | 2007006-15 | NRC | NCV | Initiating Events | Green | Failure to Incorporate and Effectively Implement Operating Experience in Reactor Trip Breaker Maintenance Activities |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR 50.65(a)(3) for the failure to incorporate external and internal operating experience into preventive maintenance activities for the reactor trip breakers. Th
Region: III | Kewaunee | 30801 | 04/17/2007 06/01/2007 | 2007006-16 | NRC | NCV | Initiating Events | Green | Acceptance Criteria Not Met Due to Failure to Follow Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, on May 22, 2006 during the performance of PMP-47-01, maintenance tec
Region: III | Kewaunee | 30802 | 04/17/2007 06/01/2007 | 2007006-17 | NRC | NCV | Mitigating Systems | Green | RWST Level Instruments Do Not Protect SI and RHR Pumps from Excessive Air Entrainment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to incorporate the results of design calculations with respect to mini
Region: III | Kewaunee | 30803 | 04/17/2007 06/01/2007 | 2007006-18 | NRC | NCV | Barrier Integrity | Green | Loss of Coolant Environment Improperly Considered in Containment Fan Coil Unit Calculation |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to use the correct data when determining the most limiting conditions
Region: III | Kewaunee | 30804 | 04/17/2007 06/01/2007 | 2007006-19 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Assumption Used in Service Water Flow Model Calculation |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to appropriately account for service water strainer plugging in the se
Region: III | Kewaunee | 30805 | 04/17/2007 06/01/2007 | 2007006-20 | NRC | NCV | Mitigating Systems | Green | Inadequate Screen House Ventilation Damper Maintenance |  |  | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," Paragraph (b)(2), for the licensee's failure to scope the
Region: III | Kewaunee | 30806 | 04/17/2007 06/01/2007 | 2007006-21 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Assumption Used for "B" Component Cooling Water Pump Room Heat Gain Calculation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III. Specifically, the licensee failed to account for component cooling water (CCW) piping temperatures as high as 176¦F in the
Region: III | Kewaunee | 30807 | 04/17/2007 06/01/2007 | 2007006-22 | NRC | NCV | Mitigating Systems | Green | Safety Injection Pump Lube Oil Coolers Testing Deficiencies |  | P.3(a) Self-Assessment | TE?: N | 05000305 Kewaunee |  | 7111121 | The inspectors identified a finding having very low significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." Specifically, the licensee failed to establish a testing program capable of identifying an unacceptable con
Region: III | Kewaunee | 30767 | 03/31/2007 05/10/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Implement E-0-05, "Response to Natural Events," During a High Wind Advisory |  | H.1(c) Communication of Decisions | TE?: N | 05000305 Kewaunee |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement procedure E-O-05, "R
Region: III | Kewaunee | 30771 | 03/31/2007 05/10/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Inappropriate QA Class Components Installed in Diesel Generator |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000305 Kewaunee |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of Technical Specification 6.8, "Procedures," during a review on January 27, 2007, of maintenance performed on the station blackout diesel ge
Region: III | Kewaunee | 30773 | 03/31/2007 05/10/2007 | 2007002-04 | NRC | NCV | Mitigating Systems | Green | Nuclear Instrument Test Performed Contrary to Procedural Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of Technical Specification 6.8, "Procedures," when the licensee failed, on January 8, 2007, to follow procedures for performing the monthly s
Region: III | Kewaunee | 30777 | 03/31/2007 05/10/2007 | 2007002-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Seismic Storage requirements in Station Housekeeping Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," during a review of procedures related to the control and sto
Region: III | Kewaunee | 30778 | 03/31/2007 05/10/2007 | 2007002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Potentially Inadequate Design of the Service Water System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000305 Kewaunee |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," when the licensee failed to have in place adequate procedures to
Region: III | Kewaunee | 30779 | 03/31/2007 05/10/2007 | 2007002-07 | NRC | NCV | Mitigating Systems | Green | Foreign Material in Containment as a Result of Inadequate Containment Closure Inspections |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of Technical Specification 6.8, "Procedures," on February 28, 2007, when the licensee failed to adequately perform a containment closeout ins
Region: III | Kewaunee | 30757 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Initiating Events | Green | Inadequate Pre-Fire Strategy Identified in Cable Spreading Room |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.05Q | A finding of very low safety significance and an associated non-cited violation of Technical Specification 6.8, "Procedures," was identified by the inspectors for the failure to identify radiological and toxic hazards in the cable spreading area fire zone
Region: III | Kewaunee | 30763 | 12/14/2006 01/26/2007 | 2006016-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Emergency Diesel Generator Air Intake Temperature Limitations Impact Upon Ability to Meet Technical Specification Surveillance Requirements |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000305 Kewaunee |  | 7111102 | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." The licensee failed to identify the impact of air intake temperature limitation on the ability of
Region: III | Kewaunee | 30766 | 12/14/2006 01/26/2007 | 2006016-05 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Suppression for Safe Shutdown Equipment in Appendix R, III.G.3 Area |  |  | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR Part 50, Appendix R, "Fire Protection Program for Nuclear Power Facilities Operating Prior to January 1, 1979." The licensee failed to provide required fi
Region: III | Kewaunee | 30759 | 10/23/2006 01/30/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Scaffolding in Contact with the Safety Injection System Affects Operability |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71111.2 | A finding of very low safety significance and an associated non-cited violation of Technical Specification 6.8, "Procedures," was identified by the inspectors on October 23, 2006, for the failure to install scaffolding in accordance with station procedure
Region: III | Kewaunee | 30758 | 10/11/2006 01/30/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Inadvertent Drain Down of the Reactor Coolant system During Fill and Vent of the Containment Spray System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000305 Kewaunee |  | 71111.2 | A finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed during performance of a plant safety-related procedure to fill and vent the
Region: III | Kewaunee | 30751 | 09/30/2006 11/08/2006 | 2006004-03 | NRC | FIN | Mitigating Systems | Green | Technical Specification LCO Not Entered for Diesel Generators Inoperable While in Refueling Shutdown |  | H.4(b) Procedural Compliance | TE?: N | 05000305 Kewaunee |  | 71153 | A finding of very low safety significance (Green) was identified by the inspectors when the licensee failed to properly apply shutdown Technical Specifications (TSs) for the residual heat removal (RHR) system with both emergency diesel generators (EDGs) d
Region: III | Kewaunee | 30738 | 06/30/2006 08/07/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Reactor Protection System Surveillance Procedure Revised Without Proper Review |  |  | TE?: N | 05000305 Kewaunee |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification 6.8, "Procedures," during a review of a procedure. The licensee had changed the procedure to allow the turbine-driven auxi
Region: III | Kewaunee | 30739 | 06/30/2006 08/07/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Leak Developed in Service Water Pipe after Wall Thinning Evaluation was Cancelled |  |  | TE?: N | 05000305 Kewaunee |  | 7111114 | A self-revealed finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," were identified on April 25, 2006, when a leak due to pipe-wall thinning was identified in a 9
Region: III | Kewaunee | 30742 | 06/30/2006 08/07/2006 | 2006003-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Properly Calibrate the Waste Discharge Liquid and the Steam Generator Blowdown Radiation Monitors |  |  | TE?: N | 05000305 Kewaunee |  | 7112201 | The inspectors identified a finding of very low safety significance and an associated violation of NRC requirements for the failure to comply with technical specification and Offsite Dose Calculation Manual (ODCM) requirements in the calibration of two li
Region: III | Kewaunee | 30746 | 06/23/2006 08/02/2006 | 2006011-01 | NRC | NCV | Initiating Events | Green | Procedure for Reactor Startup Not Followed |  |  | TE?: N | 05000305 Kewaunee |  | 93812 | The inspectors identified a finding associated with a non-cited violation of Technical Specification 6.8.a (written procedures and administrative policies). The finding was for the licensee's failure to follow approved procedures during a plant startup. T
Region: III | Kewaunee | 30747 | 06/23/2006 08/02/2006 | 2006011-02 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Reactor Startup |  |  | TE?: N | 05000305 Kewaunee |  | 93812 | The inspectors identified a finding associated with an non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," of very low safety significance associated with an event. The inspectors identified that Proce
Region: III | Kewaunee | 30733 | 05/19/2006 07/03/2006 | 2006007-01 | NRC | NCV | Initiating Events | Green | Criterion XVI: Failed to Identify Causes and Corrective Actions to Preclude Repetition for Significant Conditions Adverse to Quality |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The NRC inspectors identified a finding of very low safety significance that involved a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions." Specifically, for the turbine building flooding and auxiliary feedwater air entrainment p
Region: III | Kewaunee | 30734 | 05/19/2006 07/03/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | Criterion V: Failed to Incorporate Appropriate Acceptance Criteria for Assessing Operability of the AFW Pump |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The NRC inspectors identified a finding of very low safety significance that involved a violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, the licensee failed to incorporate appropriate acceptance
Region: III | Kewaunee | 30735 | 05/19/2006 07/03/2006 | 2006007-03 | NRC | NCV | Mitigating Systems | Green | Criterion III: Failed to Correctly Translate Containment Sump Volume into Design |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The NRC inspectors identified a finding of very low safety significance that involved a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to ensure that design basis calculations correctly translat
Region: III | Kewaunee | 30736 | 05/19/2006 07/03/2006 | 2006007-04 | NRC | NCV | Mitigating Systems | Green | Criterion III: Failed to Verify or Check the Adequacy of the Design Canceling Design Change Request 2548 |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The NRC inspectors identified a finding of very low safety significance that involved a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to properly evaluate the minimum flow requirements of the h
Region: III | Kewaunee | 30728 | 05/19/2006 07/03/2006 | 2006007-05 | NRC | NCV | Barrier Integrity | Green | Criterion III: Failed to Properly Translate the ICS Design Basis into the Technical Specifications |  |  | TE?: N | 05000305 Kewaunee |  | 95002 | The NRC inspectors identified a finding of very low safety significance that involved a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to ensure that design basis calculations correctly translat
Region: III | Kewaunee | 30727 | 05/05/2006 06/14/2006 | 2006010-01 | NRC | NCV | Initiating Events | Green | Failure to Incorporate Operating Experience Into Preventive Maintenance Procedures |  |  | TE?: N | 05000305 Kewaunee |  | 93812 | The inspectors identified a finding associated with a non-cited violation (NCV) of 10 CFR 50.65 (the Maintenance Rule), having very low safety significance for the licensee's failure to incorporate into station procedures available internal and external o
Region: III | Kewaunee | 30732 | 05/05/2006 06/14/2006 | 2006010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Separation of Cables |  |  | TE?: N | 05000305 Kewaunee |  | 93812 | The inspectors identified a finding associated with a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that pertained to a modification that failed to incorporate applicable design requirements for cable separation. Nons
Region: III | Kewaunee | 30717 | 03/31/2006 05/02/2006 | 2006002-01 | NRC | FIN | Initiating Events | Green | Failure to Control Loose Materials Within the Protected Area in Response to Adverse Weather Conditions |  |  | TE?: N | 05000305 Kewaunee |  | 71111.01 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to control loose materials within the protected area south of the transformer bays in response to adverse weather conditions. The material could have bee
Region: III | Kewaunee | 30718 | 03/31/2006 05/02/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Ineffective Corrective Actions to Resolve Boric Acid Leakage from the 1A RHR Pump Flange Studs and Nuts |  |  | TE?: N | 05000305 Kewaunee |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for ineffective identification and the initiation of corrective actions to
Region: III | Kewaunee | 30719 | 03/31/2006 05/02/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Apply Appropriate Quality Classification to TSC Diesel Generator Modifications as Required by Procedures |  |  | TE?: N | 05000305 Kewaunee |  | NONE | A finding of very low safety significance and an associated non-cited violation of the Kewaunee Technical Specifications, Section 6.8, "Procedures," was identified by the inspectors during a review of plant modification Design Change Request 3490, which r
Region: III | Kewaunee | 30724 | 03/30/2006 05/02/2006 | 2006002-04 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Evaluate the Extent-of-Condition of Degraded Fuses in Installed Equipment |  |  | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance was identified by the inspectors for the failure to adequately evaluate the extent-of-condition relative to installed equipment for a 10 CFR Part 21 notification for degraded Bussmann« fuses. The primary cause of
Region: III | Kewaunee | 30725 | 03/30/2006 05/02/2006 | 2006002-05 | NRC | FIN | Initiating Events | Green | Failure to Adequately Evaluate an Inoperative Indicating Lamp for a Turbine Control Valve |  |  | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance was identified by the inspectors for the failure to adequately evaluate an inoperative indicating lamp associated with the turbine control valves. The primary cause of this finding was attributed to the cross-cutt
Region: III | Kewaunee | 30726 | 03/30/2006 05/02/2006 | 2006002-06 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately Evaluate Degraded Flow Conditions on a SW System Radiation Monitor |  |  | TE?: N | 05000305 Kewaunee |  | 71152 | A finding of very low safety significance and an associated non-cited violation of the Kewaunee Technical Specifications, Section 6.8, "Procedures," was identified by the inspectors for the failure to adequately evaluate degraded flow in a service water s
Region: III | LaSalle | 126375 | 12/31/2019 01/31/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Design Review Did Not Identify Neutral Required To Be Switched When Field Change Was Performed |  | NPP | TE?: N | 05000374 LaSalle 2 | Design Control | 71153 | The inspectors identified a finding of very low safety significance and an associated violation of Title 10 CFR Part 50, Appendix B, Criteria III, "Design Control," for the licensee's failure to verify the adequacy of design during the performance of a de
Region: III | LaSalle | 125433 | 09/30/2019 11/07/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with National Fire Protection Association 13, "Standard for the Installation of Sprinkler Systems," Requirements During Installation of the Unit 1 Cable Spreading Room Preaction Fire System |  | P.1 - Identification | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 | Protection Against External Factors | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of the Unit 1 License Condition C.25, and Unit 2 License Condition C.15, Fire Protection Program, for the failure to install the cable spread
Region: III | LaSalle | 125586 | 09/30/2019 11/07/2019 | 2019003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Implement the Primary Containment Leakage Rate Testing Program for Traversing Incore Probes System Containment Isolation Valve 2C51-J004C |  | H.6 - Design Margins | TE?: N | 05000374 LaSalle 2 | SSC and Barrier Performance | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of Technical Specification 5.5.13, Primary Containment Leakage Rate Testing Program, for the licensee's failure to perform a cause determinat
Region: III | LaSalle | 125241 | 06/30/2019 08/13/2019 | 2019002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Post Maintenance Test to Demonstate 2C Traversing In-core Probe System was able to Perform its Intended Function |  | H.5 - Work Management | TE?: N | 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance for the licensee's failure to perform a post maintenance test in accordance with station procedure MA-AA-716-012, "Post Maintenance Testing," Revision 23. Specifically, after performing r
Region: III | LaSalle | 125383 | 06/30/2019 08/13/2019 | 2019002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate General Electric Hitachi Nuclear Energy Safety Communication 11-05 Criteria into Surviellance Procedures for Control Rod Operability |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 | Procedure Quality | 71153 | The inspectors documented a self-revealed Green finding and associated Non-cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the licensee's failure to incorporate Safety Communication (SC) 11-05 friction limits into surveill
Region: III | LaSalle | 124496 | 03/31/2019 05/08/2019 | 2019001-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Make an Individual Knowledgable of Dose Rates Prior To Entry Into a High Radiation Area |  | H.3 - Change Management | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 | Program & Process | 71124.01 | An NRC identified Green finding and associated Non-cited Violation of Technical Specification 5.7.1. (e) High Radiation Areas, was identified when the licensee allowed an individual to make entry into a high radiation area where dose rates had been determ
Region: III | LaSalle | 124795 | 03/31/2019 05/08/2019 | 2019001-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Station Erosion in Piping and Components Guide Results in Three Inch Hole in 2TEC5A-Header |  | P.2 - Evaluation | TE?: N | 05000374 LaSalle 2 | Equipment Performance | 71153 | The inspectors documented a self-revealed finding of very low safety significance for the licensee’s failure to follow station procedure ER-AA-430-1004, “Erosion in Piping and Components (EPC) Guide,” Revision 1. Specifically, design engineering personnel
Region: III | LaSalle | 25927 | 12/31/2018 02/14/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adhere to Scaffolding Program |  | H.13 - Consistent Process | TE?: N | 05000373 LaSalle 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure follow station procedu
Region: III | LaSalle | 5 | 12/31/2018 02/14/2019 | 2018004-02 | NRC | NCV | Barrier Integrity | Green | Control of instrument used in an activity affecting quality not appropriate to the circumstance |  | NPP | TE?: N | 05000373 LaSalle 1 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Technical Specification 5.4.1.a “Instructions, Procedures, and Drawings,” for the licensee’s failure to establish procedures of a type appropriate to the
Region: III | LaSalle | 24647 | 11/16/2018 11/26/2018 | 2018011-01 | NRC | FIN | Mitigating Systems | Green | Failure to Validate an Electrical Strategy |  | H.13 - Consistent Process | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 2515/191 | The team identified a Green finding for the failure to validate one deployment path of the electrical strategy procedure was feasible. Specifically, the team identified that there was insufficient electrical cabling to implement the contingency path of LO
Region: III | LaSalle | 24653 | 09/30/2018 11/08/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Heat Exchanger Inspection Procedures Appropriate for the Circumstances |  | H.12 - Avoid Complacency | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, “Instructions Procedures, and Drawings,” for the licensee’s failure to ensure that activiti
Region: III | LaSalle | 24654 | 09/30/2018 11/08/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Appropriate Inservice Testing Procedure |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings”, for the licensee’s failure to prescribe procedures that were appropriat
Region: III | LaSalle | 24655 | 09/30/2018 11/08/2018 | 2018003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Goals to Monitor Steam Tunnel Check Dampers |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | The inspectors identified a finding and an associated violation of 10 CFR 50.65(a)(1) for the licensee’s failure to establish goals to monitor the performance of steam tunnel check dampers. Specifically, the licensee’s goals for functional failure and con
Region: III | LaSalle | 24658 | 09/30/2018 11/08/2018 | 2018003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Manage the Increase in Risk During a Battery Charger Capacity Test |  | H.13 - Consistent Process | TE?: N | 05000373 LaSalle 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50.65(a)(4) for the failure to manage risk when the licensee failed to adhere to procedure WC–AA–101, Revision 28, “On-line Work Co
Region: III | LaSalle | 24660 | 09/30/2018 11/08/2018 | 2018003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Fuel Oil Relief Valve Setting into Design Drawing of Record |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to assure that applicable regulatory require
Region: III | LaSalle | 24662 | 09/30/2018 11/08/2018 | 2018003-08 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Engineering Change Results in Reactor Coolant Boundary Leakage |  | H.4 - Teamwork | TE?: N | 05000373 LaSalle 1 |  | 71153 | The inspectors documented a self-revealed Green finding of very low safety significance and an associated Non-Cited Violation (NCV) of LaSalle County Station Unit 1 Technical Specification (TS) 5.4.1 “Procedures,” and an associated violation of TS 3.4.5 f
Region: III | LaSalle | 24368 | 06/30/2018 08/14/2018 | 2018002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement a Preventative Maintenance Strategy for Residual Heat Removal Service Water Pump Shorting Relays |  | NPP | TE?: N | 05000373 LaSalle 1 |  | 71111.18 | A self-revealed finding of very low safety significance was identified for the licensee’s failure to implement a PM strategy for the residual heat removal service water (RHRSW) pump shorting relays in accordance with procedure MA–AA–716–210, “Performance
Region: III | LaSalle | 24369 | 06/30/2018 08/14/2018 | 2018002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedure and Perform Database Revision Review Requirements |  | NPP | TE?: N | 05000373 LaSalle 1 |  | 71111.18 | The inspectors identified a Green finding of very low safety significance for the licensee’s failure to follow procedure NSWP–WM–03, “Predefine Database Revisions,” Revision 0, for retiring procedure LES–GM–108, “Inspection of 480V Motor Control Center Eq
Region: III | LaSalle | 23980 | 04/06/2018 05/08/2018 | 2018010-01 | NRC | NCV | Initiating Events | Green | Failure to Translate Reactor Building Superstructure Design Basis |  | H.12 - Avoid Complacency | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.17T | Inspectors identified a Green finding and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to assure that the applicable Updated Final Safety An
Region: III | LaSalle | 23542 | 03/31/2018 05/15/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Post-Maintenance Testing Failed to Demonstrate Testable Check Valve Function |  | H.5 - Work Management | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | A self-revealed Green finding of very low safety significance and an associated Non-Cited Violation of Title 10 CFR 50 Appendix B, Criterion XI, “Test Control,” was documented by the inspectors for the failure to perform post-maintenance testing that woul
Region: III | LaSalle | 23543 | 03/31/2018 05/15/2018 | 2018001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Update Throttle Valve Position in Accordance with Station Procedures |  | H.12 - Avoid Complacency | TE?: N | 05000373 LaSalle 1 |  | 71111.19 | The inspectors identified a Green finding of very low safety significance and an associated Non-Cited Violation of LaSalle Technical Specifications 5.4.1, “Procedures,” for the failure to implement station procedures covering the applicable procedures rec
Region: III | LaSalle | 23168 | 12/31/2017 02/13/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Brazing Repair Procedures with Appropriate Acceptance Criteria |  | H.5 - Work Management | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified by the inspectors for the failure to establish instructions with acceptanc
Region: III | LaSalle | 23167 | 12/31/2017 02/13/2018 | 2017004-03 | NRC | NCV | Barrier Integrity | Green | Primary Containment Structure, Suppression Pool Columns, Downcomer Vent and Downcomer Vent Bracing Did Not Meet Seismic Category I Requirements |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified by the inspectors for the failure to ensure the adequacy of the design for the primary containme
Region: III | LaSalle | 23166 | 12/31/2017 02/13/2018 | 2017004-04 | Self - Revealed | NCV | Initiating Events | Green | Failure of Offsite Power Backfeed Procedure to be Appropriate to the Circumstances Caused Unit 1 Scram |  | NPP | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71153 | A finding of very low safety significance and an associated non-cited violation of LaSalle Technical Specification (TS) 5.4.1, “Procedures,” occurred on February 13, 2017, for the station’s failure to maintain instructions of a type appropriate to the cir
Region: III | LaSalle | 23457 | 12/01/2017 01/04/2018 | 2017010-01 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure Fire Door Was Engaged And Pinned |  | H.8 - Procedure Adherence | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05T | The inspectors identified a finding of very-low safety significance (Green) and associated Non-Cited Violation of License Condition 2.C.15 for Unit 2, for the licensee’s failure to ensure all fire rated assemblies (i.e., fire doors) were operable. Specifi
Region: III | LaSalle | 22296 | 09/30/2017 11/08/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Rule Monitoring of the Low Pressure Core Spray System |  | P.2 - Evaluation | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | The inspectors identified a Green non-cited violation (NCV) of Title 10 of the Code of Federal Regulation (CFR) 50.65(a)(1) for the failure to monitor the performance of the Unit 1 low pressure core spray system against licensee-established goals. Specif
Region: III | LaSalle | 34565 | 07/14/2017 08/17/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Evaluate/Justify Post-Accident Operability Qualification for the Reliance Motor 1(2)VY03C RHR Pumps Room Cooling Fan (Section 1R21.3.b(1)) |  | H.6 Design Margins | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.21N | Green. The inspectors identified a finding of very-low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50.49, Paragraph (f)(4), for the licensee's failure to provide adequate analysis in combination w
Region: III | LaSalle | 34566 | 07/14/2017 08/17/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Failure to have Adequate Justification for Extending the life of Lubricant used in EQ Motor Bearings (Section 1R21.3.b(2)) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.21N | Green. The inspectors identified a finding of very-low safety significance and an associated NCV of 10 CFR Part 50.49, Paragraph (j), "Environmental Qualification of Electrical Equipment Important to Safety for Nuclear Power Plants," for the licensee's fa
Region: III | LaSalle | 34562 | 06/30/2017 08/03/2017 | 2017002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Implement a Preventive Maintenance Strategy for 1B RHR Low Pressure Permissive Pressure Switch |  |  | TE?: N | 05000373 LaSalle 1 |  | 71152 | An NRC identified, Green Finding was identified for the failure to implement a preventive maintenance strategy for the 1B residual heat removal injection valve low pressure permissive switch in accordance with procedure ER-AA-200-1001, "Equipment Classifi
Region: III | LaSalle | 34564 | 06/30/2017 08/03/2017 | 2017002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement a Preventive Maintenance Strategy for Main Generator Auxiliaries |  | H.5 Work Management | TE?: N | 05000374 LaSalle 2 |  | 71153 | A self revealed, Green Finding was identified for the failure to implement a preventive maintenance strategy for main generator auxiliaries in accordance with MA-AA-716-210. Specifically, a performance centered maintenance template was issued in 2004 that
Region: III | LaSalle | 34560 | 03/31/2017 04/28/2017 | 2017001-01 | NRC | NCV | Initiating Events | Green | Inadequate Controls for ASME Code VT-3 Internal Examination of Pumps and Valves |  | H.5 Work Management | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.08G | The inspectors identified a finding of very low safety significance with an associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licens
Region: III | LaSalle | 34561 | 03/31/2017 04/28/2017 | 2017001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Preventive Maintenance Resulted in Stem to Disc Separation of Safety Related Valve |  | P.3 Resolution | TE?: N | 05000373 LaSalle 1 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the licensee's failure to ens
Region: III | LaSalle | 34554 | 12/31/2016 02/01/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Monthly Fire Extinguisher Inspections per National Fire Protection Association Code |  | H.7 Documentation | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance with an associated NCV of the LaSalle County Station Unit 1 and Unit 2 operating licenses, NFP-11, Section 2.C.(25), "Fire Protection Program," and NFP-18, Section 2.C.(15), "Fire Protect
Region: III | LaSalle | 34555 | 12/31/2016 02/01/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Sufficient Guidance for the Successful Troubleshooting of Safety-Related Equipment |  | P.5 Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance with an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to prov
Region: III | LaSalle | 34556 | 12/31/2016 02/01/2017 | 2016004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Preventive Maintenance Resulting in Two Subsequent Unit 1 RCIC Turbine Trips During Surveillance Testing |  |  | TE?: N | 05000373 LaSalle 1 |  | 71152 | A finding of very low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to perform preventive maintenance on the Unit 1 reactor core
Region: III | LaSalle | 34557 | 12/31/2016 02/01/2017 | 2016004-04 | NRC | FIN | Mitigating Systems | Green | Block Wall Evaluations Not Consistent with As-Built Condition |  | H.2 Field Presence | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71153 | The inspectors identified a finding of very-low safety significance when licensee personnel failed to ensure that the design inputs used in block wall evaluations for determination of their seismic capacities were consistent with the conditions as built o
Region: III | LaSalle | 34552 | 06/30/2016 08/04/2016 | 2016002-01 | NRC | NCVIV | Barrier Integrity | Green | Partial-Length Rods Exceeded Burnup Limit in Design Basis Method of Analysis |  | H.6 Design Margins | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.18 | A finding of very low safety significance and a Severity Level IV non cited violation of Title 10 of the Code of Federal Regulations 50.59, "Changes, Tests, and Experiments," was discovered by the inspectors for the station's failure to provide a written
Region: III | LaSalle | 34553 | 06/30/2016 08/04/2016 | 2016002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement and Maintain Written Procedures Regarding Respirator Fit Testing |  | H.1 Resources | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.03 | A finding of very-low safety significance and associated non-cited violation of Title 10 Code of Federal Regulations, Part 20.1703 was identified by the inspectors on May 11, 2016, for the licensee's failure to implement and maintain written procedures re
Region: III | LaSalle | 34543 | 05/13/2016 06/22/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Fouling Conditions of the CSCS Equipment Area Coolers (Section 1R21.3.b(1) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very-low safety significance (Green) and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to monitor the fouling
Region: III | LaSalle | 34546 | 05/13/2016 06/22/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Both Feed Supply Breakers for Swing DG Components Were Closed During Normal Plant Operation (Section 1R21.3.b(2)) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to have the capability to verify the supply breakers of both reactor units feeding
Region: III | LaSalle | 34547 | 05/13/2016 06/22/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Containment Debris Management (Section 1R21.4.b(1)) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish procedures that were appropriate to manage conta
Region: III | LaSalle | 34548 | 05/13/2016 06/22/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Alternate Shutdown Procedures Failed to Ensure RCIC MOVs Supply Breakers Were Closed (Section 4OA2.b(1)) |  | P.3 Resolution | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very-low safety significance (Green) and associated NCV of the LaSalle County Station Operating License for the failure to ensure that procedures were in effect to implement the alternate shutdown capability. Specifically,
Region: III | LaSalle | 34532 | 12/31/2015 02/09/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Monthly Fire Extinguisher Inspections per National Fire Protection Association Code |  | P.2 Evaluation | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of LaSalle Unit 1 and Unit 2 operating licenses, NFP 11 section 2.C.(25) and NFP 18 section 2.C.(15), respectively, for failing to ensure tha
Region: III | LaSalle | 34533 | 12/31/2015 02/09/2016 | 2015004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure that Painting Instructions were Appropriate to Preclude Challenging the Operability of Standby Gas Treatment and Control Room Ventilation Charcoal Filters |  | H.6 Design Margins | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings" for the licensee's failure to have
Region: III | LaSalle | 34534 | 12/31/2015 02/09/2016 | 2015004-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure Associated with Sealed Source Inventory and Leak Testing |  | P.6 Self Assessment | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.01 | The inspectors identified a finding of very low safety significance (Green), and an associated non-cited violation of Technical Specification (TS) requirements for the failure to perform leak tests required by station procedures. The inspectors identified
Region: III | LaSalle | 34539 | 12/31/2015 02/09/2016 | 2015004-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entry into an Area with Unknown Dose Rates |  | H.4 Teamwork | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.01 | The inspectors reviewed a finding of very low safety significance (Green) with an associated non-cited violation of Technical Specification (TS) 5.7.1, that was self-revealed when a worker received a dose rate alarm from an electronic dosimeter when he en
Region: III | LaSalle | 34531 | 07/17/2015 08/20/2015 | 2015009-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Preform a Required 50.59 Evaluation (Section 1R17.1.b.(2)) |  | P.2 Evaluation | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.17T | Severity Level IV/Green. The inspectors identified a Severity Level IV, NCV of Title 10, Code of Federal Regulations (CFR), Part 50.59, "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the failure to
Region: III | LaSalle | 34518 | 06/30/2015 08/12/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Operation of Breaker for Unit 2 Train A Residual Heat Removal Suppression Chamber Spray Isolation Valve |  | H.12 Avoid Complacency | TE?: N | 05000374 LaSalle 2 |  | 71111.13 | A finding of very low safety significance (Green) and associated non-cited violation of Technical Specification 5.4.1, "Procedures," was self revealed when the licensee failed to properly preplan and perform maintenance in accordance with written procedur
Region: III | LaSalle | 34519 | 06/30/2015 08/12/2015 | 2015002-03 | NRC | NCVIV | Barrier Integrity | Green | Inadequate 10 CFR 50.59 Evaluation for Jet Pump Plugs Affecting Fuel Bundle Cooling |  | H.14 Conservative Bias | TE?: Y SL-IV-NCVIV | 05000374 LaSalle 2 |  | 71111.18 | The inspectors identified a Severity Level IV non-cited violation of Title 10 of the Code of Federal Regulations (10 CFR) 50.59, "Changes, Tests, and Experiments," having very low safety significance (Green), for the licensee's failure to provide a writte
Region: III | LaSalle | 34529 | 06/30/2015 08/12/2015 | 2015002-04 | NRC | NCVIV | Barrier Integrity | Green | Failure to Include Limiting Conditions for Operation in the Technical Specifications |  | H.3 Change Management | TE?: Y SL-IV-NCVIV | 05000374 LaSalle 2 |  | 71111.18 | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.36, "Technical Specifications," having very low safety significance (Green), for the licensee's failure to ensure that limiting conditions for operation were contained in the s
Region: III | LaSalle | 34509 | 03/31/2015 05/01/2015 | 2015001-01 | NRC | NCV | Initiating Events | Green | Liquid Penetrant Testing Procedure Was Not Qualified for Its Full Applicability Range |  | P.5 Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.08G | The inspectors identified a Green NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure, as of February 13, 2015, to properly qualify a non-destructive testing proc
Region: III | LaSalle | 34510 | 03/31/2015 05/01/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Measure Interpass Temperature |  | H.8 Procedure Adherence | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.08G | The inspectors identified a Green NCV of Title 10, CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for a failure of the licensee on February 12, 2015, to measure the interpass temperature while performing welding on the 2 diesel g
Region: III | LaSalle | 34542 | 02/18/2015 05/10/2016 | 2016001-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Appropriate Work Instructions Led to Lost Parts in the Reactor Vessel |  | H.5 Work Management | TE?: N | 05000374 LaSalle 2 |  | 71152 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self-revealed for the licensee's failure to verify zero differential pressure across t
Region: III | LaSalle | 34502 | 01/22/2015 02/27/2015 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Circuits associated with Alternate Shutdown Capability Free of Fire-induced Damage (Section 1R05.6.b) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05T | -Green. The inspectors identified a finding of very-low safety significance (Green) and associated NCV of the LaSalle County Station Operating License for the licensee's failure to ensure that the alternate shutdown capability was independent of the fire
Region: III | LaSalle | 34501 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Scaffold Installed Without Engineering Review |  | H.9 Training | TE?: N | 05000374 LaSalle 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure on September 11, 2014, to develop and s
Region: III | LaSalle | 34500 | 12/31/2014 02/10/2015 | 2014005-02 | Self - Revealed | NCV | Initiating Events | Green | Inappropriate Instructions Led to Failure of MSIV |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the licensee's failure to establish instructions for an activity affec
Region: III | LaSalle | 34496 | 10/03/2014 10/31/2014 | 2014004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Unit 1 Reactor Protection System Limit Switch Testing Failure |  | H.9 Training | TE?: N | 05000373 LaSalle 1 |  | 71111.19 | A self revealed non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to provide instructions appropriate to the circumstances for an activity affecting quality.
Region: III | LaSalle | 34497 | 10/03/2014 10/31/2014 | 2014004-02 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evacuation Time Estimate Submittals |  | H.7 Documentation | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | NONE | The NRC identified an non-citied violation of 10 CFR 50.54(q)(2) associated with 10 CFR 50.47(b)(10) and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effectiveness of the LaSalle County Station Emergency Plan, as a result of faili
Region: III | LaSalle | 33922 | 06/30/2014 08/01/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adhere to Postings Led to Prohibited Items Being Left in ECCS Corner Rooms |  | H.9 Training | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.04Q | Inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow written instructions, pro
Region: III | LaSalle | 34494 | 06/30/2014 08/01/2014 | 2014003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Lack of Appropriate Procedure Guidance Led to Reactor Vessel Level Excursion During Refueling Outage Operations |  | H.1 Resources | TE?: N | 05000374 LaSalle 2 |  | 71111.2 | A finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1.a, "Procedures" was self revealed for the licensee's failure to maintain procedures, as appropriate, for controlling reactor vessel level, an act
Region: III | LaSalle | 33915 | 03/31/2014 04/25/2014 | 2014002-01 | NRC | NCVIV | Barrier Integrity | Green | Untimely Test, Evaluation, and Report on Reactor Vessel Surveillance Material |  | P.3 Resolution | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 |  | 71111.08G | A finding of very low safety significance (Green) and an associated Severity Level IV non-cited violation (NCV) of 10 CFR 50.60 "Acceptance Criteria for Fracture Prevention Measures for Lightwater Nuclear Power Reactors for Normal Operation" was identifie
Region: III | LaSalle | 33916 | 03/31/2014 04/25/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Drywell Closeout Procedure when Declaring Primary Containment Ready for Power Operations |  | H.5 Work Management | TE?: N | 05000373 LaSalle 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to conduct primary contain
Region: III | LaSalle | 33921 | 03/31/2014 04/25/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure that Activities Affecting Quality were Performed in Accordance with Current Procedure Revisions |  | H.1 Resources | TE?: N | 05000373 LaSalle 1 |  | 71111.2 | A finding of very low safety significance and associated non-cited violation (NCV) of Technical Specification 5.4.1.a, "Procedures," was identified by inspectors for the licensee's failure to ensure that activities affecting quality were conducted in acco
Region: III | LaSalle | 33893 | 12/31/2013 02/11/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Winter Operation Preparations Procedure |  | H.4 Teamwork | TE?: N | 05000373 LaSalle 1 |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow the procedure for wint
Region: III | LaSalle | 33894 | 12/31/2013 02/11/2014 | 2013005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Comply with Radiation Work Permit Requirements |  | H.14 Conservative Bias | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.01 | The inspector identified a finding of very low safety significance (Green) and associated non-cited violation of Technical Specification (TS) 5.7.1.b for the failure to comply with the requirements of the radiation work permit (RWP) during the loading of
Region: III | LaSalle | 33895 | 12/31/2013 02/11/2014 | 2013005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Provide Station ALARA Committee With Necessary Information to Ensure Occupational Radiation Exposure Is Maintained ALARA |  | H.8 Procedure Adherence | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.02 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of NRC requirements for the licensee's failure to provide the Station ALARA Committee with information needed to ensure that occupational radiat
Region: III | LaSalle | 33899 | 12/31/2013 02/11/2014 | 2013005-04 | NRC | NCVIV | Barrier Integrity | Green | Failure to Maintain and Report UFSAR Revisions for Safety Analysis and Methodology Changes |  | H.2 Field Presence | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated Severity Level IV (SL IV) non-cited violation of 10 CFR 50.71, "Maintenance of records, making of reports." Specifically, 50.71(e) requires that the licensee period
Region: III | LaSalle | 33908 | 12/31/2013 02/11/2014 | 2013005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain a Testing Program that Ensured RCIC Components Will Perform Satisfactorily in Service |  | P.3 Resolution | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to ensure that the surveillance testing program was suff
Region: III | LaSalle | 33909 | 12/31/2013 02/11/2014 | 2013005-06 | NRC | NCV | Barrier Integrity | Green | Improper Classification of Secondary Containment Doors as Nonsafety-Related |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71153 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the licensee's failure to classify secondary containment doors with a q
Region: III | LaSalle | 33886 | 11/22/2013 12/06/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Pump Test Instruments Were Not Maintained Within Required Accuracy Limits |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to use instrumentation that met the data collection requirements of America Society of Mech
Region: III | LaSalle | 33887 | 11/22/2013 12/06/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Battery Margin Maintained for Station Blackout |  | P.5 Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure that 5 percent battery margin would be maintained for
Region: III | LaSalle | 33885 | 09/30/2013 11/15/2013 | 2013004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedures Led to Pin Hole Leaks in High Pressure Core Spray Piping |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71153 | A self revealed finding of very low safety significance and associated non cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to have procedures adequate for the circu
Region: III | LaSalle | 33871 | 06/30/2013 08/02/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Required Risk Assessment Following a Failed RCIC Surveillance |  | H.3(a) Work Planning | TE?: N | 05000373 LaSalle 1 |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50.65, Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants, section (a)(4), was identified by inspectors for the licensee's failure to perform an adequ
Region: III | LaSalle | 33878 | 04/18/2013 07/18/2013 | 2013009-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Satisfy 10 CFR 50.72 Reporting Requirements |  | P.2(b) Implementing Operating Experience | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 |  | 93812 | The inspectors identified a finding of very low safety significance with an associated Severity Level IV non cited violation of the NRC's reporting requirements in 10 CFR 50.72(a)(1), "Immediate Notification Requirements for Operating Nuclear Power Reacto
Region: III | LaSalle | 33869 | 03/31/2013 05/09/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Implement Steps Outlined in Technical Specification Surveillance Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000374 LaSalle 2 |  | 71111.13 | A finding of very low safety significance and associated NCV of Technical Specification 5.4.1, "Procedures," was self-revealed on March 14, 2013, when an unexpected isolation of the Reactor Core Isolation Cooling (RCIC) system occurred as a result of the
Region: III | LaSalle | 33870 | 03/31/2013 05/09/2013 | 2013002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiological Surveys to Ensure Appropriate Control and Access to a High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71124.01 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 20.1501, and licensee Technical Specification(TS) 5.4, "Procedures." Specifically, the licensee failed to adequately identify, plan, evaluate, and control the
Region: III | LaSalle | 33862 | 12/31/2012 01/28/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Prompt Corrective Actions to Address a Safety Related Degraded Component |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure to take prompt corrective actions to address the de
Region: III | LaSalle | 33850 | 09/30/2012 10/30/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Lack of Adequate Design Review of Effects of Fish Kills on Systems Needed During an Ultimate Heat Sink Design Basis Accident |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately verify the adequacy of the desi
Region: III | LaSalle | 33851 | 09/30/2012 10/30/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Plant Barrier Control Process for High Energy Line Break Protection Doors |  | H.4(b) Procedural Compliance | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to follow procedure CC AA 201, Revision 9, "Plan
Region: III | LaSalle | 33852 | 09/30/2012 10/30/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Testing Program for Safety-Related Watertight Doors |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.22 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the licensee's failure to maintain an adequate testing program for the station's safety related water
Region: III | LaSalle | 33855 | 09/30/2012 10/30/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Operability of Low Pressure Core Injection and Containment Cooling In Mode 3 Not Maintained |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to ensure low pressure coolant injection (LPCI) and containment cooling (CC) operabil
Region: III | LaSalle | 33856 | 09/30/2012 10/30/2012 | 2012004-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Pressure Locking and Thermal Binding of the RHR Suction Isolation Valves from the Suppression Pool |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately assess the susceptibility to pressure locking and thermal binding of the R
Region: III | LaSalle | 33857 | 09/30/2012 10/30/2012 | 2012004-06 | NRC | NCV | Mitigating Systems | Green | Piping Interaction Between SW and RHR Systems Was Not Evaluated |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to evaluate piping interactions between the service water (SW) and residual heat removal
Region: III | LaSalle | 33858 | 09/21/2012 10/29/2012 | 2012007-01 | NRC | NCVIV | Initiating Events | Green | Failure to Perform a Written Safety Evaluation for TRM Changes Section |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-IV-NCVIV | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.17T | The inspectors identified a Severity Level IV Non-Cited Violation and an associated finding of very low safety significance (Green) of 10 CFR 50.59, "Changes, Tests, and Experiments," Section (d)1 for the licensee's failure to perform a written safety eva
Region: III | LaSalle | 33861 | 09/21/2012 10/29/2012 | 2012007-02 | NRC | FIN | Initiating Events | Green | Failure to Perform a Written Safety Evaluation for TRM Changes |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.17T | The inspectors identified a Severity Level IV Non-Cited Violation and an associated finding of very low safety significance (Green) of 10 CFR 50.59, "Changes, Tests, and Experiments," Section (d)1 for the licensee's failure to perform a written safety eva
Region: III | LaSalle | 33846 | 06/30/2012 07/25/2012 | 2012003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Surveillance Test Procedure Step |  | H.3(b) Work Activity Coordination | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.22 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to implement a station required procedure step during surveillance testing of the standby gas treatment (SBGT) system. Specifically, the licensee failed
Region: III | LaSalle | 33844 | 03/31/2012 05/02/2012 | 2012002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Proceduralized Corrective Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | A finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to im
Region: III | LaSalle | 33839 | 12/31/2011 01/25/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct an Oil Leak on the HPCS Waterleg Pump |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000373 LaSalle 1 |  | 71111.12 | A finding of very low safety significance and associated non-cited violation of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the failure to promptly identify and
Region: III | LaSalle | 33841 | 12/31/2011 01/25/2012 | 2011005-03 | NRC | FIN | Barrier Integrity | Green | Failure to Perform an Adequate 10 CFR 50.59 Screening for the Use of Racklife Spent Fuel Pool Monitoring Computer Model |  |  | TE?: N | 05000374 LaSalle 2 |  | 71111.18 | A finding of very low safety significance and associated SL IV NCV of 10 CFR 50.59(c)(2) was identified by the inspectors for the licensee's failure to perform an adequate 10 CFR 50.59 screening when evaluating if the implementation of Racklife to monitor
Region: III | LaSalle | 33815 | 09/30/2011 10/31/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Voltage Input for Motor Starting Calculations |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Title 10 Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to perform adequate analysi
Region: III | LaSalle | 33833 | 07/29/2011 08/25/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Technical Specification Violation Due to Failure to Follow Operability Determination Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000373 LaSalle 1 |  | 71152B | A finding of very low safety significance (Green) and associated non-cited violation of Technical Specifications was identified by the inspectors for the licensee's failure to follow station procedure OP-AA-108-115, "Operability Determinations," Revisions
Region: III | LaSalle | 33834 | 07/29/2011 08/25/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Corrective Action to Prevent Recurrence to Address a Significant Condition Adverse to Quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152B | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure to develop and implement adequate corrective action to prevent recurrenc
Region: III | LaSalle | 33832 | 06/22/2011 07/21/2011 | 2010503-02 | NRC | FIN | Emergency Preparedness | Green | Changes to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval. |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: III | LaSalle | 33814 | 03/31/2011 05/11/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Post Protected Pathway Signs for a Red Risk Path System |  | H.4(a) Human Error Prevention | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(4), Maintenance Rule, was identified by inspectors for the licensee's failure to implement all necessary prescribed risk management actions during a Unit 2 Reactor Core Isolat
Region: III | LaSalle | 33818 | 03/31/2011 05/11/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Plant Barrier Control Process Caused Secondary Containment to Become Inoperable |  | H.3(b) Work Activity Coordination | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, was identified by the inspectors for the licensee's failure to follow steps 3.6 and 3.7 of procedure CC-AA-201
Region: III | LaSalle | 33804 | 01/03/2011 02/15/2011 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Supporting Structure for Standby Liquid Control System Test Tank Non-Functional During Postulated Design Basis Earthquake (DBE). |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to have an adequate calculation to demonstrate the seismic qualification of the
Region: III | LaSalle | 33805 | 01/03/2011 02/15/2011 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | EDG Usable Fuel and RHR Pump NPSH Calculations Failed to Consider Appropriate EDG Frequency Variations |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to account for allowable frequency variations on the emergency di
Region: III | LaSalle | 33811 | 01/03/2011 02/15/2011 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Insufficient Design Bases for Degraded Voltage Time Delay and LOV Relay Settings |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to have appropriate analyses for the loss of voltage relay setpoints and t
Region: III | LaSalle | 33812 | 01/03/2011 02/15/2011 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Fast Transfer Scheme |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The team identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to analyze the capability of the electrical system to transfer safety related
Region: III | LaSalle | 33793 | 12/31/2010 02/15/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to follow the performance centered monitoring process specified in procedure MA-AA-716-210 |  |  | TE?: N | 05000374 LaSalle 2 |  | 71153 | A finding of very low safety significance (Green) and an associated NCV of Technical Specification (TS) 5.4.1, "Procedures", was self-revealed, for the failure to follow procedural guidance specified in procedure MA-AA-716-210, "Performance Centered Monit
Region: III | LaSalle | 33794 | 12/31/2010 02/15/2011 | 2010005-03 | NRC | NCV | Initiating Events | Green | Failure to Perform Adequate Evaluation for Reactor Building Crane Upgrade |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | NONE | During an inspection of pre-operational testing activities of an independent spent fuel storage installation (ISFSI) at the LaSalle County Station, the inspectors identified a finding of very low safety significance with an associated NCV of Part 10 of th
Region: III | LaSalle | 33800 | 06/30/2010 08/06/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to develop and implement an adequate surveillance test procedure to accurately assess the as found trip setpoint for the pressure switches associated with the main steam line low pressure isol |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | This NCV is for licensee failure to develop and implement an adequate surveillance test procedure to accurately assess the as found trip setpoint for the pressure switches associated with the main steam line low pressure isolation function and various oth
Region: III | LaSalle | 33792 | 03/31/2010 04/21/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of SBLC system |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, Design Control was identified by the inspectors for the licensee's failure to ensure the SBLC system could mitigate the consequences of all design basis
Region: III | LaSalle | 33798 | 02/11/2010 04/21/2010 | 2010002-02 | Self - Revealed | NCV | Initiating Events | Green | Improper Procedure Implementation During Testing of Excess Flow Check Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000373 LaSalle 1 |  | 71111.2 | Introduction: Using routine surveillance testing, a finding of very low safety significance (Green) was self revealed. The finding has an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to pro
Region: III | LaSalle | 33783 | 09/18/2009 10/08/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Revision for Technical Requirement Manual Section |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.17T | A finding of very low safety-significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedure, and Drawings" was identified by the inspectors for the licensee's failure to ensure that specific re
Region: III | LaSalle | 33786 | 08/15/2009 10/30/2009 | 2009004-03 | NRC | FIN | Initiating Events | Green | Reactor SCRAM during turbine testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000374 LaSalle 2 |  | 71153 | The inspectors identified a finding of very low safety significance for the licensee failing to recognize that an existing alarm condition in the Unit 2 DEHC trip logic would result in a turbine trip and subsequent reactor SCRAM when weekly turbine trip t
Region: III | LaSalle | 33784 | 07/31/2009 10/30/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to declare SBLC system inoperable during surveillance testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance during a monthly SBLC pump run on Unit 2. Specifically, operations personnel performing LOS-SC-Q1, "SBLC pump operability test," did not posses appropriate procedural guidance while perfo
Region: III | LaSalle | 33772 | 06/24/2009 08/07/2009 | 2009003-01 | NRC | NCV | Initiating Events | Green | Failure to implement a fire protection program procedure for combustible controls |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05Q | A finding of very low safety significance and associated NCV of Technical Specifications was identified by the inspectors for the failure to implement a fire protection program procedure for combustible controls. Specifically, the inspectors identified th
Region: III | LaSalle | 33771 | 12/31/2008 02/06/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Regulatory Guide 1.9 Testing Methodology into Procedures |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors' identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control", for the failure to establish a minimum DG run time of at least five minutes when performing the hot
Region: III | LaSalle | 33767 | 11/17/2008 12/31/2008 | 2008007-01 | NRC | NCV | Initiating Events | Green | Unauthorized Transient Combustibles |  | H.4(b) Procedural Compliance | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05T | A finding of very low safety significance and associated NCV of Technical Specifications was identified by the inspectors for the failure to implement a fire protection program procedure for combustible controls. Specifically, the inspectors identified th
Region: III | LaSalle | 33768 | 11/17/2008 12/31/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Failure to provide a sprinkler system for Fire Zone 4F3 |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.05T | A finding of very low safety significance and associated NCV of the license condition was identified by the inspectors for the failure to install a sprinkler system. Specifically, the licensee had installed a pre-action spray system above the suspended ce
Region: III | LaSalle | 33765 | 03/31/2008 04/28/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of MSIV prior to performing ASME Stroke Time Testing |  | P.2(b) Implementing Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance involving the unacceptable preconditioning of the Unit 1 Main Steam Isolation Valves (MSIVs). Specifically, the inspectors identified that the licensee performed maintenance on the MSIVs
Region: III | LaSalle | 33766 | 03/31/2008 04/28/2008 | 2008002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Restore Available Seismic Monitoring System Channels to an Operable and Available Status in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152 | The inspectors identified a finding of very low safety significance involving the licensee's seismic monitoring system. Specifically, the inspectors identified that the licensee had not appropriately prioritized restoration activities for three channels o
Region: III | LaSalle | 33763 | 12/14/2007 01/15/2008 | 2007006-01 | NRC | NCV | Initiating Events | Green | Failure to perform root cause for significant condition adverse to quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152B | The NRC identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to perform an adequate RCA to determine the corrective actions necessary to prevent recurrence for a SCAQ. Specifically, the licensee did not eval
Region: III | LaSalle | 33764 | 12/14/2007 01/15/2008 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Failure to correct a signifcant condition adverse to quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71152B | The NRC identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct a SCAQ in a timely manner. Specifically, the licensee had not repaired or replaced all of the affected CSCS valves that are susceptible
Region: III | LaSalle | 33751 | 09/30/2007 11/02/2007 | 2007004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Instrument Maintenance Technicians Cause Pressure Spike when Valving in Flow Transmitter and Render RHR Train Inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000374 LaSalle 2 |  | 71111.22 | A self-revealing finding of very low safety significance was identified following the inadvertent actuation of the 2B RHR pump minimum flow valve (2E12-F064B) during a Unit 2 RHR pump 2B/2C flow indication calibration. Specifically, licensee instrument te
Region: III | LaSalle | 33752 | 09/30/2007 11/02/2007 | 2007004-02 | Self - Revealed | NCV | Public Radiation Safety | Green | External Radiation Levels on Package Exceeds 200 mrem/hr on Contact |  | P.2(b) Implementing Operating Experience | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7112202 | A self-revealing NCV of 10 CFR 71.5 was identified when a package of licensed material offered for shipment exceeded the external radiation limit contained in 49 CFR 173. The shipment was surveyed upon receipt at the final destination by individuals quali
Region: III | LaSalle | 33754 | 09/28/2007 11/09/2007 | 2007009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Test Keylock Switches |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and an associated NCV of the LaSalle County Station Facility Operating License associated with the Fire Protection Program for failure to ensure that all necessary testing was identified
Region: III | LaSalle | 33173 | 09/28/2007 11/09/2007 | 2007009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Backwash Valve Settings into Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, the design bases for the manual backwash valve position values for the Diesel Generator Cooling Water (DGCW) backwash strainers were not correctly
Region: III | LaSalle | 33195 | 09/28/2007 11/09/2007 | 2007009-03 | NRC | NCV | Mitigating Systems | Green | Lack of Station Blackout Analysis for RCIC |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111121 | A finding of very low safety significance was identified by the inspectors associated with a Non-Cited Violation of 10 CFR 50.63, "Loss of All Alternating Current Power." Specifically, the licensee did not have an appropriate analysis to determine the cap
Region: III | LaSalle | 33749 | 06/30/2007 07/30/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to properly control and execute work during a Unit 1 LPCS Inservice Test |  | H.4(b) Procedural Compliance | TE?: N | 05000373 LaSalle 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance during a monthly low pressure core spray (LPCS) pump run on Unit 1. Specifically, operations personnel performing LOS-LP-Q1, "LPCS System Inservice Test," did not exhibit proper work cont
Region: III | LaSalle | 33750 | 06/30/2007 07/30/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Licensee Relied on Operator Manual Actions for Post-fire SSD. |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | NONE | The inspectors identified a non-cited violation (NCV) of the LaSalle County Station Operating License for the failure to establish the required physical protection or separation of cables to ensure that one redundant train of systems necessary to achieve
Region: III | LaSalle | 33747 | 05/18/2007 06/04/2007 | 2007007-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure for Removal of Drywell Head Bolts |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111117B | Green. The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving an inadequate maintenance procedure used to remove drywell head bolts. Specifica
Region: III | LaSalle | 33748 | 05/18/2007 06/04/2007 | 2007007-02 | NRC | NCV | Barrier Integrity | Green | Lack of Calibrated Air Wrench ofor Drywell Head Assembly Bolt Installation |  | H.2(d) Facilities & Equipment | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 7111117B | Green. The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XII, "Control of Measuring and Test Equipment," involving lack of calibrated tools used to establish torque for t
Region: III | LaSalle | 33732 | 03/31/2007 04/27/2007 | 2007002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Use Valve Alignment Checklist When Clearing Tag Out Results in Mispositioned Valve and Low Instrument Nitrogen System Header Pressure. |  | H.4(b) Procedural Compliance | TE?: N | 05000374 LaSalle 2 |  | 71111.04Q | A self-revealing finding of very low safety significance was identified following the removal of a safety tag out and valve realignment for the 2A instrument nitrogen (IN) compressor. Specifically, operations personnel were restoring the system valve line
Region: III | LaSalle | 33733 | 03/31/2007 04/27/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Incomplete Residual Heat Removal Heat Exchanger Vessel Weld Examinations. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.08G | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50.55a(g)4 for the licensee's failure to perform examinations of the ASME Code Section XI required weld volume for the Unit 1 and 2 'B' res
Region: III | LaSalle | 33741 | 03/31/2007 04/27/2007 | 2007002-04 | NRC | FIN | Barrier Integrity | Green | De-Tensioning Drywell Head in Mode 3 Has Unanticipated Impact on Technical Specifications. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000374 LaSalle 2 |  | 71111.2 | A finding of very low safety significance was identified by the inspectors during review of the licensee's activities associated with de-tensioning the drywell head in preparation for scheduled reactor refueling operations. Specifically, the inspectors id
Region: III | LaSalle | 33742 | 03/31/2007 04/27/2007 | 2007002-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Plan and Proceduralize Reactor Vessel Nozzle Flushing Activities Results in Inadvertent ECCS Injection into the Reactor Vessel. |  | H.3(a) Work Planning | TE?: N | 05000374 LaSalle 2 |  | 71111.2 | A self-revealing finding of very low safety significance was identified following the inadvertent initiation of the Division 1 emergency core cooling system (ECCS) on Unit 2 during reactor vessel nozzle flushing from the refuel floor for radiation dose re
Region: III | LaSalle | 33743 | 03/31/2007 04/27/2007 | 2007002-06 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedural Instructions to Place Shutdown Cooling in Service Results in Inadvertent ECCS Injection into the Reactor Vessel. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000374 LaSalle 2 |  | 71111.13 | A self-revealing finding of very low safety significance was identified following the inadvertent initiation of Unit 2 Division 2 ECCS, which occurred when operators started shutdown cooling (SDC) while reactor coolant system was pressurized. Specifically
Region: III | LaSalle | 33192 | 12/31/2006 01/16/2007 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Operator Manual Actions For Maintaining EDG Availability During Surveillance Testing Not Adequately Implemented, as Required by 10 CFR 50.65(a)(4) |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.22 | A finding of very low safety significance was identified by inspectors during observation of a scheduled 1A emergency diesel generator (EDG) fast start surveillance. Specifically, the inspectors identified that the licensee's manual operator actions in pl
Region: III | LaSalle | 33187 | 09/30/2006 10/24/2006 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Repair a Degraded Condition Associated with the 2B EDG Day Tank Room Structure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000374 LaSalle 2 |  | 71152 | A finding of very low safety significance was identified by inspectors during a quarterly fire protection zone inspection of the 2B Emergency Diesel Generator (EDG) day tank room. Specifically, the inspectors identified a section of structural steel that
Region: III | LaSalle | 33188 | 09/30/2006 10/24/2006 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Used for GL 89-13 Program Thermal Performance Tests on RHR Heat Exchangers |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | A finding of very low safety significance was identified by inspectors during observation of a GL 89-13 residual heat removal system heat exchanger (RHR HX) thermal performance test. Specifically, the inspectors identified that the licensee's engineering
Region: III | LaSalle | 33191 | 09/30/2006 10/24/2006 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Identified Issues Associated with the GL 89-13 Program for RHR Heat Exchangers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.12 | A finding of very low safety significance was identified by the inspectors. The inspectors determined that the licensee did not fully evaluate problems and properly prioritize corrective actions with respect to the RHR HX thermal performance test procedur
Region: III | LaSalle | 33182 | 03/31/2006 05/02/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Establish and Maintain Written Procedures and Instructions for the Technical Specification Administrative Control of Primary Containment Isolation Valve 1E51-F069 |  |  | TE?: N | 05000373 LaSalle 1 |  | 7111114 | Inspectors identified a finding of very low safety significance for the lack of written procedures and instructions related to the Technical Specification administrative control of a primary containment isolation valve (PCIV). An associated Non-Cited Viol
Region: III | LaSalle | 33183 | 03/31/2006 05/02/2006 | 2006003-03 | Licensee - Identified | URI | Mitigating Systems | Green | Operability and Calculational Issues Associated with the Failure to Install Procedurally Required Temporary Seismic Supports During L1R11 CSCS Valve Replacement Work |  |  | TE?: N | 05000373 LaSalle 1 05000374 LaSalle 2 |  | 71111.15
Region: III | LaSalle | 33184 | 03/31/2006 05/02/2006 | 2006003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Instrument Maintenance Technician Enters a High Radiation Area on the Wrong RWP |  |  | TE?: N | 05000373 LaSalle 1 |  | 7112101 | A finding of very low safety significance was self-revealed as a result of an alarm on a worker's electronic dosimeter. The issue was identified when an instrument maintenance technician logged onto the wrong radiation work permit (RWP) and entered the as
Region: III | LaSalle | 33180 | 02/20/2006 03/23/2006 | 2006009-02 | Self - Revealed | URI | Mitigating Systems | Green | Inaccurate Control Rod Position Indication Provided to Control Room Operators Following a Unit 1 Reactor Scram on February 20, 2006 |  |  | TE?: N | 05000373 LaSalle 1 |  | 71153
Region: III | Monticello | 125392 | 11/22/2019 11/27/2019 | 2019012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage the Shutdown Risk at Monticello | EA Case: EA-19-066 | H.14 - Conservative Bias | TE?: N | 05000263 Monticello | RCS Equipment and Barrier Performance | 71111.13 | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of 10 CFR 50.65(a)(4) when the licensee failed to effectively assess and manage shutdown risk associated with concurrent maintenance activities, resulting in the degradatio
Region: III | Monticello | 125207 | 06/30/2019 08/02/2019 | 2019002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures Resulting in Operating in a Mode Prohibited by Technical Specifications. |  | H.5 - Work Management | TE?: N | 05000263 Monticello | RCS Equipment and Barrier Performance | 71153 | A self-revealed Green finding and associated NCV of Technical Specification (TS) 5.4.1(a) was identified on June 11, 2019, for the failure of the licensee to follow licensee procedure FP-OP-COO-17, “Equipment Manipulation and Status Control,” Revision 3.
Region: III | Monticello | 24677 | 09/13/2018 10/24/2018 | 2018012-01 | NRC | NCV | Barrier Integrity | Green | Inboard Main Steam Isolation Valve Closure Time Test Acceptance Criteria Did Not Account for the Design Basis Accident Containment Back Pressure and Pneumatic Supply Operating Pressure |  | NPP | TE?: N | 05000263 Monticello |  | 71111.21M | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the failure to assure that applicable requirements and acceptance limits contained in the inboard MSIV design documents were i
Region: III | Monticello | 24678 | 09/13/2018 10/24/2018 | 2018012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Condition Adverse to Quality for Inadequate Freeze Protection Monitoring for CST Instrumentation Piping |  | P.2 - Evaluation | TE?: N | 05000263 Monticello |  | 71111.21M | The inspectors identified a Green finding and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to establish measures to ensure conditions adverse to quality are promptly identified and correct
Region: III | Monticello | 23944 | 03/31/2018 04/18/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure For Storage of Equipment near Safety Related Equipment |  | H.5 - Work Management | TE?: N | 05000263 Monticello |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) with an associated NCV of 10 CFR 50 Appendix B Criterion V for the failure to accomplish activities affecting quality as prescribed by documented procedures. Specifically, the lic
Region: III | Monticello | 23149 | 01/30/2018 01/30/2018 | 2017004-01 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA |  | H.5 - Work Management | TE?: N | 05000263 Monticello |  | 71124.07 | A finding of very low safety significance (Green) was self-revealed due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee’s radiological work planning and work control progra
Region: III | Monticello | 27066 | 08/11/2017 08/11/2017 | 2017002-01 | NRC | NCV | Initiating Events | Green | LOW REACTOR WATER LEVEL DURING SHUTDOWN OF 11 REACTOR FEEDWATER PUMP. |  | H.3 Change Management | TE?: N | 05000263 Monticello 05000263 Monticello |  | 71153 | A self revealed finding of very low safety significance and an NCV of Technical Specification (TS) 5.4.1.a occurred on April 15, 2017, due the licensee's failure to establish, implement and maintain procedures regarding shutdown operations. Specifically,
Region: III | Monticello | 27073 | 07/14/2017 08/21/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | IMPLEMENTATION OF INADEQUATE ALTERNATE COMPENSATORY MEASURE FOR DEGRADED FIRE BARRIER (SECTION 1R05.11b). |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very-low significance (Green) and an associated Non-Cited Violation of License Condition 2.C.4 of the Monticello Nuclear Generating Plant, Unit No. 1, Renewed Facility Operating License for implementing an alternativ
Region: III | Monticello | 27072 | 06/09/2017 07/21/2017 | 2017010-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE ADEQUATE DESIGN CONTROLS DURING INSTALLATION OF FLEXIBLE HOSE ON HIGH PRESSURE COOLANT INJECTION AUXILIARY OIL SYSTEM (SECTION 4OA4). |  | P.6 Self Assessment | TE?: N | 05000263 Monticello |  | 95001 | A finding of very low safety significance and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," was self-revealed as a result of an equipment cause investigat
Region: III | Monticello | 27063 | 10/03/2016 11/18/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE FOR IDENTIFICATION OF SIGNIFICANT CONDITIONS ADVERSE TO QUALITY. |  | P.6 Self Assessment | TE?: N | 05000263 Monticello |  | 71152B | Green. The inspectors identified a finding of very low safety significance and non-cited violation of Title 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to prescribe a procedure appropriate to the
Region: III | Monticello | 27064 | 09/30/2016 11/08/2016 | 2016003-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURES WHILE PERFORMING ACTIVITIES AFFECTING QUALITY. |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71111.15 | Green. Inspectors identified a self revealed, finding of very low safety significance (Green) and associated Non Cited Violation (NCV) of Technical Specification 5.4.1.a, on June 24, 2016, when the licensee failed to follow procedures while performing act
Region: III | Monticello | 27061 | 03/31/2016 05/04/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO USE PROCEDURES WHILE PERFORMING ACTIVITIES AFFECTING QUALITY. |  | H.4 Teamwork | TE?: N | 05000263 Monticello |  | 71111.15 | An NRC identified finding of very low safety significance (Green) and associated of 10 CFR 50, Appendix B, Criterion V; "Instructions, Procedures, and Drawings", was identified on February 5, 2016, as a result of the licensee's failure to use procedures w
Region: III | Monticello | 27044 | 09/30/2015 11/03/2015 | 2015003-01 | NRC | NCV | Barrier Integrity | Green | INADEQUATE EVALUATION OF REFUELING FLOOR STRUCTURAL STEEL BEAMS. |  |  | TE?: N | 05000263 Monticello |  | 71111.18 | The inspectors identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to provide for verifying or checking the adequacy of design, such as by t
Region: III | Monticello | 27045 | 09/30/2015 11/03/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM HIGH RADIATION AREA PORTABLE FIRE EXTINGUISHER SURVEILLANCES. |  | H.5 Work Management | TE?: N | 05000263 Monticello |  | 71152 | The inspectors identified a finding of very low safety significance and an NCV of Technical Specification (TS) 5.4.1.d when the licensee failed to implement procedures associated with Fire Protection Program Implementation, to ensure that required refueli
Region: III | Monticello | 27050 | 09/30/2015 11/03/2015 | 2015003-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY SAFE SHUTDOWN EQUIPMENT IMPACTS IN FIRE STRATEGY PROCEDURES. |  | P.6 Self Assessment | TE?: N | 05000263 Monticello |  | 71152 | The inspectors identified a finding of very low safety significance and an NCV of Technical Specification (TS) 5.4.1.d when the licensee failed to maintain procedures associated with Fire Protection Program Implementation, consistent with the Updated Safe
Region: III | Monticello | 27038 | 07/24/2015 09/02/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Quality Assurance Controls for Nitrogen Supply for the AN2 System (Section 1R21.3.b.(1)) |  |  | TE?: N | 05000263 Monticello |  | 7111121 | Green. The inspectors identified a finding having very low safety significance, and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure the nitrogen supply for t
Region: III | Monticello | 27043 | 07/24/2015 09/02/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Review for Suitability of Application of Safety Related Relays Installed Beyond Their Service Life (Section 1R21.3.b.(2)) |  |  | TE?: N | 05000263 Monticello |  | 7111121 | Green. The inspectors identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure measures were established for the selection and review for suitabil
Region: III | Monticello | 27022 | 06/30/2015 08/12/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN PORTABLE FIRE EXTINGUISHERS IN ACCORDANCE WITH FIRE STRATEGY. |  | P.1 Identification | TE?: N | 05000263 Monticello |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an NCV of TS 5.4.1.d when the licensee failed to implement procedures associated with Fire Protection Program Implementation to ensure that portable fire extinguishers were maintained
Region: III | Monticello | 27023 | 06/30/2015 08/12/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MEASURE INTERPASS TEMPERATURE. |  | P.5 Operating Experience | TE?: N | 05000263 Monticello |  | 71111.08G | The inspectors identified a Green NCV of Title 10, CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for a failure to measure the interpass temperature while performing welding on diesel generator fuel oil modification supports. Conse
Region: III | Monticello | 27024 | 06/30/2015 08/12/2015 | 2015002-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO MAINTAIN SECONDARY CONTAINMENT AND STANDBY GAS TREATMENT SYSTEM OPERABLE DURING OPDRV ACTIVITIES. |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 3.6.4.1, Secondary Containment and TS 3.6.4.3, Standby Gas Treatment System (SBGT) because the licensee did not maintain secondary containment and the standby
Region: III | Monticello | 27025 | 06/30/2015 08/12/2015 | 2015002-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FILL THE REACTOR CAVITY IN ACCORDANCE WITH REFUELING PREPARATION PROCEDURE. |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.4.1, "Procedures," on April 15, 2015, when the licensee failed to implement procedure 9001, "Reactor Well & Dryer Separator Storage Pool Filling Procedure,"
Region: III | Monticello | 27036 | 06/30/2015 08/12/2015 | 2015002-05 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE CLEARANCE ORDER RESULTS IN UNPLANNED OPDRV. |  | H.11 Challenge the Unknown | TE?: N | 05000263 Monticello |  | 71111.15 | A self revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1, "Procedures," was identified on May 16, 2015, when the licensee failed to implement procedure FP OP TAG 01, "Fleet Tagging," for equipment
Region: III | Monticello | 27037 | 06/30/2015 08/12/2015 | 2015002-06 | Self - Revealed | NCV | Initiating Events | Green | LOSS OF ELECTRICAL BUSES AND SHUTDOWN COOLING (SDC) DUE TO INADEQUATE PROCEDURE ADHERENCE. |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71153 | A self revealed finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified due to the failure to properly implement
Region: III | Monticello | 27018 | 03/31/2015 05/08/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY HIGH PRESSURE COOLANT INJECTION (HCPI) SEISMIC SUPPORT NONCONFORMANCE. |  | P.1 Identification | TE?: N | 05000263 Monticello |  | 71111.04Q | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify conditions adverse to quality, such as deficiencies, deviatio
Region: III | Monticello | 27019 | 03/31/2015 05/08/2015 | 2015001-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO MAINTAIN FIRE PROTECTION PROGRAM PROCEDURES FOR CONTROL OF PORTABLE HEATER/EXTENSION CORD FIRE HAZARDS. |  | P.2 Evaluation | TE?: N | 05000263 Monticello |  | 71111.05Q | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1.d was self-revealed when the licensee failed to maintain procedures for Fire Protection Program Implementation to ensure that ignition sources (space hea
Region: III | Monticello | 27020 | 03/31/2015 05/08/2015 | 2015001-03 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO MAINTAIN A STANDARD EMERGENCY ACTION LEVEL SCHEME FOR FLOODING. |  | P.2 Evaluation | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a finding of very low safety significance and an NCV of Title 10 CFR 50.54(q)(2) and 10 CFR 50.47(b)(4) for the licensee's failure to maintain the effectiveness of the emergency plan. Specifically, from May 28, 2014, until Februa
Region: III | Monticello | 27021 | 03/31/2015 05/08/2015 | 2015001-05 | Self - Revealed | NCV | Mitigating Systems | Green | TWO EMERGENCY DIESELS INOPERABLE DUE TO HUMAN ERROR. |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71153 | A self-revealing finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified on December 28, 2014, due to the failure to properly implement Procedure 0187-02B, "12
Region: III | Monticello | 27010 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO COMPLY WITH ASME CODE AND MAINTAIN CONFIGURATION APPROVED BY IST RELIEF REQUEST. |  | H.13 Consistent Process | TE?: N | 05000263 Monticello |  | 71111.04Q | The inspectors identified a finding of very low safety significance and NCV of 10 CFR 50.55a(f)(4) for the licensee's failure to test main steam line drain containment isolation valves MO-2373 and MO-2374 in accordance with the American Society of Mechani
Region: III | Monticello | 27014 | 12/02/2014 01/16/2015 | 2014009-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN PROCEDURES TO ENSURE DESIGN REQUIREMENTS WOULD BE MET DURING CONSTRUCTION OF THEEXTERNAL FLOODING PROTECTION LEVEE. |  | H.5 Work Management | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a finding of very low safety significance with an associated NCV of Technical Specification 5.4.1.a for the licensee's failure to maintain adequate procedures to protect the plant from external flooding events. Specifically, the
Region: III | Monticello | 27015 | 12/02/2014 01/16/2015 | 2014009-04 | NRC | FIN | Mitigating Systems | Green | SAFETY/SECURITY INTERFACE ASSESSMENT FAILURE. |  | H.3 Change Management | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a finding of very low security significance for the licensee's failure to adequately assess and manage the potential for adverse effects on safety and security associated with the development and planned implementation of its ext
Region: III | Monticello | 27008 | 09/30/2014 11/05/2014 | 2014004-01 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW REACTIVITY MANAGEMENT PROCEDURE. |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71111.15 | A finding of very low safety significance and a NCV of Technical Specification (TS) 5.4.1, "Procedures," was self-revealed when the licensee failed to implement requirements specified in FP-OP-RM-01, "Reactivity Management Program." Specifically, the lice
Region: III | Monticello | 26995 | 06/30/2014 08/11/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE STANDBY LIQUID CONTROL QUARTERLY PUMP AND VALVE TEST DUE TO PROCEDURALIZED UNACCEPTABLE PRECONDITIONING. |  | H.3 Change Management | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and a non cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," on May 7, 2014, for the licensee's failure to ensure that activities affecting
Region: III | Monticello | 26997 | 06/30/2014 08/11/2014 | 2014003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO COMPLY WITH ASME CODE PIPING DESIGN REQUIREMENTS. |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71111.18 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," when the licensee failed to comply with the appropriate American Society of Mechanical Eng
Region: III | Monticello | 26985 | 03/31/2014 05/09/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | RCS PRESSURE BOUNDARY LEAKAGE OPERATION PROHIBITED BY TECHNICAL SPECIFICATIONS. |  | P.2 Evaluation | TE?: N | 05000263 Monticello |  | 71111.15 | A finding of very low safety significance and a non-cited violation of Technical Specification (TS) 3.4.4, "RCS Operational Leakage," was self revealed when the licensee failed to comply with TS 3.4.4, Condition C, which required the plant to be in MODE 3
Region: III | Monticello | 26986 | 03/31/2014 05/09/2014 | 2014002-02 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURE FOR RCS OPERABILITY DETERMINATION. |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.15 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure that activities affecting quality be prescr
Region: III | Monticello | 26987 | 03/31/2014 05/09/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | DRYWELL-TORUS VACUUM BREAKER INADEQUATE POST-MAINTENANCE AND RETURN-TO-SERVICE TEST. |  | H.5 Work Management | TE?: N | 05000263 Monticello |  | 71111.15 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to assure that all testing required to demonstrate that SSCs will perform sati
Region: III | Monticello | 26991 | 03/31/2014 05/09/2014 | 2014002-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE FOR DRYWELL-TORUS VACUUM BREAKER OPERABILITY DETERMINATION. |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.15 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure that activities affecting quality be prescr
Region: III | Monticello | 26992 | 03/31/2014 05/09/2014 | 2014002-05 | NRC | NCV | Barrier Integrity | Green | INADEQUATE DRYWELL-TORUS MONTHLY VACUUM BREAKER TEST PROCEDURE DUE TO PROCEDURALIZED UNACCEPTABLE PRECONDITIONING. |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," on February 14, 2014, for the licensee's failure to ensure that activities affec
Region: III | Monticello | 26993 | 03/31/2014 05/09/2014 | 2014002-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | UNCONTROLLED HIGH RADIATION AREA FOLLOWING SHUT-DOWN COOLING RE-ALIGNMENT. |  | P.5 Operating Experience | TE?: N | 05000263 Monticello |  | 71124.01 | A finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) 5.7.1 was self-revealed following a worker's unexpected electronic dosimeter alarm, which resulted in the identification of an unbarricaded and
Region: III | Monticello | 26979 | 03/28/2014 04/29/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Shorting Switch Modification Failed to ensure Drywell Spray Valves would not Spuriously Open. |  | P.2 Evaluation | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very-low-safety significance and associated NCV of 10 CFR Part 50, Appendix R, Section III.G.2 for the licensee's failure to ensure that safe shutdown (SSD) equipment were not susceptible to fire induced failures. Sp
Region: III | Monticello | 26980 | 03/28/2014 04/29/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Both Redundant Safe Shutdown Trains of Nitrogen Bottles were Found Located In the Same Fire Area. |  |  | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very-low-safety significance and associated NCV of 10 CFR Part 50, Appendix R, Section III.G.1 for the licensee's failure to ensure one of the redundant SSD trains located in the same fire area was free of fire damag
Region: III | Monticello | 26981 | 03/28/2014 04/29/2014 | 2014008-03 | NRC | NCV | Mitigating Systems | Green | Repairs Credited for Hot Shutdown Conditions. |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very-low-safety significance and associated NCV of 10 CFR Part 50, Appendix R, Section III.G.1 for the licensee's failure to provide one train of systems necessary to achieve and maintain hot shutdown conditions. Spe
Region: III | Monticello | 26975 | 12/31/2013 02/07/2014 | 2013005-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE FOR AO 13022 FURMANITE INJECTION. |  | H.2 Field Presence | TE?: N | 05000263 Monticello |  | 71111.19 | The inspectors identified a finding of very low safety significance and a NCV of Technical Specification (TS) 5.4.1 due to the failure to perform safety related maintenance in accordance with documented instructions. Specifically, the improper control of
Region: III | Monticello | 26976 | 12/31/2013 02/07/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | SBLC DISCHARGE PRESSURE PROCEDURAL LIMITS EXCEEDED. |  | H.11 Challenge the Unknown | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to accomplish activities affecting quality in accordance with
Region: III | Monticello | 26977 | 12/31/2013 02/07/2014 | 2013005-03 | Self - Revealed | FIN | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN RADIATION EXPOSURE ALARA DURING RFO 26. |  | H.5 Work Management | TE?: N | 05000263 Monticello |  | 71124.02 | A finding of very low safety significance was self revealed due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee's radiological work planning and work control program. Specifica
Region: III | Monticello | 26969 | 11/22/2013 12/30/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Effects of the HPCI Steam Isolation Outboard Valve Closure Time Increase |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71111.17T | Green. The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to evaluate the effects of increasing the high pressure coolant injection (HPCI)
Region: III | Monticello | 26970 | 11/22/2013 12/30/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Required Design Basis Analysis was Maintained |  | H.12 Avoid Complacency | TE?: N | 05000263 Monticello |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify that required analysis was in-place prior to superseding CA 00 082. Specifical
Region: III | Monticello | 26971 | 11/22/2013 12/30/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Qualification of UV Relay 27 43A |  | H.13 Consistent Process | TE?: N | 05000263 Monticello |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to maintain seismic qualification of safety-related undervoltage (UV) relay 27-43A, wher
Region: III | Monticello | 26972 | 11/22/2013 12/30/2013 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | EDG Fuel Oil Supply System Design does Not Meet the Single Failure Criteria |  |  | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the emergency diesel generator (EDG) fuel oil system original design met the s
Region: III | Monticello | 26962 | 09/30/2013 11/19/2013 | 2013004-01 | Self - Revealed | FIN | Initiating Events | Green | RECIRCULATION SYSTEM VULNERABILITIES DUE TO INADEQUATE MODIFICATION REVIEW. |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71111.18 | . A self revealed finding of very low safety significance occurred on August 27, 2013, due to the licensee's failure to adequately review and control modification work. Specifically, the licensee failed to follow FP E MOD 07, "Design Verification and Tech
Region: III | Monticello | 26963 | 09/30/2013 11/19/2013 | 2013004-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO MAINTAIN THE ODCM. |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71124.06 | A NRC identified finding of very low safety significance and an associated non cited violation of Technical Specification (TS) 5.5.1.a for the failure to perform an adequate technical review which led to the Offsite Dose Calculation Manual (ODCM) not bein
Region: III | Monticello | 26964 | 09/30/2013 11/19/2013 | 2013004-03 | Self - Revealed | NCV | Initiating Events | Green | LOSS OF ACCURATE LEVEL INDICATION DURING PARTIAL RCS DRAIN DOWN. |  | H.14 Conservative Bias | TE?: N | 05000263 Monticello |  | 71152 | A self revealed finding of very low safety significance and non cited violation of Technical Specification (TS) 5.4.1.a, "Procedures," occurred on June 3, 2013, due to the licensee's failure to implement procedures regarding maintenance or operations acti
Region: III | Monticello | 26965 | 09/30/2013 11/19/2013 | 2013004-04 | Self - Revealed | NCV | Mitigating Systems | Green | INAPPROPRIATE EMERGENCY SHUTDOWN OF BOTH EDGS DURING A LONOP EVENT. |  | H.7 Documentation | TE?: N | 05000263 Monticello |  | 71153 | A self revealed finding of very low safety significance and an associated non cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred on June 13, 2013, due to the licensee's failure to accomplish activit
Region: III | Monticello | 26944 | 06/30/2013 08/05/2013 | 2013003-01 | Self - Revealed | NCV | Initiating Events | Green | INADVERTENT MISPOSITIONING OF INSTRUMENT AIR VALVE AND LOSS OF SPENT FUEL POOL COOLING. |  | H.3(a) Work Planning | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance and an associated non-citied violation was self-revealed for the site's failure to implement the requirements of FP-OP-SC-01, "Status Control," when, on April 23, 2013, a valve in the instrument air system was mis
Region: III | Monticello | 26945 | 06/30/2013 08/05/2013 | 2013003-02 | Self - Revealed | NCV | Barrier Integrity | Green | SAFETY RELIEF VALVE TAILPIPE SENSING LINE ISOLATION VALVE FOUND CLOSED. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance and non-cited violation of Technical Specification (TS) 3.3.6.3, "Low-Low Set (LLS) Instrumentation," was self-revealed when the licensee discovered during the performance of an unrelated surveillance test that an
Region: III | Monticello | 26936 | 05/15/2013 06/11/2013 | 2013008-02 | NRC | FIN | Mitigating Systems | Green | INADEQUATE TI-187 PROCEDURE WALK-THROUGH. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000263 Monticello |  | NONE | The inspectors identified a finding of very low safety significance for the site's failure to perform adequate procedure walkthroughs to comply with NRC endorsed NEI 12-07, "Guidelines for Performing Walk-downs of Plant Flood Protection Features." Spec
Region: III | Monticello | 26744 | 03/31/2013 05/13/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | 14 RHR POWER CABLE INADVERTENTLY CUT. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to provide adequate work instructions for work o
Region: III | Monticello | 26745 | 03/31/2013 05/13/2013 | 2013002-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO ENTER RADIONUCLIDE ON RADIOACTIVE WASTE SHIPMENT DOCUMENTATION. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71124.08 | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR 71.5 for the failure to correctly complete radioactive waste shipping documents for radioactive shipments containing condensate resins.
Region: III | Monticello | 26734 | 12/31/2012 02/06/2013 | 2012005-01 | Self - Revealed | NCV | Mitigating Systems | Green | MANIPULATION OF SAFETY RELATED EQUIPMENT WITHOUT APPROPRIATE GUIDANCE OR APPROVAL OF SHIFT SUPERVISION. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71111.13 | A self-revealed finding of very low safety significance and non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when the licensee failed to properly restore the reactor core isolation c
Region: III | Monticello | 26724 | 09/30/2012 11/05/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONTROL THE CONFIGURATION OF DOOR 45 DURING MODIFICATION. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to properly implement work instructio
Region: III | Monticello | 26725 | 09/30/2012 11/05/2012 | 2012004-02 | NRC | FIN | Initiating Events | Green | BUS 12 LOCKOUT CAUSED BY INADEQUATE WORK PLAN. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance was self -revealed on September 25, 2012, when a reactor scram occurred during planned testing of the 2R to Bus 12 local (switchgear cubicle A201) and remote (control room panel C-08) ammeter switches. As a resu
Region: III | Monticello | 26719 | 06/30/2012 08/09/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MONITOR RESIDUAL HEAT REMOVAL SYSTEM UNDER 10 CFR 50.65(a)(1) DUE TO INAPPROPRIATE a(2) TRANSITION. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000263 Monticello |  | 71111.12 | The inspectors identified a finding of very low safety significance and non cited violation (NCV) of 10 CFR 50.65(a)(1)/(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to establish
Region: III | Monticello | 26720 | 06/30/2012 08/09/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MONITOR SSF PLANT LEVEL PERFORMANCE CRITERION EQUIPMENT UNDER 10 CFR 50.65(a)(1) DUE TO INADEQUATE SSF DATA TRACKING. |  | H.4(a) Human Error Prevention | TE?: N | 05000263 Monticello |  | 71111.12 | The inspectors identified a finding of very low safety significance and non cited violation (NCV) of 10 CFR 50.65(a)(1)/(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to evaluate
Region: III | Monticello | 26705 | 05/30/2012 07/12/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Station Battery Capacity Test Procedure |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawing," for the licensee's failure to ensure the bases for si
Region: III | Monticello | 26706 | 05/30/2012 07/12/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Voltage Requirements for Operability of Non-Motor Loads and 120 Vac Instrument Panels. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a finding of very low safety significance(Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate the operability of safety-related 12
Region: III | Monticello | 26711 | 05/30/2012 07/12/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Degraded Voltage Function Time Delay Design |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III for the licensee's failure to translate the actual time delay of the degraded voltage relay s
Region: III | Monticello | 26712 | 05/30/2012 07/12/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Effect of Degraded Voltage on Proper Operation of Thermal Overload Relays |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly analyze thermal overload relays (TO
Region: III | Monticello | 26713 | 05/30/2012 07/12/2012 | 2012007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Alignment of 120 Vac Instrument Buses |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure single failure
Region: III | Monticello | 26694 | 03/31/2012 04/17/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO MONITOR CONDENSATE FEEDWATER SYSTEM UNDER 50.65(a)(1) DUE TO INADEQUATE MAINTENANCE RULE FAILURE TRACKING. |  | P.1(b) Trend Performance CAP | TE?: N | 05000263 Monticello |  | 71111.12 | The inspectors identified a finding of very low safety significance and non-cited violation (NCV) of 10 CFR 50.65(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to establish an
Region: III | Monticello | 26695 | 03/31/2012 04/17/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MONITOR RESIDUAL HEAT REMOVAL SYSTEM UNDER 50.65(a)(1) DUE TO INADEQUATE MAINTNENACE RULE EVALUATIONS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71111.12 | The inspectors identified a finding of very low safety significance and non-cited violation (NCV) of 10 CFR 50.65(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to establish an
Region: III | Monticello | 26696 | 03/31/2012 04/17/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE EVALUATION OF COMPENSATORY MEASURE. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71111.15 | The inspectors identified a finding of very low safety significance and violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to identify and properly evaluate a compensatory measure imbedded in
Region: III | Monticello | 26704 | 03/31/2012 04/17/2012 | 2012002-06 | Self - Revealed | FIN | Initiating Events | Green | INEFFECTIVE MANAGEMENT OF TURBINE LUBE OIL TANK VACUUM RESULTING IN FOULING OF GROUNDING BRAIDS. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance was self -revealed on November 19, 2011, when a reactor scram occurred during planned turbine-generator testing, as a result of the site's failure to effectively monitor and control turbine lube oil (TLO) tank
Region: III | Monticello | 26666 | 12/31/2011 02/01/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | 'E' CONDENSATE DEMINERALIZER ALARM RESPONSE PROCEDURE LIMITS EXCEEDED. |  | H.3(a) Work Planning | TE?: N | 05000263 Monticello |  | 71111.13 | The inspectors identified a finding of very low safety significance and non cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," when the operators did not take conservative action to address a high differential pressure condition on
Region: III | Monticello | 26667 | 12/31/2011 02/01/2012 | 2011005-02 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE COMPLETION OF CAPRS ASSOCIATED WITH 2RS TO 2R FEEDER CABLE TESTING. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71111.2 | A finding of very low safety significance and NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was self revealed following a reactor scram, which was the direct result of an electric plant realignment caused by a faulted feeder cable and
Region: III | Monticello | 26671 | 12/31/2011 02/01/2012 | 2011005-03 | Self - Revealed | NCV | Initiating Events | Green | ROD WORTH MINIMIZER INOPERABLE DURING REACTOR PLANT STARTUP. |  | H.4(a) Human Error Prevention | TE?: N | 05000263 Monticello |  | 71111.2 | A finding of very low safety significance and NCV of TS 3.3.2.1, "Control Rod Block Instrumentation," was self revealed to the operating crew, when normal startup testing could not be accomplished due to improperly configured equipment. Specifically, the
Region: III | Monticello | 26672 | 12/31/2011 02/01/2012 | 2011005-04 | Self - Revealed | NCV | Public Radiation Safety | Green | FAILURE TO PROPERLY BLOCK AND BRACE A RADIOACTIVE PACKAGE FOR TRANSPORT. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000263 Monticello |  | 71124.08 | The inspectors reviewed a self revealed finding of very low safety significance and an associated NCV of 10 CFR 71.5. Specifically, the licensee failed to appropriately block and brace a radioactively contaminated condensate demineralizer vessel within a
Region: III | Monticello | 26693 | 12/31/2011 02/01/2012 | 2011005-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO MAKE A REQUIRED 60 DAY EVENT REPORT PER 10 CFR 50.73(a)(2)(vii)(A-D). |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71153 | The inspectors identified a Severity Level IV NCV and associated finding of very low safety significance of 10 CFR 50.73(a)(2)(vii)(A D), "Licensee Event Report System," for the failure to report an event to the NRC within 60 days, where a single cause or
Region: III | Monticello | 26664 | 12/15/2011 12/29/2011 | 2011010-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Fire Water Aging Management Program Implementing Procedure |  |  | TE?: N | 05000263 Monticello |  | 93812 | The inspectors identified a finding of very low safety significance (Green) involving the licensee's failure to accomplish activities affecting quality in accordance with procedures. Specifically, the licensee failed to incorporate operating experience in
Region: III | Monticello | 26662 | 09/30/2011 11/01/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW EMERGENCY DIESEL GENERATOR QUARTERLY SURVEILLANCE PROCEDURE. |  | H.4(a) Human Error Prevention | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated non cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to follow the quarterly emergency die
Region: III | Monticello | 26592 | 07/15/2011 08/23/2011 | 2011008-01 | NRC | NCV | Initiating Events | Green | HYDROGEN BOTTLES LOCATED BELOW RHR SYSTEM CABLES. |  |  | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," for the failure to evaluate the impact of the installation of the h
Region: III | Monticello | 26573 | 07/15/2011 08/23/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO INSPECT AND TEST THE MCR AIR INTAKE SMOKE DETECTOR. |  |  | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of License Condition 2.C.4 for the licensee's failure to inspect and test the main control room (MCR) air intake smoke detector. Specifically, the licensee failed to in
Region: III | Monticello | 26660 | 07/15/2011 08/23/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | B.5.b Strategy Did Not Ensure Minimum Flow Rate for Injection into RPV with Portable Pump. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of License Condition 2.C.(11), for the failure to develop and maintain an adequate strategy for the depressurization of the reactor pressure vessel (RPV) and injection
Region: III | Monticello | 26653 | 06/30/2011 08/08/2011 | 2011003-01 | Self - Revealed | FIN | Initiating Events | Green | POOR MAINTENANCE PRACTICES RESULT IN CV-3490 FAILING SHUT. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance was self revealed when, on two separate occasions, CV 3490 (12 reactor feedwater pump recirculation to the condenser) failed closed while the 12 reactor feedwater pump was being placed in service. The cause of eac
Region: III | Monticello | 26655 | 06/30/2011 08/08/2011 | 2011003-03 | NRC | FIN | Barrier Integrity | Green | FAILURE TO UPDATE USAR FOR CASK LEFT HEIGHT RESTRICTIONS. |  |  | TE?: N | 05000263 Monticello |  | 71111.2 | "Periodic Update of the Final Safety Analysis Report" and an accompanying Green finding were identified by the inspectors for the licensee's failure to update the Updated Safety Analysis Report (USAR) with the cask maximum lift height restrictions imposed
Region: III | Monticello | 26656 | 06/30/2011 08/08/2011 | 2011003-04 | Self - Revealed | FIN | Occupational Radiation Safety | Green | FAILURE TO MAINTAIN RADIATION EXPOSURE ALARA DURING INBOARD MAIN STEAM ISOLATION VALVE REPAIR. |  | H.3(b) Work Activity Coordination | TE?: N | 05000263 Monticello |  | NONE | A finding of very low safety significance (Green) was self revealed due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee's as-low-as-is-reasonably-achievable (ALARA) planning an
Region: III | Monticello | 26657 | 06/30/2011 08/08/2011 | 2011003-05 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE C.1 STARTUP PROCEDURE REVIEW. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance and non cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when an unexpected recirculation pump runback occurred during the performance of Rea
Region: III | Monticello | 26651 | 03/31/2011 05/10/2011 | 2011002-01 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE SYSTEM ISOLATION DURING CHECK VALVE MAINTENANCE. |  | H.3(a) Work Planning | TE?: N | 05000263 Monticello |  | 71111.2 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to adequately implement the requirements of their fleet tagging pro
Region: III | Monticello | 26652 | 03/31/2011 05/10/2011 | 2011002-03 | NRC | NCV | Barrier Integrity | Green | FAILURE TO CONTROL A LEVEL 1 FME AREA DURING NEW FUEL RECEIPT ACTIVITIES. |  | H.4(b) Procedural Compliance | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance and associated NCV of Technical Specification 5.4, "Procedures," was identified by the inspectors when the licensee failed to implement the requirements of their foreign material exclusion (FME) and control pro
Region: III | Monticello | 26649 | 12/31/2010 02/09/2011 | 2010005-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PROPERLY STORE LOOSE MATERIAL IN CLOSE PROXIMITY TO SAFETY RELATED EQUIPMENT. |  | H.4(b) Procedural Compliance | TE?: N | 05000263 Monticello |  | 71111.05Q | A finding of very low safety significance was identified by the inspectors when the licensee failed to properly control loose material located above the sensing lines for the safety related residual heat removal pump minimum flow switches. No violation of
Region: III | Monticello | 26650 | 12/31/2010 02/09/2011 | 2010005-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IMPLEMENT CORRECTIVE ACTIONS TO ADDRESS A DEFICIENCY ASSOCIATED WITH THE DOOR INTERLOCK ON AIRLOCK 413. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, was identified by the inspectors when the licensee failed to implement corrective actions for a condition adverse to quality. The cond
Region: III | Monticello | 26643 | 09/30/2010 11/03/2010 | 2010004-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE ELECTRICAL ISOLATION DURING DEMOLITION ACTIVITY. |  | H.3(a) Work Planning | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance and associated non cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when the licensee failed to adequately implement the requirements of thei
Region: III | Monticello | 26633 | 06/30/2010 08/06/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH TURBINE FLOOR HEAVY LIFT PROCEDURE. |  | H.3(a) Work Planning | TE?: N | 05000263 Monticello |  | 71111.18 | A finding of very low safety significance and associated non cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee, on two occasions during the lift and tra
Region: III | Monticello | 26634 | 06/30/2010 08/06/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | UNACCEPTABLE PRECONDITIONING OF 250 VDC BATTERY CHARGERS. |  | H.3(b) Work Activity Coordination | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1 for the licensee's failure to appropriately implement an applicable procedure recommended in Regulatory Guide 1.33, Appendix A, Re
Region: III | Monticello | 26624 | 03/31/2010 04/26/2010 | 2010002-02 | NRC | NCV | Barrier Integrity | Green | SRV LOW LOW SET SURVEILLANCE PROCEDURE IMPLEMENTATION. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low safety significance and NCV of Technical Specification 5.4.1 for the licensee failing to appropriately implement an applicable procedure recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February
Region: III | Monticello | 26625 | 03/31/2010 04/26/2010 | 2010002-03 | NRC | NCV | Barrier Integrity | Green | INADEQUATE CORRECTIVE ACTIONS FOR UNEXPECTED SRV LOW LOW SET TRIPS ENCOUNTERED DURING SURVEILLANCE TESTING. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71152 | The inspectors identified a finding of very low safety significance and NCV of 10 CFR 50, Appendix B, Criterion XVI, for the licensee's failure to adequately evaluate and take corrective actions for a condition adverse to quality. Specifically, the licens
Region: III | Monticello | 26641 | 03/26/2010 05/03/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform 10 CFR 50.59 Evaluation For Isolation of Room Cooler Which Addressed Temperature Limitations - performance deficiency |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000263 Monticello |  | 71111.17T | The inspectors identified a finding of very low safety significance for the licensee's failure to perform a written evaluation, which provided the bases for the determination that a change did not require a license amendment as required by 10 CFR 50.59. S
Region: III | Monticello | 26617 | 12/31/2009 02/05/2010 | 2009005-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE MAINTENANCE PROCEDURE FOR 'A' SBGT SYSTEM. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000263 Monticello |  | 71111.12 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to include acceptance criteria appropriate to
Region: III | Monticello | 26605 | 12/04/2009 01/06/2010 | 2009007-01 | NRC | NCV | Barrier Integrity | Green | Calculation Errors Associated With the Pneumatic Pressure Requirements for the Inboard Main Steam Isolation Valves |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to incorporate the actual physical configuration of the inboard main steam isolation valves (MSIVs) and th
Region: III | Monticello | 26606 | 12/04/2009 01/06/2010 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Emergency Service Water Piping Supports Did Not Meet Seismic Category 1 Design Basis Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," having very low safety significance for the failure to restore the emergency service water (ESW) piping supports to their design specificat
Region: III | Monticello | 26611 | 12/04/2009 01/06/2010 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Minimum Voltage Available at Safety-Related Electrical Components |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to adequately evaluate circuit loads in determining design limits in electrical calculation
Region: III | Monticello | 26612 | 12/04/2009 01/06/2010 | 2009007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing for Motor Control Center (MCC) Contactors |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance for the failure to have adequate testing for safety-related equipment to monitor component degradation. Specif
Region: III | Monticello | 26616 | 12/04/2009 01/06/2010 | 2009007-07 | NRC | NCV | Mitigating Systems | Green | Pipe Support Design Deficiencies |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure of two pipe supports to meet their design requirements. Specifically, the calculation for p
Region: III | Monticello | 26602 | 09/30/2009 10/26/2009 | 2009004-01 | NRC | NCV | Initiating Events | Green | PRECONDITIONING OF SAFETY RELATED PRESSURE SWITCHES DURING SURVEILLANCE TESTING. |  |  | TE?: N | 05000263 Monticello |  | 71111.22 | The inspectors identified a finding of very low significance and NCV of 10 CFR 50, Appendix B, Criterion V, for the licensee's failure to develop and implement an adequate surveillance test procedure to accurately assess the as found trip setpoint for the
Region: III | Monticello | 26603 | 09/30/2009 10/26/2009 | 2009004-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO APPROPRIATELY IMPLEMENT TS 3.6.4.3. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000263 Monticello |  | 71153 | The inspectors identified a finding of very low significance and NCV of Technical Specification (TS) 3.6.4.3.B for the licensee not entering the associated limiting condition for operation (LCO) when presented with information that the 'A' standby gas tre
Region: III | Monticello | 26594 | 06/30/2009 08/04/2009 | 2009003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION AND RWP REQUIREMENTS DURING WORK IN A LOCKED HIGH RADIATION AREA. |  | H.4(b) Procedural Compliance | TE?: N | 05000263 Monticello |  | 7112101 | A self-revealed finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification 5.7.1.b was identified for the failure to comply with the requirements of the radiation work permit during ultrasonic testing pr
Region: III | Monticello | 26583 | 04/01/2009 05/14/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | USE OF NON-QUALITY DOCUMENTS IN THE ABSENCE OF APPROVED PROCEDURES TO MODIFY THE NORMAL OPERATION OF IRM 11 AND IRM 18. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000263 Monticello |  | 71111.15 | The inspectors identified a finding of very low significance and NCV of 10 CFR 50, Appendix B, Criterion V, for the licensee approving the use of non-quality documents in the absence of approved procedures to modify the normal operation of intermediate ra
Region: III | Monticello | 26588 | 04/01/2009 05/14/2009 | 2009002-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY EVALUATE TEMPORARY CHANGES TO RCIC SURVEILLANCE PROCEDURES PRIOR TO IMPLEMENTATION. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71111.22 | A finding of very low safety significance and NCV of 10 CFR 50, Appendix B, Criterion V, was self revealed when the performance of an inadequately prepared temporary procedure change resulted in the inadvertent repositioning of a reactor core isolation co
Region: III | Monticello | 26568 | 11/07/2008 11/28/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY IDENTIFY A CONDITION ADVERSE TO QUALITY AND IDENTIFY CORRECTIVE ACTIONS TO PREVENT RECURRENCE. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71152B | The NRC identified a Green NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify a Condition Adverse to Quality (CAQ). Specifically, the licensee did not identify a maintenance preventable functional failure (MPFF)
Region: III | Monticello | 26569 | 11/07/2008 11/28/2008 | 2008008-02 | NRC | NCV | Initiating Events | Green | FAILURE TO IDENTIFY A CONDITION ADVERSE TO QUALITY. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000263 Monticello |  | 71152B | The NRC identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to identify and correct a Condition Adverse to Quality (CAQ). Specifically, the licensee failed to capture in the CAP a co
Region: III | Monticello | 26571 | 11/03/2008 12/16/2008 | 2008009-01 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURAL GUIDANCE FOR CONTROL ROD DRIVE SYSTEM VALVE OPERATION. |  | P.1(e) Alternative CAP Process | TE?: N | 05000263 Monticello |  | 93812 | A self-revealed finding of very low safety significance, associated with a NCV of 10 CFR 50, Appendix B, Criterion V, was identified for inadequate procedural guidance after operator response to the reactor scram and vessel isolation was complicated by ri
Region: III | Monticello | 26572 | 11/03/2008 12/16/2008 | 2008009-02 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE/IMPROPER MAINTENANCE ON HPCI SV-1 VALVE. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 93812 | A self-revealed finding of very low safety significance, associated with a NCV of TS 5.4.1, was identified following a failure of the high pressure coolant injection (HPCI) System to trip when reactor pressure vessel (RPV) water level reached the trip set
Region: III | Monticello | 26574 | 11/03/2008 12/16/2008 | 2008009-03 | NRC | NCV | Initiating Events | Green | FAILURE TO SCOPE INTO THE MAINTENANCE RULE MONITORING PROGRAM THE 34.5KV CABLES. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 93812 | The inspectors identified a finding of very low safety significance and NCV of 10 CFR 50.65 (a)(1) for the licensee's failure to establish an effective monitoring and corrective action plan that included the 34.5kV underground feeder cables routed from 2R
Region: III | Monticello | 26575 | 11/03/2008 12/16/2008 | 2008009-04 | NRC | FIN | Initiating Events | Green | INADEQUATE MEDIUM VOLTAGE CABLE TESTING PROGRAM. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000263 Monticello |  | 93812 | The inspectors identified a finding of very low safety significance with no associated violation of regulatory requirements for the licensee's failure to establish and implement an effective test control program that demonstrated that underground 34.5kV m
Region: III | Monticello | 26576 | 11/03/2008 12/16/2008 | 2008009-05 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO CORRECTLY IMPLEMENT THE POST SCRAM CHECKLIST. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 93812 | A self-revealed finding of very low safety significance, associated with a NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified following a loss of shutdown cooling on September 20, 2008. Specifically, operat
Region: III | Monticello | 26565 | 09/30/2008 11/14/2008 | 2008004-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS FOLLOWING REPETITIVE FAILURE OF LPCI RECIRCULATION RISER DIFFERENTIAL PRESSURE INSTRUMENT. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was self-revealed for failing to appropriately correct a known condition adverse-to-quality associated with a low pressure coolant i
Region: III | Monticello | 26567 | 09/30/2008 11/14/2008 | 2008004-03 | Self - Revealed | FIN | Initiating Events | Green | IMPROPER INSTALLATION OF GROUNDING TRUCKS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000263 Monticello |  | 71152 | . A finding of very low safety significance was self-revealed when plant operators attempted to install incorrect components (motor test devices instead of bus grounding trucks) into two 4160 volt breaker cubicles during the implementation of a clearance
Region: III | Monticello | 25609 | 06/30/2008 08/01/2008 | 2008003-01 | Self - Revealed | NCV | Barrier Integrity | Green | LICENSEE INADVERTENTLY ACTUATED AND RESET THE STANDBY GAS TREATMENT SYSTEM WHILE CONDUCTING ROUTINE CONTROL ROOM PANEL LAMP CHECKS. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance and NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the licensee failed to operate safety significant equipment in accordance with approved operating pro
Region: III | Monticello | 25637 | 04/18/2008 05/30/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | SHUTDOWN PANEL REQUIREMENTS REMOVED FROM IMPROVED TECHNICAL SPECIFICATIONS. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71111.05T | A finding of very low safety significance and associated NCV of license condition 2.C.4 was identified by the inspectors for the removal of the alternative shutdown system (ASDS) panel's administrative control requirements from the Improved Technical Spec
Region: III | Monticello | 25638 | 04/18/2008 05/30/2008 | 2008006-02 | NRC | NCV | Initiating Events | Green | UNCONTROLLED TRANSIENT COMBUSTIBLES. |  | H.4(b) Procedural Compliance | TE?: N | 05000263 Monticello |  | 71111.05T | A finding of very low safety significance and associated NCV of license condition 2.C.4 was identified by the inspectors for the presence of uncontrolled transient combustible material stored in the turbine building. Specifically, in response to an inspec
Region: III | Monticello | 25630 | 04/18/2008 05/19/2008 | 2008007-01 | NRC | NCV | Barrier Integrity | Green | This is a security Related Finding - see inspection report for details. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02-
Region: III | Monticello | 25631 | 04/18/2008 05/19/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | This is a security Related Finding - see inspection report for details. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02
Region: III | Monticello | 25624 | 03/31/2008 04/25/2008 | 2008002-01 | NRC | NCV | Barrier Integrity | Green | IMPROPER PROCEDURE IMPLEMENTATION RESULTS IN UNEVALUATED PRECONDITIONING OF MSIV'S. |  | H.3(b) Work Activity Coordination | TE?: N | 05000263 Monticello |  | 71111.12 | A finding of very low safety significance and NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified by the inspectors for the failure to accomplish inservice TS surveillance testing in accordance with documente
Region: III | Monticello | 25629 | 03/31/2008 04/25/2008 | 2008002-03 | Self - Revealed | NCV | Initiating Events | Green | UNPLANNED LOSS OF 345kV POWER SOURCE. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance and associated non-cited violation (NCV) of Technical Specification (TS) 5.4 was self-revealed for failing to establish procedures to adequately control work activities in the owner-controlled switchyard. Due to t
Region: III | Monticello | 25621 | 09/30/2007 10/30/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | UNQUALIFIED PROCEDURE FOR DETECTION OF PITTING. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000263 Monticello |  | NONE | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR 50, Appendix B, Criterion IX, "Control of Special Processes," associated with the licensee's failure to use a nondestructive examination (NDE) procedure q
Region: III | Monticello | 25622 | 09/30/2007 10/30/2007 | 2007004-02 | Self - Revealed | FIN | Initiating Events | Green | FEEDWATER PERTURBATION DUE TO INSTRUMENT AIR PRESSURE REDUCTION TO FEEDWATER HEATER DRAIN VALVE POSITIONER. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71111.13 | A finding of very low safety significance was self-revealed when the 12B low pressure feedwater heater drain valve unexpectedly closed, causing a feedwater temperature perturbation. Specifically, the drain valve closed when technicians attached calibratio
Region: III | Monticello | 25623 | 09/30/2007 10/30/2007 | 2007004-03 | Self - Revealed | NCV | Mitigating Systems | Green | OPERATORS FAILED TO PERFORM TEST PROCEDURE IN ACCORDANCE WITH PROCEDURE. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000263 Monticello |  | 71153 | A finding of very low safety significance was self-revealed for a violation of 10 CFR 50, Appendix B, Criterion V, when licensed operators failed to perform Procedure OSP-RHR-0545-02, "RHR Containment Spray/Cooling Logic Test - Division II," in accordance
Region: III | Monticello | 25615 | 06/30/2007 07/18/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ACCOMPLISH SERVICE WATER INSPECTION PROGRAM REQUIREMENTS. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000263 Monticello |  | 71152 | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to perform portions of Fleet Procedure FP-PE
Region: III | Monticello | 25605 | 03/31/2007 04/27/2007 | 2007002-01 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE PREPARATION TO ADDRESS THE POTENTIAL LOSS OF THE STATION HEATING BOILER PRIOR TO THE ONSET OF EXTREME COLD OUTSIDE AMBIENT TEMPERATURES. |  | H.2(d) Facilities & Equipment | TE?: N | 05000263 Monticello |  | 71111.01 | A finding of very low safety significance was self-revealed when, due to the licensee's inadequate preparation to address the potential loss of the station heating boiler prior to the onset of extreme cold outside ambient temperatures, a temporary heating
Region: III | Monticello | 25606 | 03/31/2007 04/27/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE WRITTEN INSTRUCTIONS FOR THE COMPENSATORY ACTIONS DENOTED IN OPERABILITY RECOMMENDATION. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 71111.15 | An inspector-identified finding of very low safety significance was identified for a violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to provide written instructions for the compensatory a
Region: III | Monticello | 25607 | 03/31/2007 04/27/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE 14 EMERGENCY SERVICE WATER SURVEILLANCE PROCEDURE. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000263 Monticello |  | 71152 | An inspector-identified finding of very low safety significance was identified for a violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the licensee failed to maintain written instructions which adequately veri
Region: III | Monticello | 25613 | 03/31/2007 04/27/2007 | 2007002-05 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE CLEARANCE ORDER FOR BUS 16 ISOLATION RESULTING IN LOSS OF BUS 16 AND GROUP II ISOLATION. |  | H.3(b) Work Activity Coordination | TE?: N | 05000263 Monticello |  | 71153 | A self-revealed finding of very low safety significance was identified for a violation of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when the Division II essential 4160 Vac Bus 16 was lost,
Region: III | Monticello | 25595 | 12/31/2006 01/22/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | LICENSEE ANNOUNCED FIRE DRILL IMPLEMENTATION PRACTICE INCONSISTENT WITH THE REQUIREMENTS OF APPENDIX R. |  | P.3(a) Self-Assessment | TE?: N | 05000263 Monticello |  | 71111.05A | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR 50, Appendix R, Section III.I.3.e, when the licensee did not demonstrate the minimum-required attributes to successfully complete a required quarterly ann
Region: III | Monticello | 25596 | 12/31/2006 01/22/2007 | 2006005-02 | Self - Revealed | NCV | Initiating Events | Green | UNEXPECTED HALF SCRAM DUE TO INADEQUATE WORK PLAN. |  | H.3(b) Work Activity Coordination | TE?: N | 05000263 Monticello |  | 71111.13 | A self-revealed finding of very low safety significance was identified for a violation of 10 Code of Federal Regulations (CFR) 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when an unexpected half scram occurred on October 3, 2006
Region: III | Monticello | 25599 | 12/31/2006 01/22/2007 | 2006005-03 | NRC | NCV | Barrier Integrity | Green | LICENSEE FAILED TO INCORPORATED CURRENT LICENSING BASIS INFORMATION INTO THE ENGINEERING CHANGE PACKAGE AND 50.59 SCREEN PRIOR TO THE IMPLEMENTING THE MODIFICATION. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000263 Monticello |  | 7111117A | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR 50, Appendix B, Criterion III, when the licensee failed to incorporate current licensing basis information into the engineering change package and 50.59 s
Region: III | Monticello | 25592 | 06/30/2006 07/17/2006 | 2006003-01 | NRC | FIN | Mitigating Systems | Green | IMPROPER LOOSE MATERIAL STORAGE ADJACENT TO LPCI COMPONENTS. |  |  | TE?: N | 05000263 Monticello |  | 71111.05Q | A finding of very low safety significance was identified by the inspectors for failure to control loose materials, located above and adjacent to the Division II low pressure coolant injection (LPCI) inboard isolation valve and associated piping. Once iden
Region: III | Monticello | 25593 | 06/30/2006 07/17/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | I&C TECHNICIANS PERFORMED UNAUTHORIZED POST MAINTENANCE TESTS DURING A TORUS TO REACTOR BUILDING VACUUM BREAKER OPERABILITY CHECK. |  |  | TE?: N | 05000263 Monticello |  | 71111.22 | A finding of very low safety significance was identified by the inspectors for a violation of 10 CFR 50, Appendix B, Criterion V, when licensee Instrumentation & Controls (I&C) technicians deviated from existing procedural guidance to perform unauthorized
Region: III | Monticello | 25586 | 06/23/2006 08/03/2006 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Voltage Drop Assumption in Calculation Was Not Met |  |  | TE?: N | 05000263 Monticello |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving the voltage drop on cables from motor control center (MCC) 134 to various loads. Specific
Region: III | Monticello | 25584 | 03/31/2006 04/26/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT EXISTING PROCEDURAL GUIDANCE FOR THE CONTROL OF CLEARANCES BETWEEN INSTALLED SCAFFOLDING AND PLANT EQUIPMENT. |  |  | TE?: N | 05000263 Monticello |  | 71111.19 | A Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, was identified by the inspectors when the licensee failed to implement existing procedural guidance for the control of clearances between installed scaffolding and plant equipment. Specifi
Region: III | Monticello | 25585 | 03/31/2006 04/26/2006 | 2006002-02 | Self - Revealed | NCV | Barrier Integrity | Green | UNMONITORED CONTROL ROD MOVEMENT DURING CONTROL ROD TESTING. |  |  | TE?: N | 05000263 Monticello |  | 71111.22 | A Green self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, was identified during the performance of control rod drive scram insertion time testing when an operator initiated the movement of a control rod without first verifying that
Region: III | Monticello | 24347 | 07/27/2018 |  | Licensee - Identified | NCV |  | Green | Correction of Emergency Planning Weaknesses and Deficiencies |  |  | TE?: N | 05000263 Monticello |  | 71114.05
Region: III | Monticello | 125893 | 10/29/2019 |  |  | LIV |  | Green | Operations Personnel Not Assigned to the Critical Group |  |  | TE?: N | 05000263 Monticello |  | 71130.01
Region: III | Palisades | 125782 | 09/12/2019 10/21/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Environmentally Qualify Electric Equipment Inside Containment for the Most Severe Chemical Composition |  | NPP | TE?: N | 05000255 Palisades | Equipment Performance | 71111.21N | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50.49, "Environmental Qualification of Electric Equipment Important to Safety for Nuclear Power Plants," Paragraph (e)(3),
Region: III | Palisades | 125304 | 06/30/2019 07/26/2019 | 2019002-01 | NRC | NCV | Initiating Events | Green | Inadequate Ultrasonic Examination of Reactor Head Nozzles Results in Operation with Pressure Boundary Leakage |  | H.2 - Field Presence | TE?: N | 05000255 Palisades |  | 71111.08P | The inspectors identified a Green finding and associated Non-Cited Violation (NCV) of Technical Specification (TS) 3.4.13.a, “Reactor Coolant System Operational Leakage,” for the licensee’s failure to place the plant in Mode 3 (Hot Standby) within 6 hours
Region: III | Palisades | 24676 | 09/30/2018 10/29/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Wire Not Landed on Safety Injection Initiation Relay Circuit |  | H.12 - Avoid Complacency | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a Green finding and an associated NCV of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to accomplish an activity affecting quality in accordance with the implementing pro
Region: III | Palisades | 24063 | 04/06/2018 06/26/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Fire Protection System Functional Test Procedure |  | NPP | TE?: N | 05000255 Palisades |  | 71111.05XT | The inspectors identified a finding of very-low safety significance and associated violation of Technical Specification 5.4, “Procedures,” for the licensee’s failure to maintain fire protection system functional test procedure. Specifically, the licensee
Region: III | Palisades | 24062 | 04/06/2018 06/26/2018 | 2018415-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Guidance and Strategies for B.5.b Event |  | H.3 - Change Management | TE?: N | 05000255 Palisades |  | 71111.05XT | "**OUO-Security Related Information** The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR 50.54(hh)(2) for the licensee’s failure to implement guidance and strategies intended to maintain or restore
Region: III | Palisades | 23972 | 03/31/2018 05/14/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain an Appropriate Documented Work Instruction for Reassembly of Primary Makeup Tank Makeup Control Valve CV–2008 |  | P.2 - Evaluation | TE?: N | 05000255 Palisades |  | 71152 | A self-revealed Green finding and an associated Non-Cited Violation (NCV) of Technical Specification (TS) 5.4.1, “Procedures,” was identified for the licensee’s failure to have an adequate maintenance work instruction for the reassembly of Primary Makeup
Region: III | Palisades | 22671 | 12/31/2017 02/12/2018 | 2017004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Improperly Connected M&TE Leads to Unexpected AFU Fan Trip |  | H.2 - Field Presence | TE?: N | 05000255 Palisades |  | 71111.22 | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was self-revealed when the licensee failed to follow step 5.4.
Region: III | Palisades | 23458 | 11/17/2017 12/29/2017 | 2017007-01 | NRC | NCV | Barrier Integrity | Green | Containment Spray Pipe Support Strap Deficiencies |  | NPP | TE?: N | 05000255 Palisades |  | 71111.21M | The inspectors identified a finding of low safety significance (Green) and an associated potential NCV of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, “Design Control,” for failure to meet Updated Final Safety Analysis
Region: III | Palisades | 22273 | 09/30/2017 10/25/2017 | 2017003-03 | Self - Revealed | NCV | Mitigating Systems | Green | 1-2 Diesel Generator Trip During Maintenance Resulting in Additional Unavailability of the 1-2 Diesel Generator |  | H.5 - Work Management | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1, “Procedures”, was self-revealed on March 31, 2017, when the 1-2 Diesel Generator (DG) tripped during performance of the monthly TS surveillance procedure M
Region: III | Palisades | 38021 | 12/31/2016 02/14/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Have Appropriate Controls in Place for Combustible Materials |  | H.9 Training | TE?: N | 05000255 Palisades |  | 71111.05Q | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR), Part 50, Section 48(c) was identified by the inspectors for the licensee's failure to appropriately implement the requirements of proc
Region: III | Palisades | 38022 | 12/31/2016 02/14/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct an Adverse Condition Associated with Diesel Generator Load Sequencer Module |  |  | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance and an associated NCV of 10 CFR, Part 50, Appendix B, Criterion XVI, "Corrective Action," was self revealed for the licensee's failure to promptly correct a condition adverse to quality. Specifically, the licensee
Region: III | Palisades | 38028 | 12/31/2016 02/14/2017 | 2016004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Translate Design Analysis Stack-up Configuration into Specifications, Drawings, Procedures, and Instructions |  | H.2 Field Presence | TE?: N | 05000255 Palisades |  | NONE | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to establish measures to assure that the app
Region: III | Palisades | 38019 | 09/30/2016 11/10/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Appropriately Select and Review for Sutability of Application the Control Switch and Circuit Design of the Engineered Safeguards Room Cooler Fans |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71111.13 | A self revealed finding of very low safety significance and an associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to appropriately selec
Region: III | Palisades | 38017 | 07/15/2016 08/02/2016 | 2016009-01 | NRC | NCVIV | Barrier Integrity | Green | Failure to Document 50.59 Evaluation for Removal of Eight Hour Operator Rounds from the FSAR (Section 1R17.1.b) |  | H.9 Training | TE?: Y SL-IV-NCVIV | 05000255 Palisades |  | 71111.17T | The inspectors identified a Severity Level IV, Non-Cited Violation of Title 10 of the Code of Federal Regulations (CFR), Part 50.59, "Changes, Tests, and Experiments," and an associated finding of very low safety significance (Green) for the licensee's fa
Region: III | Palisades | 38010 | 04/08/2016 05/19/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Containment Spray Pump Non-conformance |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71152B | The team identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct a condition adverse to quality. Specifically, the license
Region: III | Palisades | 38008 | 03/31/2016 05/04/2016 | 2016001-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Movement of Radioactive Material Results in an Unposted and Un-Barricaded High-Radiation Area |  | H.4 Teamwork | TE?: N | 05000255 Palisades |  | 71124.01 | A self revealed finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.7.1 was identified when movement of a bag of radioactive material caused an area to become a high radiation area without the proper
Region: III | Palisades | 38009 | 03/31/2016 05/04/2016 | 2016001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Meet the Minimum Staffing Requirements of the Fire Brigade |  | H.7 Documentation | TE?: N | 05000255 Palisades |  | 71152 | An NRC identified finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Section 48(c) and the National Fire Protection Association (NFPA) Standard 805 Section 3.4.1 was identified fo
Region: III | Palisades | 38004 | 12/31/2015 02/12/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate PT Examination of Pipe Lug Welds |  | H.2 Field Presence | TE?: N | 05000255 Palisades |  | 71111.08P | The inspectors identified a finding of very-low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure to perform a d
Region: III | Palisades | 38005 | 12/31/2015 02/12/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Components Required to be Covered by the Quality Assurance Program |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very-low safety significance, and an associated NCV of 10 CFR, Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the licensee's failure to identify all component cooling water (CCW) structures, syst
Region: III | Palisades | 38007 | 12/31/2015 02/12/2016 | 2015004-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a Required 50.59 Evaluation for Declassification of the CVCS |  |  | TE?: Y SL-IV-NCVIV | 05000255 Palisades |  | NONE | The inspectors identified a SL IV, NCV of 10 CFR, Part 50.59, "Changes, Tests, and Experiments," and an associated finding of very-low safety significance (Green) for the licensee's failure to maintain a record of the declassification of the Chemical Volu
Region: III | Palisades | 38000 | 09/30/2015 10/30/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Justify Continued Service of Safety-Related Electrolytic Capacitors Installed Beyond Their Service Live |  | P.5 - Operating Experience | TE?: N | 05000255 Palisades | Equipment Performance | 71111.15 | An NRC identified finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to justify continued service of sa
Region: III | Palisades | 38001 | 09/30/2015 10/30/2015 | 2015003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Establish, Implement, and Maintain the Offsite Dose Calculation Manual |  | H.9 - Training | TE?: N | 05000255 Palisades | Program & Process | 71124.06 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.5.1, "Offsite Dose Calculation Manual," was identified for the failure to establish, implement, and maintain the Offsite Dose Calculation Manual (ODCM) relat
Region: III | Palisades | 37999 | 08/19/2015 09/17/2015 | 2015012-02 | NRC | NCV | Initiating Events | Green | Operability Evaluation Not Performed in Accordance with Station Procedure (Section 1R15) | EA Case: 2015171 | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71111.15 | Green. An NRC identified finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the licensee's failu
Region: III | Palisades | 37991 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Appropriate Corrective Action for the Charging System While in Maintenance Rule (a)(1) Status |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71111.12 | An NRC identified finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) 50.65(a)(1) was identified for the failure to take appropriate corrective actions for the charging system, while in Mainte
Region: III | Palisades | 37994 | 06/30/2015 08/05/2015 | 2015002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Wear Prescribed Respiratory Protection |  | H.10 Bases for Decisions | TE?: N | 05000255 Palisades |  | 71124.03 | A self revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1 was identified for insulation work activities during the refueling outage associated with pressurizer spray valve CV-1057. Specifically, pr
Region: III | Palisades | 37990 | 04/17/2015 05/15/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Assess the Suppression System in the Cable Spreading Room in the Probabilistic Risk Assessment for NFPA 805 (Section 1R05.3b) |  | H.4 Teamwork | TE?: N | 05000255 Palisades |  | 71111.05XT | Green. The inspectors identified a finding of very-low safety significance, and an associated NCV of Title 10, Code of Federal Regulations (CFR) 50.48(c), and National Fire Protection Association Standard 805, Section 2.4.3.3 for the licensee's failure to
Region: III | Palisades | 37974 | 03/31/2015 04/30/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Failure of Component Cooling Water Pump |  | H.12 Avoid Complacency | TE?: N | 05000255 Palisades |  | 71111.12 | A finding of very low safety significance and an associated NCV of TS 5.4.1(a) was self-revealed on January 6, 2015, after the licensee identified smoke coming from the 'C' component cooling water (CCW) pump (P-52C) as a result of incorrect assembly of th
Region: III | Palisades | 37975 | 03/31/2015 04/30/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Inoperability of Safety Injection Tank Due to Long-Term Leakage |  | H.12 Avoid Complacency | TE?: N | 05000255 Palisades |  | 71111.12 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors when licensee personnel failed to assure that leakage out of the 'B' safety injection tank (SIT)
Region: III | Palisades | 37981 | 03/31/2015 04/30/2015 | 2015001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Credited High Energy Line Break Barriers |  |  | TE?: N | 05000255 Palisades |  | 71111.13 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors when the licensee credited fire doors for High Energy Line Break (HELB) protection without a suppor
Region: III | Palisades | 37982 | 03/31/2015 04/30/2015 | 2015001-05 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of the Use of Non-Seismic Temporary Jumpers |  |  | TE?: Y SL-IV-NCVIV | 05000255 Palisades |  | 71111.18 | A Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance was identified by the inspectors when licensee personnel failed to maintain a written safety evaluation that provid
Region: III | Palisades | 37983 | 03/31/2015 04/30/2015 | 2015001-06 | NRC | FIN | Mitigating Systems | Green | Failure to Evaluate the Adverse Effects of the Use of Non-Seismic Temporary Jumpers |  | H.14 Conservative Bias | TE?: N | 05000255 Palisades |  | 71111.18 | A Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance was identified by the inspectors when licensee personnel failed to maintain a written safety evaluation that provid
Region: III | Palisades | 37989 | 03/31/2015 04/30/2015 | 2015001-07 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Leads to primary Coolant Pump Seal Degradation |  | H.5 Work Management | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1(a) was self-revealed when the 'C' primary coolant pump (PCP) seal degraded as a result of an inadequate maintenance procedure. Specifically, maintenance
Region: III | Palisades | 37972 | 02/27/2015 03/26/2015 | 2015009-01 | NRC | NCV | Initiating Events | Green | Failure to Determine the Cause of Head Penetration Nozzle J-Grove Weld Cracking (Section 4OA2.1) |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71152 | Green: The inspector identified a finding of very-low safety significance with an associated NCV of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to establish measures to
Region: III | Palisades | 37973 | 02/27/2015 03/26/2015 | 2015009-02 | NRC | NCV | Initiating Events | Green | Unqualified Non-Destructive Examinations of J-Grove Welds 29 and 30 (Section 4OA2.1) |  |  | TE?: N | 05000255 Palisades |  | 71152 | Green: The inspector identified a finding of very-low safety significance with an associated NCV of 10 CFR Part 50, Appendix B, Criterion IX "Control of Special Processes," for the licensee's failure to use qualified personnel and procedures for the dy
Region: III | Palisades | 37970 | 12/31/2014 02/03/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Storage of Equipment in the Vicinity of Safety-Related Equipment |  | P.1 Identification | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding of very low safety significance (Green) with an associated non-citied violation of Technical Specification (TS) 5.4.1, Procedures and Programs, for the failure to follow site procedures covering the storage of material
Region: III | Palisades | 37947 | 11/04/2014 12/02/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Engineered Safeguards Systems Aren't Adversely Affected By Air Entrainment |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the failure to ensure the safety-related Engineered Safeguard Systems trains would no
Region: III | Palisades | 37948 | 11/04/2014 12/02/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Undersized Supply Cables from Startup Transformer to 2400V Buses |  | H.6 Design Margins | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure the incoming feeder cables from startup transformer 1-2 to 2400 V s
Region: III | Palisades | 37955 | 11/04/2014 12/02/2014 | 2014008-03 | NRC | NCV | Mitigating Systems | Green | Undersized Motors |  | H.6 Design Margins | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure electric motors are sized in accordance with the design basis, as d
Region: III | Palisades | 37956 | 11/04/2014 12/02/2014 | 2014008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that 480V System Voltages do not Exceed Equipment Ratings |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that voltages on the 480V system do not exceed equipment ratings. S
Region: III | Palisades | 37957 | 11/04/2014 12/02/2014 | 2014008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Comprehensive Pump Testing of Containment Spray Pump P-54A in Accordance with the Inservice Testing Program |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of Technical Specifications 5.5.7, "Inservice Testing Program," for the failure to perform comprehensive pump testing of Containment Spray Pump P-54A in
Region: III | Palisades | 37958 | 11/04/2014 12/02/2014 | 2014008-06 | NRC | NCV | Barrier Integrity | Green | Failure to Correctly Translate Valve Leakage Limits into Test Procedure |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate design valve leakage limits into the applicabl
Region: III | Palisades | 37962 | 11/04/2014 12/02/2014 | 2014008-07 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Non-Safety-Related Sub-Components Improperly Supplied with Safety-Related Valves |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," for the licensee's failure to identify non-safety-relate
Region: III | Palisades | 37963 | 11/04/2014 12/02/2014 | 2014008-08 | NRC | NCV | Barrier Integrity | Green | Failure to Establish an Adequate Test Program for the Shutdown Cooling Heat Exchangers |  | H.14 Conservative Bias | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish an adequate test program for the Shutdown Cooling (SDC) Heat Exchan
Region: III | Palisades | 37964 | 11/04/2014 12/02/2014 | 2014008-09 | NRC | NCV | Initiating Events | Green | Failure to Include the Degraded Voltage Channel Time Delay in TS Surveillance Requirement 3.3.5.2a |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated Non-Cited Violation (NCV) of 10 CFR Part 50.36(c)(3), "Surveillance Requirements," for the failure to ensure the channel time delay for the degraded-voltage monitor
Region: III | Palisades | 37968 | 11/04/2014 12/02/2014 | 2014008-13 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Surveillance for Emergency Diesel Generator Largest Load Reject Test |  | H.1 Resources | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to have adequate acceptance criteria in the emergency diesel generator surveilla
Region: III | Palisades | 37943 | 09/30/2014 11/06/2014 | 2014004-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Protection against High Winds |  | H.9 Training | TE?: N | 05000255 Palisades |  | 71111.01 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) 5.4.1 when licensee personnel failed to maintain and implement an adequate procedure covering Acts of Nature. Specifi
Region: III | Palisades | 37944 | 09/30/2014 11/06/2014 | 2014004-02 | NRC | NCV | Barrier Integrity | Green | Spent Fuel Pool Region II Criticality Analysis |  | P.5 Operating Experience | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to follow procedure EN OP 104, "Opera
Region: III | Palisades | 37932 | 06/30/2014 07/25/2014 | 2014003-01 | NRC | FIN | Mitigating Systems | Green | Written NRC Biennial Written Examinations Did Not meet Qualitative Standards |  |  | TE?: N | 05000255 Palisades |  | 71111.11A | The inspectors identified a finding of very low safety significance associated with 10 CFR 55.59, "Requalification," based on a determination that greater than 20 percent of the biennial requalification written exam questions administered to licensed oper
Region: III | Palisades | 37933 | 06/30/2014 07/25/2014 | 2014003-02 | NRC | NCV | MISC | Green | Exam Security Issues |  | H.8 Procedure Adherence | TE?: N | 05000255 Palisades |  | 71111.11A | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 55.49, "Integrity of Examinations and Tests," which stated, "Applicants, licensees, and facility licensees shall not engage in any activity
Region: III | Palisades | 37934 | 06/30/2014 07/25/2014 | 2014003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Long-Term Scaffolds in Accordance with Procedures |  | H.4 Teamwork | TE?: N | 05000255 Palisades |  | 71111.18 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to adequately implement procedure EN
Region: III | Palisades | 37935 | 06/30/2014 07/25/2014 | 2014003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure Associated with Sealed Source Inventory and Leak Testing |  | P.6 Self Assessment | TE?: N | 05000255 Palisades |  | 71124.01 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) 5.4.1 for the failure to maintain a sealed source inventory and perform leak tests required by station procedures. Th
Region: III | Palisades | 37936 | 06/30/2014 07/25/2014 | 2014003-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Inadequate Control of Entry into High Radiation Areas |  | H.14 Conservative Bias | TE?: N | 05000255 Palisades |  | 71124.01 | The inspectors reviewed a self revealed finding of very low safety significance and an associated non-cited violation of TS 5.7.1 for unauthorized entries into high radiation areas (HRAs). Specifically, on January 30, 2014, a worker replacing lights in lo
Region: III | Palisades | 37942 | 06/30/2014 07/25/2014 | 2014003-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entries into High Radiation Areas without Required Dosimetry |  | H.12 Avoid Complacency | TE?: N | 05000255 Palisades |  | 71124.01 | The inspectors reviewed a self revealed finding of very low safety significance and an associated non-cited violation of TS 5.7.1 for entry into HRAs without a required monitoring device. On two separate occasions, two separate workers entered HRAs withou
Region: III | Palisades | 37916 | 03/31/2014 05/07/2014 | 2014002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Insatallation of Steam Generator Nozzle Dams |  | H.3 Change Management | TE?: N | 05000255 Palisades |  | 71111.04Q | A finding of very low safety significance and an associated non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when licensee personnel failed to have an adequate procedure and work order
Region: III | Palisades | 37917 | 03/31/2014 05/07/2014 | 2014002-02 | NRC | NCV | Initiating Events | Green | Failure To Complete Volumetric Examinations for DM Butt Welds in Branch Connections |  | P.2 Evaluation | TE?: N | 05000255 Palisades |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated non-citied violation of 10 CFR 50.55a(g)(6)(ii)(F)(3) when licensee personnel failed to complete required baseline volumetric examinations for nine dissimilar metal (DM)
Region: III | Palisades | 37925 | 03/31/2014 05/07/2014 | 2014002-04 | NRC | NCV | Initiating Events | Green | Introduction of Foreign Material Into the SW System |  | H.5 Work Management | TE?: N | 05000255 Palisades |  | 71111.2 | A finding of very low safety significance and an associated non-citied violation of Technical Specification (TS) 5.4.1, "Procedures," was identified by the inspectors when licensee personnel failed to follow procedure EN MA 118, "Foreign Material Exclusio
Region: III | Palisades | 37926 | 03/31/2014 05/07/2014 | 2014002-05 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures During Reactor Vessel Head Lift |  | H.11 Challenge the Unknown | TE?: N | 05000255 Palisades |  | 71111.2 | A finding of very low safety significance and an associated non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when licensee personnel failed to follow maintenance procedure RFL R 16, "R
Region: III | Palisades | 37930 | 03/31/2014 05/07/2014 | 2014002-06 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA on CRDM 24 Repairs |  | H.5 Work Management | TE?: N | 05000255 Palisades |  | 71124.02 | A finding of very low safety significance was self revealed when workers received unplanned and unintended occupational radiation dose during a maintenance outage conducted in August 2012 due to deficiencies in the licensee's Radiological Work Planning an
Region: III | Palisades | 37895 | 12/31/2013 02/12/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Complete a Transient Combustible Evaluation |  | H.8 Procedure Adherence | TE?: N | 05000255 Palisades |  | 71111.05Q | An NRC identified finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1, "Procedures," was identified by the inspectors when licensee personnel failed to complete a transient combustibl
Region: III | Palisades | 37898 | 12/31/2013 02/12/2014 | 2013005-02 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Control of Entry into High Radiation Areas |  | H.8 Procedure Adherence | TE?: N | 05000255 Palisades |  | 71124.01 | . The inspectors identified a finding of very low safety significance and two associated NCVs of TS 5.7.1 and one associated NCV of TS 5.7.2 when on three separate occasions, three separate workers unknowingly entered areas with greater than expected dose
Region: III | Palisades | 37901 | 12/31/2013 02/12/2014 | 2013005-05 | NRC | NCV | Mitigating Systems | Green | The Aging Effects of the Biological Shield Wall Wetted Environment Were Not Being Managed |  | P.1 Identification | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when licensee personnel failed to evaluate the aging effects of th
Region: III | Palisades | 37894 | 09/30/2013 11/13/2013 | 2013004-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Monitor in Alpha 3 Area |  | P.3 Resolution | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1. Specifically, the licensee failed to perform air sampling as required by station procedure EN RP-122 "Alpha Monitoring." The i
Region: III | Palisades | 37887 | 06/30/2013 08/06/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Welding at the F East Nozzle Reinforcement Plate |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-citied violation of 10 CFR 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure to perform adequate pre weld cleaning and control
Region: III | Palisades | 37893 | 06/30/2013 08/06/2013 | 2013003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Process for Service Water Leaks |  | P.2(b) Implementing Operating Experience | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance with an associated non-citied violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to adhere to the requirements of the site's corrective acti
Region: III | Palisades | 37874 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Acceptable Component Cooling Water Heat Exchanger Final Test Frequency |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control", for failure to establish testing to demonstrate the safety-related Component Coolin
Region: III | Palisades | 37875 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Component Cooling Water Heat Exchanger |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 71111.18 | The inspectors identified a finding of very low safety significance (Green) with an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to properly plan and document work on the s
Region: III | Palisades | 37876 | 03/31/2013 05/14/2013 | 2013002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Damage to 'A' Auxiliary Feedwater (AFW) Pump Packing During Surveillance Run |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.22 | A self-revealed finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion V was identified for the failure to conduct the 'A' Auxiliary Feedwater (AFW) pump technical specification surveillance test in accor
Region: III | Palisades | 37879 | 03/31/2013 05/14/2013 | 2013002-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Derived Air Concentration (DAC)-Hour Tracking |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.4.1. Specifically, the licensee failed to perform Derived Air Concentration (DAC)-Hour tracking for airborne transuranic
Region: III | Palisades | 37880 | 03/31/2013 05/14/2013 | 2013002-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Take Corrective Action to Prevent Recurrence of Control Rod Drive Mechanism Pressure Boundary Leakage |  |  | TE?: N | 05000255 Palisades |  | 71152 | A self-revealing finding of very low safety significance (Green) with associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, and Technical Specification (TS) 3.4.13, Primary Coolant System (PCS) Operational Leakage, was identified fo
Region: III | Palisades | 37886 | 03/31/2013 05/14/2013 | 2013002-06 | NRC | NCV | Initiating Events | Green | Failure to Adequately Address the Generic Implications of the Cracking Identified in Control Rod Drive Mechanism- 24 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding of very low safety significance (Green) with an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to accomplish quality activities in accordance with the prescribed pr
Region: III | Palisades | 37870 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Immediate Operability Determination |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50 Appendix B, Criterion V, for the failure to perform an immediate operability determination in accordance with EN OP 104, Operability Determination
Region: III | Palisades | 37871 | 12/31/2012 02/11/2013 | 2012005-02 | NRC | FIN | Initiating Events | Green | Failure to Appropriately Implement Procedure, "Working Hour Limits for Non-Covered Workers." |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance was identified by the inspectors for the programmatic failure to appropriately implement procedure, EN FAP OM 006, "Working Hour Limits for Non Covered Workers." Two non covered supervisors and six individual cont
Region: III | Palisades | 37856 | 09/30/2012 11/13/2012 | 2012004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Work Management Processes |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71111.13 | A self-revealed finding of very low safety significance and two associated NCVs were identified for the failure to conduct maintenance activities in accordance with work management procedures. Two NCVs are being documented in accordance with NRC Enforceme
Region: III | Palisades | 37862 | 09/30/2012 11/13/2012 | 2012004-02 | Self - Revealed | NCV | Initiating Events | Green | Water Leakage into Control Room During Maintenance |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 71111.15 | A finding of very low safety significance with an associated NCV of TS 5.4.1 was self-revealed for the failure to implement work management procedures when operators noticed water leakage into the control room from the ceiling during maintenance activitie
Region: III | Palisades | 37863 | 09/30/2012 11/13/2012 | 2012004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Foreign Material in Safety Injection and Refueling Water Tank (SIRWT) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71111.15 | A finding of very-low safety significance with an associated NCV of TS 5.4.1 was self revealed for failure to implement a maintenance procedure when it was discovered that foreign material had entered the SIRWT during a forced outage to repair the tank. A
Region: III | Palisades | 37855 | 09/28/2012 11/09/2012 | 2012011-01 | NRC | NCV | Initiating Events | Green | Failure to Complete Previous Occurrence Evaluation for Root Cause Evaluations |  |  | TE?: N | 05000255 Palisades |  | 95002 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," was identified by the inspectors for the failure to complete the Previous Occurrence Evaluation as re
Region: III | Palisades | 37832 | 06/30/2012 08/08/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Margins for Evaluation of Leaking SIRWT Nozzles |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control" for the licensee's failure to adequately evaluate leaking Safety Injection and Refueling Water Tank (SIRWT)
Region: III | Palisades | 37833 | 06/30/2012 08/08/2012 | 2012003-02 | NRC | NCV | Initiating Events | Green | Operation of Primary Coolant Pumps Outside Design Basis |  |  | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50 Appendix B, Criterion III, Design Control, for the failure to operate the Primary Coolant Pumps (PCPs) in accordance with their design operating criteria.
Region: III | Palisades | 37839 | 06/30/2012 08/08/2012 | 2012003-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Work Management Process for Reactor Head Work |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71111.2 | The inspectors identified a finding of very low safety significance with an associated NCV of Technical Specification (TS) 5.4.1, Procedures, for the failure to properly follow the work management process for work done to loosen stuck reactor head studs.
Region: III | Palisades | 37824 | 03/31/2012 05/02/2012 | 2012002-01 | NRC | NCVIV | Initiating Events | Green | Potential Exam Compromise During Requalification Exams |  |  | TE?: Y SL-IV-NCVIV | 05000255 Palisades |  | 71111.11B | A finding of very low safety significance and associated NCV of 10 CFR 55.49, "Integrity of Examination and Tests" was identified by the inspectors for failure to ensure there were no activities which compromised exam integrity. Specifically, the licensee
Region: III | Palisades | 37829 | 03/31/2012 05/02/2012 | 2012002-02 | NRC | NCV | Initiating Events | Green | Potential Exam Compromise During Requalification Exams |  |  | TE?: N | 05000255 Palisades |  | 71111.11B | A finding of very low safety significance and associated NCV of 10 CFR 55.49, "Integrity of Examination and Tests" was identified by the inspectors for failure to ensure there were no activities which compromised exam integrity. Specifically, the licensee
Region: III | Palisades | 37830 | 03/31/2012 05/02/2012 | 2012002-03 | Self - Revealed | NCV | Initiating Events | Green | Intermittent Fuse Contact Causes Feedwater Transient and Plant Trip |  | P.2(b) Implementing Operating Experience | TE?: N | 05000255 Palisades |  | 71111.12 | A self revealed finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1, Procedures, was identified for the failure to adequately implement the fuse control procedure during the reinstallation of a safety related f
Region: III | Palisades | 37831 | 03/31/2012 05/02/2012 | 2012002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Ensure Reactor Head Vetns Closed During PCS Fill |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71111.2 | A finding of very low safety significance with an associated NCV of TS 5.4.1 was self revealed on January 7, 2012, for the failure to adequately implement a procedure when indications of Primary Coolant System (PCS) leakage exceeding 10 gallons per minute
Region: III | Palisades | 37818 | 12/31/2011 02/02/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Establish Maintenance Procedures for Safety Related Breakers in Panel D11-2 |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4 was identified by the inspectors for failure to properly establish written procedures for maintenance that can affect the performance of safety related equipm
Region: III | Palisades | 37822 | 12/31/2011 02/02/2012 | 2011005-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Control Packing Configuration of Pressurizer Spray Control Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance was self revealed on September 16, 2011, when the packing for CV 1057, one of two pressurizer spray control valves, failed resulting in unidentified Primary Coolant System (PCS) leakage in excess of TS limits. As
Region: III | Palisades | 37800 | 10/28/2011 11/29/2011 | 2011014-03 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Human Performance Tools and to Perform an Infrequently Performed Test or Evolution Brief. |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 93812 | A finding of very low significance was identified by the inspectors for the licensee's failure to implement Procedure EN HU 102, "Human Performance Tools," which established standards and expectations for the use of specific human performance tools with t
Region: III | Palisades | 37803 | 10/28/2011 11/29/2011 | 2011014-04 | NRC | FIN | Mitigating Systems | Green | Failure to Comply with Work Hour Rules for Non-Covered Workers. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000255 Palisades |  | 93812 | A finding of very low significance was identified by the inspectors for the licensee's failure to implement Procedure EN FAP OM 006, "Working Hour Limits for Non Covered Workers," which established standard fleet guidance for working hour limits for Enter
Region: III | Palisades | 37804 | 10/28/2011 11/29/2011 | 2011014-05 | NRC | NCV | Initiating Events | Green | Failure to Implement Emergency Operating Procedure Immediate Actions. | EA Case: 2011243 | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 93812 | A finding of very low safety significance and associated non cited violation of Technical Specification 5.4.1 was identified by the inspectors for the failure to implement procedures for combating emergencies and other significant events as required by Re
Region: III | Palisades | 37809 | 10/28/2011 11/29/2011 | 2011014-06 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Procedure for the Loss of a DC Bus and the Simultaneous Loss of Two Preferred AC Power Sources. | EA Case: 2011243 |  | TE?: N | 05000255 Palisades |  | 93812 | A finding of very low safety significance and associated NCV of TS 5.4.1 was identified by the inspectors for the failure to establish a procedure for combating emergencies and other significant events as required by RG 1.33, Section 6. Specifically, Sect
Region: III | Palisades | 37810 | 10/28/2011 11/29/2011 | 2011014-07 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Evaluation. | EA Case: 2011243 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 93812 | A finding of very low safety significance and associated non cited violation of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failu
Region: III | Palisades | 37816 | 10/14/2011 11/29/2011 | 2011014-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design and Procurement Control of the 125-Volt DC System. | EA Case: 2011243 |  | TE?: N | 05000255 Palisades |  | 93812 | A self revealed finding of very low safety significance (Green) and associated NCV of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," and Criterion IV, "Procurement Document Control," was identified for the licensee's failure to establi
Region: III | Palisades | 37791 | 09/30/2011 11/08/2011 | 2011004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Dose to Worker in Locked High Radiation Area |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71124.01 | A finding of very low safety significance and an NCV was self revealed following the licensee's failure to control dose to workers as specified in the radiation work permit (RWP) and as required by Technical Specification (TS) 5.7.2. Specifically, inadequ
Region: III | Palisades | 37792 | 09/30/2011 11/08/2011 | 2011004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry to High Radiation Area |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71124.01 | A self revealed finding of very low safety significance and associated NCV of TS 5.7.1, occurred when an individual entered a high radiation area without proper authorization. The individual was not knowledgeable of dose rates in the area. The licensee ha
Region: III | Palisades | 37793 | 09/30/2011 11/08/2011 | 2011004-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Implement the Approved Emergency Classification Scheme |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000255 Palisades |  | 71153 | The inspectors identified a finding of very low safety significance with an associated NCV of 10 CFR 50.47(b)(4) for the failure to properly implement the approved Emergency Action Level (EAL) classification scheme. Specifically, the licensee implemented
Region: III | Palisades | 37794 | 09/30/2011 11/08/2011 | 2011004-04 | NRC | FIN | Mitigating Systems | Green | Failure to Maintain SAMGs |  |  | TE?: N | 05000255 Palisades |  | 71153 | The inspectors identified a finding of very low safety significance for the licensee's failure to review and update the Severe Accident Management Guidelines (SAMGs) as required by the site's procedure review process for SAMG's. Specifically, the SAMG wri
Region: III | Palisades | 37776 | 08/25/2011 09/12/2011 | 2011009-01 | NRC | FIN | Initiating Events | Green | Failure to Adequately Evaluate the Enclosure Installed Over the 1F/1G Buses. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding of very low safety significance involving the licensee's failure to adequately evaluate the enclosure installed over the 1F/1G Buses to be in compliance with all applicable requirements. Specifically, the licensee did n
Region: III | Palisades | 37777 | 08/25/2011 09/12/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | GL 2008-01 Design Reviews Did Not Adequately Assess the Potential to Accumulate Voids Within Piping Systems. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately review the design of emergency core cooling and containmen
Region: III | Palisades | 37784 | 08/25/2011 09/12/2011 | 2011009-03 | NRC | NCV | Initiating Events | Green | Procedures Were Not Appropriate to Address Gas Accumulation Issues. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000255 Palisades |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish appropriate procedures for managing g
Region: III | Palisades | 37785 | 08/25/2011 09/12/2011 | 2011009-04 | NRC | NCV | Mitigating Systems | Green | Void Size Acceptance Criteria is Non-Conservative. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to develop conservative void size acceptance criteria. Specifically, the
Region: III | Palisades | 37755 | 06/30/2011 08/03/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Failure to Evaluate Corrosion During Reactor Vessel Visual Examination |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | NONE | A finding of very low safety significance and associated NCV of 10 CFR Part 50.55a(g)(6)(ii)(D)(1), "Reactor Vessel Head Inspections," was identified by the inspectors for the licensee's failure to evaluate corrosion present on the reactor vessel head dur
Region: III | Palisades | 37761 | 06/30/2011 08/03/2011 | 2011003-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Establish a Back-up Radiation Monitor |  |  | TE?: N | 05000255 Palisades |  | 71111.13 | The inspectors identified a finding of very low safety significance and associated NCV of TS 5.5.1 for failure to establish, implement and maintain the Offsite Dose Calculation Manual (ODCM). Specifically, the licensee failed to establish a backup radiati
Region: III | Palisades | 37759 | 06/30/2011 08/03/2011 | 2011003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Inspect ASME Class 2 Piping |  |  | TE?: N | 05000255 Palisades |  | 71111.15 | A self-revealed finding of very-low safety significance with an associated NCV of TS 5.4.1, Procedures, occurred for the licensee's failure to properly implement the procedure for inspection of American Society of Mechanical Engineers (ASME) Class 2 pipin
Region: III | Palisades | 37769 | 06/30/2011 08/03/2011 | 2011003-06 | NRC | NCV | Public Radiation Safety | Green | Failure to Include The Steam Generator Mausoleum in the Groundwater Protection Risk Ranking Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000255 Palisades |  | 71124.07 | The inspectors identified a finding of very low-safety-significance and an associated NCV of TS 5.4.1, Procedures, for the failure to implement procedures and include the steam generator mausoleum in the groundwater risk-ranking program for structures, sy
Region: III | Palisades | 37773 | 06/30/2011 08/03/2011 | 2011003-08 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately Manage Changes to the Offsite Dose Calculation Manual |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71124.07 | The inspectors identified a finding of very low-safety significance and associated NCV of TS 5.5.1.c, for a change that was made to the ODCM in 2004 to eliminate drinking water well sampling with an inaccurate evaluation for the change. This evaluation fa
Region: III | Palisades | 37746 | 03/31/2011 05/04/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Potential Age-Related Degradation in EDG Governors |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion III, Design Control, for the failure to recognize and account for potential age-related degradation of capacitors in the emergency d
Region: III | Palisades | 37747 | 03/31/2011 05/04/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | Violation of Fatigue Rule Requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 26.205(d) for the failure to control the work hours of covered workers. Specifically, contract workers violated the minimum days off requirements during the O
Region: III | Palisades | 37748 | 03/31/2011 05/04/2011 | 2011002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Maintain Switchgear Weather Proof |  |  | TE?: N | 05000255 Palisades |  | 71153 | A finding of very low safety significance without an associated NCV was self-revealed when a loss of the rear bus and loss of one cooling tower occurred. The licensee failed to maintain the enclosure for F and G busses weatherproof as stipulated in the de
Region: III | Palisades | 37749 | 03/31/2011 05/04/2011 | 2011002-04 | NRC | NCV | Public Radiation Safety | Green | Inadequate Procedural Controls for Liquid Radioactive Waste |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4 for failure to establish and implement procedures recommended by Regulatory guide 1.33. Specifically, the licensee failed to establi
Region: III | Palisades | 37750 | 03/22/2011 05/06/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assure Adequate Resolution for Remote Visual Examinations |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure of a licensee non-destructive examination examiner to accom
Region: III | Palisades | 37751 | 03/22/2011 05/06/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Test Results for Diesel Fuel Oil Tanks Not Evaluated |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the failure to evaluate test results for tank wall thickness under the scope of the Diesel Fuel
Region: III | Palisades | 37752 | 03/22/2011 05/06/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Tank T-10A Not Age Managed for Effect of Identified Water |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to promptly correct a condition adverse to quality associat
Region: III | Palisades | 37753 | 03/22/2011 05/06/2011 | 2011008-04 | NRC | FIN | Mitigating Systems | Green | Flow Accelerated Corrosion Program Acceptance Limits Not in Accordance with Design Standard |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety significance was identified by the inspectors for the failure to assure an engineering evaluation was initiated if pipe wall thickness measurements fall below 87.5 percent of nominal pipe wall thickness. Specifically, computer
Region: III | Palisades | 37754 | 03/22/2011 05/06/2011 | 2011008-05 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Adequate Oil Sampling and Analysis Aging Management Program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety significance was identified by the inspectors for the failure to: (1) develop and implement an oil sampling and analysis aging management program with specific acceptance criteria and trending requirements; and (2) age manage
Region: III | Palisades | 37723 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Pipe Welds Not Incorporated into the ISI Program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.08P | A finding of very low safety significance and associated NCV of 10 CFR 50.55a(g)4 was identified by the inspectors for the licensee's failure to establish a weld reference system for 11 welds in the cross-tie line between the chemical and volume control s
Region: III | Palisades | 37726 | 12/31/2010 02/08/2011 | 2010005-02 | NRC | NCV | Initiating Events | Green | Inadequate Examination of Head Penetration Nozzles Nos. 1 and 3 |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 71111.08P | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified by the inspectors for the licensee's failure to follow Procedure CEP-NDE-0955, "Visual Exami
Region: III | Palisades | 37728 | 12/31/2010 02/08/2011 | 2010005-04 | Self - Revealed | NCV | Initiating Events | Green | Low Pressure Alarms During Reduced Inventory Operations |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 71111.13 | A finding of very low safety significance and associated NCV of 10 CFR 50.65a(4) was self-revealed for the failure to properly assess and manage risk when service water low pressure alarms were received during orange risk reduced inventory operations. The
Region: III | Palisades | 37736 | 12/31/2010 02/08/2011 | 2010005-05 | NRC | NCV | Initiating Events | Green | Failure to Perform Daily Crane Checks |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a NCV of TS 5.4 for the licensee's failure to implement procedures specified by Regulatory Guide 1.33. Specifically, the licensee failed to perform a check of the main hook in preparations for the head lift. The procedure used to
Region: III | Palisades | 37737 | 12/31/2010 02/08/2011 | 2010005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000255 Palisades |  | 71152 | Inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that Quality Control (QC) verification inspections were consistently included and correctly specified in quality-affecting procedures and work inst
Region: III | Palisades | 37720 | 10/22/2010 12/03/2010 | 2010010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Ultrasonic Examination on Primary System Makeup Storage Tank in Accordance with Procedures. |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 71003 | A finding of very low safety-significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to accomplish activities affecting
Region: III | Palisades | 37706 | 09/30/2010 11/08/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Risk Assessment for Maintenance Activities |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50.65 a(4) for failing to properly assess and manage the risk associated with the removal of the auxiliary feedwater (AFW) pump room floor plug during
Region: III | Palisades | 37707 | 09/30/2010 11/08/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Complete Actions Required by LCO 3.0.3 and 3.3.1 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of TS 3.3.1 and 3.0.3 for failure to comply with required TS actions. Specifically, on August 23, the licensee lost the automatic Loss of Load Trip but neither
Region: III | Palisades | 37709 | 09/30/2010 11/08/2010 | 2010004-04 | NRC | NCV | Initiating Events | Green | Failure to Ensure Code Requirements Met When Performing VT-2 Exams |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.4.1, Procedures, for the failure to ensure that American Society of Mechanical Engineers (ASME) Code and site procedural requi
Region: III | Palisades | 37710 | 09/30/2010 11/08/2010 | 2010004-05 | NRC | NCV | Mitigating Systems | Green | Ground on Preferred AC Bus Due to Improperly Installed electrical Bushing |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR 50 Appendix B, Criterion V for failure to accomplish activities affecting quality as prescribed by the documented instructions, procedures, or drawing
Region: III | Palisades | 37705 | 09/17/2010 10/20/2010 | 2010009-01 | NRC | NCV | Initiating Events | Green | Corrective Action to Prevent Recurrence Failed to Address Root Causes | EA Case: 2009269 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 95001 | The inspectors identified a finding of very low safety significance with an associated Non-Cited Violation of Palisades Technical Specification 5.4.1, "Procedures." Specifically, the licensee's procedure for the performance of root cause analysis required
Region: III | Palisades | 37701 | 03/31/2010 05/04/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Barrier |  |  | TE?: N | 05000255 Palisades |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of License Section 2.C(3), Fire Protection Program for failing to maintain in effect all provisions of the Fire Protection Program. Specifically, the fire pr
Region: III | Palisades | 37702 | 03/31/2010 05/04/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Improper Construction of Scaffolding |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 71111.05Q | A finding of very low safety significance (Green) and associated NCV of Palisades Technical Specification (TS) 5.4.1, Procedures, was identified by the inspectors for failing to adequately implement a procedure to construct a scaffold near the 1 2 emergen
Region: III | Palisades | 37703 | 03/31/2010 05/04/2010 | 2010002-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately manage Changes to the ODCM |  |  | TE?: N | 05000255 Palisades |  | 71153 | The inspectors identified a finding of very low-safety-significance and an associated NCV for the failure to implement TS requirement 5.5.1, Offsite Dose Calculation Manual (ODCM). Specifically, the inspectors determined that the evaluation written to sup
Region: III | Palisades | 37700 | 03/05/2010 04/13/2010 | 2010502-01 | NRC | NCV | Emergency Preparedness | Green | Inadequate Evaluation of Interface with State and Local Governments |  | P.3(a) Self-Assessment | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.54(t), "Conditions of licenses," for the failure to complete an independent review of all program elements of the emergency preparedness program. The indep
Region: III | Palisades | 37690 | 12/16/2009 01/20/2010 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Agastat Time Delay Relays Design, Testing and Configuration Control Issues |  | P.2(b) Implementing Operating Experience | TE?: N | 05000255 Palisades |  | 71111.17T | A finding of very low safety-significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III "Design Control," was identified by the inspectors for the licensee's failure to translate the design bases into design drawi
Region: III | Palisades | 37691 | 12/16/2009 01/20/2010 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate the Design Basis for the CV-11 Control Room HVAC Chiller Into Specifications and Drawings |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71111.17T | A finding of very low safety-significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to translate and incorporate design basis criteria that ensure
Region: III | Palisades | 37677 | 09/30/2009 11/04/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Gas Void in High Pressure Safety Injection Suction Line |  | P.2(b) Implementing Operating Experience | TE?: N | 05000255 Palisades |  | 71111.19 | The inspectors identified an NCV of TS 5.4.1 for failure to implement and maintain procedural guidance for filling the High Pressure Safety Injection (HPSI) lines. Specifically, the licensee used procedure ESSO-01 to fill the Emergency Core Cooling System
Region: III | Palisades | 37678 | 09/30/2009 11/04/2009 | 2009004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entering a High Radiation Area without an adequate awareneses of radiological conditions |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 7112101 | A self-revealed finding of very low safety-significance and an associated NCV of TS 5.7 were identified for workers entering a high radiation area (HRA) without an adequate awareness of radiological conditions and while working under a Radiation Work Perm
Region: III | Palisades | 37679 | 09/30/2009 11/04/2009 | 2009004-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to perform work-in-progress reviews |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 7112102 | The inspectors identified a finding of very low safety significance and associated NCV of TS 5.4.1 for failure to implement procedures required to conduct timely reviews of job progress and implement actions necessary to reduce workers' exposure. Specific
Region: III | Palisades | 37680 | 09/30/2009 11/04/2009 | 2009004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Reduction in containment spray header level during maintenance |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance (Green) and associated NCV of TS 5.4.1, Procedures, was self-revealed when operators incorrectly implemented a procedure that connected a temporary pump to a containment spray header while attempting to fill the h
Region: III | Palisades | 37684 | 09/30/2009 11/04/2009 | 2009004-05 | NRC | FIN | Initiating Events | Green | Inadequate analysis of reheater drain tank T-4B Drain Line Vibration |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71152 | A finding of very low safety significance without an associated violation was identified by the inspectors for the licensee's operation of the moisture separator reheater (MSR) system outside of its design such that significant vibration occurred in the d
Region: III | Palisades | 37685 | 09/30/2009 11/04/2009 | 2009004-06 | NRC | NCV | Initiating Events | Green | Failures of the shutdown cooling flow bypass valve CV-3006 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Technical Specifications (TS) 5.4.1, Procedures, for the failure to implement procedures to properly align the positioner feedback arm for the shutdown co
Region: III | Palisades | 37667 | 06/30/2009 08/06/2009 | 2009003-01 | NRC | FIN | Initiating Events | Green | Failure to conduct an adequate risk assessment for an orange risk condition |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) without an associated NCV for failure to conduct an adequate risk assessment and recognize a procedurally required orange risk condition for the vacuum fill of the primary coolant
Region: III | Palisades | 37668 | 06/30/2009 08/06/2009 | 2009003-02 | NRC | NCV | Initiating Events | Green | Failure to Manage Risk in Reduced Inventory |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000255 Palisades |  | 71111.2 | The inspectors identified a Green NCV of 10 CFR 50.65 (a)(4) for the licensee's failure to manage the increase in risk by minimizing the plant's exposure to elevated risk during the 1R20 refueling outage. Specifically, during the first period of reduced i
Region: III | Palisades | 37658 | 03/31/2009 05/14/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperability of HPSI Valve Due to Foreign Material |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 71152 | On February 7, 2009, while attempting to fill the T 82C safety injection tank during routine operations, control room operators attempted to throttle open MO 3064, one of two HPSI isolation valves to primary coolant loop 2A. The valve did not reposition.
Region: III | Palisades | 37659 | 03/31/2009 05/14/2009 | 2009002-02 | NRC | NCV | Initiating Events | Green | Failure to Implement Technical Specification |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | NONE | On February 20, 2009 the inspectors identified a Green NCV of TS 5.4, "Procedures". Specifically, the licensee failed to revise procedures needed to implement Technical Specification (TS) amendment 236; although, the licensee notified the NRC via letter o
Region: III | Palisades | 37660 | 03/31/2009 05/14/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Degradation of Fire Doors |  |  | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of License Condition 2.C.(3), "Fire Protection," during performance of a surveillance procedure inspection in accordance with IP 71111.22. Specifically, the
Region: III | Palisades | 37653 | 12/31/2008 02/09/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of Control Room Chillers |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion XI, "Test Control", for the inadequate testing of the heat removal capacity of the CR HVAC system. Specifically, the lice
Region: III | Palisades | 37654 | 12/31/2008 02/09/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency Diesel Generator Inoperable in Excess of Technical Specification Requirements |  |  | TE?: N | 05000255 Palisades |  | 71153 | A self-revealed finding of very low safety significance (Green) and an associated NCV of technical specification requirement 3.8.1.b was discovered when metal fragments were found in the valve assembly area of the 1-2 Emergency Diesel Generator (EDG) cyli
Region: III | Palisades | 37655 | 12/04/2008 01/15/2009 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Emergency Diesel Generator 1-2 Loading During Design Basis Events. |  |  | TE?: N | 05000255 Palisades |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to assure the loading on emergency diesel generator 1 2 was maintained wi
Region: III | Palisades | 37656 | 12/04/2008 01/15/2009 | 2008009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Correct Technical Specification Limits. |  |  | TE?: N | 05000255 Palisades |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to correctly translate the applicable design basis into the Technical Spe
Region: III | Palisades | 37647 | 11/19/2008 12/19/2008 | 2008011-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Implement Effective Radiological Controls For Working With Equipment In Contact With Failed Fuel |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 7112101 | An NRC-identified finding of very low safety significance and associated NCV of 10 CFR 20.1501 was identified for failure to perform adequate radiological evaluations necessary to properly assess the radiological hazards and prescribe appropriate radiolog
Region: III | Palisades | 37648 | 11/19/2008 12/19/2008 | 2008011-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Post and Control Access to High Radiation Area |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 7112101 | A self-revealed finding of very low safety significance and associated NCV of Technical Specification 5.7.1 was identified for the failure to post and control an area with dose rates greater than 100 millirem/hour as a high radiation area. Specifically, t
Region: III | Palisades | 37635 | 09/30/2008 11/13/2008 | 2008004-02 | NRC | NCV | Public Radiation Safety | Green | Failure to incorporate results from the annual land use census |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 7112203 | The inspector identified a finding of very low safety significance (Green) and an NCV of Tecnical Specification 5.5.1 and ODCM Appendix A, Section J.3.c associated with the failure to incorporate the annual land use census in the Radioactive Environmental
Region: III | Palisades | 37637 | 09/30/2008 11/13/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | Degradation of the 3-hour Fire Barrier |  |  | TE?: N | 05000255 Palisades |  | 71111.04Q | The inspectors identified a Green NCV of License condition 2.C.(3), Fire Protection, for failure to maintain a three hour barrier between two safety related rooms. Specifically, the inspectors noted a through-wall crack in the htree hour fire wall between
Region: III | Palisades | 37638 | 09/30/2008 11/13/2008 | 2008004-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Auxilliary Feed Water Low Suction Pressure Trip Setpoints |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part50, Appendix B, Criterion III, "Design Control, " for the tank damage from tornado born missiles. Specifically, the licensee used low CST level trips t
Region: III | Palisades | 37639 | 09/25/2008 11/04/2008 | 2008010-01 | NRC | NCV | Barrier Integrity | Green | Failiure to Develop and Maintain Contaiment Personnel and Emergency Escape Hatch Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance and associated NCV of TS 5.4.1.a, for the failure to ensure the personnel and emergency escape hatch instructions were adequately maintained and properly implemented for use during a time
Region: III | Palisades | 37640 | 09/25/2008 11/04/2008 | 2008010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish and Implement Procedures Controlling Access to Containment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1 for failure to implement procedures required to control access into containment. The corrective actions planned by the licensee in
Region: III | Palisades | 37641 | 09/25/2008 11/04/2008 | 2008010-03 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Properly Maintain the Emergency Escape Hatch as an Escape Hatch |  |  | TE?: N | 05000255 Palisades |  | 93812 | A self-revealed finding of very low significance was identified for the failure to ensure the emergency escape hatch would operate as designed when needed. The licensee failed to maintain the hatch in a condition that it could be operated as an emergency
Region: III | Palisades | 37642 | 09/25/2008 11/04/2008 | 2008010-04 | NRC | FIN | Mitigating Systems | Green | Organizational Evaluation of Shur\\tdown Risk for the Forced Outage. |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance for failure to implement procedure EN-OU-101, "Forced Outage Planning and Preparation." This procedure stated, in part, that forced outages should undergo a risk assessment in accordance
Region: III | Palisades | 37633 | 08/01/2008 08/24/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | This is a security related item - see inspection report for details. |  | H.2(d) Facilities & Equipment | TE?: N | 05000255 Palisades |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02
Region: III | Palisades | 37623 | 06/30/2008 08/14/2008 | 2008003-01 | NRC | NCV | Initiating Events | Green | Failure to Maintain and Implement Procedure Guidance for Offiset Power Source Operability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71111.01 | The inspectors identified an NCV of Technical Specification (TS) 5.4.1 for the failure to maintain and implement procedure guidance for offsite power source operability. Specifically, the procedure guidance for the transmission system operator (TSO) to no
Region: III | Palisades | 37624 | 06/30/2008 08/14/2008 | 2008003-02 | Self - Revealed | NCV | Mitigating Systems | Green | High Pressure Safety Injection Train Inoperable |  |  | TE?: N | 05000255 Palisades |  | 71111.15 | A self-revealed finding and associated NCV of 10 CFR 50 Appendix B Criteria III was identified on March 26 when the licensee attempted to remove the breaker for the 'A' High Pressure Safety Injection (HPSI) pump from its cubicle. An inspection of the Mech
Region: III | Palisades | 37626 | 06/30/2008 08/14/2008 | 2008003-04 | Self - Revealed | FIN | Mitigating Systems | Green | Improper Maintenance of Safeguards Transformer |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71153 | A self-revealed finding occurred on April 1 when a non-safety related, offsite transformer was declared inoperable due to evidence of internal arcing based on gas testing of the load tap change oil reservoir of the transformer. The failure occurred due to
Region: III | Palisades | 37630 | 06/30/2008 08/14/2008 | 2008003-06 | NRC | NCV | Mitigating Systems | Green | 1-1 Emergency Diesel Generator Fuel Header Leak |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000255 Palisades |  | 71153 | The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criteria V, "Instructions, Procedures and Drawing" for failure of the licensee to have documented instructions for maintenance of the 1-1 emergency diesel generator (EDG). Specifically, the li
Region: III | Palisades | 37379 | 03/31/2008 05/15/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Fire Door Was Closed |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades 05000255 Palisades |  | 71111.05Q | The inspectors identified a Green Non-Cited Violation (NCV) of License Condition 2.C.(3), Fire Protection, for failure to ensure a fire door between an emergency diesel generator room and a vital switchgear room was closed. This partially open door degrad
Region: III | Palisades | 37380 | 03/31/2008 05/15/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Feedwater System Under 10 CFR 50.65a(1) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71111.12 | The inspectors identified a Green NCV of Title 10, Code of Federal Regulations (CFR) 50.65 for the failure to include a 'B' feed regulating valve deficiency to close during startup operations as a functional failure in the maintenance rule program. The in
Region: III | Palisades | 37381 | 03/31/2008 05/15/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate General Operating Procedure for Mode Transition |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 71111.2 | The inspectors identified a NCV of Technical Specification (TS) 5.4.1 for the failure to have adequate procedure guidance for the general operating procedures for mode transition to power operations. Specifically the general plant operating procedure for
Region: III | Palisades | 37382 | 03/31/2008 05/15/2008 | 2008002-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Procedures for the Maintenance of PAPR Batteries |  |  | TE?: N | 05000255 Palisades |  | 7112101 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 20.1703(c) for the failure to implement written procedures to ensure batteries for powered air purifying respirators (PAPRs) are adequately charged before use
Region: III | Palisades | 37388 | 03/31/2008 05/15/2008 | 2008002-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Use, to the Extent Practical, Process or Other Engineering Controls to Control the Concentraion of Radioactive Material in Air |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 7112101 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR 20.1701 was identified for the failure to use, to the extent practical, process or other engineering controls to control the concentration of radioactive material in air.
Region: III | Palisades | 37395 | 03/31/2008 05/15/2008 | 2008002-07 | NRC | NCV | Public Radiation Safety | Green | Failure to Control the Release of Radioactive Material |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000255 Palisades |  | NONE | A self-revealed finding of very low safety significance and associated NCV of 10 CFR 20.1501 was identified for failure to perform an adequate radiological survey to assure compliance with 10 CFR 20.1802, which requires that the licensee control and maint
Region: III | Palisades | 37396 | 03/31/2008 05/15/2008 | 2008002-08 | NRC | FIN | Initiating Events | Green | Main Feed Pump trip due to Inadequate Configuration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 71153 | Introduction: A Green self-revealed finding occurred on January 13 when the 'B' Main Feed Pump failed. The failure occurred due to improper maintenance on the lube oil pump associated with the Main Feed Pump that resulted in a loss of lube oil flow and tr
Region: III | Palisades | 37397 | 03/31/2008 05/15/2008 | 2008002-09 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Comply with TS 3.8.4 B and C |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71153 | A self revealing NCV of TS 3.8.4 B and C was identified for failing to recognize that battery cell parameters were not within TS limits and for failing to take actions in accordance with TS for an inoperable battery. Specifically, cell 43 of the right tra
Region: III | Palisades | 37622 | 03/31/2008 05/15/2008 | 2008002-10 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Comply with TS 3.5.2 B and C |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 71153 | A self revealing NCV of TS 3.5.2 B and C was identified for the inability of an automatic valve in the Emergency Core Cooling System (ECCS), CV-3047, to reposition fully closed on an actuation signal. As a result, one train of ECCS was inoperable for long
Region: III | Palisades | 37365 | 12/31/2007 01/30/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Testing for High Pressure Safety Injection Pumps |  |  | TE?: N | 05000255 Palisades |  | 71111.19 | The inspectors identified a Green Non-Cited Violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawing" for failure by the licensee to follow procedural requirements for testing safety-related pumps after bearing replacement. Sp
Region: III | Palisades | 37366 | 12/31/2007 01/30/2008 | 2007007-02 | NRC | NCV | Initiating Events | Green | Failure to Comply with Operating Requirements Manual Restrictions on Heavy Load Movement |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 71111.2 | NRC identified violations of Technical Specification (TS) 5.4.1 occurred on October 4, and October 13, 2007 when the licensee violated Operational Requirements Manuals limits on movement of heavy loads. On October 4, the licensee moved a heavy load in the
Region: III | Palisades | 37367 | 12/31/2007 01/30/2008 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Containment sump Debris Found during NRC Closeout |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings" failure by the licensee to follow procedural requirements for closing out the containment sump. Specifically, the licensee failed to comply
Region: III | Palisades | 37371 | 12/31/2007 01/30/2008 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | Inoperable Safety Systems Due to Improper Door Positioning |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71153 | NRC identified violations of Technical Specification 5.4.1 occurred on October 1, 2007; October 28, 2007 and November 19, 2007 due to licensee personnel failing to maintain doors in the proper configuration to support operability of TS required systems. T
Region: III | Palisades | 37373 | 12/12/2007 01/24/2008 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish correct Tech Spec Limits |  |  | TE?: N | 05000255 Palisades |  | 7111117B | Green. The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" requirements. Specifically, the licensee failed to incorporate a number of uncertainties when calculating the technical specificati
Region: III | Palisades | 37356 | 09/30/2007 11/06/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Plant Radiation Monitors Not Fully Scoped into the Maintenance Rule |  |  | TE?: N | 05000255 Palisades |  | 71111.12 | The inspectors identified a Green NCV of 10 CFR 50.65(b)(2) because the licensee did not scope all plant radiation monitors used in site emergency operating procedures into the maintenance rule monitoring program. The licensee entered the item into their
Region: III | Palisades | 37357 | 09/30/2007 11/06/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Safety Injection Actuation Test |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 71111.13 | The inspectors identified a Green NCV of 10 CFR Part 50.65(a)(4), because the licensee did not adequately assess and manage online risk while performing a safety injection system actuation test. Specifically, prior to performance of the safety injection t
Region: III | Palisades | 37361 | 09/30/2007 11/06/2007 | 2007006-06 | NRC | NCV | Barrier Integrity | Green | LPSI Check Valve Unseated |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71152 | A self-revealed finding and associated NCV of Technical Specification 5.4.1 was identified for failure by the licensee to follow procedural requirements. On May 13, 2007, the licensee failed to monitor for leakage across a Low Pressure Safety Injection (L
Region: III | Palisades | 37362 | 09/30/2007 11/06/2007 | 2007006-07 | NRC | NCV | Mitigating Systems | Green | AFW Pumps Inoperable Due to High Energy Line Breaks in the Turbine Building |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a Green non-cited violation NCV of 10 CFR 50, Appendix B, Criteria III, "Design Control" for failing to adequately translate the design and licensing basis requirements into equipment specifications for the 8A and 8B Auxiliary Fe
Region: III | Palisades | 37344 | 06/30/2007 08/10/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to preclude Water Hammer in HPSI Injection Piping |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion III for failing to control system parameters in the HPSI system injection lines to preclude water hammer from occurring during either routine or accident conditions. As a result, the
Region: III | Palisades | 37345 | 06/30/2007 08/10/2007 | 2007004-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to effectively survey slings before granting unconditional release from the RCA |  |  | TE?: N | 05000255 Palisades |  | 7112203 | A self-revealed finding of very low safety significance and an associated violation of NRC requirements was identified for the failure to effectively survey slings before granting unconditional release from the Radiologically Controlled Area (RCA). This w
Region: III | Palisades | 37346 | 06/30/2007 08/10/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Service Water Pump 7A Shaft Degraded |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000255 Palisades |  | 71152 | The inspectors identified a Green NCV of 10 CFR 50 Appendix B, Criterion III for failing to establish adequate measures to ensure suitability of the application of the material for the 7A Service Water (SW) pump. Specifically the shaft for the A SW pump w
Region: III | Palisades | 37347 | 06/30/2007 08/10/2007 | 2007004-04 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip Caused by Human Performance Error |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71153 | A self-revealing finding was identified for the licensee's failure to follow work order instructions when performing maintenance on a main feedwater regulating valve position indicator. As a result, an automatic reactor trip occurred on a Reactor Protecti
Region: III | Palisades | 37348 | 06/30/2007 08/10/2007 | 2007004-05 | NRC | NCV | Emergency Preparedness | Green | Failure to Properly Implement Approved EAL Scheme |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000255 Palisades |  | 71114.06 | The inspectors identified a Green NCV of 10 CFR 50.47 for failure to properly implement approved Emergency Action Levels (EAL). As a result of the improper EAL implementation, site personnel responsible for EAL declarations could improperly classify some
Region: III | Palisades | 37355 | 06/30/2007 08/10/2007 | 2007004-06 | NRC | NCV | Mitigating Systems | Green | Defective Part Installed on 1-2 EDG |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 71111.19 | A self-revealing NCV of 10 CFR 50, Appendix B, Criterion VIII, "Identification and Control of Materials, Parts and Components" was identified for failing to have adequate control measures to prevent the use of defective parts. Specifically, a fuel leak de
Region: III | Palisades | 37327 | 03/31/2007 05/08/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | CV-0821 Corrective Actions Not Effective to Prevent Repeat Failure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000255 Palisades |  | 71111.2 | The inspectors identified a finding of very low safety significance and an associated Non-Citied Violation of 10 CFR 50, Appendix B, Criterion XVI for failing to take adequate corrective action to prevent recurrence of a significant condition adverse to q
Region: III | Palisades | 37329 | 03/31/2007 05/08/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | Control Rod Drive Mechanism Testing Practice Violates TS 3.1.4 |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated Non-Citied Violation of Technical Specifications for the failure to take actions for the appropriate Limiting Condition for Operation (LCO) not being met when surveillan
Region: III | Palisades | 37334 | 03/31/2007 05/08/2007 | 2007002-04 | NRC | NCV | Mitigating Systems | Green | Failure To Comply with Technical Specification 3.9.5 |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 3.9.5 for removing a train of safety equipment without complying with the required action and completion time when the Lim
Region: III | Palisades | 37336 | 03/31/2007 05/08/2007 | 2007002-06 | NRC | NCV | Mitigating Systems | Green | Incorrect Auxiliary Feedwater Vortex Limit Calculation |  |  | TE?: N | 05000255 Palisades |  | NONE | The inspectors identified a finding of very low safety significance and an associated Non-Citied Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to use a conservative value for auxiliary pump air entrainment in vo
Region: III | Palisades | 37325 | 02/27/2007 04/10/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Valve Body Inadvertently Discarded Due to Ineffective Quarantine |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 95001 | The inspectors identified an Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately quarantine a component for failure analysis as required by the licensee's procedures. The licen
Region: III | Palisades | 37326 | 02/27/2007 04/10/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition for High Pressure Safety Injection Valve Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000255 Palisades |  | 95001 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to assure that conditions adverse to quality were promptly corrected. Specifically, the inspectors concluded that the licensee failed to develo
Region: III | Palisades | 37287 | 12/31/2006 01/24/2007 | 2006013-01 | NRC | NCV | Barrier Integrity | Green | Inaccurate Surveillance Procedure for Primary Coolant System Leakrate Calculation |  |  | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Citied Violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control" for the failure to have an accurate Technical Specification (TS) surveillance procedu
Region: III | Palisades | 37288 | 12/31/2006 01/24/2007 | 2006013-02 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Adequately Implement Radiological Dose Controls |  | H.3(a) Work Planning | TE?: N | 05000255 Palisades |  | 7112102 | A Green finding was self-revealed for failure to adequately implement radiological dose controls during Refueling Outage 18 (RO18). Specifically, work control and planning issues (worker fatigue, worker proficiency, and material condition) contributed to
Region: III | Palisades | 37303 | 12/31/2006 01/24/2007 | 2006013-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Component on 1-2 Emergency Diesel Generator Causes Surveillance Failure |  |  | TE?: N | 05000255 Palisades |  | NONE | A Green self-revealing Non-Citied Violation of 10 CFR 50, Appendix B, Criterion VIII, "Identification and Control of Materials, Parts and Components" was identified for failing to have adequate control measures needed to prevent the use of defective parts
Region: III | Palisades | 37305 | 12/15/2006 02/13/2007 | 2006009-02 | NRC | NCV | Initiating Events | Green | Reduction in Fast Bus Transfer Capability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to evaluate the potentially adverse effects that a mod
Region: III | Palisades | 37311 | 12/15/2006 02/13/2007 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Voltage Drop Calculations for Motor Control Center Control Circuits |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to include the voltage drop across control power trans
Region: III | Palisades | 37312 | 12/15/2006 02/13/2007 | 2006009-04 | NRC | NCV | Mitigating Systems | Green | Effect of Accident Temperatures on Cable Resistance Not Evaluated |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Ccited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to consider the effects of accident temperatures on c
Region: III | Palisades | 37313 | 12/15/2006 02/13/2007 | 2006009-05 | NRC | NCV | Mitigating Systems | Green | Molded-Case Circuit Breaker Testing Program Deficiencies |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." for the licensee's failure to ensure that the molded-case circuit breaker (MCCB) testing pr
Region: III | Palisades | 37314 | 12/15/2006 02/13/2007 | 2006009-06 | NRC | NCV | Mitigating Systems | Green | Battery Terminals Not Coated with Anti-Corrosion Material |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of Technical Specification Surveillance Requirement 3.8.4.4. Specifically the licensee failed to verify that the 125V DC battery cable-to-terminal plate
Region: III | Palisades | 37320 | 12/15/2006 02/13/2007 | 2006009-07 | NRC | NCV | Mitigating Systems | Green | Diesel Generator Frequency Variation not Considered in Loading Calculations |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to take into account the effect of emergency diesel ge
Region: III | Palisades | 37321 | 12/15/2006 02/13/2007 | 2006009-08 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Automatic Fuel Transfer Equipment not Rated for Expected Max Temp |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to verify that eight components involved with transfer
Region: III | Palisades | 37322 | 12/15/2006 02/13/2007 | 2006009-09 | NRC | NCV | Mitigating Systems | Green | High Pressure Safety Injection Pump Vortex Limit Calculation Inaccuracies |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee incorrectly interpreted a graph used to determine the percent
Region: III | Palisades | 37323 | 12/15/2006 02/13/2007 | 2006009-10 | NRC | NCV | Mitigating Systems | Green | Potential for Safety Injection and Refueling Water Tank Level Switch Setpoints to be Outside TS Limit |  |  | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to to establish a proper setpoint for safety injection
Region: III | Palisades | 37324 | 12/15/2006 02/13/2007 | 2006009-11 | NRC | FIN | Barrier Integrity | Green | Failure to Correctly Apply Pressure Locking Thrust in MOV Performance Test Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000255 Palisades |  | 7111121 | The inspectors identified a finding having very low significance. Specifically, the licensee failed to correctly apply the effect due to pressure locking in the valve actuator capability margin to open for the boric acid gravity feed motor operated valves
Region: III | Palisades | 37289 | 12/01/2006 12/29/2006 | 2006014-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operating Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance associated with a Non-Cited Violation of Technical Specification 5.4.1a for an operator failing to comply with the site quality procedure for Conduct of Operations by manipulating safety
Region: III | Palisades | 37290 | 12/01/2006 12/29/2006 | 2006014-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications |  | H.4(b) Procedural Compliance | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance associated with a Non-Cited Violation of Technical Specification (TS) 3.7.5 for the licensee's failure to comply with the required action time to be in Mode 4 in 30 hours with no Auxiliar
Region: III | Palisades | 37296 | 12/01/2006 12/29/2006 | 2006014-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000255 Palisades |  | 93812 | The inspectors identified a finding of very low safety significance associated with a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide adequate procedures, appr
Region: III | Palisades | 37281 | 09/30/2006 10/27/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | The licensee failed to demonstrate that the performance or condition of High Pressure Injection System had been effectively controlled per 10 CFR 50.65 |  |  | TE?: N | 05000255 Palisades |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50.65 "Requirements for monitoring effectiveness of maintenance at nuclear power plants." Specifically, contrary to 50.65(a)(2), th
Region: III | Palisades | 37282 | 09/30/2006 10/27/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | Control Valve CV-3070 Failed to Stroke |  |  | TE?: N | 05000255 Palisades |  | 71153 | A Green Non-Cited Violation was self-revealed on March 29, 2006, when control valve CV-3070, left train HPSI sub-cooling valve for HPSI pump P-66B, failed to open during preventive maintenance. Subsequent investigation by the licensee identified that a de
Region: III | Palisades | 37269 | 06/30/2006 07/28/2006 | 2006004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Comply with 10 CFR 50 Appendix B, Criterion XVI for Recurring Fuel Assembly Cladding Failure |  |  | TE?: N | 05000255 Palisades |  | 71111.2 | A self-revealed NCV of Criterion XVI was identified when damage to a fuel pin was found. The finding of very low safety significance (Green) occurred because the licensee failed to assure adequate corrective actions were implemented to prevent recurrence
Region: III | Palisades | 37275 | 06/30/2006 07/28/2006 | 2006004-03 | NRC | NCV | Initiating Events | Green | Power Operations with One Rod Unlatched Due to an Inadequate Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71111.2 | A self-revealed Non-Cited Violation of Technical Specification (TS) 5.4 of very low safety significance was identified on May 11, 2006, when abnormal flux distribution prevented the licensee from continuing power ascension. The licensee determined a rod w
Region: III | Palisades | 37276 | 06/30/2006 07/28/2006 | 2006004-04 | NRC | NCV | Initiating Events | Green | Polar Crane Struck Jib Crane |  | H.4(a) Human Error Prevention | TE?: N | 05000255 Palisades |  | 71153 | A self-revealed Non-Citied Vioilation of Technical Specificaiton (TS) 5.4 occurred on April 22, 2006, when the polar crane bridge struck and severely damaged the jib crane. The licensee violated TS 5.4 for failing to have adequate procedures in place duri
Region: III | Palisades | 37277 | 06/30/2006 07/28/2006 | 2006004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with 10 CFR 50.59 for P-5 Removal from the FSAR |  |  | TE?: N | 05000255 Palisades |  | 71153 | The inspectors identified a Severity Level IV Non-Citied Violation of 10 CFR 50.59 for improperly removing commitments to maintain a keep warm pump from the Final Safety Analysis Report (FSAR). The licensee had committed to maintaining this pump in lieu o
Region: III | Palisades | 37267 | 04/19/2006 07/21/2006 | 2006008-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Faliure To Develop an Adequate Procedure For Cask And Liner Reuse |  |  | TE?: N | 05000255 Palisades |  | 93812 | A self-revealing finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.4 "Procedures," were identified. On April 19, 2006, while lowering a shielded cask and its liner into the reactor cavity in prepara
Region: III | Palisades | 37257 | 03/31/2006 05/11/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to comply with TS 5.4.1, "Procedures," for an Inadequate Procedure Installing a commercial grade, portable ground detector |  |  | TE?: N | 05000255 Palisades |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) when the procedure used to install commercial grade portable ground detection equipment did not provide adequate Class 1E to non-Class 1E separation. During this installation, the
Region: III | Palisades | 37264 | 03/31/2006 05/11/2006 | 2006002-02 | NRC | FIN | Initiating Events | Green | Moisture Separator Reheater Relief Valve Could Not Be Reseated |  |  | TE?: N | 05000255 Palisades |  | 7111114 | The inspectors determined that a finding of very low safety significance (Green) was self-revealed when a Moisture Separator Reheater relief valve failed to reseat during testing. This failure resulted in a slight power rise due to the additional steam de
Region: III | Palisades | 37265 | 03/31/2006 05/11/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Test the Emergency Diesel Generators Resulting in Preconditioning |  |  | TE?: N | 05000255 Palisades |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) when the Emergency Diesel Generators (EDGs) were unacceptably preconditioned prior to testing. This finding represented a non-cited violation of 10 CFR 50 Appendix B, Criterion XI
Region: III | Palisades | 37256 | 02/17/2006 03/14/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failed Swagelok Fitting on High Pressure Safety Injection Flow Transmitter FT-0312 |  |  | TE?: N | 05000255 Palisades |  | 71152B | A finding of very low safety significance was self-revealed on January 4, 2006, when an incorrectly installed swagelok fitting on high pressure safety injection flow transmitter FT-0312 failed. A Non-Cited Violation of 10 CFR 50 Appendix B, Criterion V, "
Region: III | Palisades | 125583 | 11/14/2019 |  |  | LIV |  | Green | Licensee Identified Missed Technical Specification Surveillance Requirement |  |  | TE?: N | 05000255 Palisades |  | 71111.15
Region: III | Perry | 125739 | 09/30/2019 11/14/2019 | 2019003-02 | Self - Revealed | FIN | Initiating Events | Green | LER 2019-001-00 for Perry Nuclear Power Plant, Loss of Generator Excitation Causes Turbine Trip and Reactor Protection System Actuation. |  | NPP | TE?: N | 05000440 Perry 1 | Equipment Performance | 71153
Region: III | Perry | 25969 | 12/31/2018 02/12/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Preventative Maintenance on Non-safety Structures, Systems and Components |  |  | TE?: N | 05000440 Perry 1 |  | 71111.12 | The inspectors identified a Green finding and associated non-cited violation (NCV) of 10 CFR 50.65(a)(2), “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plant,” for the failure to perform, monitor and assess the condition o
Region: III | Perry | 25970 | 12/31/2018 02/12/2019 | 2018004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures Results in Inoperable Division 1 Diesel Generator |  | H.12 - Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.22 | A self-revealed Green and associated NCV of Technical Specification 5.4, “Procedures,” was identified for the licensee’s failure to implement the established surveillance procedure for diesel generator (DG) testing. Specifically, during the scheduled surv
Region: III | Perry | 24725 | 10/18/2018 11/26/2018 | 2018011-01 | NRC | NCV | Initiating Events | Green | Vulnerability to Cause Secondary Fire due to Unfused Circuit |  | NPP | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very-low safety significance (Green), and associated NCV of License Condition 2.C(6), “Fire Protection,” for the licensee’s failure to implement and maintain all provision of the approved Fire Protection Program to e
Region: III | Perry | 25854 | 10/18/2018 11/26/2018 | 2018011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Watch in Combustible Control Zone due to Exceeded Combustible |  | H.2 - Field Presence | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very-low safety significance and associated violation of License Condition 2.C(6), “Fire Protection,” for failure to meet the requirements of its Fire Protection Program. Specifically, the licensee failed to implemen
Region: III | Perry | 25855 | 10/18/2018 11/26/2018 | 2018011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Install Smoke Detection System in Accordance with Code of Record |  | NPP | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very-low safety significance and an associated NCV of License Condition 2.C.6, “Fire Protection,” for the licensee’s failure to install smoke detection system in accordance with National Fire Protection Association (
Region: III | Perry | 24403 | 08/14/2018 09/19/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Establish Maintenance/Replacement Frequency for the Weed Temperature Transmitters In Zone FB-7 |  | NPP | TE?: N | 05000440 Perry 1 |  | 71111.21N | The inspectors identified a finding of very-low safety significance (Green), and associated NCV of 10 CFR 50.49(e)(5), “Environmental Qualification of Electrical Equipment Important to Safety for Nuclear Power Plants,” for the licensee’s failure to correc
Region: III | Perry | 24133 | 06/30/2018 08/10/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Combustible Materials in a Designated Combustible Control Zone |  | H.12 - Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of Perry Operating License Condition 2.C(6), Fire Protection, for the licensee’s failure to control transient combustible materials in a designated combustib
Region: III | Perry | 23196 | 12/31/2017 02/14/2018 | 2017004-01 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Radiation Exposure ALARA |  | H.5 - Work Management | TE?: N | 05000440 Perry 1 |  | 71124.02 | A finding of very-low safety significance (Green), with no associated regulatory violation, was self-revealed due to the licensee having unplanned and unintended occupational collective radiation dose because of deficiencies in the licensee’s Radiological
Region: III | Perry | 23476 | 11/30/2017 01/03/2018 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Address the Susceptibility of the Condensate Storage Tank Low Level Instrument Lines to Freeze |  | NPP | TE?: N | 05000440 Perry 1 |  | 71111.21M | The team identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, “Design Control,” and 10 CFR 50.63, “Loss of All Alternating Current Powe
Region: III | Perry | 23477 | 11/30/2017 01/03/2018 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Emergency Closed Cooling System Pipe Support |  | H.12 - Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.21M | The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the failure to consider all stresses resulting from the emergency closed cooling system as buil
Region: III | Perry | 23478 | 11/30/2017 01/03/2018 | 2017008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Capability to Manually Backwash the Emergency Service Water Strainer during Loss of Offsite Power |  | NPP | TE?: N | 05000440 Perry 1 |  | 71111.21M | The team identified a finding of very-low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the failure to verify the capability to manually backwash the emergency service water (ESW) str
Region: III | Perry | 16600 | 05/15/2017 05/15/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedures for Combating a Loss of Shutdown Cooling |  |  | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very-low safety significance and associated NCV of TS 5.4, "Procedures," was identified by the inspectors for the failure to implement procedures for combating a loss of shutdown cooling (SDC). Specifically, the licensee failed to implement i
Region: III | Perry | 16590 | 12/31/2016 02/09/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | ECC 'B' Heat Exchanger Flow Root Valves Out of Position |  | H.12 Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.04Q | A finding of very-low safety significance and associated NCV of TS 5.4.1, "Procedures," was self-revealed for the licensee's failure to follow valve lineup procedure restoration requirements after an emergency service water (ESW) pump 'B' and valve operab
Region: III | Perry | 16595 | 12/31/2016 02/09/2017 | 2016004-02 | NRC | NCVIV | Mitigating Systems | Green | Modifications to Underdrain and Gravity Discharge System Manhole Covers Without a 10 CFR 50.59 Safety Evaluation |  | H.8 Procedure Adherence | TE?: Y SL-IV-NCVIV | 05000440 Perry 1 |  | 71111.18 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Test, and Experiments," and an associated finding, for the licensee's failure to perform a written evaluation which provided the bases for the determination that a change d
Region: III | Perry | 16596 | 12/31/2016 02/09/2017 | 2016004-03 | Self - Revealed | NCV | Initiating Events | Green | RCS Pressure Boundary Leakage Operation Prohibited by TSs |  |  | TE?: N | 05000440 Perry 1 |  | 71151 | A finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification (TS) 3.4.5, "RCS Operational Leakage," was self-revealed when the licensee operated with reactor coolant system (RCS) pressure boundary leakag
Region: III | Perry | 16586 | 08/12/2016 09/14/2016 | 2016009-01 | NRC | FIN | Mitigating Systems | Green | Failure to Implement a Periodic Replacement Program for FLEX Hoses |  | H.8 Procedure Adherence | TE?: N | 05000440 Perry 1 |  | 2515/191 | -Green. A finding of very low safety significance was identified by the inspectors for failing to establish a periodic replacement program for the high-temperature rated hoses used during a mitigating strategy for suppression pool cooling. Specifically, t
Region: III | Perry | 16587 | 08/12/2016 09/14/2016 | 2016009-02 | NRC | FIN | Emergency Preparedness | Green | Failure to Establish a Periodic Maintenance Program for Communications Equipment Associated with FLEX |  | H.5 Work Management | TE?: N | 05000440 Perry 1 |  | 2515/191 | -Green. A finding of very low safety significance was identified by the inspectors for failing to establish period tasks to check the operation of recently installed FLEX related communications equipment in accordance with the Perry Nuclear Power Plant FL
Region: III | Perry | 16585 | 06/30/2016 08/10/2016 | 2016002-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Comply with ODCM during Liquid Effluent Discharge |  | H.8 Procedure Adherence | TE?: N | 05000440 Perry 1 |  | 71124.06 | A finding of very low safety significance, and an associated NCV of Technical Specification (TS) 5.5.1 was identified by the NRC inspectors for the failure to follow Offsite Dose Calculation Manual (ODCM) requirements during the execution of a liquid effl
Region: III | Perry | 16577 | 05/27/2016 06/16/2016 | 2016007-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Document 50.59 Evaluation for Replacement of a Manual Action with an Automatic Action (Section 1R17.1.b) |  | H.8 Procedure Adherence | TE?: Y SL-IV-NCVIV | 05000440 Perry 1 |  | 71111.17T | The inspectors identified a Severity Level IV, NCV of Title 10 of the Code of Federal Regulations (CFR), Part 50.59, "Changes, Tests, and Experiments," having very low safety significance (Green) for failure to document the basis for performing a plant mo
Region: III | Perry | 16583 | 05/27/2016 06/16/2016 | 2016007-02 | NRC | NCVIV | Mitigating Systems | Green | Use of Unapproved Statndard for Site Flooding Modifications of Analysis (Section 1R17.2.b) |  | P.1 Identification | TE?: Y SL-IV-NCVIV | 05000440 Perry 1 |  | 71111.17T | The inspectors identified a Severity Level IV, NCV of 10 CFR 50.59, "Changes, Tests, and Experiments," having very-low safety significance (Green) for the licensee's failure to conclude that site flooding modifications and associated analysis included a s
Region: III | Perry | 16584 | 05/27/2016 06/16/2016 | 2016007-03 | NRC | NCV | Initiating Events | Green | Failure to Comply with ASME Code Requirements for Repair on Code Class 1 Component (Section 4OA2.1) |  | H.6 Design Margins | TE?: N | 05000440 Perry 1 |  | 71111.17T | A finding of very-low safety significance (Green) and associated NCV of 10 CFR 50.55a(g)(4) was identified by the inspectors for the licensee's failure to maintain the American Society of Mechanical Engineers (ASME) Code Class 1 component in accordance wi
Region: III | Perry | 16566 | 03/31/2016 05/13/2016 | 2016001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Properly Implement System Operating Instructions to Maintain Control of Reactor Pressure Vessel Level |  | H.1 Resources | TE?: N | 05000440 Perry 1 |  | 71111.2 | A finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1., "Procedures," was self-revealed on January 24, 2016, when an unplanned automatic reactor protection system (RPS) actuation occurr
Region: III | Perry | 16567 | 03/31/2016 05/13/2016 | 2016001-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Control Welding and Inspection Activities to Maintain Reactor Coolant System Integrity |  | H.1 Resources | TE?: N | 05000440 Perry 1 |  | 71111.2 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," was self-revealed on January 24, 2016, for the licensee's failure to control welding and inspection activities dur
Region: III | Perry | 16568 | 03/31/2016 05/13/2016 | 2016001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Actions to Prevent a Loss of Safety Function during Reactor Recirculation Pump Downshift |  | H.12 Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.2 | A finding of very low safety significance and an associated NCV of TS 5.4.1, "Procedures," was self-revealed on January 24, 2016, when a loss of safety system function occurred as a result of the operators failing to take steps to prevent all operable ave
Region: III | Perry | 16570 | 03/28/2016 03/25/2016 | 2016008-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide Instructions to Completely Vent Reference Legs |  | H.11 Challenge the Unknown | TE?: N | 05000440 Perry 1 |  | 93812 | A self-revealed finding and an associated NCV of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the licensee's failure to prescribe instructions appropriate to the circumstance into procedures f
Region: III | Perry | 16571 | 03/28/2016 03/25/2016 | 2016008-03 | NRC | NCV | Initiating Events | Green | Hardcard Development Failed to Follow Procedure Change Process |  | H.14 Conservative Bias | TE?: N | 05000440 Perry 1 |  | 93812 | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow fleet procedure
Region: III | Perry | 16576 | 03/28/2016 03/25/2016 | 2016008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Traceability of Safety Related Fuses |  | H.7 Documentation | TE?: N | 05000440 Perry 1 |  | 93812 | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10 CFR 50, Appendix B, Criterion VIII, "Identification and Control of Materials, Parts, and Components," for the licensee's failure to assure that identific
Region: III | Perry | 16563 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Required 3 Hour Fire Barriers Were In-Place |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated NCV of Perry Operating License Condition 2.C(6), Fire Protection, for the licensee's failure to maintain a three-hour fire barriers as required by the Updated Safety Ana
Region: III | Perry | 16565 | 12/31/2015 02/11/2016 | 2015004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Implement the System Operating Instruction to Restore RHR "B" to Service |  | P.3 Resolution | TE?: N | 05000440 Perry 1 |  | 71152 | A finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1, "Procedures," was self-revealed on November 4, 2015 when operators failed to follow procedures and caused an increase in level of the suppression pool.
Region: III | Perry | 16545 | 12/18/2015 12/04/2015 | 2015010-01 | NRC | VIO | Occupational Radiation Safety | Green | Unqualified Radiation Protection Manager |  | H.3 Change Management | TE?: N | 05000440 Perry 1 |  | 71152 | Green. The inspectors identified a finding of very low safety significance, and an associated violation of Technical Specification (TS) 5.3.1 when an unqualified individual was designated and performed the duties of the Radiation Protection Manager since
Region: III | Perry | 16552 | 10/23/2015 01/05/2016 | 2015008-01 | NRC | NCV | Initiating Events | Green | Failure to Ensure that Systems, Structures, and Components Necessary to Achieve and Maintain Hot Shutdown Conditions were Free of Fire Damage without Repair Actions (Section 1R05.1b) |  | H.7 Documentation | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specifications (TS) Section 5.4.1.a for the licensee's failure to perform fire watches in two fire areas for a non-functional fire barrier. Specifically
Region: III | Perry | 16553 | 10/23/2015 01/05/2016 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Inspect Penetration Seals Within the Required Time Frequency (Section 1R05.2b) |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green), and associated NCV of license condition 2.C(6) for the licensee's failure to ensure that systems, structures, and components necessary to achieve and maintain hot shutdown condit
Region: III | Perry | 16554 | 10/23/2015 01/05/2016 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Guidance to Override Spurious CO2 Initiation Signal in the Diesel Generator Rooms (Section 1R05.6b) |  | H.5 Work Management | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green), and an associated NCV of license condition 2.C(6) for the licensee's failure to adequately implement and maintain surveillance procedures and work processes associated with fire
Region: III | Perry | 16555 | 10/23/2015 01/05/2016 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Fire Watches (Section 1R05.10b) |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green), and an associated NCV of TS Section 5.4.1.a for the licensee's failure to have adequate procedural guidance in their fire response procedure. Specifically, Procedure ONI-P54, "Fi
Region: III | Perry | 16543 | 09/30/2015 11/10/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operating Procedure for Diesel Generator Building Ventilation System |  | H.6 Design Margins | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's fail
Region: III | Perry | 16544 | 09/30/2015 11/10/2015 | 2015003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Implement Steps Outlined in a Technical Specification Surveillance Procedure |  | H.12 Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.22 | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1., "Procedures," was self-revealed on August 5, 2015, when an unexpected isolation of the reactor core isolation cooling (RCIC) system occurred as a result o
Region: III | Perry | 16536 | 08/07/2015 09/21/2015 | 2015007-01 | NRC | URI | Barrier Integrity | Green | ASME Code Pressure Tests of Reactor Vessel Flange Seal Leak-Off Line were not Performed |  |  | TE?: N | 05000440 Perry 1 |  | 71152B | The inspectors identified an unresolved item (URI) concerning the licensee's failure to properly classify the reactor vessel flange seal leak-off line and perform the pressure tests in accordance with the applicable editions of the American Society of Mec
Region: III | Perry | 16537 | 08/07/2015 09/21/2015 | 2015007-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Evaluate Damaged CRD Flange |  | H.12 Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of 10CFR50, Appendix B, Criterion III, "Design Control," for the licensee's failure to adequately evaluae a non-conforming safety-related component prior to returnin
Region: III | Perry | 16534 | 03/31/2015 05/14/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO INITIATE A TRANSIENT COMBUSTIBLE PERMIT |  | H.5 Work Management | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated NCV of Perry Operating License Condition 2.C(6) for failure to follow the site Fire Protection Program. Specifically, a large quantity of material from the previous space u
Region: III | Perry | 16535 | 03/31/2015 05/14/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | LIQUID PENETRANT TESTING PROCEDURE WAS NOT QUALIFIED FOR ITS FULL APPLICABILITY RANGE |  |  | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion IX, "Control of Special Processes," for the licensee's failure to properly qualify a
Region: III | Perry | 16518 | 12/31/2014 02/13/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Unevaluated Preconditioning of Emergency Service Water Motor Operated Valves and Check Valves prior to conducting As-Found Inservice Surveillance Testing |  | H.5 Work Management | TE?: N | 05000440 Perry 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's unevaluated preconditioning, on October 15, 2014, of emergency service water (ESW) pump
Region: III | Perry | 16521 | 12/31/2014 02/13/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Performing an Acceptable Technical Specification Required Channel Check |  |  | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1.a., "Procedures," was identified for the licensee's failure to establish and maintain a correct surveillance inspection procedure
Region: III | Perry | 16522 | 12/31/2014 02/13/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Licensee Procedure to Properly Screen and Evaluate Temporary Changes to Plant Facilities / Structures, Systems, or Components |  | H.3 Change Management | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement the requirements of Nuclear Operating Business Practice (NOBP)-LP-4003A, "
Region: III | Perry | 16516 | 09/30/2014 11/04/2014 | 2014004-01 | Self - Revealed | NCV | Public Radiation Safety | Green | RADIOACTIVE MATERIAL FOUND OFF-SITE AT A SCRAP METAL VENDOR FACILITY |  | H.11 Challenge the Unknown | TE?: N | 05000440 Perry 1 |  | NONE | A self-revealed finding of very low safety significance (Green) and an associated non-cited violation (NCV) of 10 CFR 20.1501 was identified on July 14, 2014, for the failure to conduct surveys that may be necessary for the licensee to comply with the reg
Region: III | Perry | 16515 | 06/30/2014 08/08/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality on Division 2 EDG |  | P.2 Evaluation | TE?: N | 05000440 Perry 1 |  | 71111.19 | A self-revealed finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR, Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified on May 7, 2014, for the failure to correct a condition adverse to quality.
Region: III | Perry | 16513 | 03/31/2014 05/12/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Extreme Cold Weather |  | H.12 Avoid Complacency | TE?: N | 05000440 Perry 1 |  | 71111.01 | A self-revealed finding of very low safety significance (Green) and associated non-cited violation of Technical Specification 5.4.1.a was identified for the licensee's failure to maintain adequate procedures to respond to acts of nature as required by Reg
Region: III | Perry | 16514 | 03/31/2014 05/12/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Required 3-Hour Fire Barriers (Seals) Were In-Place |  | H.5 Work Management | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of Perry Operating License Condition 2.C(6) for failure to establish a required 3-hour fire barrier as required by design. Specifically, on Marc
Region: III | Perry | 16509 | 11/22/2013 01/03/2014 | 2013007-01 | NRC | NCV | Barrier Integrity | Green | Revised NCV to Appendix B, Criterion V for Rx Vessel Pressure/Temperature Controls | EA Case: 2014143 | H.7 Documentation | TE?: N | 05000440 Perry 1 |  | 71152B | By letter dated September 3, 2014, the NRC stated: We have concluded that a violation of TS 3.4.11 did not occur during the 5 reactor cold startups and 1 cooldown discussed in the inspection report, however, we have concluded that the operation of the rea
Region: III | Perry | 16512 | 11/22/2013 01/03/2014 | 2013007-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PROMPTLY CORRECT A NON-CONCERVATIVE TECHNICAL SPECIFICATION |  | H.10 Bases for Decisions | TE?: N | 05000440 Perry 1 |  | 71152B | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly correct a non-conservative Technical Specification. S
Region: III | Perry | 16501 | 09/30/2013 11/14/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MEET FIRE BRIGADE DRILL TRAINING REQUIREMENTS |  | P.3 Resolution | TE?: N | 05000440 Perry 1 |  | 71111.05A | The inspectors identified a finding of very low safety significance and associated non-cited violation (NCV) of License Condition 2.C(6) for failure to ensure that an individual met the fire drill participation requirements for fire brigade members and fi
Region: III | Perry | 16502 | 09/30/2013 11/14/2013 | 2013004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | WORKER ACCESS INTO A HIGH RADIATION AREA CONTRARY TO THE REQUIREMENTS OF THE RADIATION WORK PERMIT |  |  | TE?: N | 05000440 Perry 1 |  | 71124.01 | A finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification 5.4.1 was self-revealed through an electronic dosimeter alarm when, on August 6, 2013, a licensee worker inappropriately entered a high radiat
Region: III | Perry | 16506 | 09/30/2013 11/14/2013 | 2013004-03 | Self - Revealed | FIN | Occupational Radiation Safety | Green | FAILURE TO FOLLOW PROCEDURE IN MINIMIZING DOSE INSIDE A LOCKED HIGH RADIATION AREA IN THE TURBINE BUILDING 620' AUXILIARY STEAM TUNNEL |  | H.2 Field Presence | TE?: N | 05000440 Perry 1 |  | 71124.01 | The inspectors reviewed a self-revealed finding (FIN) of very low safety significance involving an unauthorized activity inside a radiologically contaminated locked high radiation area. Specifically, on April 30, 2013, licensee contract personnel inapprop
Region: III | Perry | 16507 | 09/30/2013 11/14/2013 | 2013004-04 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO PERFORM REPRESENTATIVE SAMPLING OF FISH IN ORDER TO ACCURATELY ASSESS INGESTION RADIATION AS REQUIRED BY THE OFF-SITE DOSE CALCULATION MANUAL |  | H.8 Procedure Adherence | TE?: N | 05000440 Perry 1 |  | 71124.07 | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification 5.5.1, "Offsite Dose Calculation Manual (ODCM)." Specifically, the licensee failed to follow the "Fish and Invertebr
Region: III | Perry | 16499 | 07/28/2013 10/03/2013 | 2013008-02 | NRC | FIN | Initiating Events | Green | Title 10 CFR 50.59 Evaluation Did Not Consider the Freeze Seal Effect to the RCPB (Section 1R17.1.b(1)) |  |  | TE?: N | 05000440 Perry 1 |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated Severity Level IV Non-Cited Violation of Title 10 Code of Federal Regulations (CFR) 50.59, "Changes, Test, and Experiments," for the failure to perform a written evaluation
Region: III | Perry | 16500 | 07/28/2013 10/03/2013 | 2013008-04 | NRC | NCV | Mitigating Systems | Green | Insufficient Controls to Prevent Common Mode Flooding of ECCS Rooms (Section 4OA2.1.b(1)) |  | P.6 Self Assessment | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to control drainage of the emergency core cooling system room sumps in a
Region: III | Perry | 16492 | 06/28/2013 08/12/2013 | 2013009-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement the Operational and Radiological Controls Necessary to Prevent Plant Manipulations from Adversely Impacting Dose Rates or Airborne Radioactivity Levels |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 95002 | The inspectors identified a finding of very low safety significance and associated non-cited violation of Technical Specification (TS) 5.4, "Procedures." Specifically, TS 5.4 "Procedures", Step 5.4.1 states, in part, that the licensee shall establish, i
Region: III | Perry | 16493 | 06/28/2013 08/12/2013 | 2013009-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Lock or Continuously Guard Doors to Prevent Unauthorized Entry to an LHRA |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 95002 | A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.7, "High Radiation Area," was self-revealed when the access point to the locked high radiation area of the auxiliary steam tunnel on the 620'
Region: III | Perry | 16243 | 06/28/2013 08/12/2013 | 2013009-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Post and Barricade a HRA in the Under-Condenser Area Turbine Building Cubicles 13 and 14 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 95002 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification 5.7. "High Radiation Area," when the inspectors identified an unposted, unbarricaded high radiation area under the condens
Region: III | Perry | 16496 | 06/28/2013 08/12/2013 | 2013009-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedural Requirements for RWCU System Fill and Vent |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 95002 | A finding of very low safety significance and associated non-cited violation of Technical Specification 5.4, "Procedures," was self revealed when the licensee failed to adhere to procedural requirements during the filling and venting of the reactor water
Region: III | Perry | 16497 | 06/28/2013 08/12/2013 | 2013009-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement a Procedure Appropriate to the Circumstances Leads to Reactor Overfeed Event |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 95002 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed when the licensee failed to perform a procedure that was appropriate to
Region: III | Perry | 16477 | 05/03/2013 05/10/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE RESULTED IN LOSS OF HIGH-PRESSURE CORE SPRAY FUNCTION |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 71111.13 | A self-revealed finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1.a., "Procedures," was identified for the licensee's failure to establish and maintain a correct surveillance inspection procedure f
Region: III | Perry | 16481 | 05/03/2013 05/10/2013 | 2013002-02 | Self - Revealed | NCV | Mitigating Systems | Green | VALVE MIS-POSITION CAUSES SDV LEVEL DETECTOR INOPERABILITY |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.2 | A self-revealed finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1.a., "Procedures," was identified for the licensee's failure to correctly implement a surveillance procedure for calibration of a sc
Region: III | Perry | 16482 | 05/03/2013 05/10/2013 | 2013002-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES FOR CONDUCTING A STANDBY LIQUID CONTROL SYSTEM SURVEILLANCE |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.22 | A self-revealed finding of very low safety significance and associated non cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when the licensee failed to correctly implement procedures for testi
Region: III | Perry | 16490 | 05/03/2013 05/10/2013 | 2013002-04 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO PERFORM VENDOR RECOMMENDED PREVENTIVE MAINTENANCE ON THE BALANDE-OF-PLANT STATIC TRANSFER SWITCH |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71152 | A self-revealed finding of very low safety significance was identified for the licensee's failure to implement recommended preventive maintenance on a balance-of-plant (BOP) inverter and static transfer switch. Specifically, the licensee failed to impleme
Region: III | Perry | 16248 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO CLASSIFY AND UNUSUAL EVENT |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance with an associated non-citied violaiton of 10 CFR 50.54(q)(2) for the failure to follow the Perry Nuclear Power Plant Emergency Plan that uses a standard emergency classification and acti
Region: III | Perry | 16252 | 12/31/2012 02/07/2013 | 2012005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO APPROPRIATELY CONTROL ACCESS TO A LOCKED HIGH RADIATION AREA |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71124.01 | A finding of very low safety significance and associated non-cited violation of 10 CFR 20.1501 was self-revealed for the failure of the licensee to make surveys to ensure compliance with 10 CFR 20.1601 and Technical Specification 5.7.2 from June 3 throu
Region: III | Perry | 16253 | 12/31/2012 02/07/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | INAPPROPRIATE PROCEDURES FOR RESTORING LPCI MODE OF RHR FOLLOWING A LOCA AT MODE 3 |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish appropriate procedures capable of res
Region: III | Perry | 16254 | 12/31/2012 02/07/2013 | 2012005-04 | NRC | NCV | Mitigating Systems | Green | DEFICIENCIES WITH PERIODIC VENTING PROCEDURES AND VOID QUANTIFICATION |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to ensure adequate test instrumentation was available and used during the p
Region: III | Perry | 16473 | 12/31/2012 02/07/2013 | 2012005-05 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE FUEL HANDLING BUILDING CRANE MAINTENANCE CHALLENGES SINGLE-FAILURE-PROOF COMPLIANCE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to perform adequate maintenance on the single-failure-pr
Region: III | Perry | 16246 | 09/14/2012 12/28/2012 | 2012009-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement Existing Plant Procedures) | EA Case: 2012228 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 95002 | The inspectors identified a finding of very low safety significance and multiple examples of an associated NCV for failure to comply with Technical Specification (TS) 5.4.1. Specifically, the inspectors identified that the licensee failed to implement mul
Region: III | Perry | 16247 | 09/14/2012 12/28/2012 | 2012009-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Appropriately Control Access to a Locked High Radiation Area | EA Case: 2012228 | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 95002 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.7.2 for the failure to control and establish barriers that would prevent unauthorized entry to an area that was accessible to personnel with radiation levels
Region: III | Perry | 16238 | 06/30/2012 07/31/2012 | 2012003-01 | NRC | FIN | Initiating Events | Green | FAILUR TO FOLLOW OPERATIONS PROCEDURES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance when the licensee failed to identify logged readings on the Daily Surveillance Requirements Sheets which were above Operational Decision Making Issue (ODMI) trigger points and subsequentl
Region: III | Perry | 16239 | 06/30/2012 07/31/2012 | 2012003-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO APPRORPRATELY CONTROL ACCESS TO A LOCKED HIGH RADIATION AREA |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of Technical Specification 5.7.2 for the failure to appropriately barricade and conspicuously post an area that was accessible to personnel with radiation levels suc
Region: III | Perry | 16240 | 06/30/2012 07/31/2012 | 2012003-03 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE LIFT PLANT CAUSES LIFING RIG FAILURE |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71152 | A self-revealed finding of very low safety significance was identified when a rigging evolution in the fuel handling building resulted in suspension of an approximately 10,000 pound support column by only part of the planned lift rig. Specifically, on Apr
Region: III | Perry | 16183 | 04/13/2012 05/20/2012 | 2012008-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Transient Combustible Program |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specifications Section 5.4.1.a for the failure to control transient combustible materials in accordance with fire protection program requirements. Specific
Region: III | Perry | 16149 | 04/13/2012 05/20/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Design Spray Density is Achieved |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of License Condition 2.C(6) for the failure to ensure design spray density was achieved for the Unit 1 Division 2 cable chase area. Specifically
Region: III | Perry | 16235 | 04/13/2012 05/20/2012 | 2012008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Sprinkler Piping Could be Drained |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of License Condition 2.C(6) for the failure to ensure that sprinkler piping could be drained. Specifically, the licensee failed to install sprin
Region: III | Perry | 16236 | 04/13/2012 05/20/2012 | 2012008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Install Sequential Timing Device for Fire Pumps |  | P.3(a) Self-Assessment | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of License Condition 2.C(6) for the failure to install a sequential timing device for the diesel driven fire pump. Specifically, the standard fo
Region: III | Perry | 16237 | 04/13/2012 05/20/2012 | 2012008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Full Area Detection |  | P.3(a) Self-Assessment | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of License Condition 2.C(6) for the failure to provide detection throughout Fire Area 1CC-4a. Specifically, Fire Area 1CC-4a was described by th
Region: III | Perry | 16234 | 03/31/2012 04/24/2012 | 2012002-01 | NRC | NCV | Initiating Events | Green | REACTOR MANUAL SCRAM ASSOCIATED WITH INADEQUATE MAINTENANCE RISK EVALUATION |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.2 | A self-revealed finding of very low safety significance (Green) and an associated NCV of 10 CFR 50.65(a)(4) was identified for failure to assess and manage risk associated with maintenance activities. Specifically, the licensee planned and conducted maint
Region: III | Perry | 16226 | 12/31/2011 02/06/2012 | 2011005-02 | NRC | NCV | Initiating Events | Green | FAILURE TO COMPLY WITH TS 5.5.11, TS BASES CONTROL PROGRAM |  |  | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated Severity Level IV NCV of Technical Specification (TS) 5.5.11 for failure to comply with the TS Bases Control Program. Specifically, the licensee made a change to the TS
Region: III | Perry | 16229 | 12/31/2011 02/06/2012 | 2011005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH A PROCEDURE TO PERFORM MAINTENANCE ON SAFETY-RELATED EQUIPMENT |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of TS 5.4.1.a for failure to implement a maintenance procedure for safety-related equipment required by Regulatory Guide 1.33, "Quality Assurance Program Requirements (
Region: III | Perry | 16230 | 12/31/2011 02/06/2012 | 2011005-04 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO MAINTAIN THE PLANT UNDERDRAIN SYSTEM WITHIN USAR DESCRIBED CAPABILITIES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to maintain the plant underdrain system as described in the Updated S
Region: III | Perry | 16231 | 12/31/2011 02/06/2012 | 2011005-05 | NRC | NCV | Mitigating Systems | Green | DIESEL GENERATOR ROOM'S FIRE PROTECTION SYSTEM CONCERN |  |  | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of License Condition 2.C.6 for the failure to install heat detectors in the emergency diesel generator (EDG) rooms in accordance with their listed approval. Specificall
Region: III | Perry | 16232 | 12/31/2011 02/06/2012 | 2011005-06 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM ADEQUATE EVALUATION OF CRANE SUPPORT STRUCTURE ELEMENTS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for failure to provide adequate design control meas
Region: III | Perry | 16215 | 12/02/2011 01/13/2012 | 2011008-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Protect Safety Related Equipment from Internal Flooding |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to ensure safety-related equipment would be adequately protected from intern
Region: III | Perry | 16216 | 12/02/2011 01/13/2012 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Control Circuit Voltage Calculation for Safety-Related Motor Starter Contactors |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for failure to adequately evaluate the capability of motor control starter contact
Region: III | Perry | 16223 | 12/02/2011 01/13/2012 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Test Safety-Related Contactors at Degraded Voltage Conditions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to test safety-related motor starter contactors at design basis conditions.
Region: III | Perry | 16207 | 09/30/2011 11/01/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECTLY ASSESS RISK DURING 'A' ESW PUMP MAINTENANCE ACTIVITIES |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.13 | A self-revealed finding of very low safety significance and associated Non-Cited Violation (NCV) of 10 CFR 50.65(a)(4) was apparent in the licensee's failure to accurately assess plant risk during maintenance activities. The inspectors determined that the
Region: III | Perry | 16208 | 09/30/2011 11/01/2011 | 2011004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO VERIFY RADIOLOGICAL CONDITIONS PRIOR TO ENTERING HIGH RADIATION AREAS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000440 Perry 1 |  | 71124.01 | The inspectors reviewed a self-revealed finding of very low safety significance and an associated NCV of Technical Specification 5.7.1 for the failure of workers to comply with established radiological protective measures as specified for entry into and w
Region: III | Perry | 16213 | 09/30/2011 11/01/2011 | 2011004-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO ACCURATELY ASSESS OCCUPATIONAL DOSE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71124.04 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 20.1201(c) for the failure to accurately assess occupational dose specific to effective dose equivalent (EDE) determinations. The issue has been entered in
Region: III | Perry | 16206 | 07/08/2011 08/02/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | Emergency Service Water System Piping did not meet ASME Code Requirements (Section 4OA5) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 60853 | A finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for failure to perform an adequate
Region: III | Perry | 16192 | 06/30/2011 07/28/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH A PROCEDURE TO OPERATE SAFETY-RELATED EQUIPMENT |  | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification 5.4.1.a, for failure to establish a procedure to remove power from the shutdown cooling isolation valves while shutdown cooling was in operat
Region: III | Perry | 16193 | 06/30/2011 07/28/2011 | 2011003-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO FOLLOW TECHNICAL SPECIFICATION BASES |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance for failure to follow Technical Specification Limiting Condition for Operations 3.0.2 bases. The inspectors determined that the licensee rendered safety-related plant equipment inoperable
Region: III | Perry | 16194 | 06/30/2011 07/28/2011 | 2011003-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO VERIFY EXPECTED EFFECTS RESULTS IN OVERFLOWING THE AUXILIARY BUILDING SUMP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and associated NCV of Technical Specification 5.4.1 was self-revealed for the licensee's failure to follow plant procedures. The inspectors determined that the licensee failed to follow a procedure which requires
Region: III | Perry | 16190 | 05/25/2011 06/30/2011 | 2011013-01 | NRC | NCV | Occupational Radiation Safety | Green | Insufficient detail in work instructions when retracting a Source Range Monitor. (Section 4OA5.6) | EA Case: 2011148 | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | 93812 | The NRC identified a finding of very low safety significance and a non-cited violation (NCV) of regulatory requirements contained in TS 5.4. "Procedures." Specifically, the licensee had insufficient detail in its instructions to workers, to ensure that th
Region: III | Perry | 16189 | 03/31/2011 04/28/2011 | 2011002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Establish Radiological Conditions in a Locked HRA [i.e., the fuel pool cooling and cleanup (FPCC) Heat Exchanger Room] Prior to Allowing Personnel Access. |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated NCV of Technical Specifications (TS) 5.7.2 was self-revealed following the licensee's failure to adequately identify the radiological conditions in the fuel pool cooling and cleanup (FPCC) heat e
Region: III | Perry | 16179 | 12/31/2010 02/01/2011 | 2010005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedures Results in Unplanned Half Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71111.12 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for a failure to follow plant procedures. Specifically, the licensee faile
Region: III | Perry | 16180 | 12/31/2010 02/01/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of HPCS Suction and Pump Minimum Flow Valves Prior to ASME Inservice Testing |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 71111.13 | The inspectors identified a finding of very low safety significance and associated non cited violation of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, for unacceptable preconditioning of the high-pressure core spray (HPCS) suction valves and th
Region: III | Perry | 16181 | 12/31/2010 02/01/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of HPCS Valve Prior to ASME Inservice Testing |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1.a, for failure to establish an adequate procedure to test the high-pressure core spray (HPCS) test return valve to the
Region: III | Perry | 16188 | 12/31/2010 02/01/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate System Functionality of Control Room Breathing Air |  | H.2(d) Facilities & Equipment | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to evaluate and maintain functionality assessments
Region: III | Perry | 16176 | 11/30/2010 12/30/2010 | 2010007-01 | Self - Revealed | NCV | Initiating Events | Green | Unexpected Recirculation Flow Control Valve Runback Due to Inadequate Work Plan |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 71152B | : A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to have an adequate work plan for replacing v
Region: III | Perry | 16177 | 11/30/2010 12/30/2010 | 2010007-02 | NRC | FIN | Public Radiation Safety | Green | Failure to Follow Procedure when Completing Regulatory Applicability Form for a New WARF, RISB, and OSSC Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71152B | A finding of very low safety significance was identified by the inspectors for the licensee's failure to follow procedure NOBP-LP-4003A, FENOC 10 CFR 50.59 User Guidelines, when a new procedure was written and implemented describing the operation of the w
Region: III | Perry | 16165 | 09/30/2010 10/29/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | UNACCEPTABLE PRECONDITION OF RHR VALVE PRIOR TO ASME IN-SERVICE TESTING |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion XI, Test Control, for the unacceptable preconditioning of the 'A' residual heat removal (RHR) pump minimum flow valve prior to quart
Region: III | Perry | 16175 | 09/30/2010 10/29/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION LCOS WHEN REACTOR VESSEL LEVEL INSTRUMENTS WERE DECLARED INOPERABLE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance and associated NCV for a failure to comply with TS 3.0.2 by not entering TS Limiting Condition for Operation (LCO) 3.3.5.1 Condition A and TS LCO 3.3.6.1 Condition A when required. The in
Region: III | Perry | 16162 | 08/03/2010 08/30/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Effectively Manage, Prioritize and Disposition Numerous Operations Procedures Document Change Requests (DCRs) Notifications |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification 5.4.1.a for the licensee's failure to maintain written procedures covering "General Plant Operating Procedures," "Procedures for Startup, Ope
Region: III | Perry | 16115 | 07/01/2010 07/30/2010 | 2010008-02 | NRC | NCV | Public Radiation Safety | Green | Deliberate Failure to Follow Portal Monitor Use Procedure - Performance Deficiency portion. | EA Case: 2010035 |  | TE?: N | 05000440 Perry 1 |  | NONE | A willful violation was identified through an OI Investigation for the failure to comply with the procedure that governed portal radiation monitor usage. Specifically, a contract radiation protection technician deliberately violated a radiation protection
Region: III | Perry | 16143 | 06/30/2010 08/05/2010 | 2010003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Adequately Establish the Radiological Conditions In A Locked High Radiation Area to Allow Workers to Be Properly Briefed Prior to Entry. |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated Non-Cited Violation (NCV) of Technical Specification 5.7.1 was self-revealed following worker entry into the fuel pool cooling and cleanup (FPCC) heat exchanger room. At the time, the FPCC heat e
Region: III | Perry | 16147 | 06/30/2010 08/05/2010 | 2010003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Work In High Radiation Areas Within The Bounds Of The Radiological Briefing Resulting In Entry Into Areas Without Knowledge Of The Radiological Conditions. (Section 2RS1.3) |  | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated NCV of Technical Specification 5.7.1 was self-revealed after workers entered into high radiation areas (HRAs) on March 28, 2010. On two occasions, workers entered HRAs without knowledge of the ra
Region: III | Perry | 16148 | 06/30/2010 08/05/2010 | 2010003-03 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate ALARA Planning And Radiological Controls That Did Not Prevent Unplanned, Unintended Dose For Several Work Activities In Refuel Outage 12. |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | NONE | 3The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 20.1101.b for inadequate ALARA planning and radiological controls. The inspectors determined that as a result of these inadequacies, the licensee's ALARA
Region: III | Perry | 16155 | 06/30/2010 08/05/2010 | 2010003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Evaluate The Need For Radiological Engineering Measures To Control Contamination During Installation Of A Cover Over The Drywell Head. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | NONE | 4A finding of very low safety significance and an associated NCV of 10 CFR 20.1501 was self-revealed during an activity associated with the installation of a contamination control cover element (i.e., the parachute) over the drywell head. The inspectors c
Region: III | Perry | 16156 | 06/30/2010 08/05/2010 | 2010003-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Effectively Use The Intended Radiological Engineering Controls During Cavity Drain-Down In Preparation For Its Decontamination. |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | NONE | 5A finding of very low safety significance and an associated NCV of Technical Specification 5.4.1 was self-revealed during reactor cavity drain down. On March 14, 2009, an airborne radioactivity condition (about 3.3 DAC (derived air concentration)) was ge
Region: III | Perry | 16139 | 03/31/2010 05/04/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECTLY ASSESS RISK DURING POST-MAINTENANCE ACTIVITIES |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.13 | . A finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(4) was identified by the inspectors for the licensee's failure to accurately assess plant risk during maintenance activities. The inspectors determined that the licensee fai
Region: III | Perry | 16142 | 03/31/2010 05/04/2010 | 2010002-02 | NRC | FIN | Mitigating Systems | Green | FAILURE TO MAKE AN ACCURATE IMMEDIATE OPERABILITY DETERMINATION |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very low safety significance was identified by the inspectors for the licensee's failure to make an accurate immediate operability determination (IOD) based on the actual plant conditions and the available information to provide reasonable as
Region: III | Perry | 16131 | 12/31/2009 02/01/2010 | 2009005-01 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO ADHERE TO MAINTENANCE INSTRUCTIONS RESULTED IN LOSS OF RECIRCULATION PUMP 'A' |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very low significance was self-revealed on October 15, 2009, when one of two reactor recirculation pumps failed to transfer to slow speed while operators were attempting to downshift both pumps. The finding involved the licensee's failure to
Region: III | Perry | 16135 | 12/31/2009 02/01/2010 | 2009005-02 | NRC | NCV | Occupational Radiation Safety | Green | UNPOSTED HIGH RADIATION AREA AT THE TIP MACHINES |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification 5.7.1 for the failure to conspicuously post a high radiation area on the 599' elevation of the containment building. Corre
Region: III | Perry | 16136 | 12/31/2009 02/01/2010 | 2009005-04 | NRC | FIN | Occupational Radiation Safety | Green | EXCESS DOSE INCURRED FOR THE ALTERNATE DECAY HEAT REMOVAL PROJECT |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance for inadequate job planning and ineffective work controls which adversely impacted the licensee's ability to minimize dose for the alternate decay heat removal (ADHR) project during Refue
Region: III | Perry | 16126 | 09/30/2009 11/04/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEUQATE POST-MAINTENANCE TEST FOLLOWING INSTALLATION OF NEW EMERGENCY DIESEL GENERATOR CARBON DIOXIDE SYSTEM CONTROL PANELS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.18 | A finding of very low safety significance (Green) and associated non-cited violation of license condition 2.C.(6), Fire Protection, was self-revealed for the licensee's failure implement and maintain in effect all provisions of the approved fire protectio
Region: III | Perry | 16127 | 09/30/2009 11/04/2009 | 2009004-02 | Self - Revealed | NCV | Mitigating Systems | Green | MMAINTENANCE ERRORS CAUSE LOSS OF DIVISION 1 ECCS ELECTRICAL POWER |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance (Green) and associated non-cited violation of Technical Specification 5.4.1 was self-revealed when the licensee failed to follow Nuclear Operating Procedure (NOP)-WM-3001; Work Management PM Processes. Specificall
Region: III | Perry | 16129 | 09/30/2009 11/04/2009 | 2009004-03 | Self - Revealed | NCV | Initiating Events | Green | UNEXPECTED HALF SCRAM DUE TO FAULTY TROUBLESHOOTING PLAN |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to have an appropriate troubleshooting plan for
Region: III | Perry | 16130 | 09/30/2009 11/04/2009 | 2009004-04 | Self - Revealed | FIN | Initiating Events | Green | MOISTURE SEPARATOR REHEATER LEVEL SWITCH MAINTENACE CAUSED UNIT TRIP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed on June 21, 2009, for the failure to adequately implement the requirements of Nuclear Operating Procedure (NOP)-WM-4300, Order Execute Process. Specifically, a supervisor authorized work order st
Region: III | Perry | 16107 | 06/30/2009 07/30/2009 | 2009003-01 | Self - Revealed | NCV | Barrier Integrity | Green | RCS Temp Below Minimum Allowed by TS due to Inadequate Station Procedures |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when operators failed to maintain reactor coolant system (RCS) temperature greater than th
Region: III | Perry | 16110 | 06/30/2009 07/30/2009 | 2009003-02 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Follow Industrial Safety Manual Results in Damage to Fuel Handling building Roll-up Door |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very low safety significance was self-revealed when contract personnel failed to follow the FENOC Industrial Safety Manual to control vehicle movement inside the fuel handling building (FHB). Specifically, a Sea-land truck backed into the FHB
Region: III | Perry | 16098 | 06/30/2009 07/30/2009 | 2009003-03 | Self - Revealed | NCV | Initiating Events | Green | Inability to Operate RHR common suction Line Valve |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 71111.2 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to implement the requirements of licensee (normal operating procedure) NOP
Region: III | Perry | 16105 | 06/30/2009 07/30/2009 | 2009003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent Contact of Energized Components Renders RCIC System Inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.22 | A finding of very low safety significance (Green) and associated NCV of Technical Specification 5.4.1 was self-revealed when technicians failed to implement actions to prevent contact of energized electrical components during maintenance. Specifically, th
Region: III | Perry | 16111 | 06/30/2009 07/30/2009 | 2009003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Appropriate Water Sheilding Between Irradiated Fuel and in-vessel 360 degree platform |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 7112101 | The inspectors identified a finding of very low safety significance and an associated NCV of TS 5.4.1.a for the failure to establish, implement, and maintain adequate written procedures regarding the radiation safety program. The licensee failed to implem
Region: III | Perry | 16112 | 06/30/2009 07/30/2009 | 2009003-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Barricade and Conspicuously Post a High Radiation Area |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 7112101 | The inspectors reviewed a self-revealing finding of very low safety significance and an associated NCV of Technical Specification 5.4.7.a for the failure to barricade and conspicuously post a high radiation area on the 599' elevation of the auxiliary buil
Region: III | Perry | 16099 | 06/30/2009 07/30/2009 | 2009003-09 | NRC | NCV | Initiating Events | Green | Near Loss of Shutdown Cooling due to Maintenance Activity |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71153 | . A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when technicians performed maintenance on protected equipment without implementing risk
Region: III | Perry | 16100 | 06/30/2009 07/30/2009 | 2009003-10 | Self - Revealed | FIN | Initiating Events | Green | Work on Wrong Relay Potential Impact on Shutdown Cooling |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed on April 28, 2009, for the failure to follow maintenance procedure PTI-N41-P0002, "Generator Switchgear Protective Relay Trip Test," when electricians performed maintenance on an incorrect relay
Region: III | Perry | 16106 | 06/30/2009 07/30/2009 | 2009003-11 | Self - Revealed | NCV | Mitigating Systems | Green | RHR System Over-Pressurization Due to Failure to Implement Corrective Actions for a Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was self-revealed for the failure to implement corrective actions to ensure residual heat removal (RHR) check valve 1E12F0050A
Region: III | Perry | 16119 | 06/26/2009 08/05/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Procedures for Post Fire Operation of Control Room HVAC Fans and Control of Remote Shutdown Room Toolbox Inventory. |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1a for failure to maintain procedures for post-fire operation of control room heating, ventilation, and air conditioning (HVAC) Trai
Region: III | Perry | 16120 | 06/26/2009 08/05/2009 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assure That Systems Structures and Components Necessary to Achieve And Maintain Hot Shutdown Conditions Were Free of Fire Damage Without Repair Actions. |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of the Perry Nuclear Power Plant, Unit 1, Facility Operating License Condition 2.C.(6) and 10 CFR Part 50, Appendix R, Section III.G.2, involving the licensee's failure
Region: III | Perry | 16121 | 06/26/2009 08/05/2009 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Required Electrical Isolation for Post Fire Safe Shutdown Electrical Circuits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71111.05T | The inspectors identified a finding of very low safety significance and associated NCV of the Perry Nuclear Power Plant, Unit 1, Facility Operating License Condition 2.C.(6) and 10 CFR Part 50, Appendix R, Section III.G.3, for failure to provide the requi
Region: III | Perry | 16085 | 03/31/2009 05/05/2009 | 2009002-01 | NRC | NCV | Initiating Events | Green | INEFFECTIVE CORRECTIVE ACTIONS ASSOCIATED WITH THE MOTOR FEEDWATER PUMP IN 10 CFR 50.65(a)(1) STATUS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71111.12 | A finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(1) was identified by the inspectors for the licensee's failure to take reasonable corrective action to avoid recurrence of unavailability of a component in accordance with the
Region: III | Perry | 16086 | 03/31/2009 05/05/2009 | 2009002-02 | NRC | NCV | Initiating Events | Green | INADEQUATE INSPECTIONS ON THE RPV HEAD STRONGBACK LIFTING DEVICE MAJOR LOAD-CARRYING WELDS AND CRITICAL AREAS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." The inspectors determined that the licensee failed to perform required nondestructive testing on the reactor pressu
Region: III | Perry | 16087 | 03/31/2009 05/05/2009 | 2009002-03 | Self - Revealed | NCV | Initiating Events | Green | LOSS OF SERVICE AIRE TO MAIN STEAM LINE PLUGS |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 71111.22 | A finding of very low safety significance and associated NCV of Technical Specification Section 5.4.1 was self-revealed on March 7, 2009, when main steam line plug seal pressure began to drop unexpectedly while the reactor cavity was flooded for refueling
Region: III | Perry | 16090 | 03/31/2009 05/05/2009 | 2009002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO PERFORM AN ADEQUATE EVALUATION TO DETERMINE THE USE OF RESPIRATORY PROTECTION EQUIPMENT AND/OR ENGINEERING CONTROLS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 7112101 | A self-revealed finding of very low safety significance and an associated NCV of 10 CFR 20.1501 was identified for the failure to perform an adequate survey (evaluation) to determine whether the use of respiratory protection equipment and/or engineering c
Region: III | Perry | 16091 | 03/31/2009 05/05/2009 | 2009002-05 | Self - Revealed | NCV | Public Radiation Safety | Green | FAILURE TO DOCUMENT ALL APPLICABLE HAZARDS ON SHIPPING MANIFEST |  |  | TE?: N | 05000440 Perry 1 |  | 7112202 | A self-revealed finding of very low safety significance and an associated NCV of Title 10 CFR 71.5 was identified. Specifically, the licensee failed to comply with Title 49 CFR 172.203(c) and shipped a package of radioactive material with a transport mani
Region: III | Perry | 16092 | 03/31/2009 05/05/2009 | 2009002-06 | Self - Revealed | NCV | Initiating Events | Green | MAINTENANCE ON HPCS SYSTEM RESULTED IN EMERGENCY OPERATING PROCEDURE ENTRY |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and associated NCV of Technical Specification Section 5.4.1 was self-revealed on February 3, 2009, when the control room received an unexpected high pressure core spray (HPCS) pump room sump level high alarm and e
Region: III | Perry | 15700 | 01/30/2009 02/25/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ADHERE TO PROCEDURES FOR SCAFFOLD AFFECTING CONTAINMENT SYSTEMS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 71152B | A finding of very low safety significance and associated non-cited violation of Technical Specification 5.4, "Procedures," was identified by the team for the failure to erect scaffolding in accordance with procedural requirements. Specifically, scaffold c
Region: III | Perry | 16082 | 12/31/2008 01/26/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | INSPECTION PROCEDURE FOR RPV HEAD STRONGBACK OMITTED NON-DESTRUCTIVE TESTING OF STRUCTURAL WELDS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings." Specifically, the licensee failed to perform nondestruct
Region: III | Perry | 16083 | 12/31/2008 01/26/2009 | 2008005-02 | NRC | NCV | Initiating Events | Green | CONTAINMENT POLAR CRANE TROLLEY SEISMIC RESTRAINTS DID NOT MEET SEISMIC CATEGORY I REQUIREMENTS |  |  | TE?: N | 05000440 Perry 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, the design basis structural analysis for the containment polar crane
Region: III | Perry | 16084 | 12/31/2008 01/26/2009 | 2008005-03 | Self - Revealed | FIN | Emergency Preparedness | Green | LOSS OF THE V-1F AND V-2F NON-VITAL BUSES RESULTING THE THE LOSS OF TECHNICAL SUPPORT CENTER COMPUTERS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed on October 30, 2008, when licensee personnel failed to appropriately respond to a Technical Support Center (TSC) computer room high temperature alarm. As a result, electrical power supply to plan
Region: III | Perry | 16073 | 09/30/2008 10/27/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Impaired Fire Barrier for Safety-Related Building |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated NCV of the Perry Nuclear Power Plant Operating License Condition C(6). During a maintenance activity, licensee personnel degraded a fire barrier in a manner that was con
Region: III | Perry | 16074 | 09/30/2008 10/27/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Compenatory Measures for a Risk-Management Activity |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a)(4) for failure to assess and manage the risk associated with maintenance activity affecting the low pressure core spray system. Specifically, the
Region: III | Perry | 16075 | 09/30/2008 10/27/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Procedurally-Required Risk management Activity for a Protected Train |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.13 | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR 50.65(a)(4) for failure to implement a procedurally-required risk management activity for a safety system protected train. The licensee failed to provide required mana
Region: III | Perry | 16076 | 09/30/2008 10/27/2008 | 2008004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Use procedures for Work Affecting Safety |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71111.15 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on August 4, 2008, when contract workers bored a hole into a safety-related structure in a
Region: III | Perry | 16077 | 09/30/2008 10/27/2008 | 2008004-05 | Self - Revealed | NCV | Barrier Integrity | Green | Adequacy of Airlock Ball Valve Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71152 | A self-revealed finding of very low safety significance and an associated NCV of 10áCFRáPart 50 Appendix B, Criterion 5 ," Procedures," was identified on Juneá1,á2008, when a containment airlock door seal failed during routine operations. On Marchá26,á200
Region: III | Perry | 15686 | 09/30/2008 10/27/2008 | 2008004-06 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adequately Manage Risk Associated With Working Around a Risk-Significant Underground Vault |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed on July 30, 2008. While performing inspection and dewatering of an underground vault area, plant workers inadvertently dropped a man-hole cover into the vault. The 15-foot vault area contained 12
Region: III | Perry | 16081 | 09/30/2008 10/27/2008 | 2008004-07 | Self - Revealed | FIN | Initiating Events | Green | Loss of Configuration Control of the Hydrogen Water Chemistry Injection System Resulting in High Radiation Levels. |  | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed on June 28, 2008, when high radiation alarms for all four main steam lines were received in the control room during a plant power maneuver. Specifically, maintenance technicians failed to adhere
Region: III | Perry | 15842 | 06/30/2008 07/24/2008 | 2008003-02 | NRC | FIN | Initiating Events | Green | FAILURE TO IDENTIFY A DEGRADED FLOW CONTROL VALVE CONNECTOR |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance for the failure of licensee personnel to adhere to corrective action program procedures. Specifically, during inspection of the linear velocity transducer connector for the 'A' flow contr
Region: III | Perry | 15843 | 06/06/2008 07/18/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | FAILED TO PERFORM AN ADEQUATE DESIGN REVIEW FOR EXPECTED CONDITIONS OF THE OFFSITE POWER SUPPLY IN DETERMINING DESIGN INPUTS FOR EVALUATING THE EFFECTS OF OFFSITE VOLTAGE |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 7111121 | -Green. A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure that the design limits in electrical calculations bound expecte
Region: III | Perry | 16070 | 06/06/2008 07/18/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT EQUIPMENT INSTALLED IN THE PLANT WAS IN ACCORDANCE WITH THE DESIGN DOCUMENTATION |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 7111121 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure that equipment installed in the plant was in accordance with the design
Region: III | Perry | 16071 | 06/06/2008 07/18/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY AND CORRECT ERRORS AND DISCREPANCIES IN SEISMIC QUALIFICATION DOCUMENTS FOR THE STANDBY LIQUID CONTROL (SLC) STORAGE TANK |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to identify and correct errors and discrepancies in seismic qualification documen
Region: III | Perry | 16072 | 06/06/2008 07/18/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TEST REACTOR PROTECTION SYSTEM KEY LOCKED BYPASS SWITCHES |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the failure to test reactor protection system key locked bypass switches. The licensee entered t
Region: III | Perry | 15829 | 03/31/2008 05/08/2008 | 2008002-01 | Self - Revealed | NCV | Mitigating Systems | Green | ADEQUACY OF MAINTENANCE ASSOCIATED WITH EMERGENCY SERVICE WATER STRAINER FAILURE |  |  | TE?: N | 05000440 Perry 1 |  | 71111.12 | A finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," was self-revealed when the 'B' emergency service water (ESW) system pump discharge strainer failed on December 27, 2007. A strain
Region: III | Perry | 15830 | 03/31/2008 05/08/2008 | 2008002-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT ADEQUATE CONFIGURATION CONTROL AFFECTING 'A' REACTOR WATER CLEANUP SYSTEM |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000440 Perry 1 |  | 71111.13 | A finding of very low safety significance and a non-cited violation of Technical Specification (TS) 5.4, "Procedures," was self-revealed on January 4, 2008, when reactor steam was observed coming from the from the 'A' reactor water cleanup (RWCU) system a
Region: III | Perry | 15831 | 03/31/2008 05/08/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY CORRECT AND EVALUATE A CONDITION AFFECTING THE ESW PUMP AND ITS ASSOCIATED DISCHARGE VALVES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding having very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to adequately evaluate and take appropriate correct
Region: III | Perry | 15832 | 03/31/2008 05/08/2008 | 2008002-04 | Self - Revealed | NCV | Mitigating Systems | Green | ADEQUACY OF REACTOR CORE ISOLATION COOLING SYSTEM FLOW CONTROLLER TUNING PROCEDURES |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 71111.22 | A finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," was self-revealed during the reactor scram and plant response on November 28, 2007, when reactor core isolation cooling (RCIC) fa
Region: III | Perry | 15834 | 03/31/2008 05/08/2008 | 2008002-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT TESTING OF THE REACTOR CORE ISOLATION COOLING INSTRUMENT LINES WITH APPROPRIATE PROCEDURES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," while observing a periodic test associated with the reactor core isolation cooling (RCIC) s
Region: III | Perry | 15836 | 03/31/2008 05/08/2008 | 2008002-08 | NRC | FIN | Initiating Events | Green | FAILURE TO REPORT TIMELY PERFORMANCE INDICATOR INFORMATION |  |  | TE?: N | 05000440 Perry 1 |  | 71151 | The inspectors identified a finding associated with the licensee's reporting of Unplanned Scram Performance Indicator (PI) data for the second quarter 2007. On July 23, 2007, Perry plant personnel submitted PI data to the NRC that included one unplanned s
Region: III | Perry | 15837 | 03/31/2008 05/08/2008 | 2008002-09 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE (NON)-RECURRENCE OF REACTOR CORE ISOLATION COOLING INOPERABILITY DUE TO IMPROPER CONTROLLER SETTINGS |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000440 Perry 1 |  | 71153 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR Part 50 Appendix B, Criterion XVI, "Corrective Action," when the reactor core isolation cooling (RCIC) system was declared inoperable on December 12, 2
Region: III | Perry | 15838 | 03/31/2008 05/08/2008 | 2008002-10 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CLASSIFICATION OF CONDITION REPORT FOR REACTOR CORE ISOLATION COOLING |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000440 Perry 1 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," during a review of the licensee's treatment of the safety-related reactor core isolation co
Region: III | Perry | 15839 | 03/31/2008 05/08/2008 | 2008002-11 | Self - Revealed | NCV | Barrier Integrity | Green | LOSS OF SAFETY FUNCTION OF THE ANNULUS EXHAUST GAS TREATMENT SYSTEM |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," was self-revealed when a loss of the annulus exhaust gas treatment system (AEGTS) safety function occurred on December 21, 2007.
Region: III | Perry | 15811 | 12/31/2007 02/12/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADHERE TO PROCEDURES FOR SCAFFOLD AFFECTING REACTOR CORE ISOLATION COOLING |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.04Q | The inspectors identified a finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," during an inspection of the reactor core isolation cooling (RCIC) system on December 12, 2007. The inspectors obser
Region: III | Perry | 15812 | 12/31/2007 02/12/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY A CONDITION ADVERSE TO QUALITY ASSOCIATED WITH SCAFFOLDING CONTACTING THE REACTOR CORE ISOLATION COOLING SYSTEM |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," during an inspection of the reactor core isolation cooling (RCIC) system. On December 12, 2007, the inspectors observed conditions adverse t
Region: III | Perry | 15813 | 12/31/2007 02/12/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CONTROL POST- MAINTENANCE TESTING |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71111.19 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," during an inspection of reactor core isolation cooling (RCIC) system testing between December 8 and
Region: III | Perry | 15814 | 12/31/2007 02/12/2008 | 2007005-04 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO DEVELOP AN ACCURATE DOSE ESTIMATE FOR SCAFFOLDING WORK AND TO MAINTAIN WORKERS' DOSES ALARA |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 7112102 | The inspectors identified a finding of very low safety significance and a non cited violation of Technical Specification 5.4.1.a was for the failure to adequately implement radiological dose controls as a result of ineffective radiological/As Low As Is Re
Region: III | Perry | 15815 | 12/31/2007 02/12/2008 | 2007005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO TAKE PROMPT CORRECTIVE ACTION TO ADDRESS EXTENT OF CONDITION FOR NONCONFORMING CONDITIONS AFFECTING THE DIVISION 1 EDG |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000440 Perry 1 |  | 71152 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," when a nonconforming condition associated with the Division 1 Emergency Diesel Generator was discove
Region: III | Perry | 15816 | 12/31/2007 02/12/2008 | 2007005-06 | Self - Revealed | FIN | Barrier Integrity | Green | FAILURE OF DESIGN CONTROL LEADING TO DROP OF FUEL CHANNEL ONTO SPENT FUEL |  | H.2(d) Facilities & Equipment | TE?: N | 05000440 Perry 1 |  | 71152 | A finding of very low safety significance was self-revealed on October 18, 2007, when a fuel channel dislodged from a grapple during movement in the spent fuel pool. The licensee implemented a design change to the spent fuel handling bridge grapple system
Region: III | Perry | 15817 | 12/31/2007 02/12/2008 | 2007005-07 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CORRECT LACK OF AN ALTERNATE DECAY HEAT REMOVAL SYSTEM IN A TIMELY MANNER - RESULTS IN OPERATION PROHIBITED BY TECHNICAL SPECIFICATIONS |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and an associated non cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was self revealed on July 11, 2007, when the licensee failed to assure that deficiencies associated with alterna
Region: III | Perry | 15818 | 12/31/2007 02/12/2008 | 2007005-08 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ADHERE TO PROCEDURES RESULTS IN TEMPORARY LOSS OF DECAY HEAT REMOVAL |  | H.3(b) Work Activity Coordination | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and a non cited violation of Technical Specification 5.4, "Procedures," was self-revealed when a loss of cooling water flow to the reactor occurred while the reactor was shutdown on July 11, 2007. A maintenance te
Region: III | Perry | 15824 | 12/14/2007 01/25/2008 | 2007010-03 | NRC | FIN | Initiating Events | Green | FAILURE TO APPROPRIATELY INSTALL DIGITAL FEEDWATER CONTROL POWER SUPPLIES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000440 Perry 1 |  | 93812 | The Team identified a finding having very low safety significance for improper installation of replacement power supplies in the digital feedwater control system. The Team observed that the orientation of installed replacement power supplies was 90 degree
Region: III | Perry | 15808 | 09/30/2007 10/26/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES DISABLED EMERGENCY DIESEL OVERSPEED TRIP |  | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | 71111.22 | A finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," was self-revealed when the Division 2 emergency diesel generator failed to trip during surveillance testing on August 20, 2007. Specifically,
Region: III | Perry | 15797 | 06/30/2007 07/26/2007 | 2007003-01 | NRC | NCV | Initiating Events | Green | IMPROPER STORAGE OF COMBUSTIBLE MATERIAL |  | H.4(b) Procedural Compliance | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low significance and an associated non-cited violation of the operating license section C(6) for the storage of transient combustible material in the Turbine Building 620' elevation. Specifically, on May 7 and M
Region: III | Perry | 15798 | 06/30/2007 07/26/2007 | 2007003-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT APPROPRIATE PROCEDURE IN REASSEMBLY OF REACTOR CORE ISOLATION COOLING PIPING |  |  | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," was self-revealed when reactor water level indication was lost while the reactor was shut down on May 5, 2007. Specifically, licensee personn
Region: III | Perry | 15799 | 06/30/2007 07/26/2007 | 2007003-03 | NRC | FIN | Initiating Events | Green | MAIN TURBINE GENERATOR TRIPPED ON REVERSE POWER |  | H.4(a) Human Error Prevention | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed when, during reactor power ascension after a refueling outage, the main turbine generator tripped on reverse power on May 13, 2007. The primary cause of this event was licensee personnel's failur
Region: III | Perry | 15804 | 06/30/2007 07/26/2007 | 2007003-04 | NRC | FIN | Initiating Events | Green | REACTOR SCRAMMED ON LOW REACTOR WATER LEVEL |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 71153 | A finding of very low safety significance was self-revealed when, during post-modification testing of the feedwater system after a refueling outage, the reactor scrammed on low reactor water level on May 15, 2007. The primary cause of this event was the l
Region: III | Perry | 15790 | 03/31/2007 04/25/2007 | 2007002-01 | NRC | NCV | Barrier Integrity | Green | NON-NRC APPROVED CODE USED IN FLAW EVALUATION OF AN ASME CLASS 3 SYSTEM |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000440 Perry 1 |  | 71111.15 | The inspectors identified a finding a very low safety significance and an associated non-cited violation of 10 CFR 50.55(a)(b)(5), "Codes and Standards," for the failure to appropriately implement American Society of Mechanical Engineers (ASME) Section XI
Region: III | Perry | 15796 | 03/31/2007 04/25/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | PROCEDURES INAPPROPRIATE TO CIRCUMSTANCES FOR DEGRADED CONTAINMENT LOWER AIRLOCK INNER DOOR SEAL SYSTEM |  | P.2(b) Implementing Operating Experience | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," during a review of the containment airlock system. Specifically, the inspectors identified that the licensee had fa
Region: III | Perry | 15781 | 12/31/2006 01/30/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DEMONSTRATE SIMULATOR FIDELITY FOR STEADY STATE OPERATIONS |  | P.3(a) Self-Assessment | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 55.46, "Simulation Facilities," when licensee personnel failed to adhere to simulator fidelity requirements prescribed by ANSI/ANS-3.5-1998
Region: III | Perry | 15788 | 12/31/2006 01/30/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT DEGRADED CONDITION OF THE REACTOR RECIRCULATION PUMP CO2 SYSTEM |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of License Condition C(6) for the failure to promptly correct the long-term recurring condition of insufficient CO2 tank level that was required to s
Region: III | Perry | 15789 | 12/31/2006 01/30/2007 | 2006005-03 | NRC | FIN | Mitigating Systems | Green | MINIMUM PUMP FLOW SETTING NOT SUFFICIENT FOR UNLIMITED OPERATION |  |  | TE?: N | 05000440 Perry 1 |  | NONE | The inspectors identified a finding of very low safety significance associated with the minimum flow settings for the high pressure core spray, low pressure core spray, and residual heat removal pumps. Bulletin 88-04 identified that many pump minimum flow
Region: III | Perry | 15785 | 12/15/2006 01/25/2007 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide full electrical isolation in the design of the post-fire safe shutdown control logic circuitry |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000440 Perry 1 |  | 71111.05T | The team identified a NCV of the Perry 1 Nuclear Power Plant Facility Operating License Condition 2.C.(6) and 10 CFR Part 50, Appendix R, Section III.L.3, having very low safety significance (Green), for failure to provide the required electrical isolatio
Region: III | Perry | 15786 | 12/15/2006 01/25/2007 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate the floor drain capacity in the division 1 and 2 cable spreading rooms |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05T | The team identified a NCV of the Perry 1 Nuclear Power Plant Facility Operating License Condition 2.C.(6) having very low safety significance (Green) for failing to implement and maintain in effect all provisions of the approved fire protection program as
Region: III | Perry | 15779 | 12/13/2006 12/29/2006 | 2006015-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE REPAIRS TO OUTER LOWER CONTAINMENT AIRLOCK |  | H.3(a) Work Planning | TE?: N | 05000440 Perry 1 |  | 95003 | A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.4.1.a, "Procedures," was self-revealed when the lower outer containment airlock door failed to close as a result of improper maintenance on the do
Region: III | Perry | 15780 | 12/13/2006 12/18/2006 | 2006017-01 | Self - Revealed | NCV | Mitigating Systems | Green | IMPROPER FUSE REMOVAL DURING CLEARANCE HANGING |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000440 Perry 1 |  | 95003 | A finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," was self revealed after licensee personnel failed to adhere to clearance procedures affecting the Division 1 emergency diesel generator (EDG)
Region: III | Perry | 15784 | 09/30/2006 10/05/2006 | 2006004-01 | NRC | URI | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT DEGRADED REACTOR RECIRCULATION PUMP CO2 FIRE SUPPRESSION SYSTEM |  |  | TE?: N | 05000440 Perry 1 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated non-cited violation of License Condition C(6) for the failure to promptly correct the long-term recurring condition of insufficient CO2 tank level that was required to s
Region: III | Perry | 15749 | 06/30/2006 08/02/2006 | 2006003-01 | NRC | FIN | Initiating Events | Green | FAILURE TO PROMPTLY COMPLETE HOT WEATHER PREPARATIONS |  |  | TE?: N | 05000440 Perry 1 |  | 71111.01 | The inspectors identified a finding of very low significance when licensee personnel failed to complete tasks designed to prepare equipment for operation during high temperature conditions by March 30, 2006. The finding also affected the cross-cutting are
Region: III | Perry | 15777 | 06/30/2006 08/02/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT A TESTING DEFICIENCY AFFECTING A REACTOR CORE ISOLATION COOLING REMOTE SHUTDOWN SYSTEM FUNCTION |  |  | TE?: N | 05000440 Perry 1 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," following a review of Licensee Event Report 05000440/2006-001-00, "Incorrect Wiring in
Region: III | Perry | 15775 | 03/31/2006 04/24/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW MAINTENACE PROCEDURES FOR ELECTRICAL EQUIPMENT VENTILATION FAN MOTOR WHEN VIBRATION LEVELS EXCEEDED ALERT CRITERIA |  |  | TE?: N | 05000440 Perry 1 |  | 7111114 | A finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," was self-revealed on February 11, 2006, when licensee personnel failed to adhere to predictive maintenance program procedures after "B" Motor
Region: III | Perry | 15776 | 03/31/2006 04/24/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW BELT TENSIONING MAINTENANCE PROCEDURES FOR ELECTRICAL EQUIPMENT VENTILATION FAN MOTOR |  |  | TE?: N | 05000440 Perry 1 |  | 71111.19 | The inspectors identified a finding of very low safety significance and a non-cited violation of Technical Specification 5.4, "Procedures," when licensee personnel failed to adhere to maintenance procedures during "B" Motor Control Center Switchgear and M
Region: III | Perry | 15769 | 03/23/2006 05/05/2006 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | ADS and MSIV Air Accumulators Stress Analysis Deficiencies |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving an inadequate stress analysis performed for the automatic depressurization system (
Region: III | Perry | 15770 | 03/23/2006 05/05/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative Safety-Related Air Storage Tank Sizing Calculation |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving the sizing of the main steam isolation valve and automatic depressurization system
Region: III | Perry | 15774 | 03/23/2006 05/05/2006 | 2006009-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Controlling Flow into Reactor Vessel |  |  | TE?: N | 05000440 Perry 1 |  | 7111121 | The inspectors identified a Non-Cited Violation of Technical Specification Requirement 5.4.1, which requires, in part, that written procedures/instructions be established, implemented, and maintained covering the emergency operating procedures required to
Region: III | Perry | 15767 | 03/17/2006 03/30/2006 | 2006007-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM REQUIRED STEPS PRESCRIBED BY PROCEDURE GEI-0009 |  |  | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.4,"Procedures," was identified on January 19, 2006, when the inspectors identified during a safety-related breaker maintenance activity, that lice
Region: III | Perry | 15768 | 03/17/2006 03/30/2006 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM REQUIRED STEPS PRESCRIBED BY PROCEDURE ICI-B12-0001 |  |  | TE?: N | 05000440 Perry 1 |  | NONE | A finding of very low safety significance and an associated non-cited violation of Technical Specification 5.4, "Procedures," was identified on January 10, 2006, when the inspectors observed during a calibration check of a Division III Emergency Diesel Ge
Region: III | Perry | 125754 | 11/14/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Seat Essential Service Water "A" Pump Control Power Fuses results in Loss of Safety Function |  | H.9 - Training | TE?: N | 05000440 Perry 1 | Equipment Performance | 71152 | A self-revealed finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to accomplish work activities in accordance
Region: III | Point Beach | 126103 | 12/31/2019 02/05/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Main Feedwater Isolation Valve Component Materials not Suitable for Environmental Conditions |  | NPP | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 | Equipment Performance | 71111.15 | The inspectors identified a Green finding and associated Non-cited Violation (NCV) of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," when the licensee failed to assure the main feedwater isolation valve actuators and supporting subsyst
Region: III | Point Beach | 125829 | 09/30/2019 11/01/2019 | 2019003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Barricade and Conspicuously Post a High Radiation Area in Unit 1 Containment |  | H.4 - Teamwork | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 | Program & Process | 71124.01 | A self-revealed finding of very low safety significance (i.e., Green) and an associated Non-Cited Violation (NCV) of Technical Specification 5.7.1(a), "High Radiation Areas," was identified by the inspectors when licensee personnel failed to barricade and
Region: III | Point Beach | 124977 | 06/30/2019 07/30/2019 | 2019002-01 | Self - Revealed | NCV | Initiating Events | Green | Human Performance Error Causes Unplanned Pressurizer Pressure Drop |  | H.12 - Avoid Complacency | TE?: N | 05000266 Point Beach 1 | Human Performance | 71111.2 | A self-revealed finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification 5.4.1, "Procedures," was identified when licensee personnel failed to adequately implement a procedure for the normal sequence o
Region: III | Point Beach | 24356 | 06/30/2018 08/06/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Primary Auxiliary Building Floor Plug Removal Creates Unanalyzed Flood Path |  | H.7 - Documentation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | A Green finding and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” was identified by the inspectors for the licensee’s failure to ensure that applicable regulatory requir
Region: III | Point Beach | 23545 | 03/31/2018 05/08/2018 | 2018001-01 | NRC | FIN | Mitigating Systems | Green | Failure To Evaluate and Characterize Fire Protection Pipe Wall Degradation |  | P.2 - Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.04Q | The inspectors identified a finding of very low significance, for the failure to follow procedure NP 7.7.22, “Service Water and Fire Protection Inspection Program.” Specifically, Section 4.10, Degraded Component Characterization and System Failure Analysi
Region: III | Point Beach | 23547 | 03/31/2018 05/08/2018 | 2018001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Evaluate Material Acceptability for a Safety-Related Door |  | NPP | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A self-revealed Green finding and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III was identified when the licensee failed to evaluate the suitability of material prior to installation in the plant. Specifically, the licensee in
Region: III | Point Beach | 23548 | 03/31/2018 05/08/2018 | 2018001-03 | NRC | NCVIV | Initiating Events | Green | Inadequate Basis for Deletion of TRM 3.4.3 - Primary System Integrity Requirements |  | NPP | TE?: Y SL-IV-NCVIV | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | The inspectors identified a Severity Level IV, Non-Cited Violation of 10 CFR 50.59, “Changes, Tests, and Experiments,” and an associated finding of very low safety significance (Green) for failure to provide a written evaluation, which provided the basis
Region: III | Point Beach | 23192 | 12/31/2017 01/31/2018 | 2017004-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Required Provisions of NFPA 805 |  | H.3 - Change Management | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | A finding of very low safety significance and associated non-cited violation of Point Beach Nuclear Plants 1 and 2, Renewed Operating License Condition 4.F (fire protection) was identified by the inspectors for the licensee’s failure to either de-energize
Region: III | Point Beach | 22281 | 09/30/2017 11/08/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | NCV 05000266/2017003-01; 05000301/2017003-01; Inappropriate Instructions for Testing Safety-Related Power Supplies |  | H.6 - Design Margins | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | A finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified by the inspectors for the failure to have instr
Region: III | Point Beach | 22282 | 09/30/2017 11/08/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | NCV 05000266/2017003–02; 05000301/2017003–02; Service Water Cable Support Failure |  | H.14 - Conservative Bias | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified by the inspectors for the failure to promptly identify and correct degraded structural supports
Region: III | Point Beach | 21013 | 07/13/2017 08/09/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with a Seismic Interaction of the Motor Driven Auxiliary Feedwater Piping |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.21M | Green. The NRC identified a finding of very-low safety significance (Green) and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee failure to correct a Condition Adve
Region: III | Point Beach | 21014 | 07/13/2017 08/09/2017 | 2017007-02 | NRC | NCV | Initiating Events | Green | Failure to Identify Non-Conforming Conditions after Receipt of Anchor Darling Double Disc Gate Valve Related Part 21 Report |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.21M | Green. The inspectors identified a finding of very-low safety significance (Green), and an associated (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify a condition adverse to quality. Specifica
Region: III | Point Beach | 21012 | 06/30/2017 08/07/2017 | 2017002-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Evaluate Operating Experience |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | A finding of very low safety significance was self-revealed for the failure to follow program description PI-AA-102, "Operating Experience Program," Revision 3. Specifically, the licensee failed to evaluate operating experience that applied to Point Beach
Region: III | Point Beach | 21008 | 12/31/2016 01/31/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Scaffolding Constructed Without Required Engineering Approvals |  | H.4 Teamwork | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.13 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by inspectors for the licensee failing to follow step 4.1.3 (2) of procedure
Region: III | Point Beach | 20989 | 06/30/2016 08/01/2016 | 2016002-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Required Fire Watches in Areas Containing Transient Combustibles |  | H.10 Bases for Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | A finding of very low safety significance and associated NCV of license condition 4.F was identified by the inspectors for the licensee's failure to conduct required fire watch inspections in accordance with the licensee's Fire Protection Program requirem
Region: III | Point Beach | 20995 | 06/30/2016 08/01/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Submerged Safety-Related Emergency Diesel Generator Fuel Oil Transfer Pump Cables |  | P.2 Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.06 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors, for the failure to maintain emergency diesel generator (EDG) fuel oil transfer pump safety-relat
Region: III | Point Beach | 20997 | 06/30/2016 08/01/2016 | 2016002-04 | NRC | NCV | Barrier Integrity | Green | Violation of Technical Specifications During Mode 4 Entry With LCO 3.6.6 Not Met |  | H.11 Challenge the Unknown | TE?: N | 05000266 Point Beach 1 |  | 71111.2 | A finding of very low safety significance and associated NCV of Technical Specification 3.0.4 was identified by the inspectors for the licensee's failure to follow procedure OP 1A, "Cold Shutdown to Hot Standby Unit 1" and checklist CL 2C, "Mode 5 to Mode
Region: III | Point Beach | 21006 | 06/30/2016 08/01/2016 | 2016002-05 | NRC | FIN | Barrier Integrity | Green | Fuel Assembly Move Sequence Planned Incorrectly |  | H.12 Avoid Complacency | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance was identified by the inspectors, for the licensee's failure to follow procedure REI 26.0, "Fuel/Insert/Component Movement Planning." Specifically, the licensee failed to follow procedure REI 26.0, Step 5.5.7.b, w
Region: III | Point Beach | 21007 | 06/30/2016 08/01/2016 | 2016002-06 | Self - Revealed | NCV | Initiating Events | Green | Incorrectly Wiring Causes Transformer Lockout |  | H.12 Avoid Complacency | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated NCV's of TS 3.8.1, "AC Sources Operating" and TS 3.8.2, "AC Sources Shutdown," were self revealed for the licensee's failure to follow procedure RMP 9056-9B, "1X-03, Protective Relay Calibration and
Region: III | Point Beach | 20988 | 03/31/2016 05/03/2016 | 2016001-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Electrical Safety Procedures Results in Plant Transient |  | H.1 Resources | TE?: N | 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance was self-revealed for the licensee's failure to follow electrical safety procedures when hanging danger tags on electrical components with exposed conductors. Specifically, danger tags were attached directly to th
Region: III | Point Beach | 20724 | 12/31/2015 01/27/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Fire Protection Program Requirements for Care, Use and Maintenance of Fire Hose |  | H.9 Training | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of license condition 4.F for the licensee's failure to have procedures or instructions to prevent firefighting booster hoses from being kinked and/or tw
Region: III | Point Beach | 20725 | 12/31/2015 01/27/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Non-Conforming Auxiliary Feedwater System Pipe Defects |  | H.4 Teamwork | TE?: N | 05000301 Point Beach 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to maintain a Unit 2 auxiliary feedwater system (AFW) pipe se
Region: III | Point Beach | 20721 | 09/30/2015 10/29/2015 | 2015003-01 | NRC | FIN | Mitigating Systems | Green | Incomplete Functionality Assessment for Flooding in the Diesel Generator Building |  | P.2 Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance for the licensee's failure to follow procedure EN AA 203 1001, "Operability Determinations/Functionality Assessments," Revision 19. Specifically, when the licensee identified that interna
Region: III | Point Beach | 20722 | 09/30/2015 10/29/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Potential Failure of Multiple Safety-Related Trains During Flooding Events | EA Case: 2015003 |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that a non Category I (seismic) component failure, that results in
Region: III | Point Beach | 20723 | 09/30/2015 10/29/2015 | 2015003-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a Written Safety Evaluation for FSAR Changes | EA Case: 2015003 |  | TE?: Y SL-IV-NCVIV | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," and an associated finding of very low safety significance for the licensee's failure to perform a safety evaluation to demonstrate that the removal
Region: III | Point Beach | 20714 | 08/28/2015 09/16/2015 | 2015010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Containment spray system for Potential Gas Intrusion (Section 1R17.1b) |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.17T | Green. The inspectors identified a finding of very low safety significance, and an associated NCV of Title 10, Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate for potential gas intr
Region: III | Point Beach | 20713 | 07/10/2015 08/18/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Functionality of a Credited Safe Shutdown Component (Section 4OA2.2b.(2)) |  | P.3 Resolution | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152B | The inspectors identified a finding of very low safety significance and an associated NCV of license condition 4.F for the licensee's failure to demonstrate the capabilities of systems needed to perform a design function for Appendix R cold shutdown. Spec
Region: III | Point Beach | 20720 | 06/30/2015 07/30/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Combustibles During Service Water Pumphouse Maintenance |  | H.2 Field Presence | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | A finding of very low safety significance and associated NCV of Technical Specification (TS) 5.4.1.h was identified by the inspectors for the failure to control transient combustible material in accordance with the licensee's Fire Protection Program requi
Region: III | Point Beach | 20706 | 06/30/2015 07/30/2015 | 2015002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Measures to Control Spare Firing Card Assemblies |  | H.3 Change Management | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," was self-revealed for the licensee's failure to establish measures to ensure non-conforming tantalum
Region: III | Point Beach | 20690 | 03/31/2015 04/30/2015 | 2015001-01 | NRC | FIN | Mitigating Systems | Green | Failure to Process Vendor Technical Information |  | P.5 Operating Experience | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | A finding of very low safety significance was identified by the inspectors for the failure to follow site procedure NP 7.2.13, "Processing of Vendor Technical Information." Specifically, the licensee failed to process a vendor technical bulletin in accord
Region: III | Point Beach | 20691 | 03/31/2015 04/30/2015 | 2015001-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Quantify Radionuclides in the Body for Internal Dose Assessments |  | H.1 Resources | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71124.04 | The inspectors identified a finding of very low safety significance, and an associated NCV of 10 CFR 20.1204 for the licensee's failure to take suitable measurements of quantities of radionuclides in the body for assessing internal dose for occupational e
Region: III | Point Beach | 20705 | 03/27/2015 05/05/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Conditions Adverse to Quality Regarding Electrical Power Cable Sizing and Protection (Section 1R21.3.b.(1)) |  | H.6 Design Margins | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | Green. The inspectors identified a finding of very-low safety significance, and an associated Non-Cited Violation of Title 10, Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to impleme
Region: III | Point Beach | 20685 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Failed Emergency Diesel Generator Day Tank Room Heater (Section 1R01.1) |  | H.5 Work Management | TE?: N | 05000301 Point Beach 2 |  | 71111.01 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the failure to promptly repair the non-functional HX-272A, a safety-related room heater fo
Region: III | Point Beach | 20675 | 09/30/2014 10/30/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Degraded Water Sprinkler System |  | H.8 Procedure Adherence | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated NCV of license condition 4.F for the licensee's failure to identify a degraded water sprinkler system in the service water pump room and implement hourly fire watch inspect
Region: III | Point Beach | 20680 | 09/30/2014 10/30/2014 | 2014004-02 | NRC | NCV | Initiating Events | Green | Failure to Perform Required Fire Watch Inspections |  | H.12 Avoid Complacency | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated NCV of license condition 4.F for the failure to conduct required fire watch inspections. Specifically, the licensee failed to inspect multiple fire zones at the correct fre
Region: III | Point Beach | 20681 | 09/30/2014 10/30/2014 | 2014004-03 | NRC | FIN | Barrier Integrity | Green | Deficiencies in Calculation Performed to Support Containment Dome Truss Operability |  | H.14 Conservative Bias | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance for deficiencies in licensee's calculation performed to support operability of the unit 1 containment building dome truss and the safety related components supported from the truss. The l
Region: III | Point Beach | 20682 | 09/30/2014 10/30/2014 | 2014004-04 | NRC | FIN | Mitigating Systems | Green | Incomplete Prompt Operability Determination of Non-Seismic Block Wall |  | P.1 Identification | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance due to the licensee's failure to follow procedure EN AA 203 1001, "Operability Determinations/Functionality Assessments." Specifically, when the licensee identified that the north non-vit
Region: III | Point Beach | 20673 | 06/30/2014 07/31/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Control of Loose Material in Containment |  | H.9 Training | TE?: N | 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to follow procedures. Specifically, while U
Region: III | Point Beach | 20674 | 06/30/2014 07/31/2014 | 2014003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Age Related Relay Failures Result in Inoperable Inverters |  | P.3 Resolution | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self-revealed for the failure to replace safety-related inverter components at the vendor prescribed 10 year f
Region: III | Point Beach | 20664 | 03/31/2014 05/07/2014 | 2014002-01 | NRC | NCV | Initiating Events | Green | A Failure to Provide Sufficient Field Overlap to Ensure 100 Percent Coverage |  | H.2 Field Presence | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for a failure to provide sufficient magnetic field overlap to ensure 100 percent coverage while performing a magnetic partic
Region: III | Point Beach | 20667 | 03/31/2014 05/07/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Measure Interpass Temperature |  | P.4 Trending | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," for a failure to measure the interpass temperature while performing welding on the auxiliary feedwater (AFW) piping system i
Region: III | Point Beach | 20668 | 03/31/2014 05/07/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Flood Reviews of Material That Could Affect Flood Relief Paths |  | H.9 Training | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow procedures. Specifically, the licensee failed to perform a flood review, as required by N
Region: III | Point Beach | 20653 | 03/06/2014 04/25/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Corrective Actions to Address External Flooding Procedure Deficiencies |  | P.2 Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 95002 | The inspectors identified a finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," in that from March 13, 2013 until February 14, 2014, the licensee failed to assure
Region: III | Point Beach | 20654 | 03/06/2014 04/25/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain External Flooding Procedure to Address All Possible CLB Floods |  | P.3 Resolution | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 95002 | The inspectors identified a finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," in that from January 19, 1996 until November 25, 2013, the licens
Region: III | Point Beach | 20655 | 03/06/2014 04/25/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Required 10 CFR Part 50.59 Evaluation |  | P.2 Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 95002 | The inspectors identified a finding of very low safety significance and associated Severity Level IV, non-citied violation of 10 CFR 50.59(d)(1), "Changes, tests and experiments," when, on November 25, 2013, the licensee failed to perform an evaluation ag
Region: III | Point Beach | 20656 | 03/06/2014 04/25/2014 | 2014007-04 | NRC | FIN | Mitigating Systems | Green | Failure to Perform a Required 10 CFR Part 50.59 Evaluation |  |  | TE?: Y SL-IV-FIN | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 95002 | The inspectors identified a finding of very low safety significance and associated Severity Level IV, non-citied violation of 10 CFR 50.59(d)(1), "Changes, tests and experiments," when, on November 25, 2013, the licensee failed to perform an evaluation ag
Region: III | Point Beach | 20663 | 03/06/2014 04/25/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish EFR Attributes to Assess the Effectiveness of Corrective Actions |  | P.2 Evaluation | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 95002 | The inspectors identified a finding of very low safety significance (Green) and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to ensure the effectiveness review attrib
Region: III | Point Beach | 20647 | 12/31/2013 02/03/2014 | 2013005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Adequate Work Instructions |  | H.5 Work Management | TE?: N | 05000266 Point Beach 1 |  | 71111.19 | A self-revealed finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, occurred when a surveillance procedure was performed with several steps marked not applicable which resulted in Unit
Region: III | Point Beach | 20652 | 12/31/2013 02/03/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Maintenance and Test Equipment Procedure |  | H.10 Bases for Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure NP 8.7.1, "Measu
Region: III | Point Beach | 20645 | 09/30/2013 11/06/2013 | 2013004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Operability/Functionality Evaluation Process Following Radiation Monitor Failure |  | H.14 Conservative Bias | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to follow procedure EN AA 203 1001, "Operability Determinations/Functionality Assessments." Sp
Region: III | Point Beach | 20646 | 09/30/2013 11/06/2013 | 2013004-02 | NRC | NCVIV | Occupational Radiation Safety | Green | Failure to Update FSAR for Radioactive Waste Storage Changes (2RS8) |  |  | TE?: Y SL-IV-NCVIV | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71124.08 | The inspectors identified a finding of very low safety significance and an associated Severity Level IV (SL-IV) NCV of 10 CFR 50.71(e), "Maintenance of Records, Making of Reports," for the licensee's failure to comply with the requirements to periodically
Region: III | Point Beach | 20636 | 06/30/2013 08/13/2013 | 2013003-01 | NRC | FIN | Initiating Events | Green | Failure to Control Materials Classified as High Winds/Tornado Hazards |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance for the licensee's failure to maintain control over the proper storage and placement of materials that were classified as high winds/tornado hazards, in accordance with procedure NP 1.9.6
Region: III | Point Beach | 20637 | 06/30/2013 08/13/2013 | 2013003-02 | NRC | NCV | Initiating Events | Green | Failure to Follow Operability Evaluation Process Following Water Leakage into the Control Room |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V for the licensee's failure to follow procedure EN AA 203 1001, "Operability Determinations/Functionality Assess
Region: III | Point Beach | 20642 | 06/30/2013 08/13/2013 | 2013003-03 | NRC | NCV | Initiating Events | Green | Incorrect Equipment Selected for Ultrasonic Examination |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to select an appropriately contoured ultrasonic examination search unit wedge in accordance with procedure NDE 173, "PDI Generic Procedure for the Ultr
Region: III | Point Beach | 20638 | 06/30/2013 08/13/2013 | 2013003-04 | NRC | NCV | Barrier Integrity | Green | Lack of Acceptance Criteria for Containment Visual Examinations |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4), for failure to define acceptance criteria for containment visual examinations. Consequently, active containment liner degradation (pitting) was identified and the liner returned to se
Region: III | Point Beach | 20643 | 06/30/2013 08/13/2013 | 2013003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions During Bus D-40 Outage |  | H.3(b) Work Activity Coordination | TE?: N | 05000301 Point Beach 2 |  | 71111.13 | A self-revealed finding of very low safety significance and an associated non-cited violation of 10 CFR 50.65(a)(4) occurred on April 29, 2013, as a result of the licensee's failure to properly manage and assess risk during a scheduled maintenance outage
Region: III | Point Beach | 20644 | 06/30/2013 08/13/2013 | 2013003-06 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Plant-Specific Maintenance History in the Development of Preventive Maintenance Frequency |  |  | TE?: N | 05000266 Point Beach 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V for the licensee's failure to follow procedure FP PE 90 01, "Preventive Maintenance Program." Specifically
Region: III | Point Beach | 20627 | 03/31/2013 05/13/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures to Respond to Probable Maximum Precipitation Event |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to establish an abnorma
Region: III | Point Beach | 20618 | 03/31/2013 05/13/2013 | 2013002-02 | NRC | NCV | Initiating Events | Green | Failure to Properly Implement a Compensatory Fire Watch As Required by the Fire Protection Program |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | A finding of very low safety significance and an associated non-cited violation (NCV) of Technical Specification (TS) 5.4.1.h, "Fire Protection Implementation," for Units 1 and 2, was identified by the inspectors for the licensee's failure to implement co
Region: III | Point Beach | 20619 | 03/31/2013 05/13/2013 | 2013002-03 | NRC | NCV | Barrier Integrity | Green | Response for Loss of Spent Fuel Pool Cooling Did Not Consider the Most Limited Time to Boil |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.07T | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to account for the most limiting spent fuel p
Region: III | Point Beach | 20628 | 03/31/2013 05/13/2013 | 2013002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Safety Related Bus 2B-04 Supply Breaker Installed With Incorrect Setpoint |  | H.4(a) Human Error Prevention | TE?: N | 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when the supply breaker to safety-related bus 2B04 tripped premat
Region: III | Point Beach | 20631 | 03/31/2013 05/13/2013 | 2013002-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Operability Evaluation Process for a Degraded Containment Liner |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000266 Point Beach 1 |  | 71152 | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when the licensee failed to perform a prompt opera
Region: III | Point Beach | 20633 | 03/31/2013 05/13/2013 | 2013002-07 | NRC | NCV | Mitigating Systems | Green | Engineered Safety Feature Steam Line Pressure Dynamics Modules Discovered Outside of Technical Specification Values |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the licensee's failure to incorporate a design-basis drift calculation
Region: III | Point Beach | 20626 | 03/31/2013 05/13/2013 | 2013002-08 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Survey for Neutron Dose from Source Storage |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR 20.1501 was self-revealed when the licensee failed to evaluate dose to personnel from neutron radiation. Specifically, on September 5, 2012, it was self reveal
Region: III | Point Beach | 20610 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure To Update The Fire Emergency Plan |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated non-cited violation of the Point Beach Nuclear Plant Renewed Facility Operating License, because the licensee failed to include electrical and physical hazards, which were
Region: III | Point Beach | 20604 | 12/31/2012 02/07/2013 | 2012005-02 | NRC | NCV | Initiating Events | Green | Unauthorized Transient Combustibles |  | H.3(b) Work Activity Coordination | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and associated non-cited violation of Technical Specification 5.4.1.h for Units 1 and 2 for the licensee's failure to control transient combustible materials in accordance with the fire p
Region: III | Point Beach | 20611 | 12/31/2012 02/07/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Scoping Of A Non-Safety-Related System Into The Maintenance Rule |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | -The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR 50.65(b)(2)(i), because the licensee failed to adequately scope a non-safety-related component relied upon to mitigate accidents or transient
Region: III | Point Beach | 20612 | 12/31/2012 02/07/2013 | 2012005-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Implement And Maintain Procedures Regarding Breathing Air Quality |  | H.1(c) Communication of Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71124.03 | The inspectors identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR 20.1703 for the failure to implement and maintain written procedures regarding breathing air quality which resulted in the failure to
Region: III | Point Beach | 20616 | 12/31/2012 02/07/2013 | 2012005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Condition Prohibited by Technical Specification 3.8.2, AC Sources-Shutdown |  | H.4(a) Human Error Prevention | TE?: N | 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated NCV of TS 3.8.2, Condition B, Required Action 1 (Immediately) was self revealed when the licensee's outage related activities rendered both Unit 2 safety related buses inoperable. Specifically, the
Region: III | Point Beach | 20550 | 09/30/2012 11/07/2012 | 2012004-01 | NRC | FIN | Initiating Events | Green | Failure to Adequately Control Materials Classified As High Winds/Tornado Hazards |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance for the licensee's failure to maintain control over the proper storage and placement of materials that were classified as high winds/tornado hazards, within the risk significant areas of
Region: III | Point Beach | 20551 | 09/30/2012 11/07/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure To Implement Risk Management Actions During Various Emergent Work Activities |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.13 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR 50.65(a)(4) because the licensee failed to properly manage and assess risk for various emergent work activities. Specifically, the licensee fa
Region: III | Point Beach | 20555 | 09/30/2012 11/07/2012 | 2012004-03 | NRC | NCV | Initiating Events | Green | Plant Operation With An Unacceptable ASME Code Class 2 Pressure Boundary Flaw |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR 50.55a(g)(4) because the licensee failed to identify and evaluate an American Society of Mechanical Engineers (ASME) Code Class pressure bound
Region: III | Point Beach | 20556 | 09/30/2012 11/07/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Weld Design Deficiency In Emergency Diesel Generator Missile Protection Barriers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for a deficiency in weld evaluations in the licensee design calculation of the new missi
Region: III | Point Beach | 20563 | 09/30/2012 11/07/2012 | 2012004-05 | NRC | NCV | Barrier Integrity | Green | Boric Acid Not Removed From Containment Isolation Valve As Required by Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000301 Point Beach 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to clean boric acid from the Unit 2 reactor coolan
Region: III | Point Beach | 20564 | 09/30/2012 11/07/2012 | 2012004-06 | NRC | NCV | Mitigating Systems | Green | Transient Materials Not Removed From Containment Prior To Reactor Startup |  |  | TE?: N | 05000301 Point Beach 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to remove a plastic bag of transient materials tha
Region: III | Point Beach | 20569 | 09/30/2012 11/07/2012 | 2012004-07 | NRC | NCVIV | MISC | Green | Manager Working Outage Hours Contrary To Guidance |  | P.3(a) Self-Assessment | TE?: Y SL-IV-NCVIV | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a Severity Level lV non-cited violation and associated finding of very low safety significance of 10 CFR 26.207(a), "Waivers," for the licensee's failure to perform multiple activities as required when licensed reactor operators
Region: III | Point Beach | 20570 | 09/30/2012 11/07/2012 | 2012004-08 | NRC | NCV | Mitigating Systems | Green | Failure To Incorporate WOG ERG, Revision 2, Into The EOPs |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation of Technical Specification 5.4, "Procedures." Specifically, the licensee failed to maintain its emergency operating procedures (EOPs) with the safety si
Region: III | Point Beach | 20578 | 09/30/2012 11/07/2012 | 2012004-10 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Guidance For Heavy Loads Operations |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to have adequate procedures in place to
Region: III | Point Beach | 20544 | 06/30/2012 08/03/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure To Establish Emergency Diesel Generator Ventilation System Testing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee failed to establish routine testing procedure that demonstrated room t
Region: III | Point Beach | 20549 | 06/30/2012 08/03/2012 | 2012003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure To Incorporate Industry Operating Experience Into Preventive Maintenance Programs For Nuclear Instrumentation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR 50.65(a)(3) was self-revealed when an unplanned reactor trip of Unit 2 occurred on June 13, 2011, as a result of the failure of a source range detector during low power
Region: III | Point Beach | 20545 | 06/30/2012 08/03/2012 | 2012003-03 | NRC | NCV | Occupational Radiation Safety | Green | Non-Compliance With 10 CFR 20.1701 To Control The Concentration Of Radioactive Material In Air And Ensure That Radiological Airborne Hazards Would Be Minimized In TSC During Design-Based Accident |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR 20.1701. Specifically, the inspectors identified deficiencies, as of January 19, 2012, in the licensee's testing program for assuring that the
Region: III | Point Beach | 20046 | 03/31/2012 05/11/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure To Follow Procedure And Implement Post-Maintenance Testing For Main Feedwater Regulating Valves Following EPU Modifications |  | H.3(b) Work Activity Coordination | TE?: N | 05000301 Point Beach 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee failed to follow work orders to properly conf
Region: III | Point Beach | 20047 | 03/31/2012 05/11/2012 | 2012002-02 | NRC | NCV | Barrier Integrity | Green | Scaffold Construction Interferes With The Operation Of Containment Spray Suction Valve |  | P.1(b) Trend Performance CAP | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | A finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were self revealed during the preparation for surveillance testing when the licensee failed to implement e
Region: III | Point Beach | 20542 | 03/31/2012 05/11/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Perform Operability Evaluations As Required By Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an operability evaluation of t
Region: III | Point Beach | 20541 | 03/31/2012 05/11/2012 | 2012002-04 | NRC | NCV | Occupational Radiation Safety | Green | Determining An Individual's Dose Of Record With Discrepant TLD/ED Data Inputs |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 20.1201(c). Specifically, the licensee failed to accurately assess and assign the appropriate individual dose received on multiple (three)
Region: III | Point Beach | 20044 | 12/31/2011 01/30/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure To Disposition A Pipe Support In Accordance With ASME Code |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000266 Point Beach 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR 50.55a(g)(4) for the licensee's failure earlier in 2011 to accept for continued service, by correction, or evaluation or test, a safety inject
Region: III | Point Beach | 20042 | 09/30/2011 11/02/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure To Perform An Operability Evaluation For Rod Drive Control System Failures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an operability evaluation as r
Region: III | Point Beach | 20043 | 09/30/2011 11/02/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure Tornado Missile Protection For EDGs G01 And G02 Exhaust Stacks |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to ensure tornado missile protection for two of the eme
Region: III | Point Beach | 20036 | 09/02/2011 10/17/2011 | 2011009-01 | NRC | NCV | Mitigating Systems | Green | Failure To Monitor Outside Air Temperature |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to correctly translate design basis assumptions
Region: III | Point Beach | 20037 | 09/02/2011 10/17/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Failure To Incorporate Minimum AFW Flow Requirement Into Emergency Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure a minimum AFW flow of 275 gpm as specified in the acci
Region: III | Point Beach | 19875 | 09/02/2011 10/17/2011 | 2011009-03 | NRC | NCV | Barrier Integrity | Green | Containment Spray Pipe Support Deficiencies |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to ensure the Containment Spray Pipe Support 2S
Region: III | Point Beach | 20040 | 09/02/2011 10/17/2011 | 2011009-04 | NRC | FIN | Initiating Events | Green | Turbine Building Structural Steel Floor Beams Did Not Meet AISC Requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | . The inspectors identified a finding of very low safety significance involving the licensee's failure to meet the requirements of the American Institute of Steel Construction (AISC) Specification. Specifically, the licensee's design basis calculation fai
Region: III | Point Beach | 20025 | 06/30/2011 08/05/2011 | 2011003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Safety Injection Pump Discharge Flow Indicator Left Isolated |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | A finding of very low safety significance and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to implement the requirements of procedure NP 2.1.1,
Region: III | Point Beach | 20028 | 06/30/2011 08/05/2011 | 2011003-02 | NRC | NCV | Barrier Integrity | Green | Failure To Perform An Operability Evaluation For Leakage Inside Containment |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to perform an operability eva
Region: III | Point Beach | 20034 | 06/30/2011 08/05/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Failure To Follow Procedures Needed To Maintain Equipment Operability With Hazard Barriers Out-Of-Service |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions Procedures, and Drawings," was identified by the inspectors for the licensee's failure to have appropriate procedures for the
Region: III | Point Beach | 20017 | 03/31/2011 04/29/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure To Maintain Internal Flood Protection Features On Emergency Diesel Generators G-01 And G-02 Control Cabinets |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.06 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure of the licensee from 1995 through January 20, 2011, to correctly
Region: III | Point Beach | 20018 | 03/31/2011 04/29/2011 | 2011002-02 | NRC | NCV | Initiating Events | Green | Failure To Perform Required Ultrasonic Exam In Accordance With Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.08P | On March 3, 2010, the inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a vendor examiner's failure to follow procedure instr
Region: III | Point Beach | 20024 | 03/31/2011 04/29/2011 | 2011002-03 | NRC | NCV | Barrier Integrity | Green | Unacceptable Preconditioning Of Technical Specification Required Surveillance Test |  | H.3(b) Work Activity Coordination | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the licensee's unacceptable preconditioning of a technical specification require
Region: III | Point Beach | 20003 | 12/31/2010 02/10/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Ultrasonic Assessment of Safety System Voids as Required by Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | A finding of very low safety significance and associated non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to perform ultrasonic testing on
Region: III | Point Beach | 20002 | 12/31/2010 02/10/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Safety System Venting Procedure Void Assessment Requirements |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to establish adequate instructio
Region: III | Point Beach | 20008 | 12/31/2010 02/10/2011 | 2010005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Multiple ESFAS Steam Line Pressure Channel Modules Inoperable Due to Inadequate Calibration Instructions |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to have adequate maintenance procedures for calibrating th
Region: III | Point Beach | 20010 | 12/31/2010 02/10/2011 | 2010005-05 | NRC | FIN | Mitigating Systems | Green | Failure to Document a 10 CFR 50.59 Evaluation For Changes Made to Procedure OI-38, Circulating Water System Operation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A Severity Level IV non cited violation of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," was identified by the inspectors for the failure to document an evaluation that provided a basis for the determination that the changes made to procedure OI
Region: III | Point Beach | 20016 | 12/31/2010 02/10/2011 | 2010005-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Power Operation to Hot Standby Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 |  | 71153 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed when an auxiliary operator failed to correctly perform a procedure step. S
Region: III | Point Beach | 19973 | 09/30/2010 11/09/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Hydrogen Fire Hazards on Pre-Fire Plan |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | A finding of very low safety significance and associated non-cited violations of a license condition was identified by the inspectors for the failure to identify hydrogen fire hazards on a pre-fire plan. Specifically, the licensee failed to identify that
Region: III | Point Beach | 20000 | 09/30/2010 11/09/2010 | 2010004-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Acceptance Criteria for Fire Door Surveillance Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | A finding of very low safety significance was identified by the inspectors for the failure to provide appropriate acceptance criteria for the fire door surveillance procedure. Specifically, the acceptance criteria for fire door functionality did not speci
Region: III | Point Beach | 20001 | 09/30/2010 11/09/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure That RHR Would Be Capable to Respond to a Loss of Cooling Accident in Mode 4 |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to ensure that the residual heat removal (RHR) system would be ca
Region: III | Point Beach | 19986 | 06/30/2010 08/06/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Abnormal Operating Procedure During Tornado Warning |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to implement a required abnormal
Region: III | Point Beach | 19992 | 06/30/2010 08/06/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control the Design of Partially Installed Modifications for Seismic Requirements |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.04Q | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure of the licensee's modification process to ensure that new 480 vol
Region: III | Point Beach | 19993 | 06/30/2010 08/06/2010 | 2010003-03 | NRC | NCV | Initiating Events | Green | Failure To Follow Procedures Needed To Maintain Equipment Operability With Hazard Barriers Out-Of-Service |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions Procedures, and Drawings," was identified by the inspectors for the licensee's failure to follow procedural/instructional gui
Region: III | Point Beach | 19994 | 06/30/2010 08/06/2010 | 2010003-03 | NRC | NCV | Mitigating Systems | Green | PROCEDURES WERE NOT APPROPRIATE TO ADEQUATELY VERIFY AND DOCUMENT THE DESIGN OF NEW OR MODIFIED SSCs WITH RESPECT TO SEISMIC II/I INTERACTIONS. |  | P.3(a) Self-Assessment | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to provide procedures that were appropriate
Region: III | Point Beach | 19985 | 03/31/2010 05/11/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | Untimely Corrective Actions To Address Longstanding Issue Of Submerged Cables |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.06 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified by the inspectors for the licensee's failure to implement timely corrective actions to address
Region: III | Point Beach | 19972 | 03/31/2010 05/11/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Inappropriate Application Of A Dedicated Operator During A System Venting Surveillance |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.13 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50.65(a)(4) was identified by the inspectors for the failure to properly assess risk that resulted from risk-significant maintenance being performed on the residual h
Region: III | Point Beach | 19976 | 03/31/2010 05/11/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Follow Temporary Modification Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.18 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to follow the temporary modifi
Region: III | Point Beach | 19979 | 03/31/2010 05/11/2010 | 2010002-04 | NRC | NCV | Mitigating Systems | Green | Failure To Establish Required Fire Watches |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance and associated Non-Cited Violation of Technical Specification 5.4.1.h for Units 1 and 2 was identified by the inspectors for the licensee's failure to establish appropriate fire watches required as compensatory
Region: III | Point Beach | 19984 | 03/31/2010 05/11/2010 | 2010002-05 | NRC | NCV | Barrier Integrity | Green | Failure To Evaluate Seismic Piping Interactions |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to evaluate seismic piping interactions. Specific
Region: III | Point Beach | 19978 | 03/31/2010 05/11/2010 | 2010002-06 | NRC | FIN | Occupational Radiation Safety | Green | Inadequate Communications, Incomplete As-Low-As-Is-Reasonably-Achievable Job Planning And Ineffective Implementation Of Radiological Work Controls |  | H.1(c) Communication of Decisions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low-safety-significance for inadequate as-low-as-is-reasonably achievable (ALARA) job planning and ineffective implementation of radiological work controls. This issue adversely impacted the licensee's ability t
Region: III | Point Beach | 19961 | 12/31/2009 02/10/2010 | 2009005-01 | NRC | FIN | Mitigating Systems | Green | Failure To Meet Generic Letter 89-13 Program Requirement For Mussel Control |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance for the failure to meet a commitment made in the Generic Letter 89-13 program. Specifically, the program states that biocide treatments at Point Beach are performed at least annually and
Region: III | Point Beach | 19966 | 12/31/2009 02/10/2010 | 2009005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure To Ensure Adequate Control Of Foreign Material In Safety-Related Systems |  |  | TE?: N | 05000301 Point Beach 2 |  | 71111.15 | A self-revealed finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to ensure adequate control of foreign material
Region: III | Point Beach | 19962 | 12/31/2009 02/10/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Failure To Update Safe Load Path Manual To Include Safety-Related Cable Locations |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000301 Point Beach 2 |  | 71111.18 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to update the Safe Load Path Manual for the Unit 2 turbine building (SLP 3
Region: III | Point Beach | 19964 | 12/31/2009 02/10/2010 | 2009005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Momentary Loss Of Unit 2 Reactor Vessel Level Indication In The Control Room |  | H.3(b) Work Activity Coordination | TE?: N | 05000301 Point Beach 2 |  | 71111.2 | A self-revealed finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for performing an Instrumentation and Control procedure that wa
Region: III | Point Beach | 19967 | 12/31/2009 02/10/2010 | 2009005-06 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure To Maintain Proper Control Of Radioactive Material Within The Radiologically Controlled Area |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A self-revealed finding of very low safety significance and associated Non-Cited Violation of 10 CFR 20.1101(b) was identified for the failure to adequately control radioactive material to prevent its migration outside the radiologically controlled area (
Region: III | Point Beach | 19970 | 12/18/2009 01/21/2010 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Errors Found in the Room Ventilation Calculation for G-01 and G-02 |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.17T | A finding of very low safety-significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" was identified by the inspectors for the licensee's failure to adequately calculate the maximum room temper
Region: III | Point Beach | 19957 | 06/30/2009 08/11/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Seismic Assessment Of Temporary Cable Installations Above Motor-Driven Auxiliary Feedwater Pumps |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee's modification process to ensure that new 4160-v
Region: III | Point Beach | 19958 | 06/30/2009 08/11/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions And Procedures For 2P-11B Component Cooling Water Pump Maintenance |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000301 Point Beach 2 |  | 71111.12 | A finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to have adequate work instructions and procedures
Region: III | Point Beach | 19959 | 06/30/2009 08/11/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Technical Specification Limit Value For The 48-Hour Diesel Fuel Oil Storage Volume |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the diesel fuel oil storage volume for the emergency diesel generators
Region: III | Point Beach | 19960 | 06/30/2009 08/11/2009 | 2009003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions For South Service Water Header Work |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | . The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures and Drawings," for the failure to have work instructions and procedures commen
Region: III | Point Beach | 19941 | 03/31/2009 05/01/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Of Diesel Fuel Oil Tank Vent For Tornado Protection |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.04Q | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to fully incorporate applicable tornado missile protection design requir
Region: III | Point Beach | 19942 | 03/31/2009 05/01/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure To Recognize Unit 1 Component Cooling Water Pump Was Inoperable On January 1, 2009 |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000266 Point Beach 1 |  | 71111.12 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of Technical Specification (TS) 3.7.7, "Component Cooling Water (CCW) System," for the failure to recognize that the Unit 1 1P-11B CCW pump was inoperab
Region: III | Point Beach | 19943 | 03/31/2009 05/01/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Promptly Correct Component Cooling Water Pump Oil Leak On January 27, 2009 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 |  | 71111.12 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly correct a condition adverse to quality associated with an inbo
Region: III | Point Beach | 19945 | 03/27/2009 05/08/2009 | 2009006-01 | NRC | FIN | Initiating Events | Green | Failure To Adequately Control High Winds/Tornado Hazards |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152B | A finding of very low safety significance was identified by the inspectors for the licensee's failure to maintain control over the proper storage and placement of materials, within the risk significant areas of the outdoors protected area, that were class
Region: III | Point Beach | 19946 | 03/27/2009 05/08/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Failure To Adequately Input Mechanism Operated Control Switch Failure Evaluations and Recommendations Into Maintenance Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152B | A finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, " Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to have appropriate maintenance procedu
Region: III | Point Beach | 19950 | 03/27/2009 05/08/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Inverter Maintenance Procedures Did Not Include Steps For Capacitor Replacement |  | P.2(b) Implementing Operating Experience | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152B | . A finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to have appropriate ma
Region: III | Point Beach | 19922 | 12/31/2008 02/06/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Evaluations on Boric Acid Leaks |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately perform boric acid leak evaluations
Region: III | Point Beach | 19923 | 12/31/2008 02/06/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Draindown of Reactor Coolant System with Inaccurate Pressurizer Level Indication Due to Inadequate Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to have procedures appropriate to the circumstances for th
Region: III | Point Beach | 19927 | 12/31/2008 02/06/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Install Unit 1 Debris Interceptors in Accordance with Installation Work Order |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to appropriately implement work orders for the ins
Region: III | Point Beach | 19928 | 12/31/2008 02/06/2009 | 2008005-04 | NRC | NCV | Initiating Events | Green | Inadequate Inspection Procedure for Containment Polar Crane Structures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to have inspection procedures appropriate to the circumsta
Region: III | Point Beach | 19929 | 12/31/2008 02/06/2009 | 2008005-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Establish Written Procedures to Implement the Effluent Control Program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7112201 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of Technical Specification 5.4.1 for the failure to establish written procedures to implement the radioactive effluent control program as provided in
Region: III | Point Beach | 19933 | 12/31/2008 02/06/2009 | 2008005-06 | NRC | NCV | Barrier Integrity | Green | Non-Conservative Low Temperature Overpressure Protection Setpoints |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self revealed upon discovery of the use of a non-conservative setpoint for the Low Temperature Overpressure Protection (LTOP)
Region: III | Point Beach | 19934 | 12/31/2008 02/06/2009 | 2008005-07 | NRC | NCV | Barrier Integrity | Green | Violation of Technical Specification 5.6.5(c) - Pressure and Temperature Limits Report Not Submitted | EA Case: 2008274 |  | TE?: N | 05000266 Point Beach 1 |  | 71153 | The inspectors identified a finding of very low safety significance and associated Severity Level IV Non-Cited Violation of Technical Specification 5.6.5(c), "Reactor Coolant System Pressure and Temperature Limits Report (PTLR)," for the failure to submit
Region: III | Point Beach | 19914 | 09/30/2008 11/04/2008 | 2008004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedures for Use of the Containment Hatch Doors |  | H.4(b) Procedural Compliance | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the failure to follow system operating procedure requirements to visua
Region: III | Point Beach | 19921 | 09/30/2008 11/04/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Have Adequate Maintenance Procedures for Service Water Pump Replacements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the failure to properly rig and install the P-32E service water pump s
Region: III | Point Beach | 19906 | 07/25/2008 09/08/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Equalizing Charge Voltage Not Bounded by Battery Room Hydrogen Generation Calculation |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified by the team for the failure to ensure that the design limit established in a design basis calculation
Region: III | Point Beach | 19907 | 07/25/2008 09/08/2008 | 2008009-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Design Basis for Primary Auxiliary Building Heat-up |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified by the team for the failure to verify the accuracy of design using alternative or simplified calculat
Region: III | Point Beach | 19908 | 07/25/2008 09/08/2008 | 2008009-03 | NRC | NCV | Mitigating Systems | Green | Ability to Transfer Fuel Oil Between EDG Fuel Oil Tanks T-175A/B Has Not Been Demonstrated by Testing |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | A finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, was identified by the team for the failure to test the components used for transfer of fuel oil between two underground
Region: III | Point Beach | 19909 | 07/25/2008 09/08/2008 | 2008009-04 | NRC | NCV | Mitigating Systems | Green | RHR Pump Suction Pressure Gages Repeatedly Found To Be Out Of Tolerance |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XII, Control of Measuring and Test Equipment, was identified by the team for the failure to correct a known trend of out of tolerance (OO
Region: III | Point Beach | 19873 | 06/30/2008 08/11/2008 | 2008003-01 | NRC | FIN | Initiating Events | Green | Failure to Properly Store or Secure Tornado Missile Hazards in the Protected Area |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance (Green) with no associated violation of regulatory requirements for the licensee's failure to maintain control over the proper storage and placement of materials within the protected area
Region: III | Point Beach | 19874 | 06/30/2008 08/11/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Address Sprinkler Head Obstructions in 'B' Train EDG Rooms |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05Q | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of License Condition 4.F for the failure to address fire suppression sprinkler head obstructions in the 'B' train emergency diesel generator
Region: III | Point Beach | 19881 | 06/30/2008 08/11/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage Online Risk for Breaker 1B52-16C Work |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.13 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when the licensee failed to ad
Region: III | Point Beach | 19882 | 06/30/2008 08/11/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for DY-0C Inverter Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | A self-revealing finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to have appropriate maintenance procedur
Region: III | Point Beach | 19883 | 06/30/2008 08/11/2008 | 2008003-05 | NRC | FIN | Initiating Events | Green | Failure to Implement Appropriate Design and Configuration Control for the Unit Polar Crane |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | A self-revealed finding of very low significance (Green) with no associated violation of regulatory requirements was identified for the failure to implement appropriate design and configuration control for the Unit 2 polar crane upgrade project, which res
Region: III | Point Beach | 19888 | 06/30/2008 08/11/2008 | 2008003-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Reduced Inventory With an Intact Reactor Coolant System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of TS 5.4.1, "Procedures," was identified by the inspectors for the failure to protect all of the safety equipment necessary for safe shutdown while in reduced inventory with the
Region: III | Point Beach | 19889 | 06/30/2008 08/11/2008 | 2008003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain RCS Within Procedurally Allowed Level During Reduced Inventory |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of TS 5.4.1, "Procedures," was identified by the inspectors for the failure to implement operations procedures to remain above the + pipe level indications for draining the React
Region: III | Point Beach | 19890 | 06/30/2008 08/11/2008 | 2008003-08 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Control of Containment Penetration Status |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.2 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to maintain adequate control over the status of
Region: III | Point Beach | 19897 | 06/30/2008 08/11/2008 | 2008003-09 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Adequate Total Effective Dose Equivalent ALARA Evaluations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7112102 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 20.1501 was identified by the inspectors for the failure to perform an adequate survey (evaluation) to determine the use of respiratory protection equipment and/or engi
Region: III | Point Beach | 19898 | 06/30/2008 08/11/2008 | 2008003-10 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure for Turbine-Driven Auxiliary Feedwater Pump 2P-29 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the failure to ensure that procedures associated with t
Region: III | Point Beach | 19899 | 06/30/2008 08/11/2008 | 2008003-11 | NRC | NCV | MISC | Green | Failure to Ensure Completion of New Supervisory Training | EA Case: 2006178 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A Non-Cited Violation of Confirmatory Order EA 06-178 having very low safety significance (Green) was identified by the inspectors for the licensee's failure to ensure that new employees holding supervisory positions and higher were trained on safety cons
Region: III | Point Beach | 19905 | 06/30/2008 08/11/2008 | 2008003-12 | NRC | FIN | MISC | Green | Inadequate Corrective Actions to Address Licensee Action Plans |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | A finding of very low safety significance was identified by the inspectors for the failure to take timely and effective corrective actions to address four of nine nuclear safety culture action plans and the "quick hitter" plans. Specifically, the licensee
Region: III | Point Beach | 19863 | 03/31/2008 04/25/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Failure to Take Prompt Corrective Actions for Recurring Cold Weather Issues |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," having very low safety significance (Green) for the license's failure to take prompt corrective actions to address recurri
Region: III | Point Beach | 19864 | 03/31/2008 04/25/2008 | 2008002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Take Prompt Corrective Actions for Conditions Adverse to Quality Associated with the PAB Crane |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the license's failure to implement prompt corrective actions for the degrad
Region: III | Point Beach | 19865 | 03/31/2008 04/25/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Resulted in Inadvertent Draining of Unit 1 SI Accumulator |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 |  | 71153 | A self-revealed finding and an associated Non-Cited Violation of Technical Specification 5.4.1, "Procedures," having very low safety significance (Green), was identified for the license's failure to implement procedures associated with conduct of operatio
Region: III | Point Beach | 19872 | 03/31/2008 04/25/2008 | 2008002-04 | NRC | NCV | Barrier Integrity | Green | Piping Anchor Design Not in Conformance With Design Basis Code Requirements |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate service water piping to pipe anchor integra
Region: III | Point Beach | 19856 | 03/07/2008 04/21/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Inappropriate Relay Setpoint Selection |  |  | TE?: N | 05000266 Point Beach 1 |  | 93812 | A self-revealing finding of very low safety significance and a Non-Cited Violation was identified for the licensee's failure to comply with 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the design b
Region: III | Point Beach | 19857 | 03/07/2008 04/21/2008 | 2008007-02 | NRC | NCV | Initiating Events | Green | Inadequate Cable Test Program |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000266 Point Beach 1 |  | 93812 | The inspectors identified a finding of very low safety significance and an Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a test program that adequately demonstrated that medi
Region: III | Point Beach | 19858 | 03/07/2008 04/21/2008 | 2008007-03 | NRC | NCV | Initiating Events | Green | Inadequate and Untimely Corrective Actions to Address Cable Submergence |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 |  | 93812 | A self-revealing finding of very low safety significance and a Non-Cited Violation was identified for the licensee's failure to comply with 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure develop effective correc
Region: III | Point Beach | 19273 | 12/31/2007 02/13/2008 | 2007005-01 | NRC | FIN | Initiating Events | Green | Failure to Control Loose Materials Classified as Tornado Hazards |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance with no associated violation of regulatory requirements for the licensee's failure to control loose materials in the protected area. Specifically, the inspectors identified materials that
Region: III | Point Beach | 19302 | 12/31/2007 02/13/2008 | 2007005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Assess Operability of Service Water Pump P-32C |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | A self-revealed finding with no associated violation of regulatory requirements was identified for an inadequate operability evaluation performed in June 2007 for service water pump P-32C. Specifically, the pump failed its inservice test (IST) on high vib
Region: III | Point Beach | 19303 | 12/31/2007 02/13/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Operability Evaluations for Turbine-Driven Auxiliary Feedwater Pump 2P-29 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately assess operability of the Unit
Region: III | Point Beach | 19304 | 12/31/2007 02/13/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Have Adequate Procedures for the Refueling Water Storage Tank |  | H.4(a) Human Error Prevention | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A self-revealed finding and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified for the failure to have adequate procedures to allow operators to properly set the thermostat of
Region: III | Point Beach | 19305 | 12/31/2007 02/13/2008 | 2007005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adquate Post-Maintenance Testing for the Turbine-Driven Auxiliary Feedwater Pumps |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to conduct adequate post-maintenance test
Region: III | Point Beach | 19306 | 12/31/2007 02/13/2008 | 2007005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate a Condition Adverse to Quality Associated with Turbine-Driven Auxiliary Feedwater Pump 2P-29 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000301 Point Beach 2 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to implement prompt corrective actions for the degraded oil conditions
Region: III | Point Beach | 19849 | 12/31/2007 02/13/2008 | 2007005-08 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Guidance to Ensure the Operability of the Main Steam System During a Steam Generator Tube Rupture |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a Non-Cited Violation (NCV) of Technical Specification 5.4, "Procedures," for the failure to have adequate procedures to ensure the continued operation of the steam dumps to the condenser to maintain a Reactor Coolant System (RCS
Region: III | Point Beach | 19295 | 12/14/2007 01/22/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Factor of Safety Specified in Design Evaluation of Unit 1 SGBD HX Platform |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111102 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance involving a calculation that designed the Unit 1 Steam Generator Blowdown (SGBD) Heat Exchanger (HX) Platform to with
Region: III | Point Beach | 19289 | 09/30/2007 10/26/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Service Water System Microbiologically-Induced Corrosion through-Wall Leak Due to Inadequate Corrective Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | A self-revealing finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to take prompt corrective action for microbiologically-induced corrosion (MIC) of the service water (SW) piping.
Region: III | Point Beach | 19290 | 09/30/2007 10/26/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Previous Indication of Degraded Oil in Component Cooling Water Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to implement prompt corrective actions for the degraded oil conditions initially identified with safety-related Component Cooling Water (CC
Region: III | Point Beach | 19292 | 09/30/2007 10/26/2007 | 2007004-03 | NRC | NCV | Initiating Events | Green | Inadvertent Chemical and Volume Control System Letdown Isolation Due to Inadequate Instructions, Procedures, and Drawings |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111117A | A self-revealing finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to have procedures appropriate to the circumstances for modifying the Unit 1 Charging Pump 1P-
Region: III | Point Beach | 19293 | 09/30/2007 10/26/2007 | 2007004-04 | NRC | NCV | Mitigating Systems | Green | Incorrect Calibration Methods for Engineered Safeguards Actuation System Instrumentation, Lead/Lag Time Constants for Steam Line Pressure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A self-revealing finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure to have adequate maintenance procedures for performing calibration of the Engineered Safeguard
Region: III | Point Beach | 19294 | 09/30/2007 10/26/2007 | 2007004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Account for MOV Stalling Delays for ECCS Response Time Analysis |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE
Region: III | Point Beach | 19287 | 07/13/2007 08/24/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Non-Compliant Sprinkler Heads in the EDG Rooms |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance and an associated NCV of the PBNP's Operating License for failure to take prompt corrective action for a condition adverse to quality. Specifically, in July 2002, the licensee identified
Region: III | Point Beach | 19264 | 06/30/2007 08/08/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Work Instructions for Preventive Maintenance on Safety-Related Battery Chargers |  | H.3(b) Work Activity Coordination | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.12 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to accomplish required preventive maintenance resulting in the D-108 Station Battery output becoming unstable on several occa
Region: III | Point Beach | 19265 | 06/30/2007 08/08/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately manage an Orange Risk Condition |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 |  | 71111.13 | The inspectors identified a NCV of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," after the licensee failed to adequately manage the risk associated with the installation of the Unit 1 Steam Gen
Region: III | Point Beach | 19270 | 06/30/2007 08/08/2007 | 2007003-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Program for Preventive Maintenance of Breaker Mechanism Operated Control Switches |  | P.2(b) Implementing Operating Experience | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.19 | The inspectors identified a NCV of 10 CFR Part 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," of very low safety significance (Green), for the failure to incorporate available internal and external Operating
Region: III | Point Beach | 19271 | 06/30/2007 08/08/2007 | 2007003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Establish Appropriate Test conditions for Leak-Rate Testing Outside Containment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to have procedures appropriate to the circumstances, which established the appropriate test conditions for primary coolant
Region: III | Point Beach | 19272 | 06/30/2007 08/08/2007 | 2007003-06 | NRC | NCV | Initiating Events | Green | Failure to Perform Appropriate Maintenance on Air-Operated Valve Positioner Linkage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A self-revealing finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions , Procedures, and Drawings," having very low safety significance (Green), was identified for failure to have procedures appropriate to the circumstances
Region: III | Point Beach | 19276 | 06/30/2007 08/21/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Previous Indications of High Bearing Temperatures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000266 Point Beach 1 |  | 93812 | The inspectors identified a finding involving a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very low safety significance (Green) for the licensee's failure to identify and implement prompt corrective
Region: III | Point Beach | 19277 | 06/30/2007 08/21/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Assess the Operability of the Unit 1 Turbine Driven Auxiliary Feedwater Pump on June 9, 2007 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000266 Point Beach 1 |  | 93812 | The inspectors identified a finding of very low safety significance (Green) and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately assess Operability in accordance with plan
Region: III | Point Beach | 19278 | 06/30/2007 08/21/2007 | 2007008-03 | NRC | NCV | Mitigating Systems | Green | Failure to have Procedures Appropriate to the Circumstances for Terry Turbine Overhauls |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 93812 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to ensure that procedures associated with the maintenance of the
Region: III | Point Beach | 19283 | 06/30/2007 08/21/2007 | 2007008-04 | NRC | FIN | Mitigating Systems | Green | Failure to have Specific Formal Training for Maintenance Craft on Terry Turbine Overhauls |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 93812 | The inspectors identified a finding of very low significance (Green) with no associated violation for the failure to provide appropriate training for maintenance personnel performing overhauls on the TDAFW pump turbines. Specifically, while maintenance pe
Region: III | Point Beach | 19284 | 06/30/2007 08/21/2007 | 2007008-05 | NRC | NCV | Mitigating Systems | Green | Failure to have Procedures Appropriate to the Circumstances for the Analysis and Sampling of Safety-Related Turbine and Pump Oil |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 93812 | The inspectors identified a finding of very low safety significance (Green) and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement an oil analysis program for the
Region: III | Point Beach | 19286 | 06/30/2007 08/21/2007 | 2007008-07 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Quarantining Process |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 93812 | The inspectors identified a finding of very low safety significance (Green) and a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately quarantine a component for subsequent caus
Region: III | Point Beach | 19256 | 03/31/2007 04/12/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | Failure to Take corrective Actions for Cold Weather Issues Prior to the Onset of Cold Weather |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000301 Point Beach 2 |  | 71111.01 | The inspectors identified a finding and associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," having very low safety significance (Green) for the failure to take prompt corrective actions to address a pote
Region: III | Point Beach | 19263 | 03/31/2007 04/12/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Design Margin for Control Room Emergency Filtration Fan Thermal Overload Trips |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," having very low safety significance was self-revealed for the failure to maintain sufficient design margin for the expected running currents of the control room emergen
Region: III | Point Beach | 19235 | 12/31/2006 11/21/2006 | 2006011-02 | NRC | NCV | Initiating Events | Green | Replacement Reactor Vessel Head Design Deficiencies |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 93812 | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) when the licensee failed to assure from October 2002 to April 2005 that deviations in weight,
Region: III | Point Beach | 19249 | 12/31/2006 01/25/2007 | 2006013-01 | NRC | NCV | Initiating Events | Green | Inadequate Design Control for a Flooding Barrier During a Plant Modification |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000301 Point Beach 2 |  | 71111.06 | The inspectors identified a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to maintain flooding barriers after drilling holes and installing conduit from the contain
Region: III | Point Beach | 19251 | 12/31/2006 01/25/2007 | 2006013-03 | NRC | FIN | Initiating Events | Green | Inadequate Contractor Oversight Which Resulted in Damage to a Unit 2 Steam Generator Vent Line |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000301 Point Beach 2 |  | 71153 | A finding of very low safety significance was self-revealed on November 14, 2006, when unqualified contract crane technicians operated the Unit 2 polar crane and damaged the 'B' steam generator vent line with the main hook of the crane. The reactor was sh
Region: III | Point Beach | 19254 | 12/31/2006 01/25/2007 | 2006013-04 | NRC | NCV | Initiating Events | Green | Inadequate Procedural Controis for Manually Operated Breakers Located in Certain Control Panels |  | H.3(a) Work Planning | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71153 | A finding and associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance was self-revealed on October 16, 2006, during the out-of-service tagging of a manually operat
Region: III | Point Beach | 19242 | 12/15/2006 01/18/2007 | 2006015-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Identifying Degraded Piping |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance involving areas of service water piping where microbiologically induced corrosion was identified but the wall thicknesses of the pipe in those areas were not measured. An NCV of 10 CFR Pa
Region: III | Point Beach | 19243 | 12/15/2006 01/18/2007 | 2006015-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Extent-of-Condition Review |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance with no associated violation for an inadequate extent-of-condition review for boric acid leakage found in the last quarter of 2005 on the safety injection-850 valves (containment recircul
Region: III | Point Beach | 19244 | 12/15/2006 01/18/2007 | 2006015-03 | NRC | FIN | Occupational Radiation Safety | Green | Untimely Completion of Three RCEs Involving Radiation Protection |  | H.3(b) Work Activity Coordination | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a finding of very low safety significance for the licensee's untimely completion of three root cause evaluations in the radiation protection area. The 3 evaluations were completed in 8-9 months instead of the 30 days stated in th
Region: III | Point Beach | 19236 | 09/30/2006 11/07/2006 | 2006005-01 | NRC | NCV | Public Radiation Safety | Green | Conditional Release of Radioactively Contaminated Material, a Check Source Mechanism |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7112203 | A self-revealed finding of very low safety significance that was a non-cited violation of 10 CFR 20.1501 was identified for the licensee's failure to perform a survey prior to unconditionally releasing a radioactively contaminated Check Source Mechanism (
Region: III | Point Beach | 19237 | 09/30/2006 11/07/2006 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Emergency Core Cooling System Sump Flow Design Control Deficiencies |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance when the licensee did not correctly interpret the results of calculations of the head available to drive fl
Region: III | Point Beach | 19241 | 09/30/2006 11/07/2006 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Containment Coatings Program Weaknesses |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance when the licensee failed to assure that the limits of unqualified and degraded coatings within the containm
Region: III | Point Beach | 19217 | 09/29/2006 11/16/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Potential Common Mode Failure Mechanism Due to Overdutied Circuit Breakers |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving electrical system short circuit studies. Specifically, the inspectors identified that the license
Region: III | Point Beach | 19209 | 09/29/2006 11/16/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative EDG Loading Calculation |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a finding of very low safety significance associated with a violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, Emergency Diesel Generator (EDG) Room exhaust fans, EDG diesel air start compress
Region: III | Point Beach | 19188 | 09/29/2006 11/16/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | Lack of a 4 Hour SBO Coping Duration Heat-Up Calculation for the AFP Rooms |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a finding of very low safety significance associated with a violation of 10 CFR 50.63, "Loss of all Alternating Current Power." Specifically, the licensee never performed a calculation that evaluated the effects of loss of ventil
Region: III | Point Beach | 19222 | 09/29/2006 11/16/2006 | 2006006-04 | NRC | NCV | Mitigating Systems | Green | Condensate Storage Tank Vortexing Calculation Did Not Bound Station Blackout Scenario |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) involving the useable volume in the condensate storage tank (CST). Specifically, the inspectors ide
Region: III | Point Beach | 19223 | 09/29/2006 11/16/2006 | 2006006-05 | NRC | NCV | Mitigating Systems | Green | Unverified Fouling Factor Assumption for Containment Fan Coolers |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The team identified a Green non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, relating to the safety-related Containment Fan Coolers (CFC) for not assuring that the fouling factor inside the tubes was not maintained abov
Region: III | Point Beach | 19224 | 09/29/2006 11/16/2006 | 2006006-06 | NRC | NCV | Mitigating Systems | Green | Reactor Water Storage Tank/Spent Fuel Pool Pipe Support Calculation Deficiencies |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 7111121 | The team identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving a modification that upgraded the Reactor Water Storage Tank/Spent Fuel Pool recirculation loop small bo
Region: III | Point Beach | 19206 | 06/30/2006 07/20/2006 | 2006004-01 | NRC | FIN | Initiating Events | Green | Failure to Take Adequate Actions for Potential High Wind Conditions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.01 | A finding of very low safety significance was identified by the inspectors for failure to control loose materials in the protected area in the vicinity of the main and auxiliary transformers. No violation of NRC requirements occurred. Failure to take acti
Region: III | Point Beach | 19207 | 06/30/2006 07/20/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a 50.59 Evaluation for Compensatory Measures Described in Operability Recommendation |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a Severity Level IV, Non-Cited Violation of 10 CFR 50.59(d)(1) for the licensee's failure to perform an evaluation for compensatory actions taken to maintain the closed function of the emergency core cooling system (ECCS) contain
Region: III | Point Beach | 19208 | 06/30/2006 07/20/2006 | 2006004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain and Implement Adequate Procedures for Control Room Ventilation Testing |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.22 | The inspectors identified a Non-Cited Violation of Technical Specification 5.4.1 for the failure to have adequately established, implemented, and maintained procedures for Technical Specification Surveillance testing of the control room emergency filtrati
Region: III | Point Beach | 19213 | 06/30/2006 07/20/2006 | 2006004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Update and Maintain the Final Safety Analysis Report as Required by 10 CFR 50.71(e) |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a Severity Level IV, Non-Cited Violation of 10 CFR Part 50.71(e) for the self-revealed failure to update the Final Safety Analysis Report (FSAR) to assure that the information in the report was the latest information developed an
Region: III | Point Beach | 19215 | 06/30/2006 07/20/2006 | 2006004-06 | NRC | NCV | MISC | Green | Failure to Perform a 50.59 Evaluation of Increased Design Loads on the Auxiliary Building |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | NONE | The inspectors identified a Severity Level IV, Non-Cited Violation of 10 CFR 50.59(d)(1) for failure to perform a written evaluation of increased design loads on the crane and the auxiliary building. The licensee performed a calculation to demonstrate the
Region: III | Point Beach | 19194 | 03/31/2006 04/17/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Maintain Leak Detection Capability |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) for the failure to maintain the design basis and configuration control for the detection of recirculatio
Region: III | Point Beach | 19197 | 03/31/2006 04/17/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Maintain Safety Function for SI-850 Valves in the Closed Direction |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) for the failure to ensure the safety function of the containment sump isolation valves was maintained an
Region: III | Point Beach | 19198 | 03/31/2006 04/17/2006 | 2006002-03 | NRC | FIN | Initiating Events | Green | Self-Revealed Failure of Unit 1 Circulating Water Pump 1P-30B Due to Indadequate Maintenance |  |  | TE?: N | 05000266 Point Beach 1 |  | 71153 | A finding of very low safety significance was self-revealed when the failure of circulating water (CW) pump 1P-30B and subsequent reactor trip occurred on December 13, 2005. This Green finding with no associated violation was identified for the licensee's
Region: III | Point Beach | 19199 | 03/31/2006 04/17/2006 | 2006002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Address Effects of Elevated Temperatures on Control Room Instruments |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152 | The inspectors identified a non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance (Green) when the licensee failed to consider the effects of elevated control room temperatures on ins
Region: III | Point Beach | 125315 | 07/30/2019 |  |  | LIV |  | Green | Failure to Adequately Control Transient Combustibles |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152
Region: III | Point Beach | 125918 | 11/01/2019 |  |  | LIV |  | Green | Failure to Identify Interrelationships Between Components Required to Achieve and Maintain Nuclear Safety Functions |  |  | TE?: N | 05000266 Point Beach 1 05000301 Point Beach 2 |  | 71152
Region: III | Prairie Island | 125696 | 09/30/2019 11/14/2019 | 2019003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Repair Leaks or Justify and Approve Priority Deviations per the Leak Management Process |  | H.4 - Teamwork | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance (Green) on August 21, 2019, for the licensee's failure to repair, or review, approve and justify priority deviations for approximately fifteen Priority 3 leaks per FP-WM-LMP-01, "Leak Man
Region: III | Prairie Island | 124482 | 03/31/2019 05/01/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Verifying the Auxiliary Feedwater Room Coolers Thermal Performance |  | H.4 - Teamwork | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance (Green) and an associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for
Region: III | Prairie Island | 124736 | 03/31/2019 05/01/2019 | 2019001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Preventive Maintenance Procedure Results in #12 Diesel-Driven Cooling Water Pump Engine Jacket Water Leak |  | H.14 - Conservative Bias | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 | Equipment Performance | 71152 | A Green finding and associated NCV of Technical Specification 5.4, “Procedures,” was self-revealed on December 10, 2018, when the licensee failed to properly implement procedure FP–PE–PM–01, “Preventive Maintenance Program,” to develop a preventive mainte
Region: III | Prairie Island | 124419 | 02/15/2019 03/20/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Valve Inspection Procedure Was Appropriate to Maintain Environmental Qualification of Limitorque Actuators |  | H.12 - Avoid Complacency | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.21N | The inspectors identified a Green finding and an associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee's failure to ensure activities aff
Region: III | Prairie Island | 25974 | 12/31/2018 02/12/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Develop Appropriate Clearance Order Results in Loss of Power to 4kV Bus 25 |  | H.2 - Field Presence | TE?: N | 05000306 Prairie Island 2 | Configuration Control | 71153 | A Green finding and associated NCV of Title 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was self-revealed when the licensee failed to properly develop a Clearance Order (C/O) for modification activities within 4kV sa
Region: III | Prairie Island | 24696 | 08/09/2018 11/14/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain a Preventative Maintenance Strategy for 12 & 22 Cooling Water Pump Diesel Engines |  | NPP | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of Prairie Island Technical Specification 5.4.1, “Procedures,” as of August 9, 2018, for the licensee’s failure to maintain a preventative maintenance strategy
Region: III | Prairie Island | 24673 | 07/18/2018 11/14/2018 | 2018003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Repair a D2 EDG Jacket Water Leak per the Leak Management Program |  | H.3 - Change Management | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance (Green) as of July 18, 2018, for the licensee’s failure to repair a D2 EDG jacket water leak per the Leak Management Program. The inspectors determined that failing to meet the self-
Region: III | Prairie Island | 24338 | 06/21/2018 08/01/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Justify Load Combinations Used in Main Steam Piping Stress Analysis |  | H.6 - Design Margins | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.21M | Inspectors identified a Green finding and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," for the licensee’s failure to correctly translate provisions from specified qual
Region: III | Prairie Island | 24675 | 02/15/2018 11/14/2018 | 2018003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct 21 125 VDC Battery Lid Conditions Adverse to Quality |  | H.14 - Conservative Bias | TE?: N | 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” as of February 15, 2018, for the licensee’s failure to promptly identify and correct conditio
Region: III | Prairie Island | 24674 | 11/28/2017 11/14/2018 | 2018003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Degradation of the 122 DDCLP FOST Vent Piping |  | P.2 - Evaluation | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” as of November 28, 2017, for the licensee’s failure to promptly identify a condition adverse
Region: III | Prairie Island | 21641 | 09/30/2017 11/08/2017 | 2017003-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Ensure Correct Operation of Meteorological Tower |  | P.3 - Resolution | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71124.07 | Green. A finding of very-low safety significance, and an associated Non-Cited Violation of Technical Specification 5.4.1 was identified by the NRC inspectors for the failure to implement and maintain procedures to ensure adequate operation of meteorologic
Region: III | Prairie Island | 22710 | 06/30/2017 08/11/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement the Minor Maintenance Process During Door 225 Transom Maintenance |  | H.4 Teamwork | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | Green. The inspectors identified a finding of very low safety significance (Green) and an associated NCV of TS 5.4.1a, "Procedures," associated with the licensee's failure to properly implement Procedure FP-WM-MMP-01, "Minor Maintenance Process," Revision
Region: III | Prairie Island | 22709 | 06/30/2017 08/11/2017 | 2017002-02 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to Implement the Emergency Plan |  | H.8 Procedure Adherence | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71114.05 | Green: A self-revealed finding, and an associated NCV of Title 10 of the Code of Federal Regulations (10 CFR) 50.54 (q)(2), and 10 CFR 50.47 (b)(5) was identified on August 13, 2016, when after an Unusual Event was declared due to reactor coolant system l
Region: III | Prairie Island | 22704 | 03/31/2017 04/28/2017 | 2017001-01 | NRC | NCVIV | Mitigating Systems | Green | FAILURE TO EVALUATE CHANGES TO NRC APPROVED METHODOLOGY |  |  | TE?: Y SL-IV-NCVIV | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | Severity Level IV/Green. The inspectors identified a Green finding and associated Severity Level IV Violation of 10 CFR 50.59(d)(1), for the licensee's failure to perform a written evaluation which provided the bases for the determination that a change in
Region: III | Prairie Island | 22702 | 11/14/2016 02/14/2017 | 2016004-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO IMPLEMENT A POST-MAINTENANCE TEST PROCEDURE DURING SAFETY INJECTION SYSTEM VALVE TESTING |  | H.4 Teamwork | TE?: N | 05000282 Prairie Island 1 |  | 71111.13 | Green. A finding of very low safety significance was self revealed, and an associated non cited violation (NCV) of TS 5.4.1.a, "Procedures," was identified for the licensee's failure to properly implement surveillance procedure (SP) 1088B, "Train B Safety
Region: III | Prairie Island | 22694 | 06/24/2016 07/21/2016 |  | NRC | NCV | Mitigating Systems | Green | 21 safegaurds diesel exhaust fan connectors not fully engaged or aligned |  |  | TE?: N | 05000306 Prairie Island 2 |  | 71152B | A finding of very low safety significance and associated non-cited violation of Technical Specification Section 5.4.1, "Procedures," was identified by the inspectors for the licensee's failure to ensure the 21 safeguards diesel exhaust fan main contact
Region: III | Prairie Island | 22700 | 06/24/2016 07/21/2016 |  | NRC | NCV | Mitigating Systems | Green | Failure to perform required operability evaluations |  | P.2 Evaluation | TE?: N | 05000306 Prairie Island 2 |  | 71152B | A finding of very low safety significance with two examples and an associated non-cited violation of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspector
Region: III | Prairie Island | 22693 | 02/12/2016 03/11/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Cold Shutdown Repair Procedure (Section 1R05.9b) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | The inspectors identified a finding of very-low safety significance (Green), and an associated Non-Cited Violation of Technical Specifications Section 5.4.1.d for the licensee's failure to maintain Procedure F5 Appendix B. Specifically, the licensee faile
Region: III | Prairie Island | 22272 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Failure to Meet ANSI N14.6 Section 5.3.1 Requirements |  | H.1 Resources | TE?: N | 05000306 Prairie Island 2 |  | 71111.08P | Green. Inspectors identified a finding of very low safety significance (Green), and an associated NCV of Title 10, Code of Federal Regulations, Part 50, Appendix B, Criteria III, "Design Control," for the licensee's failure to incorporate the American Nat
Region: III | Prairie Island | 22692 | 12/31/2015 02/11/2016 | 2015004-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately Calibrate Liquid Effluent Monitors |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71124.05 | Green. The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation (NCV) of TS 5.5.1.a for the failure to comply with the Offsite Dose Calculation Manual (ODCM) for not using calibration sources which wer
Region: III | Prairie Island | 22703 | 11/30/2015 02/14/2017 | 2016004-02 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO ADEQUATELY CALIBRATE AN ELECTROMETER |  | H.11 Challenge the Unknown | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71124.05 | Green. A finding of very-low safety significance, and an associated NCV of Title 10 of the Code of Federal Regulations (CFR) 20.1501(c) was identified by the inspectors for the failure to adequately calibrate the electrometer utilized in the validation of
Region: III | Prairie Island | 22262 | 11/24/2015 01/05/2016 | 2015008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Correct an NCV Associated with Inadequate Gas Monitoring of Inaccessible RHR Gas Susceptible Locations |  | P.2 Evaluation | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green), and an associated cited violation of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to correct a co
Region: III | Prairie Island | 22263 | 11/24/2015 01/05/2016 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Manage Gas Accumulation at the RHR Train Credited for Emergency Core Cooling in MODE 4 (Section 4OA2.1.c(2)) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to manage gas accumulation at the re
Region: III | Prairie Island | 22264 | 11/24/2015 01/05/2016 | 2015008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Procedures to Verify RHR is Full of Water Following Maintenance Outages (Section 4OA2.1.c(3)) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | Green. A finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the licensee's failure to establish procedures to verify RHR is ope
Region: III | Prairie Island | 22270 | 11/24/2015 01/05/2016 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Manage Potential Gas Accumulation Due to SI Isolation Check Valve Leakage Following Maintenance Outages (Section 4OA2.1.c(4)) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green), and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to manage potential gas accumulation due to safety injecti
Region: III | Prairie Island | 22271 | 11/24/2015 01/05/2016 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Continuous Gas Intrusion into RHR (Section 4OA2.1.c(5)) |  | H.12 Avoid Complacency | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | Green. The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify a continuous gas intrusion into one train of RH
Region: III | Prairie Island | 22253 | 09/30/2015 11/06/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DETERMINE COMPENSATORY MEASURES. |  | H.13 Consistent Process | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | A finding of very low safety significance with two examples and an associated non-cited violation of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors
Region: III | Prairie Island | 22254 | 09/30/2015 11/06/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | IMPROPER OPERABILITY DETERMINATION. |  | H.11 Challenge the Unknown | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of Title 10, CFR, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to accomplish the req
Region: III | Prairie Island | 22247 | 09/04/2015 10/14/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | 4160 Vac Switchgear Preventive Maintenance Procedure Failed to Provide Adequate Resistance Values and Acceptance Criteria (Section 1R21.3.b(1)) |  | H.1 Resources | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | Green. The team identified a finding of very low safety significance, and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to have an acceptance criteria for el
Region: III | Prairie Island | 22248 | 09/04/2015 10/14/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations for Motor-Operated Valve Thermal Overload Relays (Section 1R21.3.b(2)) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | Green. The team identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure the safety-related thermal overload relay heaters were properl
Region: III | Prairie Island | 22249 | 09/04/2015 10/14/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Replacement Containment Fan Cooling Unit Component Not Designed in Accordance with ASME Section III (Section 1R21.5.b(1)) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | Green. The team identified a finding of very low safety significance, and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to design all components of the replacement Containment Fan Coil Units i
Region: III | Prairie Island | 22233 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | #12 BATTERY CHARGER DESIGN CONTROL. |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the design requirements of the #12 battery charger were ma
Region: III | Prairie Island | 22239 | 06/30/2015 08/05/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECT #12 BATTERY NONCONFORMANCE. |  | P.3 Resolution | TE?: N | 05000282 Prairie Island 1 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct a condition adverse to quality. Specifically, the l
Region: III | Prairie Island | 22241 | 06/30/2015 08/05/2015 | 2015002-04 | NRC | NCV | Mitigating Systems | Green | DESIGN CONTROL MEASURES NOT IMPLEMENTED TO ENSURE GROUP E PRESSURIZER HEATERS REMAIN OPERATIONAL POST-FIRE. |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," on October 13, 2014, for the licensee's failure to ensure the design requirements of the fire protect
Region: III | Prairie Island | 22225 | 03/31/2015 05/06/2015 | 2015001-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM IMMEDIATE OPERABILITY DETERMINATION FOR 14 CFCU AS REQUIRED BY PROCEDURE. |  | H.4 Teamwork | TE?: N | 05000306 Prairie Island 2 |  | 71111.15 | An inspector identified finding of very low safety significance and a NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," occurred on January 27, 2015, due to operations personnel failing to follow Procedure FP-OP-OL-01
Region: III | Prairie Island | 22231 | 03/31/2015 05/06/2015 | 2015001-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW FOREIGN MATERIAL EXCLUSION PROCEDURE DURING REACTOR COOLANT PUMP SEAL REPLACEMENT. |  | H.5 Work Management | TE?: N | 05000282 Prairie Island 1 |  | 71111.2 | A self-revealing finding of very low safety significance and associated NCV of TS 5.4.1 was identified on December 19, 2014, due to the licensee's failure to follow Procedure FP-MA-FME-01, "Foreign Material Exclusion and Control." Specifically, workers fa
Region: III | Prairie Island | 22232 | 03/31/2015 05/06/2015 | 2015001-03 | Self - Revealed | NCV | Initiating Events | Green | UNTIMELY RESOLUTION OF ENVIRONMENTAL QUALIFICATION ISSUES. |  | P.2 Evaluation | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A self-revealing finding of very low safety-significance and a non-cited violation of 10 CFR 50.49 was identified on March 5, 2015, for the licensee's failure to keep environmental qualification (EQ) files current and the failure to replace or refurbish E
Region: III | Prairie Island | 22217 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Winter Plant Operation Procedure |  | H.14 Conservative Bias | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," on December 4, 2014, due to the licensee's failure to follow procedure during the performanc
Region: III | Prairie Island | 22223 | 12/31/2014 01/29/2015 | 2014005-02 | NRC | NCV | Initiating Events | Green | Unqualified Reactor Vessel Examination Procedures |  | H.2 Field Presence | TE?: N | 05000282 Prairie Island 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes," on October 21, 2014, due to the licensee's failure to perform the reactor vessel weld ultrasonic exa
Region: III | Prairie Island | 22224 | 12/31/2014 01/29/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures during Emergency Diesel Generator 24 Hour Load Test |  | H.12 Avoid Complacency | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," on September 29, 2014, due to the licensee's failure to follow procedure during the performa
Region: III | Prairie Island | 22209 | 09/30/2014 11/04/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM OPERABILITY DETERMINATION AS REQUIRED BY PROCEDURE. |  | H.4 Teamwork | TE?: N | 05000306 Prairie Island 2 |  | 71111.15 | An inspector identified finding of very low safety significance and a NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings, occurred on August 31, 2014, due to the failure to follow Procedure FP-OP-OL-01, "Operability Determ
Region: III | Prairie Island | 22213 | 09/30/2014 11/04/2014 | 2014004-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO HAVE ADEQUATE PROCEDURES TO ADDRESS LOW BUS VOLTAGE CONDITIONS. |  | H.1 Resources | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self-revealing finding and a NCV of Technical Specification 5.4.1 was identified on June 23, 2014, due to the failure to establish, implement and maintain the applicable procedures to address degraded power sources as recommended in Section 6 of Regulat
Region: III | Prairie Island | 22214 | 09/30/2014 11/04/2014 | 2014004-03 | Self - Revealed | NCV | Mitigating Systems | Green | D1 EDG REVERSE POWER TRIP. |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self-revealing finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified on June 23, 2014, due to the failure to properly implement Procedure 1C20.7, "D1/D2 Dies
Region: III | Prairie Island | 22204 | 06/30/2014 08/11/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IDENTIFY 23 FCU LEAK AS A CONDITION ADVERSE TO QUALITY. |  | H.12 Avoid Complacency | TE?: N | 05000306 Prairie Island 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," on May 18, 2014, due to the licensee's failure to promptly identify a leak on the 23 containm
Region: III | Prairie Island | 22206 | 06/30/2014 08/11/2014 | 2014003-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IDENTIFY 21 FCU SPACER ALIGNMENT OFFSET AS A CONDITION ADVERSE TO QUALITY. |  | H.7 Documentation | TE?: N | 05000306 Prairie Island 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," on May 20, 2014, due to the licensee's failure to promptly identify a spacer alignment offset
Region: III | Prairie Island | 22207 | 06/30/2014 08/11/2014 | 2014003-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW SAFETY TAGGING PROCEDURE RESULTS IN UNIT 2 POWER CHANGE. |  | H.12 Avoid Complacency | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self-revealing finding of very low safety significance and associated non-cited violation Technical Specification 5.4.1 was identified on June 22, 2014, due to the licensee's failure to implement Step 5.5.2.1 of Procedure FP-OP-TAG-01, "Fleet Tagging."
Region: III | Prairie Island | 22187 | 06/27/2014 08/06/2014 | 2014007-01 | NRC | NCV | MISC | Green | FAILURE TO IMPLEMENT THE CAP ACTION REQUEST PROCESS PROCEDURE. |  | P.1 Identification | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low safety significance and non-cited violation of Title 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to accomplish FP-PA-ARP-01, "CAP Action Request Pr
Region: III | Prairie Island | 22192 | 06/27/2014 08/06/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE FOR IDENTIFICATION OF SIGNIFICANT CONDITIONS ADVERSE TO QUALITY. |  | P.6 Self Assessment | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low safety significance and non-cited violation of Title 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to prescribe a procedure appropriate to the circum
Region: III | Prairie Island | 22193 | 06/27/2014 08/06/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE PAST OPERABILITY AND REPORTABILITY OF THE COOLING WATER SYSTEM. |  | H.13 Consistent Process | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low safety significance and non-cited violation of Title 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to accomplish FP-PA-ARP-01, "CAP Action Request Pr
Region: III | Prairie Island | 22202 | 06/27/2014 08/06/2014 | 2014007-04 | NRC | NCVIV | Initiating Events | Green | FAILURE TO UPDATE THE UFSAR FOR PRESSURE ISOLATION VALVES. |  | H.7 Documentation | TE?: Y SL-IV-NCVIV | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a Severity Level IV NCV of Title 10 CFR 50.71(e), "Periodic Update of the Final Safety Analysis Report," and an associated Green finding for the licensee's failure to update the Updated Safety Analysis Report (USAR) with a comple
Region: III | Prairie Island | 22203 | 06/27/2014 08/06/2014 | 2014007-05 | NRC | NCV | MISC | Green | FAILURE TO FOLLOW PROCEDURES FOR CANCELLING NON-CAP ACTION ASSIGNMENTS. |  | P.3 Resolution | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low safety significance and non-cited violation of Title 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures and Drawings for the failure to accomplish Attachment 14, "CAP to External Process Interface,
Region: III | Prairie Island | 22186 | 05/02/2014 06/11/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | No Compensatory Measure were Established for Lack of Fuses Coordination Associated with Safe Shutdown Power Supplies. |  | H.8 Procedure Adherence | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and associated NCV of the Prairie Island Nuclear Generating Plant Facility Operating License Condition 2.C.(4) for the licensee's failure to implement the requirements as specified in the
Region: III | Prairie Island | 22185 | 03/31/2014 05/05/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT THE SCAFFOLDING, LADDERS AND CABLE TRAYS PLATFORMS PROCEDURE. |  | H.14 Conservative Bias | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," on February 13, 2014, due to the failure to construct scaffolds as requir
Region: III | Prairie Island | 22175 | 01/16/2014 02/27/2014 | 2013011-01 | NRC | NCV | Barrier Integrity | Green | Steam Generator Blowdown (SGBD) Pipe Support Anchorages Failure to Meet Design Requirements |  | H.7 Documentation | TE?: N | 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for the failure to provide adequate design control measures for the
Region: III | Prairie Island | 22176 | 01/16/2014 02/27/2014 | 2013011-02 | NRC | FIN | Initiating Events | Green | Outside Lift System (OlS) Girder Failure to Meet American Institute of Steel Construction (AISC) Requirements |  | H.6 Design Margins | TE?: N | 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) involving the licensee's failure to meet the requirements of the American Institute of Steel Construction (AISC) specification. Specifically, the licensee did not use the specifie
Region: III | Prairie Island | 22180 | 01/16/2014 02/27/2014 | 2013011-03 | NRC | NCV | Initiating Events | Green | Steam Generator Blowdown (SGBD) Pipe Support Anchorages Failure to Meet Design Requirements |  |  | TE?: N | 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) involving the licensee's failure to meet the requirements of the American Institute of Steel Construction (AISC) specification. Specifically, the licensee did not use the specifie
Region: III | Prairie Island | 22181 | 01/16/2014 02/27/2014 | 2013011-04 | NRC | FIN | Barrier Integrity | Green | Outside Lift System (OLS) Girder Failure to Meet American Institute of Steel Construction (AISC) Requirements |  |  | TE?: N | 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and associated NCV of Title 10 of the Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," for the failure to provide adequate design control measures for the
Region: III | Prairie Island | 22169 | 12/31/2013 02/12/2014 | 2013005-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO EVALUATE CORROSIVE EFFECTS OF BORIC ACID ON THE 22 RESIDUAL HEAT REMOVAL PUMP. |  | H.14 Conservative Bias | TE?: N | 05000306 Prairie Island 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance on October 7, 2013, due to the failure to perform an adequate boric acid evaluation in accordance with Procedure H2, "Boric Acid Corrosion Control Program." Specifically, the licensee fai
Region: III | Prairie Island | 22170 | 12/31/2013 02/12/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH APPROPRIATE DESIGN CONTROL MEASURES FOR SELECTION OF REPLACEMENT PARTS. |  | H.7 Documentation | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," on October 8, 2013, due to the failure to establish measures for the selection of parts that are essential to th
Region: III | Prairie Island | 22174 | 12/31/2013 02/12/2014 | 2013005-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT CONDITION ADVERSE TO QUALITY ON D1 EDG. |  | P.2 Evaluation | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | A self-revealing finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified on October 15, 2013, due to the failure to correct a condition adverse to quality. Specifically,
Region: III | Prairie Island | 22162 | 09/30/2013 11/18/2013 | 2013004-01 | Self - Revealed | NCV | Mitigating Systems | Green | IMPROPER WORK INSTRUCTIONS RENDERED 2R-49 INOPERABLE. |  | H.5 Work Management | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.12 | A self-revealing finding of very low safety significance (Green) and an non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified on July 2, 2013, for the failure to have documented instr
Region: III | Prairie Island | 22163 | 09/30/2013 11/18/2013 | 2013004-02 | Self - Revealed | NCV | Mitigating Systems | Green | IMPROPER WORK INSTRUCTIONS RENDERED REACTOR PROTECTION INSTRUMENT AC INVERTER 13 INOPERABLE. |  | H.5 Work Management | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.12 | A self-revealing finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified on July 24, 2013, for the failure to have documented instructions, procedures,
Region: III | Prairie Island | 22167 | 09/30/2013 11/18/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY ASSESS D6 EDG OPERABILITY. |  | H.14 Conservative Bias | TE?: N | 05000306 Prairie Island 2 |  | 71111.15 | An inspector-identified finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures or Drawings," was identified on August 15, 2013, due to the licensee's failure to follow Procedure FP
Region: III | Prairie Island | 22168 | 09/30/2013 11/18/2013 | 2013004-04 | NRC | NCV | Mitigating Systems | Green | INAPPROPRIATE REMOVAL OF DIESEL LUBE OIL VALVE MOUNTING CAUSES VIBRATION AND FRETTING. |  | H.2 Field Presence | TE?: N | 05000282 Prairie Island 1 |  | 71111.19 | An inspector identified finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified on August 26, 2013, due to the licensee's failure to follow Procedure F
Region: III | Prairie Island | 22153 | 06/30/2013 07/30/2013 | 2013003-01 | Self - Revealed | NCV | Mitigating Systems | Green | IMPROPER WORK INSTRUCTIONS RENDERED D1 EDG INOPERABLE. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 |  | 71111.12 | A self-revealing finding of very low safety significance (Green) and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings" was identified on June 13, 2013, due to the failure to have drawings appropriate to the circums
Region: III | Prairie Island | 22160 | 06/30/2013 07/30/2013 | 2013003-02 | NRC | VIO | Mitigating Systems | Green | FAILURE TO MONITOR SSCs AS REQUIRED BY 10 CFR 50.65. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) and a violation of 10 CFR 50.65, due to the failure to demonstrate that the performance or condition of multiple SSCs was being effectively controlled through the performance of a
Region: III | Prairie Island | 22144 | 04/19/2013 05/22/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Cooling Water System Design. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly model the effects of the strainers and isolation valves in the cooling wate
Region: III | Prairie Island | 22151 | 04/19/2013 05/22/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Review the Suitability of the CL Strainers Under Post seismic Flow Conditions. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.07T | TThe inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to review the suitability of the cooling water strainers under post seismic flow condit
Region: III | Prairie Island | 22152 | 04/19/2013 05/22/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate the Ability to Transfer Diesel Fuel Oil Between Unit 1 Fuel Oil Tanks. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to demonstrate the ability to transfer diesel fuel oil from any Unit 1 fuel oil storage tan
Region: III | Prairie Island | 22135 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY SECURE MATERIALS NEAR CRITICAL DRAINAGE PATH. |  | H.3(b) Work Activity Coordination | TE?: N | 05000306 Prairie Island 2 |  | 71111.06 | The inspectors identified a finding of very low safety significance and an non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," on February 4, 2013, due to the licensee's failure to follow procedures
Region: III | Prairie Island | 22138 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | IMPROPERLY SIZED MOTOR OVERLOAD HEATERS RENDER D6 EDG INOPERABLE. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000306 Prairie Island 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an non-citied violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to establish measures for the selection and review for suitability of applicati
Region: III | Prairie Island | 21861 | 03/31/2013 05/14/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECT CONDITION ADVERSE TO QUALITY FOR VALVE SI-6-4. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | The inspectors identified a finding of very low safety significance and an non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," on December 29, 2012, due to the failure to correct a condition adverse to quality. Specific
Region: III | Prairie Island | 22136 | 03/31/2013 05/14/2013 | 2013002-04 | Self - Revealed | UNKN | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURE DURING FUSE REMOVAL ACTIVITIES. |  | H.4(a) Human Error Prevention | TE?: N | 05000306 Prairie Island 2 |  | 71111.22 | A self-revealed finding of very low safety significance and an non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred on March 19, 2013, due to the licensee's failure to follow Procedure 5AWI 3.
Region: III | Prairie Island | 22137 | 03/31/2013 05/14/2013 | 2013002-05 | NRC | NCV | Mitigating Systems | Green | INADEQUATE WORK INSTRUCTIONS FOR FOREIGN MATERIAL REMOVAL FROM D2 EDG AIR START PIPING. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | The inspectors identified finding of very low safety significance and an non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," on January 28, 2013, due to the failure to have instructions appropriate to
Region: III | Prairie Island | 22139 | 03/31/2013 05/14/2013 | 2013002-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PROVIDE ACCURATE PERFORMANCE INDICATOR DATA. |  | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71151 | The inspectors identified a Severity Level IV non-citied violation of 10 CFR Part 50.9, "Completeness and Accuracy of Information," and an associated finding of very low safety significance (Green) due to the licensee's failure to provide information to
Region: III | Prairie Island | 22140 | 03/31/2013 05/14/2013 | 2013002-07 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE ACCURATE PERFORMANCE INDICATOR DATA. |  | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71151 | The inspectors identified a Severity Level IV non-citied violation of 10 CFR Part 50.9, "Completeness and Accuracy of Information," and an associated finding of very low safety significance (Green) due to the licensee's failure to provide information to
Region: III | Prairie Island | 22141 | 03/31/2013 05/14/2013 | 2013002-08 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECT CONDITION ADVERSE TO QUALITY ON THE D1 EDG. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 |  | 71153 | The inspectors identified a finding of very low safety significance and an non-citied violation of 10 CFR Part 50, Appendix B, Criterion XVI, on August 14, 2012, due to the licensee's failure to identify and correct a condition adverse to quality. Specifi
Region: III | Prairie Island | 22131 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | FAILURE OF SEASONAL READINESS PROCEDURE TO IDENTIFY OPERABILITY ISSUES. |  | H.3(b) Work Activity Coordination | TE?: N | 05000282 Prairie Island 1 |  | 71111.01 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, on June 26, 2012, due to the licensee's failure to have procedures appropriate to the circumstance for coordinating and preparing fo
Region: III | Prairie Island | 22128 | 12/31/2012 02/07/2013 | 2012005-02 | NRC | NCV | Initiating Events | Green | FAILURE TO DISPOSITION A RELEVANT SNUBBER INDICATION IN ACCORNANCE WITH THE ASME CODE. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 71111.08P | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR50.55a(g)(4) on November 13, 2012, due to the licensee's failure to disposition a relevant indication on a common steam generator snubber reservoir in accordance with t
Region: III | Prairie Island | 22129 | 12/31/2012 02/07/2013 | 2012005-03 | NRC | FIN | Initiating Events | Green | INADEQUATE EVALUATION OF OPERATING CREW DURING ANNUAL REQUALIFICATION EXAMINATION. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.11Q | The inspectors identified a finding of very low safety significance on October 6, 2012, due to the failure to properly evaluate an operating crew's annual requalification examination performance in accordance with Procedure FP T SAT 73, "Licensed Operator
Region: III | Prairie Island | 22130 | 12/31/2012 02/07/2013 | 2012005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO REPLACE RUBBER HOSES ON D5 AND D6 IN ACCORDANCE WITH VENDOR RECOMMENDATION. |  |  | TE?: N | 05000306 Prairie Island 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," due to the licensee's failure to implement vendor recommendations to replace rubber hoses on the emergency diese
Region: III | Prairie Island | 22132 | 12/31/2012 02/07/2013 | 2012005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DEMONSTRATE PERFORMANCE OR CONDITION OF RADIATION MONITORS WERE EFFECTIVELY CONTROLLED THROUGH THE PERFOMANCE OF MAINTENANCE. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.12 | A finding of very low safety significance and an NCV of 10 CFR 50.65 was identified by the inspectors on August 22, 2012, due to the licensee's failure to demonstrate that the performance or condition of the radiation monitoring system was being effective
Region: III | Prairie Island | 22126 | 09/30/2012 11/05/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE PAST OPERABILITY EVALUATIONS AFTER DISCOVERING DEGRADED COMPONENT COOLING HEAT EXCHANGERS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000306 Prairie Island 2 |  | 71111.07T | The inspectors identified a finding of very low safety significance and an associated non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately verify the adequacy of the design of systems need
Region: III | Prairie Island | 22115 | 06/30/2012 08/09/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY ASSESS AND MANAGE RISK |  | H.3(a) Work Planning | TE?: N | 05000306 Prairie Island 2 |  | 71111.13 | A finding of very low safety significance and a non-cited violation (NCV) of 10CFR 50.65(a)(4) was identified by the inspectors due to the licensee's failure to properly assess plant risk upon obtaining information which challenged the continued availabil
Region: III | Prairie Island | 22121 | 06/30/2012 08/09/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAKE A 60 DAY REPORT PURSUANT TO 10 CFR 50.73 |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | The inspectors identified a Severity Level IV non-cited violation (NCV) of 10 CFR 50.73(a)(2) due to the failure to report required plant events or conditions within 60 days of discovery of the event. Specifically, the licensee failed to report that the U
Region: III | Prairie Island | 22123 | 06/30/2012 08/09/2012 | 2012003-03 | NRC | FIN | Mitigating Systems | Green | FAILURE TO MAKE A 60 DAY REPORT PURSUANT TO 10 CFR 50.73 |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | In accordance with the Enforcement Policy, this violation was classified as a Severity Level IV violation because the underlying technical issue was of very low risk significance. Because this issue was of a very low safety significance, was not repetitiv
Region: III | Prairie Island | 22114 | 06/30/2012 08/09/2012 | 2012003-04 | Self - Revealed | NCV | Initiating Events | Green | UNIT 2 REACTOR TRIP DUE TO OPERATION OF LOW PRESSURE TURBINE OUTSIDE ITS DESIGN. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance and a non cited violation (NCV) of Technical Specification (TS) 5.4.1 occurred on February 21, 2012 due the licensee's failure to establish, implement and maintain procedures regarding power operatio
Region: III | Prairie Island | 22124 | 05/30/2012 09/20/2012 | 2012011-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO TAKE CORRECTIVE ACTION FOR REACTOR COOLANT SYSTEM LEVEL INDICATION ISSUES. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | An inspector-identified finding of very low safety significance was identified due to the failure to take corrective action for a Condition Adverse to Quality. The inspectors determined that the failure to correct for the loss of reactor coolant system (R
Region: III | Prairie Island | 21795 | 05/30/2012 09/20/2012 | 2012011-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO UPDATE THE CALCULATIONS FOR STEAM GENERATOR DRAINING. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | An inspector-identified finding of very low safety significance and an NCV of 10 CFR 50, Appendix B, Criterion III, was identified due to the licensee's failure to update engineering calculations for the amount of nitrogen to be used during steam generato
Region: III | Prairie Island | 22125 | 05/30/2012 09/20/2012 | 2012011-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURE FOR DRAINING OF REACTOR COOLANT SYSTEM. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | An inspector-identified finding of very low safety significance and a non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, was identified due to the licensee's use of an inadequate procedure during draining of the RCS. The inspectors determine
Region: III | Prairie Island | 22107 | 03/31/2012 05/14/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE THREE HOUR FIRE BARRIER BETWEEN BUS 26 AND BUS 27 ROOMS |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71111.05Q | A finding of very low safety significance and an NCV of Condition 2.C.4 of the Unit 2 operating license was identified by the inspectors on November 8, 2011, due to the failure to implement and maintain in effect all provisions of the approved fire protec
Region: III | Prairie Island | 22090 | 03/31/2012 05/14/2012 | 2012002-02 | Self - Revealed | NCV | Initiating Events | Green | BREAKER 212E-44 FAILURE DUE TO LACK OF PREVENTIVE MAINTENANCE |  | H.3(b) Work Activity Coordination | TE?: N | 05000306 Prairie Island 2 |  | 71111.12 | A self revealed finding of very low safety significance and an NCV of Technical Specification (TS) 5.4.1 occurred on January 19, 2012, due to the safety related breaker for the 21 reactor vessel gap cooling fan failing while in service. Specifically, prev
Region: III | Prairie Island | 22098 | 03/31/2012 05/14/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROPERLY ASSESS OPERABILITY OF D2 EMERGENCY DIESEL GENERATOR FOLLOWING SURVEILLANCE TESTING |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | A finding of very low safety significance and an NCV of TS 3.8.1 was identified by the inspectors on February 23, 2012, due to the licensee's failure to properly assess the continued operability of the D2 emergency diesel generator (EDG) following monthly
Region: III | Prairie Island | 22099 | 03/31/2012 05/14/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ASSESS OPERABILITY OF CIRCUIT BREAKERS DUE TO INADEQUATE LUBRICATION |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, on January 19, 2012, due to the licensee's failure to properly assess information contained in the Corrective Action Program (CAP) d
Region: III | Prairie Island | 22108 | 03/31/2012 05/14/2012 | 2012002-05 | NRC | NCV | Mitigating Systems | Green | INADEQUATE OPERATIONAL LOG ENTRIES |  | H.4(a) Human Error Prevention | TE?: N | 05000282 Prairie Island 1 |  | 71152 | A finding of very low safety significance and an NCV of TS 5.4.1 was identified by the inspectors between February 23 and March 27, 2012, due to the licensee's failure to maintain the control room narrative logs as required by Procedure FP OP COO 19, "Log
Region: III | Prairie Island | 22100 | 03/31/2012 05/14/2012 | 2012002-06 | NRC | FIN | Mitigating Systems | Green | FAILURE TO IMPLEMENT PROCEDURE USE AND ADHERENCE REQUIREMENTS WHILE DRAINING SODIUM HYPOCHLORITE DRAW DOWN TANK |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A finding of very low safety significance was self revealed on January 7, 2012, due to chemistry personnel failing to comply with requirements contained in Procedure FP G DOC 03, "Procedure Use and Adherence," prior to draining the sodium hypochlorite dra
Region: III | Prairie Island | 22104 | 03/31/2012 05/14/2012 | 2012002-07 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO TIMELY ACTIVATE ERDS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A self revealed finding of very low safety significance and an NCV of 10 CFR 50.72(a)(4) was identified on January 7, 2012, due to the licensee's failure to activate the Emergency Response Data System (ERDS) within one hour of an Alert declaration. Specif
Region: III | Prairie Island | 22101 | 03/31/2012 05/14/2012 | 2012002-08 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO TIMELY AUGMENT ON-SHIFT STAFF |  | H.1(c) Communication of Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance and an NCV of 10 CFR 50.54(q) was identified on January 7, 2012, due to the licensee's failure to follow and maintain their emergency plan in effect. The inspectors identified that the licensee's Eme
Region: III | Prairie Island | 22087 | 12/31/2011 02/01/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Complete Immediate Operability Determination on Molded Case Circuit Breakers |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified by the inspectors due to the licensee's failure to complete an immediate operability determination as required by Procedure FP OP OL
Region: III | Prairie Island | 22081 | 11/18/2011 12/15/2011 | 2011012-01 | NRC | NCV | Initiating Events | Green | Flammable Gas Bottles Installed and/or Stored in the Auxiliary Building |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of Title 10, Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to check the adequacy of design for
Region: III | Prairie Island | 22086 | 11/18/2011 12/15/2011 | 2011012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.17T | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct a condition adverse to quality. Specifically, the l
Region: III | Prairie Island | 21888 | 09/30/2011 10/23/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | RADIATION MONITORS NOT FULLY SCOPED INTO OR ASSESSED BY THE MAINTENANCE RULE PROGRAM. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.12 | The inspectors identified a finding of very low safety significance and a NCV of 10 CFR 50.65 due to the licensee's failure to demonstrate that the performance or condition of the Unit 1 and Unit 2 radiation monitors was effectively controlled through the
Region: III | Prairie Island | 21889 | 09/30/2011 10/23/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | CORRECTIVE ACTION ASSIGNMENTS CLOSED WITHOUT COMPLETION OF TASKS. |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," due to the licensee's failure to close corrective action assignments in accordance with pr
Region: III | Prairie Island | 22072 | 09/30/2011 10/23/2011 | 2011004-04 | NRC | FIN | Initiating Events | Green | FAILURE TO MAKE EIGHT HOUR REPORT PURSUANT TO 10 CFR 50.72. Finding. |  | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71153 | The inspectors identified a finding associated with the Severity Level IV NCV of 10 CFR 50.72(b)(3)(v)(D) for the licensee's failure to report an event or condition that could have prevented the fulfillment of a safety function to the NRC within 8 hours.
Region: III | Prairie Island | 22078 | 09/30/2011 10/23/2011 | 2011004-05 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PROVIDE COMPLETE AND ACCURATE INFORMATION IN A LICENSEE EVENT REPORT |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | The inspectors identified a Severity Level IV NCV of 10 CFR 50.9 due to the licensee's failure to provide information to the NRC that was complete and accurate in all material respects. Specifically, Licensee Event Report (LER) 05000282/2011-001-00; 05000
Region: III | Prairie Island | 22079 | 09/30/2011 10/23/2011 | 2011004-06 | Self - Revealed | FIN | Initiating Events | Green | UNIT 2 REACTOR TRIP DUE TO MIS-OPERATION OF SUBSTATION BREAKERS |  | P.2(b) Implementing Operating Experience | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance was identified by the inspectors due to personnel incorrectly implementing Procedure FP-G-DOC-03, "Procedure Use and Adherence." Specifically, maintenance personnel failed to adequately review, ident
Region: III | Prairie Island | 21871 | 06/30/2011 08/01/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | EVALUATION OF EQUIPMENT STORED NEAR SAFETY-RELATED EQUIPMENT. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.04Q | A finding of very low safety significance and a NCV of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," was identified by the inspectors on February 17, 2011, due to the licensee's failure to maintain quality records in accordance
Region: III | Prairie Island | 21867 | 06/30/2011 08/01/2011 | 2011003-02 | NRC | NCV | Initiating Events | Green | FAILURE TO MAINTAIN REACTOR HEAD HEIGHT/DISTANCE LIMITATION FROM REACTOR VESSEL. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000282 Prairie Island 1 |  | 71111.2 | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified by the inspectors on May 23, 2011, due to the licensee's failure to follow Procedure D58.1.10 "Unit 1-Reactor Vessel Head Replacemen
Region: III | Prairie Island | 21868 | 06/30/2011 08/01/2011 | 2011003-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO ASSESS THE IMPACT OF CHANGES IN THE PLANT'S ISOTOPIC PROFILE. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71124.05 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 20.1501.b due to the licensee's failure to evaluate the impact of changes in the isotopic profile (i.e., changes in the isotopic mix and percent abundance
Region: III | Prairie Island | 21872 | 06/30/2011 08/01/2011 | 2011003-04 | NRC | NCV | Barrier Integrity | Green | NO FULL FLOW TESTING OF PORV AIR SUPPLY CHECK VALVES. |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | A finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified by the inspectors for the failure to assure that all testing required to demonstrate the check valves installed as
Region: III | Prairie Island | 21873 | 06/30/2011 08/01/2011 | 2011003-05 | NRC | NCV | Mitigating Systems | Green | GL 2008-01 EVALUATIONS DID NOT ADEQUATELY VERIFY THE DESIGN FOR SUSCEPTIBLE LOCATIONS OF GAS ACCUMULATION IN PIPING SYSTEMS. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately review the design of emergency core cooling, decay heat removal, and co
Region: III | Prairie Island | 21880 | 06/30/2011 08/01/2011 | 2011003-06 | NRC | NCV | Barrier Integrity | Green | FAILURE TO EVALUTE THE EFFECTS OF DYNAMIC LOADS AT THE CS DISCHARGE PIPING. |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to evaluate the effects of dynamic loads at the containment spray discharge piping. S
Region: III | Prairie Island | 21881 | 06/30/2011 08/01/2011 | 2011003-07 | NRC | NCV | Mitigating Systems | Green | ALTERNATE METHODS WERE NOT DEVELOPED FOR MONITORING INACCESSIBLE SUSCEPTIBLE LOCATIONS. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to follow Procedure H64, "Gas Accumulation Management Program."
Region: III | Prairie Island | 21882 | 06/30/2011 08/01/2011 | 2011003-08 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PRESCRIBE APPROPRIATE PROCEDURE FOR IN-SERVICE TESTING OF CHECK VALVES. |  | H.3(b) Work Activity Coordination | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to develop appropriate procedures when performing in-service tes
Region: III | Prairie Island | 21887 | 05/20/2011 08/17/2011 | 2011011-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT THE TRAIN A AND THAIN B DC ELECTRICAL POWER SUBSYSTEMS REMAINED OPERABLE IN MODES 1 THROUGH 4. |  |  | TE?: N | 05000306 Prairie Island 2 |  | NONE | A Non-Cited Violation (NCV) of Technical Specification (TS) 3.8.4 was identified by the inspectors due to the licensee's failure to maintain the train A and train B direct current electrical power subsystems operable while operating the reactor in Modes 1
Region: III | Prairie Island | 21849 | 04/15/2011 05/02/2011 | 2011002-01 | NRC | NCV | Initiating Events | Green | FLAMMABLE GAS CYLINDER STORED IN SAFETY-RELATED AREA. |  | H.3(b) Work Activity Coordination | TE?: N | 05000306 Prairie Island 2 |  | 71111.04Q | An inspector-identified finding of very low safety significance and a non cited violation (NCV) of Technical Specification 5.4.1 was identified on February 8, 2011, due to the licensee's failure to establish, implement, and maintain procedures for the fir
Region: III | Prairie Island | 21850 | 04/15/2011 05/02/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO APPROPRIATELY COMPLETE AN OPERABILITY RECOMMENDATION FOR THE UNIT 1 BATTERY CALCULATIONS. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | An inspector identified finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified on February 9, 2011, due to the failure to follow Procedure FP OP OL 01. Specifically, the licensee did not complete an i
Region: III | Prairie Island | 21857 | 04/15/2011 05/02/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO APPROPRIATELY COMPLETE AN OPERABILITY RECOMMENDATION ON THE UNIT 1 FUEL OIL SYSTEM. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | An inspector-identified finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified due to the failure to properly complete an operability recommendation for the Unit 1 fuel oil system in accordance with P
Region: III | Prairie Island | 21860 | 04/07/2011 05/26/2011 | 2011502-02 | NRC | FIN | Emergency Preparedness | Green | Failure to identify that information provided to the NRC was Incomplete and Inaccurate regarding Emergency Action Level setpoints (1EP4.1.b) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | The NRC identified a performance deficiency for the licensee's failure to identify that the EAL submittal sent to the NRC for Alert classification EALs RA1.1 and RA1.2 were beyond the range of the associated instruments, but the information was submitted
Region: III | Prairie Island | 21847 | 12/31/2010 01/31/2011 | 2010005-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PROPERLY ASSESS AND MANAGE RISK DURING PLANNED MAINTENANCE ACTIVITY. |  | H.3(a) Work Planning | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.13 | The inspectors identified finding of very low safety significance and an NCV of 10 CFR 50.65 a(4) on August 31, 2010, due to a failure to properly assess and manage the risk associated with performing planned maintenance activities on the 111 switchgear u
Region: III | Prairie Island | 21835 | 12/31/2010 01/31/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE POST MODIFICATION TESTING FOLLOWING BATTERY CHARGER REPLACEMENT. |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | In July 2010, the inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion III, due to the failure to establish measures to assure that the design of the 12 battery charger was verified using a su
Region: III | Prairie Island | 21842 | 12/31/2010 01/31/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE COMPLIANCE WITH TS SR 3.8.1.10c. |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of Technical Specification (TS) 3.8.1 in October 2010 due to the failure to demonstrate that the D2 EDG would energize the 12 battery charger within 60 seconds of an actual or
Region: III | Prairie Island | 21836 | 12/31/2010 01/31/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLETE OPERABILITY DETERMINATIONS IN ACCORDANCE WITH PROCEDURAL REQUIREMENTS. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, in October 2010, due to the failure to complete adequate immediate and prompt operability determination on the D2 emergency diesel g
Region: III | Prairie Island | 21843 | 12/31/2010 01/31/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO APPROPRIATELY COMPLETE AN OPERABILITY DETERMINATION ON D5 EMERGENCY DIESEL GENERATOR (EDG). |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, on November 12, 2010, due to the failure to complete an immediate operability determination for the D5 EDG in accordance with Proced
Region: III | Prairie Island | 21846 | 12/31/2010 01/31/2011 | 2010005-06 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE RESULTS IN REMOVING INCORRECT RADIATION MONITOR FROM SERVICE. |  | H.4(a) Human Error Prevention | TE?: N | 05000282 Prairie Island 1 |  | 71152 | A self-revealed finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, was identified on November 12, 2010, due to the failure to follow procedure while transferring the power supply for motor control center 1T1 fro
Region: III | Prairie Island | 21845 | 12/31/2010 01/31/2011 | 2010005-07 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO INCLUDE 121 MOTOR DRIVEN COOLING WATER PUMP (MDCLP) COUPLING HARDNESS INFORMATION IN PROCUREMENT DOCUMENT. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion IV, was identified on July 25, 2010, due to the licensee's failure to specify the required 121 motor driven cooling water pump shaft coupling hardn
Region: III | Prairie Island | 21829 | 11/05/2010 11/24/2010 | 2010012-02 | NRC | FIN | Mitigating Systems | Green | INADEQUATE 50.59 EVALUATION FOR NEW MANUAL OPERATOR ACTIONS. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000306 Prairie Island 2 |  | 95001 | A Severity Level IV NCV of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," was identified by the inspector for the licensee's failure to provide an evaluation that adequately documented why implementing new manual operator actions during periods of
Region: III | Prairie Island | 21827 | 09/30/2010 11/04/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT RHR WOULD BE CAPABLE TO RESPOND DURING MODE 4 EVENTS |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A finding of very low safety significance and an associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors on July 12, 2010, due to the failure to establish measures to assure that appl
Region: III | Prairie Island | 21813 | 09/07/2010 09/22/2010 | 2010009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Design Diesels to Survive Tornado Borne Missiles (Section 4OA4.3.01 b) | EA Case: 2009167 |  | TE?: N | 05000282 Prairie Island 1 |  | 95001 | Green: The inspectors identified an NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to design the D1/D2 diesel generators to survive impact from the design basis missiles. 10 CFR 50, Appendix B, Criterion I
Region: III | Prairie Island | 21815 | 08/30/2010 10/13/2010 |  | NRC | NCV | Mitigating Systems | Green | Fuel Oil Storage Design Did Not Support EDGs 7-Day Supply |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that the fuel oil storage capability for emergency diesel ge
Region: III | Prairie Island | 21821 | 08/30/2010 10/13/2010 |  | NRC | NCV | Barrier Integrity | Green | Failure to Evaluate the Adequacy of Voltage for Safety-Related Equipment |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to consider design basis accident temperature and voltage variations when perf
Region: III | Prairie Island | 21822 | 08/30/2010 10/13/2010 |  | NRC | NCV | Barrier Integrity | Green | Inadequate Analysis Used to Determine PORV/LTOP Setpoint |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to have adequate calculation used to ensure reactor vessel 10 CFR Part
Region: III | Prairie Island | 21823 | 08/30/2010 10/13/2010 |  | NRC | NCV | Barrier Integrity | Green | PORV Stroke Timing Acceptance Criteria Failed to Include Instrument Response Time |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to ensure adequate acceptance limits were incorporated into test procedur
Region: III | Prairie Island | 21824 | 08/30/2010 10/13/2010 |  | NRC | NCV | Mitigating Systems | Green | Errors Found in the Electrical Relay Setting Calculation |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," related to calculational errors found in the licensee's relay setting analysis. Specifically, the
Region: III | Prairie Island | 21802 | 06/30/2010 07/26/2010 | 2010003-01 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO ADDRESS DESIGN VULNERABILITY RESULTS IN REACTOR TRIP |  |  | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self revealed finding of very low safety significance was identified following an automatic reactor trip on April 16, 2010. Specifically, the licensee failed to appropriately establish and implement actions to correct the causes of a turbine trip/reacto
Region: III | Prairie Island | 21803 | 06/30/2010 07/26/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | LACK OF OPERATOR PROCEDURE USE DURING SYSTEM ALIGNMENT |  | H.4(a) Human Error Prevention | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self revealed finding of very low safety significance and a non-cited violation of Technical Specification 5.4.1 was identified on April 9, 2010, due to the licensee's failure to implement Step 5.1.1 of Procedure FP G DOC 03, "Procedure Use and Adherenc
Region: III | Prairie Island | 21811 | 06/30/2010 07/26/2010 | 2010003-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE FOREIGN MATERIAL EXCLUSION CONTROLS ASSOCIATED WITH WORK ON EMERGENCY DIESEL GENERATORS |  | H.3(a) Work Planning | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A finding of very low safety significance and a non cited violation of 10 CFR Part 50, Appendix B, Criterion V was identified by the inspectors on March 15, 2010, due to the licensee's failure to have instructions and procedures appropriate to the circums
Region: III | Prairie Island | 21797 | 03/31/2010 04/29/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE COOLING WATER AND FUEL OIL SYSTEMS WERE PROTECTED FROM FLOODING IMPACTS |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.06 | The inspectors identified finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," due to the licensee's failure to implement design control measures to ensure that the functions of
Region: III | Prairie Island | 21798 | 03/31/2010 04/29/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY IMPLEMENT OPERABILITY PROCEDURE |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V for the failure to adequately implement Procedure FP OP OL 01, "Operability/Functionality Determination." The failure
Region: III | Prairie Island | 21799 | 03/31/2010 04/29/2010 | 2010002-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO HAVE ADEQUATE PROCEDURE FOR TESTING VALVE CC-5-2 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | A self-revealed finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 were identified on January 27, 2010, when the licensee failed to establish an appropriate procedure for testing component cooling water pump
Region: III | Prairie Island | 21800 | 03/31/2010 04/29/2010 | 2010002-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO ACCOMPLISH ANALOG PROTECTION FUNCTIONAL TEST PER PROCEDURE INSTRUCTIONS |  | H.4(a) Human Error Prevention | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self revealed finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V were identified on February 9, 2010, due to operations personnel failing to accomplish Surveillance Procedure (SP) 1003, "Analog P
Region: III | Prairie Island | 21794 | 03/26/2010 04/12/2010 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Determine the Minimum Cooling Water System Flow Required After a Design Basis Earthquake |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.07T | A finding of very low safety-significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to determine the minimum cooling water system flow required after a design basis
Region: III | Prairie Island | 21793 | 03/04/2010 04/09/2010 | 2010503-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain a Standard Emergency Action Level Scheme | EA Case: 2010031 |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71114.04 | A licensee identified finding and associated Apparent Violation (AV) of 10 CFR 50.54(q) and 10 CFR 50.47(b)(4) was identified for the failure to follow and maintain in effect emergency plans which use a standard emergency classification and action level s
Region: III | Prairie Island | 21785 | 12/31/2009 02/08/2010 | 2009005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | VALVE TECHNICIAN BECAME INTERNALLY AND EXTERNALLY CONTAMINATED WHEN HE BREACHED THE RH-2-1 VALVE CONTRARY TO THE REQUREMENTS OF THE RWP. |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | A self-revealed finding of very low safety-significance and an NCV of Technical Specification 5.4.1 was identified for the failure to implement written procedures in the area of radiation protection. Specifically, the licensee failed to meet radiation wor
Region: III | Prairie Island | 21786 | 12/31/2009 02/08/2010 | 2009005-02 | NRC | NCV | Public Radiation Safety | Green | RADIOACTIVE WASTE BUILDING VENTILATION SYSTEM AND THE ASSOCIATED RADIATION DETECTOR BEING OUT OF SERVICE FOR EXTENDED PERIODS OF TIME WITHOUT INSTITUTING COMPENSATORY ACTIONS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112201 | An inspector-identified finding of very low safety-significance and an NCV of 10 CFR Part 20.1501 was identified for the failure to evaluate the potential radiological environmental dose impact associated with the extended non functionality of the radioac
Region: III | Prairie Island | 21788 | 12/31/2009 02/08/2010 | 2009005-04 | Self - Revealed | FIN | Initiating Events | Green | 12 CIRCULATING WATER PUMP TRIP AND UNIT 1 AUTOMATIC REACTOR TRIP |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self-revealed finding of very low safety significance was identified on May 18, 2009, due to the licensee's failure to replace an electrical cable associated with the 12 circulating water pump after identifying that the cable was susceptible to failure.
Region: III | Prairie Island | 21792 | 12/31/2009 02/08/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE RESULTS IN FAILURE TO IDENTIFY ADVERSE TREND REGARDING COOLING WATER PUMP RIGHT ANGLE DRIVE FOULING |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR Part 50 Appendix B, Criterion V, due to the licensee's failure to accomplish an activity affecting quality in accordance with procedures. Specifically, licensee perso
Region: III | Prairie Island | 21776 | 09/30/2009 10/23/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE WORK INSTRUCTION FOR WELD REPAIRS ON THE 11 COMPONENT COOLING HEAT EXCHANGER |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 |  | 71111.08P | On September 16, 2009, the inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to have adequate work instructions associated with weld repairs on
Region: III | Prairie Island | 21777 | 09/30/2009 10/23/2009 | 2009004-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM ADEQUATE RISK ASSSESSMENT PRIOR TO PERFORMING TROUBLESHOOTING ACTIVITIES RENDERS INSTRUMENT INVERTER UNAVAILABLE AND CAUSES UNPLANNED SHUTDOWN SAFETY COLOR CHANGE |  | H.3(a) Work Planning | TE?: N | 05000282 Prairie Island 1 |  | 71111.2 | A self revealed finding of very low safety significance and a Non Cited Violation of 10 CFR 50.65(a)(4) was identified on September 14, 2009, due to the licensee's failure to perform an adequate risk assessment prior to performing troubleshooting activiti
Region: III | Prairie Island | 21780 | 09/30/2009 10/23/2009 | 2009004-05 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO HAVE WORK INSTRUCTIONS APPROPRIATE TO THE CIRCUMSTANCE FOR PERFORMING MAINTENANCE ON THE GENERATOR BEARING OIL SIGHT GLASS FOR THE D1 EMERGENCY DIESEL GENERATOR |  |  | TE?: N | 05000282 Prairie Island 1 |  | 71153 | A self revealed finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 was identified on April 5, 2009, due to the failure to ensure that maintenance affecting the performance of the D1 emergency diesel generato
Region: III | Prairie Island | 21772 | 08/13/2009 09/25/2009 | 2009009-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURES FOR HEATER DRAIN PUMP SWAPS | EA Case: 2006178 | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low significance and non-cited violation (NCV) of Technical Specification 5.4.1.a for the licensee failing to obtain a temporary or permanent procedure change, as required by their Procedure Use and Adherence pr
Region: III | Prairie Island | 21773 | 08/13/2009 09/25/2009 | 2009009-02 | NRC | NCV | Emergency Preparedness | Green | INADEQUATE TECHNICAL SUPPORT CENTER VENTILATION SYSTEM TESTING | EA Case: 2006178 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50.54(q), associated with 10 CFR 50.47(b)(8), for failing to maintain the portion of the emergency plan in effect regarding the adequate maintenance of
Region: III | Prairie Island | 21774 | 08/13/2009 09/25/2009 | 2009009-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO QUALIFY SAFETY-RELATED MOLDED CASE CIRCUIT BREAKERS | EA Case: 2006178 | P.2(b) Implementing Operating Experience | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152B | The inspectors identified a Non-Cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly correct a condition adverse to quality regarding the expired qualification of safety-related molded case
Region: III | Prairie Island | 21765 | 07/09/2009 08/05/2009 | 2009010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Design Measures Were Appropriately Established for the unit 1 Component Cooling Water System. | EA Case: 2009167 | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 |  | NONE | An inspector identified Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified due to the licensee's failure to establish design control measures to ensure that the design basis for the Unit 1 component cooling
Region: III | Prairie Island | 21753 | 06/30/2009 08/05/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO POSITIVELY CONTROL COMPENSATORY MEASURES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V on April 28, 2009, for failure to have adequate procedures to control compensatory actions for degraded/non-conforming
Region: III | Prairie Island | 21754 | 06/30/2009 08/05/2009 | 2009003-03 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO MAINTAIN CONTROL OF UNIT 1 CONTAINMENT PERSONNEL AIRLOCK CONFIGURATION |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | A self-revealed finding of very low safety significance and an Non-Cited Violation of Technical Specification 5.4.1 were identified on March 25, 2009, due to the failure of licensed operators to maintain control of the Unit 1 containment personnel airlock
Region: III | Prairie Island | 21755 | 06/30/2009 08/05/2009 | 2009003-04 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO CONTROL MAINTENANCE ACTIVITIES TO ENSURE PLANT EQUIPMENT IS NOT UNNECESSARILY CHALLENGED |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.19 | A self-revealed finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V were identified on March 19, 2009, due to the failure to have adequate procedures to control maintenance activities to ensure that
Region: III | Prairie Island | 21761 | 06/30/2009 08/05/2009 | 2009003-05 | Self - Revealed | NCV | Mitigating Systems | Green | 23 INVERTER RENDERED INOPERABLE DURING TRAINING ACTIVITIES |  | H.4(a) Human Error Prevention | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 were identified on February 27, 2009, due to operations personnel failing to adequately implement procedures which control safety related eq
Region: III | Prairie Island | 21762 | 06/30/2009 08/05/2009 | 2009003-06 | Self - Revealed | NCV | Mitigating Systems | Green | 22 BATTERY CHARGER RENDERED INOPERABLE DURING MAINTENANCE ON 22 INVERTER |  | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 were identified on April 26, 2009, due to maintenance personnel failing to implement procedures which control safety-related equipment. Spec
Region: III | Prairie Island | 21763 | 06/30/2009 08/05/2009 | 2009003-07 | Self - Revealed | FIN | Mitigating Systems | Green | 122 AIR COMPRESSOR RENDERED NON-FUNCTIONAL DURING CLEARANCE ORDER ACTIVITIES |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance was identified on April 30, 2009, due to operations personnel failing to implement procedures which control plant equipment. Specifically operations personnel operated the incorrect component, render
Region: III | Prairie Island | 21764 | 06/30/2009 08/05/2009 | 2009003-08 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO ENSURE TURBINE VALVE TESTING PROCEDURE WAS ADEQUATE |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000306 Prairie Island 2 |  | 71153 | A self-revealed finding of very low safety significance was identified on May 9, 2009, due to operations personnel failing to ensure that procedures used to test the Unit 2 turbine stop valves provided adequate guidance regarding the valve position limite
Region: III | Prairie Island | 21750 | 04/24/2009 05/28/2009 | 2009007-01 | NRC | NCV | Initiating Events | Green | Combustible Materials Present Within Safety Related Fire Area |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | A finding of very low safety significance and associated NCV of License Condition 2.C.(4) was identified by the inspectors for the failure to minimize the use of combustible materials in a safety-related area. Specifically, the inspectors identified woode
Region: III | Prairie Island | 21751 | 04/24/2009 05/28/2009 | 2009007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure Fire door Would Consistently Close |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | A finding of very low safety significance was identified by the inspectors for the failure to ensure a fire door would consistently close. The licensee entered the issue into their corrective action program. This finding has a cross cutting aspect in the
Region: III | Prairie Island | 21746 | 03/31/2009 05/14/2009 | 2009002-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO PROTECT FIRE PROTECTION EQUIPMENT FROM EFFECTS OF EXTREME COLD TEMPERATURES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.01 | The inspectors identified a finding of very low safety significance on January 13, 2009, due to the fire protection system pumps being unable to auto start, as designed, in response to a low fire header pressure condition. Corrective actions for this issu
Region: III | Prairie Island | 21740 | 03/31/2009 05/14/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES DURING PERFORMANCE OF OPERABILITY EVALUATIONS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement Procedure FP-OP OL-01, "Operability
Region: III | Prairie Island | 21747 | 03/31/2009 05/14/2009 | 2009002-03 | NRC | FIN | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURE DURING D5 POST-MAINTENANCE TESTING |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000306 Prairie Island 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance on February 25, 2009, due to operations and maintenance personnel failing to identify a turbocharger coolant vent line fretting condition during a D5 emergency diesel generator post-maint
Region: III | Prairie Island | 21748 | 03/31/2009 05/14/2009 | 2009002-04 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO ADHERE TO LICENSED POWER LEVEL SPECIFIED IN OPEATING LICENSE | EA Case: 2009152 | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 |  | 71111.22 | A self-revealed finding and an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified due to the failure to have an adequate procedure for reactivity management. Specifically the guidance in SWI O-50, "Reac
Region: III | Prairie Island | 21749 | 03/31/2009 05/14/2009 | 2009002-05 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURE USE AND ADHERENCE PROCEDURE FOLLOWING RECEIPT OF ABNORMAL OPERATING PROCEDURE ENTRY CONDITION |  | H.4(b) Procedural Compliance | TE?: N | 05000306 Prairie Island 2 |  | 71111.22 | The inspectors identified a finding of very low safety significance and a Non Cited Violation of Technical Specification 5.4.1 due to operations personnel failing to implement abnormal operating procedures following an unexpected control rod insertion on
Region: III | Prairie Island | 21745 | 01/21/2009 02/10/2009 | 2008009-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Perform Formal Job Planning to Evaluate the Radiological Hazards | EA Case: 2008349 | H.3(a) Work Planning | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | NONE | An NRC-identified finding of very low safety significance with an associated Non-Cited Violation (NCV) of Technical Specification 5.4.1 was identified in the area of occupational radiation safety associated with the licensee's failure to perform adequate
Region: III | Prairie Island | 21729 | 12/31/2008 02/10/2009 | 2008005-01 | NRC | NCV | Initiating Events | Green | FAILURE OF CONTRACTORS TO FOLLOW WELDING PROCEDURES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000306 Prairie Island 2 |  | 71111.08P | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix B, Criterion V, in September 2008 for the failure of contractor welders to adhere to welding procedures during structural weld overlay (S
Region: III | Prairie Island | 21731 | 12/31/2008 02/10/2009 | 2008005-03 | Self - Revealed | NCV | Barrier Integrity | Green | CONTROL ROD BENT DUE TO CONTRACTORS' FAILURE TO FOLLOW PROCEDURES |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000306 Prairie Island 2 |  | 71111.2 | A finding of very low safety significance and an associated NCV of TS 5.4.1 was self revealed on October 9, 2008, due to the failure of contractor staff to follow procedures during refueling activities. This failure to follow procedures resulted in the in
Region: III | Prairie Island | 21736 | 12/31/2008 02/10/2009 | 2008005-04 | Self - Revealed | NCV | Initiating Events | Green | OPERATOR MANIPULATES INCORRECT COMPONENT DUE TO FAILURE TO FOLLOW PROCEDURES |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.2 | One self-revealed finding of very low safety significance and an associated NCV of Technical Specification (TS) 5.4.1 was identified on October 13, 2008, due to an operator's failure to follow procedures during refueling activities. The failure to follow
Region: III | Prairie Island | 21737 | 12/31/2008 02/10/2009 | 2008005-05 | Self - Revealed | NCV | Initiating Events | Green | IDECREASE IN REACTOR POWER DUE TO FAILURE TO FOLLOW PROCEDURES |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000306 Prairie Island 2 |  | 71111.22 | A finding of very low safety significance and an NCV of 10 CFR Part 50, Appendix B, Criterion V, was self revealed on November 6, 2008, due to instrumentation and controls technicians failing to follow procedures during calibration of the power range nucl
Region: III | Prairie Island | 21739 | 12/31/2008 02/10/2009 | 2008005-07 | NRC | NCV | Mitigating Systems | Green | RESPIRATOR QUALIFICATION DEFICIENCY RESULTS IN NON-COMPLIANCE WITH 10 CFR PART 50, APPENDIX R |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71153 | The inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR Part 50, Appendix R, Section J, on December 30, 2008, due to the licensee's failure to ensure that an alternate safe shutdown access path was provided with
Region: III | Prairie Island | 21719 | 09/30/2008 11/07/2008 | 2008004-01 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO MAINTAIN STAFF RESPIRATORY QUALIFICATIONS INCLUDING PERSONNEL QUALIFICATIONS NECESSARY FOR EMERGENCY RESPONSE DUTIES AS REQUIRED BY STATION PROCEDURES |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112103 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50.54(q) for the failure to maintain staff respiratory qualifications, including personnel qualifications necessary for emergency response duties, as required
Region: III | Prairie Island | 21722 | 09/30/2008 11/07/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | LOAD SEQUENCER TEST PROCEDURE CONFLICTS WITH VENDOR MANUAL INFORMATION |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71152 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V for the failure to ensure that the surveillance procedures used to test the safety related load sequencers included appropriate qu
Region: III | Prairie Island | 21723 | 09/30/2008 11/07/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | 11 TURBINE-DRIVEN AUXILIARY FEEDWATER PUMP INOPERABLE DUE TO IMPROPERLY INSTALLED INSULATION | EA Case: 2008273 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000282 Prairie Island 1 |  | 71153 | The inspectors identified an apparent violation (AV) of Technical Specification 5.4.1 for the failure to establish, implement and maintain procedures governing the installation of insulation on the 11 turbine-driven auxiliary feedwater (TDAFW) pump. The f
Region: III | Prairie Island | 21718 | 07/09/2008 07/23/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | This is a security Related Finding - see inspection report for details. |  | H.2(d) Facilities & Equipment | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in respons to Section B.5.b of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-02
Region: III | Prairie Island | 21717 | 06/30/2008 08/14/2008 | 2008003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO TEST CHECK VALVE SI-9-5 UNDER SUITABLE ENVIRONMENTAL CONDITIONS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 71153 | Green. An inspector identified finding of very low safety significance and a Non Cited Violation of 10 CFR Part 50, Appendix B, Criterion XI, due to the licensee's failure to ensure Check Valve SI-9 5 was tested under suitable environmental conditions. Sp
Region: III | Prairie Island | 21710 | 03/31/2008 05/14/2008 | 2008002-01 | NRC | NCV | Emergency Preparedness | Green | TSC VENTILATION ISSUES RESULTED IN INADEQUATE EMERGENCY RESPONSE FACILITY |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.15 | Green. The inspectors identified a NCV of 10 CFR 50.54(q), associated with 10 CFR 50.47(b)(8), for failing to maintain adequate emergency facilities to support emergency response. Specifically, the licensee failed to maintain control of the Technical Supp
Region: III | Prairie Island | 21712 | 03/31/2008 05/14/2008 | 2008002-03 | NRC | NCV | Occupational Radiation Safety | Green | WORKER NOT IN COMPLIANCE WITH TS 5.7.1 B RECEIVED AN ED DOSE-RATE ALARM WHEN HE INAPPROPRIATELY ENTERED A HRA OF THE PLANT DURING STEAM GENERATOR SET-UP WORK |  | H.3(b) Work Activity Coordination | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | Green. A self-revealing finding of very low safety significance and an associated NCV were identified for the licensee's failure to comply with Technical Specification 5.7.1.b for access control to high radiation areas of the plant. As a result of poor hu
Region: III | Prairie Island | 21706 | 12/31/2007 02/11/2008 | 2007005-03 | NRC | NCV | Occupational Radiation Safety | Green | INADEQUATE IMPLEMENTATION OF VHRA CONTROLS FOR THE C-SUMP IN U1R24 |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | Green. A finding of very low safety significance and an associated Non-Cited Violation (NCV) was inspector-identified for the licensee=s failure to adequately maintain sufficient controls over a posted very high radiation area (VHRA) during the spring 200
Region: III | Prairie Island | 21709 | 12/31/2007 02/11/2008 | 2007005-04 | NRC | NCV | Occupational Radiation Safety | Green | INADEQUATE CONTROL OF VHRA KEYS IN U2R24 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | Green. A finding of very low safety significance and an associated NCV of Technical Specification 5.4.1 was inspector-identified for the licensee=s failure to adequately implement radiation safety procedures concerning the 2006 Unit-2 refueling outage whe
Region: III | Prairie Island | 21698 | 06/30/2007 08/14/2007 | 2007003-02 | NRC | NCV | Occupational Radiation Safety | Green | CONTINUE TO PERMIT UNIT 2 CONTAINMENT ACCESS ON RADIATION WORK PERMITS THAT DO NOT AUTHORIZE ACCESS TO AIRBORNE RADIOACTIVITY LEVELS |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | Green. A finding of very low safety significance and two associated Non-Cited Violations were inspector-identified associated with the licensee's failure to adequately implement radiation safety procedures concerning the control and response to airborne r
Region: III | Prairie Island | 21699 | 06/30/2007 08/14/2007 | 2007003-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO EVACUATE UNIT 2 CONTAINMENT UPON DETECTION OF ELEVATED AIRBORNE RADIOACTIVITY LEVELS |  | H.4(b) Procedural Compliance | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | Green. A finding of very low safety significance and two associated NCVs were identified by the inspectors. Specifically, the licensee failed to adequately implement radiation safety procedures concerning the control and response to airborne radiological
Region: III | Prairie Island | 21702 | 06/30/2007 08/14/2007 | 2007003-06 | NRC | FIN | Initiating Events | Green | FAILURE TO MAINTAIN SAFETY INJECTION RELAYS |  | P.2(b) Implementing Operating Experience | TE?: N | 05000306 Prairie Island 2 |  | 71152 | Green. A finding of very low safety significance was self-revealed when a Unit 2 train A safeguards actuation and reactor trip occurred during the performance of the safeguards logic test at power. The actuation occurred because of a failure of the actuat
Region: III | Prairie Island | 21204 | 06/22/2007 08/03/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Modification of Safeguards Screenhouse Ventilation System |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee modified the safeguards screenhouse ventilation syste
Region: III | Prairie Island | 21207 | 06/22/2007 08/03/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Overload Heater Sizing for Safeguards Screenhouse Ventilation Exhaust Fan |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low significance and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to ensure that the thermal overload heater for the 21
Region: III | Prairie Island | 21208 | 06/22/2007 08/03/2007 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Inputs for Motor-Operated Valve Calculations |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111121 | The inspectors identified a finding having very low significance (Green) and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee used non-conservative inputs or methodologies in calc
Region: III | Prairie Island | 21209 | 06/22/2007 08/03/2007 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Voltage at Charging Motor for Diesel Output Breaker Springs |  |  | TE?: N | 05000282 Prairie Island 1 |  | 7111121 | The inspectors identified a finding having very low significance (Green) and an associated non cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action." Specifically, the licensee failed to identify and correct a condition adverse
Region: III | Prairie Island | 21203 | 03/31/2007 05/14/2007 | 2007002-01 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO PROPERLY CONTROL ACCESS TO A LOCKED HIGH RADIATION AREA |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000282 Prairie Island 1 |  | 7112101 | A finding of very low safety significance and associated Non-Cited Violation was inspector-identified during review of an issue where a station operator entered into a Locked High Radiation Area (LHRA) without authorization while a high integrity containe
Region: III | Prairie Island | 21202 | 12/31/2006 02/05/2007 | 2006005-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM A MAGNETIC PARTICLE EXAMINATION IN ACCORDANCE WITH ASME CODE SECTION XI |  |  | TE?: N | 05000306 Prairie Island 2 |  | 71111.08P | The inspectors identified a Non-Cited Violation of 10 CFR 50.55(a)(g)(4) for failure to perform a Magnetic Particle examination (MT) of the full required exam surface on a steam generator feedwater nozzle weld (N-1) in accordance with the American Society
Region: III | Prairie Island | 21193 | 09/30/2006 11/09/2006 | 2006004-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM CODE VOLUMETRIC EXAMINATION OF THE 22 STEAM GENERATOR INLET NOZZLE WELD W-5 |  | H.3(b) Work Activity Coordination | TE?: N | 05000306 Prairie Island 2 |  | NONE | The inspectors identified a Non-Cited Violation of 10 CFR 50.55a(g)4 for failure to complete a code qualified volumetric examination of the 22 steam generator inlet nozzle weld W-5. As a corrective action, the licensee entered this issue into the correcti
Region: III | Prairie Island | 21194 | 09/30/2006 11/09/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE WRITTEN INSTRUCTIONS THAT OPERATORS OR TECHNICIANS COULD IMPLEMENT AS THE COMPENSATORY ACTION FOR A DEGRADED BUT OPERABLE UNIT 1 TRAIN A REACTOR VESSEL LEVEL INSTRUMENT SYSTEM |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000282 Prairie Island 1 |  | 71111.15 | The inspectors identified a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V for failing to provide written instructions for the compensatory action for a degraded but operable Unit 1 Train A Reactor Vessel Level Instrument System. The licensee t
Region: III | Prairie Island | 21195 | 09/30/2006 11/09/2006 | 2006004-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO EVALUATE CONCENTRATIONS OF RADIOACTIVE MATERIAL AND THE POTENTIAL RADIOLOGICAL HAZARDS |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112102 | A self-revealed finding of very low safety significance and an associated violation of NRC requirements were identified for the failure to perform adequate evaluation of concentrations or quantities of radioactive material and the potential radiological h
Region: III | Prairie Island | 21186 | 08/18/2006 10/23/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | No Fire-Rated Damper in Return Ventilation Duct |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | The inspectors identified a NCV of the Prairie Island Nuclear Generating Plant's (PINGP's) Facility Operating License, Section 2.C.(4) and 10 CFR 50.48(b)(1)(I) having very low safety significance for not having a three-hour fire-rated damper installed be
Region: III | Prairie Island | 21187 | 08/18/2006 10/23/2006 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Surveillance Did Not Include TS Requirements |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for the licensee's failure to include required instructions in a surveillance procedure. Specifically
Region: III | Prairie Island | 21192 | 08/18/2006 10/23/2006 | 2006009-04 | NRC | NCV | Mitigating Systems | Green | Lack of Smoke Detectors |  | P.3(a) Self-Assessment | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.05T | The inspectors identified a NCV of the PINGP's Facility Operating License having very low safety significance for the failure to have adequate fire detection installed in accordance with the applicable NFPA codes. Specifically, the licensee failed to inst
Region: III | Prairie Island | 21179 | 06/30/2006 08/14/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | UPDATED SAFETY ANALYSIS REPORT CHANGE THAT REMOVED THE REACTOR VESSEL HEAD LIFT ELEVATION LIMIT AND REFERENCE TO THE ASSOCIATED REACTOR VESSEL HEAD LOAD DROP CALCULATION |  |  | TE?: N | 05000282 Prairie Island 1 |  | 7111102 | The inspectors identified a Severity Level IV Non-Cited Violation associated with the failure to perform an adequate safety evaluation review as required by 10 CFR 50.59 for the changes made to the Updated Safety Analysis Report (USAR). In safety evaluati
Region: III | Prairie Island | 21180 | 06/30/2006 08/14/2006 | 2006003-02 | NRC | NCV | Occupational Radiation Safety | Green | NRC IDENTIFIED LOSS OF HIGH RADIATION AREA BARRICADE AT UNIT 1 PRESSURIZER MISSILE SHIELD |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112101 | A finding of very low safety significance and associated Non-Cited Violation (NCV) were inspector-identified during a walkdown in Unit 1 containment. The inspectors identified that a swing gate barrier to a High Radiation Area (HRA) was left in the open p
Region: III | Prairie Island | 21183 | 06/30/2006 08/14/2006 | 2006003-03 | NRC | NCV | Occupational Radiation Safety | Green | ALARA PLANNING DOES NOT IDENTIFY AND PREPARE FOR POTENTIAL AIRBORNE CONDITIONS WHEN OPENING THE STEAM GENERATOR MANWAYS |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112102 | A self-revealing finding of very low safety significance and associated NCV were identified when 110 radiation workers were contaminated as a result of opening steam generator manways during the Unit 1 1R24 refueling outage. Specific ALARA planning assess
Region: III | Prairie Island | 21184 | 06/30/2006 08/14/2006 | 2006003-04 | NRC | NCV | Public Radiation Safety | Green | PROCEDURE FOR ODCM COMPLIANCE DOES NOT INCLUDE CONTAINMENT EFFLUENT THROUGH EQUIPMENT HATCH |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7112201 | A finding of very low safety significance and associated NCV were inspector-identified for the failure to establish adequate written procedure(s) for Offsite Dose Calculation Manual (ODCM) implementation to ensure that the radiological impact from releasi
Region: III | Prairie Island | 21177 | 03/31/2006 05/11/2006 | 2006002-01 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURES FOR EXTERNAL FLOODING (EVALUATION OF EXPIRED SEALANT PERFORMANCE FOR FLOOD PROTECTION) |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 71111.06 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50 Appendix B, Criterion V for a combination of an inadequate procedure and a failure to implement the requirements of Surveillance Procedure 1293, Inspection of Flood Control Measures and the
Region: III | Prairie Island | 21176 | 03/24/2006 04/28/2006 | 2006006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Adverse Ampacity Effects of High Temperature Conditions in the Auxiliary Feedwater Pump Rooms |  |  | TE?: N | 05000282 Prairie Island 1 05000306 Prairie Island 2 |  | 7111117B | A Non-Cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance was identified by the inspectors. Specifically, the licensee had not evaluated and updated the associated plant cable ampacity calcul
Region: III | Quad Cities | 126330 | 12/31/2019 01/29/2020 | 2019004-01 | NRC | NCV | Initiating Events | Green | Failure to Inhibit Spurious Start of High Pressure Coolant Injection Within 10 Minutes for an Appendix R Fire |  | NPP | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 | Protection Against External Factors | 71111.15 | The inspectors identified a finding of very-low safety significance and associated non-cited violation (NCV) of Technical Specification 5.4.1 “Procedures,” for the licensee’s failure to implement and maintain fire protection program safe shutdown procedur
Region: III | Quad Cities | 25929 | 12/31/2018 01/25/2019 | 2018004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Causes Turbine Load Reject and SCRAM |  | H.11 - Challenge the Unknown | TE?: N | 05000254 Quad Cities 1 |  | 71152 | A self-revealed Green finding and associated Non-Cited Violation (NCV) of Technical Specification (TS) 5.4.1 was identified when the licensee failed to follow Procedure QCOP 6400-35, "Performing Transmission Switching Orders." Specifically following the c
Region: III | Quad Cities | 24687 | 09/30/2018 10/24/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Design Basis for Residual Heat Removal Torus Suction Valve |  | NPP | TE?: N | 05000254 Quad Cities 1 |  | 71111.15 | The inspectors identified a Green finding and associated Non-Cited Violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion III, “Design Control,” when the licensee performed an in-field adjustment to the torque switch s
Region: III | Quad Cities | 24145 | 06/30/2018 07/30/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to have a Procedure Appropriate to Circumstances for Degraded Voltage Relays |  | NPP | TE?: N | 05000254 Quad Cities 1 |  | 71152 | A finding of very low safety significance (Green) and a Non-Cited Violation of Title 10 of the Code of Federal Regulations (10 CFR) 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was self-revealed on April 16, 2018, for the license
Region: III | Quad Cities | 23964 | 03/31/2018 05/10/2018 | 2018001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Design Standard for Unit 2 Residual Heat Removal Service Water Pumps |  | NPP | TE?: N | 05000265 Quad Cities 2 |  | 71111.19 | The inspectors identified a finding of very low safety significance (Green) and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to ensure that the design bases standard and other requirements nec
Region: III | Quad Cities | 23965 | 03/31/2018 05/10/2018 | 2018001-03 | Self - Revealed | NCV | Initiating Events | Green | Half Scram Due to Low Voltage on 24/48 Vdc System |  | H.5 - Work Management | TE?: N | 05000254 Quad Cities 1 |  | 71152 | A finding of very low safety significance (Green) and NCV of TS 5.4.1, “Procedures,” was self-revealed on January 11, 2018, for the licensee’s failure to perform an equalizing charge on the Unit 1B 24/48 Vdc battery prior to returning the 24/48 Vdc batter
Region: III | Quad Cities | 26903 | 06/30/2017 08/01/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH A PROCEDURE APPROPRIATE FOR CALIBRATION OF RCIC GOVERNOR |  | H.9 Training | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) Section 5.4.1 was self-revealed for the licensee's failure to establish a procedure as governed by Regulatory Guide 1.33, Revision 2, Appendix
Region: III | Quad Cities | 26904 | 06/30/2017 08/01/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE TWO LOW PRESSURE ECCS SYSTEMS OPERABLE IN MODE 4 |  | H.5 Work Management | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specification (TS) 3.0.1 on April 12, 2017, for the licensee's failure to meet TS Limiting Condition for Operation (LCO) 3.5.2, "Emergen
Region: III | Quad Cities | 26905 | 06/30/2017 08/01/2017 | 2017002-03 | NRC | FIN | Initiating Events | Green | FAILURE TO JUSTIFY MSIV MAINTENANCE DEFERRAL |  | H.14 Conservative Bias | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | The inspectors identified a finding of very low safety significance for the licensee's failure to provide an adequate technical justification for deferral of a preventative maintenance task to replace or refurbish the Unit 1 2D main steam isolation valve
Region: III | Quad Cities | 26909 | 06/30/2017 08/01/2017 | 2017002-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO HAVE ADEQUATE GUIDANCE IN THE FIRE/EXPLOSION RESPONSE PROCEDURE |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance and an associated non-cited violation of TS Section 5.4.1.c, "Procedures," for the licensee's failure to establish and maintain the fire response procedure. Specifically, Procedure QCOA 0
Region: III | Quad Cities | 26899 | 03/31/2017 05/03/2017 | 2017001-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ENSURE HARDWARE SECURE FOR BREAKER MOC SWITCH LINKAGE |  | H.12 Avoid Complacency | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and an associated NCV of 10 CFR 50, Appendix B, Criterion V was self revealed on January 27, 2017, when the Unit 1C residual heat removal service water (RHRSW) pump was started for a routine surveillance evolution
Region: III | Quad Cities | 26898 | 12/31/2016 01/20/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT FOREIGN MATERIAL EXCLUSION CONTROLS |  | H.5 Work Management | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and an associated non-cited violation of Title 10 of the Code of Federal Regulations (CFR) Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self revealed for the licensee's failure t
Region: III | Quad Cities | 26892 | 08/26/2016 09/29/2016 | 2016008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Appropriate Operating Instructions for Aligning a Battery Charger to the Station Black-Out Diesel Generator (Section 1R17.1.b.) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.17T | Green. A finding of very-low safety significance (Green) and an associated NCV of Technical Specification 5.4.1.a, "Procedures," was self-revealed on December 2, 2014 when procedural guidance failed to be implemented as written. Specifically, Procedure QC
Region: III | Quad Cities | 26897 | 08/26/2016 09/29/2016 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Target Rock Relief Valve Accumulator per ASME Code (Section 1R17.2.b.) |  | H.6 Design Margins | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.17T | Green. The inspectors identified a finding of very-low safety significance (Green) and an associated NCV of Title 10 of the Code of Federal Regulations, Part 50, Appendix B, Criterion III, "Design Control," for licensee's failure to assure that quality st
Region: III | Quad Cities | 26890 | 06/30/2016 07/26/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO MAINTAIN PARAMETERS WITHIN LIMITS OF TS 3.6.2.5 AND 3.6.3.1 |  | H.14 Conservative Bias | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.13 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Technical Specifications (TS) 3.6.2.5 and 3.6.3.1 for the licensee's failure to take actions required by TS 3.6.2.5 and 3.6.3.1. Specifically, on
Region: III | Quad Cities | 26891 | 06/30/2016 07/26/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY CONDITIONS ADVERSE TO QUALITY |  | P.1 Identification | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify a condition adverse to quality. Specifically, the licensee
Region: III | Quad Cities | 26884 | 03/31/2016 04/28/2016 | 2016001-01 | Self - Revealed | NCV | Barrier Integrity | Green | FAILURE TO CONTROL DEVIATION FROM EQ STANDARD RESULTS IN LIMIT SWITCH SUBMERGENCE |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self-revealed on February 2, 2016, when the operators received an alarm due to a steam leak in the Unit 1 m
Region: III | Quad Cities | 26885 | 03/31/2016 04/28/2016 | 2016001-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO IDENTIFY STRUCTURES, SYSTEMS, AND COMPONENTS AS SAFETY-RELATED |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance," was identified by the inspectors for the licensee's failure to identify the structures, systems, and componen
Region: III | Quad Cities | 26872 | 09/30/2015 10/30/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE DEGRADED OR NON-CONFORMING CONDITIONS FOR OPERABILITY |  | P.1 Identification | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.19 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to document degraded or non c
Region: III | Quad Cities | 26873 | 09/30/2015 10/30/2015 | 2015003-02 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ESTABLISH ADEQUATE PROCEDURE TO PRECLUDE UNACCEPTABLE PRECONDITIONING OF THE STANDBY GAS TREATMENT SYSTEM |  | H.12 Avoid Complacency | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.22 | A finding of very low safety significance and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to establish a procedure appropria
Region: III | Quad Cities | 26877 | 09/30/2015 10/30/2015 | 2015003-03 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY INSPECT RELAY CONTACTS FOR OXIDATION RESULTS IN RELAY FAILURE |  | P.5 Operating Experience | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to establish a preventive maintenance proced
Region: III | Quad Cities | 26869 | 06/30/2015 07/30/2015 | 2015002-01 | Self - Revealed | UNKN | Mitigating Systems | Green | FAILURE TO CONDUCT POST MAINTENANCE TESTING FOLLOWING MANUAL OPERATION OF RCIC MOV |  | H.7 Documentation | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specification 5.4, "Procedures," was self-revealed on March 22, 2015, for the licensee's failure to conduct procedurally required post-maintenance testing on reactor core isolation
Region: III | Quad Cities | 26870 | 06/30/2015 07/30/2015 | 2015002-02 | Self - Revealed | UNKN | Initiating Events | Green | INADEQUATE ZONE OF PROTECTION FOR ELECTRICAL BUS MAINTENANCE |  | H.5 Work Management | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and associated NCV of Technical Specification 5.4, "Procedures," was self-revealed on March 14, 2015, for the licensee's failure to implement a clearance order in accordance with procedure OP-AA-109-101, "Clearanc
Region: III | Quad Cities | 26866 | 03/31/2015 04/29/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH AND MAINTAIN SERVICE LIFE FOR SAFETY-RELATED RELAY RESULTS IN FAILURE AND INOPERABILITY |  | P.2 Evaluation | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15 | A finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion III, "Design Control," was self-revealed on January 6, 2015, when an electrical maintenance worker found a tripped breaker in motor control center (MC
Region: III | Quad Cities | 26867 | 03/31/2015 04/29/2015 | 2015001-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ENSURE STANDBY LINEUP RESULTS IN STEAM RELEASE IN THE HPCI ROOM |  | H.5 Work Management | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A finding and non-cited violation of very low safety significance (Green) was self-revealed for the licensee's failure to ensure the Unit 1 high pressure coolant injection (HPCI) system was in a standby lineup configuration in accordance with station pr
Region: III | Quad Cities | 26856 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | HPCI FLOOD BARRIER DEGRADED |  | H.13 Consistent Process | TE?: N | 05000254 Quad Cities 1 |  | 71111.06 | A finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to meet the requirement
Region: III | Quad Cities | 26860 | 12/05/2014 01/15/2015 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Aging Effects on Plant Equipment and Structures |  | H.1 Resources | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The inspectors identified a finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to effectively identify, evaluate, and document aging effects on plant equ
Region: III | Quad Cities | 26846 | 09/30/2014 10/30/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | ANGLE IRON SUPPORT INSTALLED WITH MINIMAL CLEARANCE TO UNIT 2 TORUS SHELL |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15 | A finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to evaluate the impact of a conduit support in
Region: III | Quad Cities | 26847 | 09/30/2014 10/30/2014 | 2014004-02 | NRC | NCV | Emergency Preparedness | Green | INADEQUATE EVACUATION TIME ESTIMATE SUBMITTALS |  | H.7 Documentation | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) with an associated non-cited violation of 10 CFR 50.54(q)(2) as required by 10 CFR 50.47(b)(10) and 10 CFR Part 50, Appendix E, Section IV.4, for failing to maintain the effective
Region: III | Quad Cities | 26854 | 09/26/2014 10/29/2014 | 2014007-01 | NRC | FIN | Mitigating Systems | Green | INADEQUATE ROUNDS PACKAGE ACCEPTANCE CRITERIA |  | H.9 Training | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152B | A finding of very low safety significance (Green) was identified by the inspectors when they determined that non-licensed operator general area rounds and field checks were inadequate for the circumstances. The inspectors determined that the failure to ha
Region: III | Quad Cities | 26855 | 09/26/2014 10/29/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE ADMINISTRATIVE CONTROLS |  | P.3 Resolution | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152B | A finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors when they determined that Technical Specificatio
Region: III | Quad Cities | 26841 | 06/30/2014 08/12/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | SEISMIC SCAFFOLD IN CONTACT WITH SAFETY-RELATED EQUIPMENT |  | H.7 Documentation | TE?: N | 05000265 Quad Cities 2 |  | 71111.2 | A finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified by the inspectors for the licensee's failure to meet the requirements of pr
Region: III | Quad Cities | 26842 | 06/30/2014 08/12/2014 | 2014003-02 | Self - Revealed | NCV | Mitigating Systems | Green | POST MAINTENANCE TEST FAILS TO ENSURE BATTERY CHARGER CAN PERFORM FUNCTION |  | H.6 Design Margins | TE?: N | 05000254 Quad Cities 1 |  | 71152 | A finding of very low safety significance and associated non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the licensee's failure to meet the requirements of MA-AA-716-012, "P
Region: III | Quad Cities | 26843 | 06/30/2014 08/12/2014 | 2014003-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO MEET DESIGN REQUIREMENT FOR SAFETY-RELATED CABLES IN 'D' HEATER BAY |  |  | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A finding of very low safety significance (Green) with an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was self-revealed for the licensee's failure to demonstrate compliance with ComEd Standard N-EM-0035 f
Region: III | Quad Cities | 26844 | 06/30/2014 08/12/2014 | 2014003-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO OPERATE THE GLAND SEAL SYSTEM AS DESIGNED |  | H.11 Challenge the Unknown | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A finding of very low safety significance (Green) and associated non-cited violation of Technical Specification (TS) Section 5.4.1 was self-revealed on April 2, 2014 for the licensee's failure to establish a procedure in accordance with the requirements o
Region: III | Quad Cities | 26845 | 06/30/2014 08/12/2014 | 2014003-05 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO FOLLOW VENDOR REQUIREMENTS LED TO FAST DOWNPOWER |  | H.2 Field Presence | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A finding of very low safety significance was self-revealed when the licensee failed to re-establish oil level in accordance with vendor requirements in the Unit 2 Main Power Transformer (MPT-2) Conservator Oil Preservation System (COPS) tank after repair
Region: III | Quad Cities | 26840 | 03/31/2014 05/09/2014 | 2014002-01 | NRC | FIN | Initiating Events | Green | STEAM DRYER/STEAM SEPARATOR LIFTING DEVICE FAILURE TO MEET AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI) N14.6 |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.2 | The inspectors identified a finding of very low safety significance (Green) involving the licensee's failure to demonstrate compliance with American National Standards Institute (ANSI) N14.6-1978, Section 3.2.1.1. Specifically, the licensee did not establ
Region: III | Quad Cities | 26839 | 09/30/2013 11/04/2013 | 2013004-01 | Self - Revealed | NCV | Mitigating Systems | Green | WRONG PARTS INSTALLED FOR CRD HCU |  | H.3(b) Work Activity Coordination | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance (Green) and associated non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was self-revealed through repetitive low pressure alarms on a recently overhauled co
Region: III | Quad Cities | 26826 | 06/30/2013 07/22/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | CALCULATION ASSUMPTIONS NOT TRANSLATED IN TO OPERATING PROCEDURES |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.07T | A finding of very low safety significance and associated non-citied violation (NCV) of 10 CFR Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to translate design requirements into procedures to ensu
Region: III | Quad Cities | 26827 | 06/30/2013 07/22/2013 | 2013003-02 | NRC | URI | Mitigating Systems | Green | QUESTION CONCERNING LICENSING BASES OF THE ULTIMATE HEAT SINK |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.07T | As described in Section 1R07.1b(3), in April 2001, the licensee completed a 10 CFR 50.59 Safety Evaluation Screening, QC-S-2001-0026, to assess removal of the portable pumps from onsite and relocating the pumps to an offsite leasing facility located a few
Region: III | Quad Cities | 26833 | 06/30/2013 07/22/2013 | 2013003-02 | Self - Revealed | NCV | Mitigating Systems | Green | UNIT 1 MSIV SLOW CLOSURE |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71152 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified on March 11, 2013, when all four outboard main steam isolation valves (MSIVs) were st
Region: III | Quad Cities | 26831 | 06/30/2013 07/22/2013 | 2013003-04 | NRC | URI | Mitigating Systems | Green | QUESTION CONCERNING AVAILABILTY OF DAM FOLLOWING A SEISMIC EVENT |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.07T | In a letter dated November 6, 1970 to the U.S. Atomic Energy Commission (now NRC), Commonwealth Edison (the licensee) addressed questions regarding the capability of the intake flume to withstand a seismic event. Specifically, the question stated: "Dem
Region: III | Quad Cities | 26832 | 06/30/2013 07/22/2013 | 2013003-05 | NRC | URI | Mitigating Systems | Green | STEAM DRYER/STEAM SEPARATOR LIFTING DEVICE FRACTURE TOUGHNESS PROPERTIES |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.2 | The safety evaluation report for the Control of Heavy Loads Phase 1 at Quad Cities Units 1 and 2, dated June 27, 1983, classified the steam dryer/steam separator lifting device as a special lifting device and provided documentation how compliance with ANS
Region: III | Quad Cities | 26821 | 05/17/2013 06/12/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Into Toxic Chemical Response Procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.17T | A finding of very low safety significance and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the licensee's failure to translate the design basis correctly into procedures and instructio
Region: III | Quad Cities | 26819 | 03/31/2013 05/03/2013 | 2013002-01 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW CLEARANCE ORDER INSTRUCTIONS |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.2 | A finding of very low safety significance and associated non-citied violation of Technical Specifications 5.4.1.a, "Procedures," was self-revealed on March 13, 2013, when operators placing a clearance on the Unit 1 analog trip system de-energized the Unit
Region: III | Quad Cities | 26820 | 03/31/2013 05/03/2013 | 2013002-02 | Self - Revealed | NCV | Mitigating Systems | Green | DIESEL GENERATOR COOLING WATER PUMP ALIGNED TO WRONG UNIT |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and associated non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed on March 1, 2013, during restoration from the 1B core spray logic test, when
Region: III | Quad Cities | 26808 | 12/31/2012 01/31/2013 | 2012005-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW SURVEILLANCE PROCEDURE |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A self-revealed finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedure, and Drawings," were identified on October 25, 2012, when the operator performing the Unit 2 EDG surveill
Region: III | Quad Cities | 26812 | 12/31/2012 01/31/2013 | 2012005-02 | Self - Revealed | NCV | Mitigating Systems | Green | BOTH UNIT 1 CORE SPRAY SUBSYSTEMS INOPERABLE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealed finding of very low safety significance (Green) and an associated NCV of TS 3.5.1.K were identified for two core spray systems inoperable due to degraded flood barriers on August 6, 2012. The failure of the 1B core spray and Unit 2 reactor
Region: III | Quad Cities | 26807 | 12/31/2012 01/31/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | DIESEL GENERATOR TECHNICAL SPECIFICATION FREQUENCY AND VOLTAGE VARIATION NOT CONSIDERED IN LOADING CALCULATIONS |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify and ensure that operating the emergency diesel generators (EDGs) at
Region: III | Quad Cities | 26800 | 09/30/2012 10/25/2012 |  | Self - Revealed | NCV | Mitigating Systems | Green | UNIT 1 HPCI STEAM LINE DRAIN VALVE THROUGH-BODY LEAK |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71111.19 | A self-revealed finding of very low safety significance (Green) and associated NCV of Technical Specification (TS) 5.4.1.a was identified for the failure to develop a preventative maintenance schedule appropriate to the environmental conditions and potent
Region: III | Quad Cities | 26801 | 09/30/2012 10/25/2012 |  | NRC | NCV | Mitigating Systems | Green | CONTROL ROOM HVAC RCU HEAD BOLTS NOT TORQUED |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.19 | A self-revealed finding of very low safety significance (Green) and associated NCV of TS 5.4.1.a was identified for the licensee's failure to specify torque values for the control room ventilation refrigeration condensing unit condenser head in the work i
Region: III | Quad Cities | 26799 | 08/31/2012 10/02/2012 | 2012007-01 | NRC | NCV | Initiating Events | Green | CAPR NOT COMPLETED |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152B | A finding of very low safety significance (Green) and associated NCV of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program" was identified by the inspectors when they determined that a licensee-specified corrective action to prevent recurrenc
Region: III | Quad Cities | 26798 | 08/03/2012 09/06/2012 | 2012011-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Cold Shutdown Repair of 1A Recirculation Pump Discharge Valve MO 1-202-5A |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix R, Section III.L.5 for the licensee's failure to have a procedure in effect that would provide adequate cold shutdown repairs for th
Region: III | Quad Cities | 26797 | 08/03/2012 09/06/2012 | 2012011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure to Energize Bus 23-1 to Provide Torus Cooling for Unit 1 |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix R, Section III.L.3 for the licensee's failure to have an adequate procedure used to implement an alternative shutdown capability in
Region: III | Quad Cities | 26789 | 06/30/2012 08/02/2012 | 2012003-01 | Self - Revealed | NCV | Initiating Events | Green | BUS ENERGIZED WITH GROUNDING DEVICE INSTALLED |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.2 | A finding of very low safety significance with an associated NCV of TS 5.4.1.a, "Procedures," was self-revealed on March 24, 2012, when operators energized an electrical bus in the switchyard with a grounding device still installed on that bus. Failure of
Region: III | Quad Cities | 26790 | 06/30/2012 08/02/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | PROCEDURE NONCOMPLIANCE IMPACTING RELIABILITY OF HPCI |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 |  | 71111.2 | An NRC-identified finding of very low safety significance with an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Procedures," was identified on March 27, 2012, when station employees did not adhere to station seismic controls while performing Unit
Region: III | Quad Cities | 26796 | 06/30/2012 08/02/2012 | 2012003-03 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO IDENTIFY DESIGN DEFICIENCY IN VENDOR PRODUCT |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding of very low safety significance with an associated NCV of Technical Specification (TS) 3.7.7, "Main Turbine Bypass Valves System," was identified on April 18, 2012, when an unplanned reactor scram occurred during generator voltage
Region: III | Quad Cities | 26788 | 03/31/2012 05/07/2012 | 2012002-01 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW CLEARANCE ORDER INSTRUCTIONS |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 |  | NONE | A self-revealed finding of very low safety significance and associated NCV of Technical Specifications 5.4.1.a, "Procedures," was identified on November 29, 2011, when operators performing the removal of danger tags for a Unit 1 refuel bridge clearance fo
Region: III | Quad Cities | 26787 | 10/21/2011 12/05/2011 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that RHR Would Be Capable to Respond to a LOCA at Mode 3 |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 2515/177 | The inspectors identified a finding of very low safety significance and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the emergency core cooling system mode of operation of the res
Region: III | Quad Cities | 26778 | 10/21/2011 12/05/2011 | 2011009-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Calibration Tolerance Limits for Electrical Relay Settings |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to specify in a design calculation the allowabl
Region: III | Quad Cities | 26782 | 10/21/2011 12/05/2011 | 2011009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required In-Service Testing of Shutdown Cooling Suction Valves |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of Technical Specification 5.5.6, "Inservice Testing Program," for the failure to perform required testing in accordance with the American Socie
Region: III | Quad Cities | 26783 | 10/21/2011 12/05/2011 | 2011009-05 | NRC | NCV | Mitigating Systems | Green | Safety-Related Battery Charger Testing and Maintenance Procedures Did Not Include Steps for Electrolytic Capacitor Replacement |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The inspectors identified a finding of very low safety significance (Green) and associated Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for the licensee's failure to have appropriate maintenance
Region: III | Quad Cities | 26772 | 09/30/2011 11/01/2011 | 2011004-01 | Self - Revealed | NCV | Initiating Events | Green | VALVE OUT OF POSITION IN RADWASTE |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.04Q | A self revealed finding of very low safety significance with an associated NCV of Technical Specification (TS) 5.4.1.a was identified for failure to properly track the abnormal position of the waste sample tanks or floor drain sample tanks to waste collec
Region: III | Quad Cities | 26771 | 09/30/2011 11/01/2011 | 2011004-02 | NRC | NCV | Public Radiation Safety | Green | TURBINE BUILDING DIFFERENTIAL PRESSURE INDICATING POSITIVE |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.04Q | An NRC identified finding of very low safety significance with an associated NCV of 10 CFR 20.1302 was identified for failure to take action to prevent a potential unmonitored release on August 3, 2011, when the turbine building differential pressure indi
Region: III | Quad Cities | 26773 | 09/30/2011 11/01/2011 | 2011004-03 | NRC | FIN | Initiating Events | Green | NON-SAFETY RELATED MAIN STEAM MODIFICATION FAILURE |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000254 Quad Cities 1 |  | 71111.18 | NRC inspectors identified a finding of very low safety significance when analysis performed for installation of a small bore instrument sensing line modification for Unit 1 main turbine thermal performance testing did not include all applicable stresses a
Region: III | Quad Cities | 26774 | 09/30/2011 11/01/2011 | 2011004-04 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO APPROPRIATELY INSPECT SAFETY-RELATED ROOM COOLER |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self revealed finding of very low safety significance with an associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified when a service water leak occurred on the Unit 1 emergency diesel generator cool
Region: III | Quad Cities | 26762 | 06/30/2011 08/01/2011 | 2011003-01 | Self - Revealed | NCV | Initiating Events | Green | RWCU PUMPS TRIPPED ON LOW FLOW |  | H.3(b) Work Activity Coordination | TE?: N | 05000254 Quad Cities 1 |  | 71111.13 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR 50.65(a)(4) was identified for failure to adequately assess and manage risks associated with maintenance activities to prevent plant transients that upset plant stability
Region: III | Quad Cities | 26763 | 06/30/2011 08/01/2011 | 2011003-02 | Self - Revealed | NCV | Initiating Events | Green | WRONG LIMIT ERROR DURING SURVEILLANCE |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A self-revealed finding of very low safety significance and associated NCV of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures. and Drawings," was identified on May 4, 2011, when instrument technicians caused a control room alarm on Unit 2 af
Region: III | Quad Cities | 26770 | 06/23/2011 07/21/2011 | 2010503-02 | NRC | FIN | Emergency Preparedness | Green | Chnages to EAL Basis Decreased the Effectiveness of the Plan without Prior NRC Approval. |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71114.04 | The inspector identified a finding of very low safety significance involving a Severity Level IV NCV of 10 CFR 50.54(q) for failing to obtain prior approval for an emergency plan change which decreased the effectiveness of the plan. Specifically, the lice
Region: III | Quad Cities | 26758 | 03/31/2011 04/27/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | MSIV RPS LIMIT SWITCH PRECONDITIONING |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.22 | NRC inspectors identified a finding of very low safety significance (Green) and an associated NCV of 10 CFR 50, Appendix B, Criterion V on December 21, 2010. While observing performance of QCOS 0250-01, "MSIV [Main Steam Isolation Valve] Scram Sensor Chan
Region: III | Quad Cities | 26759 | 03/31/2011 04/27/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | UNIT 1/2 EDG OUTPUT BREAKER FAILURE TO UNIT 2 |  | P.2(b) Implementing Operating Experience | TE?: N | 05000265 Quad Cities 2 |  | 71111.22 | A self-revealed finding of very low safety significance (Green) and associated NCV of Technical Specification 5.4.1.a was identified on March 7, 2011, when a broken wire lug prevented closure of the 1/2 emergency diesel generator (EDG) output supply break
Region: III | Quad Cities | 26757 | 12/31/2010 02/03/2011 | 2010005-02 | NRC | NCV | Public Radiation Safety | Green | FAILURE TO UPDATE THE UFSAR FOR FIRE PROTECTION DOCUMENTS |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A Severity Level IV NCV of 10 CFR 50.71(e), "Periodic Update of the Final Safety Analysis Report," and an accompanying Green finding were identified by the inspectors for the failure to update documents incorporated by reference in the Updated Final Safet
Region: III | Quad Cities | 26755 | 09/30/2010 11/01/2010 | 2010004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to assess and manage maintenance risks resulting in a Unit 2 Manual Reactor SCRAM |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding of very low safety significance (Green) and associated NCV of 10 CFR 50.65(a)(4) was identified for failure to assess and manage risks associated with maintenance activities. The applicable maintenance activities occurred between J
Region: III | Quad Cities | 26751 | 06/30/2010 08/05/2010 | 2010003-01 | Self - Revealed | NCV | Barrier Integrity | Green | LOSS OF POWER TO FREEZE SEAL MACHINE DURING OPDRV |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and a NCV of 10 CFR Part 50.65(a)(4) was self revealed on March 25, 2010, when operators turned off the electrical power to one of the two electrical freeze seal machines being used to apply a reactor coolant syst
Region: III | Quad Cities | 26752 | 06/30/2010 08/05/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | PCIS RELAY COMMON NEUTRAL BROKEN |  | H.3(b) Work Activity Coordination | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A self revealed finding of very low safety significance and a NCV of Technical Specification (TS) 5.4.1 was identified on April 8, 2010, when a Unit 2 Group III containment isolation signal was received during replacement of a primary containment isolatio
Region: III | Quad Cities | 26753 | 06/30/2010 08/05/2010 | 2010003-03 | NRC | NCV | Emergency Preparedness | Green | INCORRECT WIND DIRECTION ON NARS FORM |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A NRC-identified finding of very low safety significance and associated NCV of 10 CFR 50.47(b)(9) was identified for delayed corrective action without appropriate compensatory actions for a defective computer point that sends wind direction data to the pl
Region: III | Quad Cities | 26754 | 06/30/2010 08/05/2010 | 2010003-04 | Self - Revealed | NCV | Mitigating Systems | Green | MODE CHANGE WITHOUT REQUIRED RPS INSTRUMENT |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A self revealed finding of very low safety significance and a NCV of TS 3.0.4 was identified on April 14, 2010, when operators changed operating modes from MODE 2 to MODE 1 without having all required channels of the reactor protection system (RPS) turbin
Region: III | Quad Cities | 26161 | 12/31/2009 01/27/2010 | 2009005-02 | Self - Revealed | FIN | Barrier Integrity | Green | DARLEY PUMP LEAKING GASOLINE FROM THE FUEL PUMP |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance was self-revealed for the failure to perform maintenance that would ensure the pump was in a standby condition and readily available to accomplish the requirements of QCOA 0010-16, "Flood Emergency Procedure." Alt
Region: III | Quad Cities | 26168 | 12/31/2009 01/27/2010 | 2009005-03 | Self - Revealed | NCV | Mitigating Systems | Green | TEMPERATURE INDICATING PROBE FOUND BROKEN IN THE UNIT 2 DIESEL GENERATOR COOLANT SYSTEM |  |  | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and an NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was self-revealed for the installation of an inappropriate component into the Unit 2 emergency diesel generator coolant sy
Region: III | Quad Cities | 26750 | 12/31/2009 01/27/2010 | 2009005-04 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE OF RHR TORUS SPRAY ISOLATION VALVE TO OPEN DUE TO DECLUTCH MECHANISM PROBLEMS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A finding of very low safety significance and an NCV of TS 3.6.2.4, "Residual Heat Removal (RHR) Suppression Pool Spray," was self-revealed for the licensee's failure to meet the TS limiting conditions of operation (LCO) requirements prior to transitionin
Region: III | Quad Cities | 26157 | 09/30/2009 11/09/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE OF LICENSEE TO PROPERLY TRANSLATE TS OPERABLE-OPERABILITY |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance and an NCV of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to provide a procedure appropriate to the circumstances for an activity affectin
Region: III | Quad Cities | 26159 | 09/30/2009 11/09/2009 | 2009004-03 | Self - Revealed | NCV | Barrier Integrity | Green | INOP RCIC PRIMARY CONTAINMENT ISOLATION VALVES |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A finding of very low safety significance and an NCV of TS 5.4.1.a were self-revealed for the failure of the Unit 1 reactor core isolation cooling (RCIC) steam exhaust check valve that resulted in a trip of the RCIC system and created a condition where bo
Region: III | Quad Cities | 26155 | 09/10/2009 10/06/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Lack of Water Spray System Piping |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | A finding of very low safety-significance and associated non-cited violation (NCV) of license condition 3.F for Units 1 and 2 was identified by the inspectors for the licensee's failure to evaluate the lack of supports for a water spray system. Specifical
Region: III | Quad Cities | 26156 | 09/10/2009 10/06/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Electrical Coordination for Control Circuit |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | A finding of very low safety-significance and NCV of 10 CFR Part 50, Appendix R, Section III.L.3 was identified by the inspectors for the licensee's failure to ensure that the alternate shutdown capability was independent from the fire area of concern. Sp
Region: III | Quad Cities | 26151 | 06/30/2009 07/31/2009 | 2009003-01 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE PROCEDURAL ADHERENCE DURING UNIT 1 TIP PM TESTING |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 |  | 71111.18 | A finding of very low safety significance and associated Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V was self-revealed during the performance of the Unit 1 traversing incore probe (TIP) modification testing on March 27, 2009. During modifica
Region: III | Quad Cities | 26152 | 06/30/2009 07/31/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURAL GUIDANCE FOR SHUTDOWN AFTER OPERATING BASIS EARTHQUAKE |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71114.06 | A finding of very low safety significance and associated Non-Cited Violation was identified by NRC inspectors for an inadequate procedure, QCOA 0010-09 "Earthquake." This procedure did not direct a shutdown in response to an earthquake event in excess of
Region: III | Quad Cities | 26153 | 06/30/2009 07/31/2009 | 2009003-03 | Self - Revealed | NCV | Mitigating Systems | Green | 1/2 EDGCWP FAILED TO SWAP FEEDS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A finding of very low safety significance and a Non-Cited Violation of Quad Cities Unit 2 Renewed License No. DPR-30 condition 3.B was self-revealed on April 10, 2009, when a previously unidentified blown fuse on a 1/2 emergency diesel generator (EDG) con
Region: III | Quad Cities | 26154 | 06/30/2009 07/31/2009 | 2009003-04 | Self - Revealed | NCV | Mitigating Systems | Green | TRIP OF UNIT 2 FUEL POOL COOLING WATER PUMPS DURING SCORPION PLATFORM REMOVAL |  | H.3(b) Work Activity Coordination | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A finding of very low safety significance and Non-Cited Violation of 10 CFR 50.65(a)(4) was self-revealed on May 11, 2009, when the licensee staff failed to manage water level in the spent fuel pool and associated skimmer surge tanks resulting in the Unit
Region: III | Quad Cities | 26143 | 03/31/2009 05/12/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | BROKEN LATCH ON FIRE DOOR 145 |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.04Q | Inspectors identified a Non-Cited Violation of License Condition 3.F, having very low safety significance for failure to ensure that Fire Door 145 could be positively latched. Section 2-8.4.4 of the National Fire Protection Association (NFPA) 80-1975, "Fi
Region: III | Quad Cities | 26144 | 03/31/2009 05/12/2009 | 2009002-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW WORK INSTRUCTIONS FOR 2A CORE SPRAY CHECK VALVE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | 71111.19 | A self-revealed finding of very low safety significance (Green) and Non-Cited Violation of Technical Specification 5.4.1.a was identified by inspectors on January 15, 2009, when the 2A core spray pump discharge check valve, 2-1402-8A, failed to close. Spe
Region: III | Quad Cities | 26145 | 03/31/2009 05/12/2009 | 2009002-03 | Self - Revealed | FIN | Mitigating Systems | Green | UNIT 1F DRYWELL COOLER IMPROPER RESTORATION FROM MAINTENANCE |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 |  | 71111.19 | A self-revealed finding of very low safety significance was identified by the inspectors for incorrect wiring of the circuit breaker for the 1F drywell cooler following system restoration from a breaker cubicle inspection. The wiring discrepancy was not d
Region: III | Quad Cities | 26149 | 03/31/2009 05/12/2009 | 2009002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATION AND RADIATION WORK PERMIT REQUIREMENTS DURING WORK IN A LOCKED HIGH RADIATION AREA |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7112101 | A self-revealed finding of very low safety significance and an associated Non Cited Violation (NCV) of Technical Specification 5.7.1 was identified by inspectors for the failure to comply with the requirements of the radiation work permit during work acti
Region: III | Quad Cities | 26150 | 03/31/2009 05/12/2009 | 2009002-05 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE OF THE UNIT 2 EMERGENCY DIESEL GENENERATOR COOLING WATER PUMP |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding of very low safety significance (Green) and NCV of 10 CFR 50, Appendix B, Criterion III, Design Control was identified by inspectors when the Unit 2 diesel generator cooling water pump failed on November 12, 2008, due to damage cau
Region: III | Quad Cities | 26136 | 12/31/2008 01/28/2009 | 2008005-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO REMOVE FME DEVICE. |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 |  | 71111.19 | A self-revealed finding of very low safety significance (Green) was identified for failure to remove a foreign material exclusion device from the thrust bearing oil supply line of a feed pump during maintenance on November 3, 2008. The pump was returned t
Region: III | Quad Cities | 26137 | 12/31/2008 01/28/2009 | 2008005-02 | NRC | FIN | Initiating Events | Green | EXPLOSION OF THE FDSgT VESTIBULE. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding of very low safety significance was identified for inadequate procedures that resulted in an onsite explosion on October 27, 2008. Specifically, operating procedures for the floor drain surge tank did not include appropriate warnin
Region: III | Quad Cities | 26132 | 10/24/2008 12/05/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Use of Non-Conservative Inputs and Methodologies in Calculating Terminal Voltages to Safety-Related MOV Motors During Design Basis Events |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | A finding of very low safety significance (Green) involving a NCV of 10 CFR Part 50, Appendix B, Criterion III, Design Control, was identified by the inspectors for the failure to evaluate the effect of lower transient voltages that would exist for safety
Region: III | Quad Cities | 26133 | 10/24/2008 12/05/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations/Analyses and Testing for Thermal Overload Relays (TOLs) on Safety-Related MOVs |  | P.3(a) Self-Assessment | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to assure that thermal overload relays (TOLs) on safety-related motor-ope
Region: III | Quad Cities | 26134 | 10/24/2008 12/05/2008 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | Seismic Qualification of 250 VDC Batteries |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | A finding of very low safety significance (Green) and associated NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified by the inspectors for the failure to assure that 250VDC safety-related batteries were installed in accordan
Region: III | Quad Cities | 26135 | 10/24/2008 12/05/2008 | 2008007-04 | NRC | FIN | Mitigating Systems | Green | Inaccurate RCIC Instrument Setpoints |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | A finding of very low safety significance was identified by the inspectors for failure to accurately implement the design setpoint for reactor core isolation cooling turbine exhaust pressure switches 1(2)-1360-26A/B. The licensee entered this issue into i
Region: III | Quad Cities | 26124 | 09/30/2008 11/10/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | 2D Vault Door Work Order Instructions Not Followed |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | 71111.06 | A self-revealing finding of very low safety significance and associated NCV of TS 5.4.1 was identified for failure to follow written work instructions resulting in a non-functional main control room alarm and degraded flood protection measures. Specifical
Region: III | Quad Cities | 26127 | 09/30/2008 11/10/2008 | 2008004-02 | NRC | NCV | Initiating Events | Green | Inadvertent Initiation of the Unit 1 Feedwater Regulating Valve Fire Protection Deluge |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000254 Quad Cities 1 |  | 71111.06 | On August 20, a self-revealing finding of very low safety significance and associated Non-Cited Violation (NCV) of Technical Specification (TS) 5.4.1 were identified for an inadequate work instruction for Work Order 00781735-01, "Replace Power Supply for
Region: III | Quad Cities | 26131 | 09/30/2008 11/10/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess and Manage Risk Associated with Work on U1 SBO. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.13 | NRC inspectors identified a finding of very low safety significance and an associated NCV of 10 CFR 50.65(a) (4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," when the licensee failed to effectively evaluate the
Region: III | Quad Cities | 26122 | 06/30/2008 07/24/2008 | 2008003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Exceeded 50 Degree Differential Temperature Limit of TS 3.4.9 when starting Recirculation Pump |  | H.1(c) Communication of Decisions | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A Non-Cited violation of Technical Specification 3.4.9, "RCS Pressure and Temperature (P/T) Limits," was identified on March 31, 2008 when operators did not establish effective controls to ensure compliance with the Technical specification when they start
Region: III | Quad Cities | 26111 | 03/31/2008 05/01/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | RISK ASSESSMENT OF REACTOR CORE ISOLATION COOLING FLOW CONTROLLER FAILURE |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 |  | 71111.13 | A self-revealing finding of very low safety significance and Non Cited Violation of 10 CFR Part 50.65(a)(4) was identified on January 15, 2008, due to the licensee's failure to properly assess and manage the risk associated with the emergent failure of th
Region: III | Quad Cities | 26112 | 03/31/2008 05/01/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | SAFE SHUTDOWN MAKEUP PUMP LOW DISCHARGE PRESSURE |  | P.1(b) Trend Performance CAP | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.13 | A self-revealing finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, was identified on December 17, 2007, for an inadequate pump fill and vent procedure that resulted in pump degradation to the safe shu
Region: III | Quad Cities | 26120 | 03/31/2008 05/01/2008 | 2008002-03 | NRC | NCV | Barrier Integrity | Green | UNIT 2 ISOLATION OF REACTOR BUILDING VENTILATION AND AUTO START OF STANDBY GAS TREATMENT |  | H.4(a) Human Error Prevention | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A self-revealing finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 was identified on March 14, 2008, when operators transferring power using procedure QCOP 6800-03, "Essential Service System," caused an unp
Region: III | Quad Cities | 26121 | 03/31/2008 05/01/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | 1/2 "A" DIESEL FIRE PUMP OIL LEAK AND FIRE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealing finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 was identified due to the failure to establish, implement, and maintain procedures associated with the fire protection program. Work instru
Region: III | Quad Cities | 26104 | 12/31/2007 01/30/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | INADEQUATE FIRE PROTECTION PROCEDURES |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | NONE | A self-revealing finding of very low safety significance and a Non-Cited Violation of Technical Specification 5.4.1 was identified on November 10, 2006, due to the failure to establish, implement, and maintain procedures associated with the fire protectio
Region: III | Quad Cities | 26110 | 12/31/2007 01/30/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURES FOR EXTERNAL FLOODING AND TESTING OF FLOODING PUMP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance and a Non Cited Violation of Technical Specification 5.4.1 due to the failure to develop adequate surveillance testing and operating procedures for equipment used during an external flood
Region: III | Quad Cities | 26093 | 09/30/2007 10/31/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | DOCUMENTATION ISSUES RESULT IN UNEXPECTED SAFETY-RELATED VALVE LEAKAGE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 |  | 71111.2 | A self-revealing finding and Non-Cited Violation of Technical Specification 5.4.1 was identified due to the failure to properly preplan and perform maintenance on safety-related equipment in May 2007. This failure resulted in unexpected leakage on two saf
Region: III | Quad Cities | 26095 | 09/30/2007 10/31/2007 | 2007004-03 | NRC | NCV | Initiating Events | Green | FAILURE TO HAVE ADEQUATE PROCEDURES AND USE HUMAN PERFORMANCE TOOLS RESULTS IN REACTOR WATER CLEANUP ISOLATION |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealing finding and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, was identified on August 22, 2007. The finding occurred due to the failure to have instructions and procedures appropriate to the circumstance for performing valve o
Region: III | Quad Cities | 26096 | 09/30/2007 10/31/2007 | 2007004-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO FOLLOW PROCEDURES AND USE HUMAN PERFORMANCE TOOLS RESULTS IN REACTOR BUILDING VENTILATION ISOLATION |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealing finding and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, was identified on September 8, 2007, due to the failure to follow procedures during the performance of Unit 1 125 Vdc ground detection activities. The failure t
Region: III | Quad Cities | 26101 | 09/30/2007 10/31/2007 | 2007004-05 | NRC | NCV | Barrier Integrity | Green | INADEQUATE CLEARANCE ORDER RESULTS IN FUEL POOL COOLING PUMP TRIP |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealing finding and Non-Cited Violation of Technical Specification 5.4.1 was identified on July 30, 2007, due to the failure to properly implement OP-AA-109-101, "Clearance and Tagging." This failure resulted in tripping the 1A fuel pool cooling
Region: III | Quad Cities | 26102 | 09/30/2007 10/31/2007 | 2007004-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT MARCH 2007 1D RESIDUAL HEAT REMOVAL PUMP BREAKER FAILURE |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | A self-revealing finding and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI, was identified in September 2007 for the failure to identify and correct a condition adverse to quality. Specifically, the licensee failed to assure that the cause
Region: III | Quad Cities | 26103 | 09/30/2007 10/31/2007 | 2007004-07 | NRC | NCV | Initiating Events | Green | FAILURE TO CONTROL TRANSIENT COMBUSTIBLES IN THE CABLE SPREADING ROOM |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000265 Quad Cities 2 |  | NONE | An inspector-identified finding and a Non-Cited Violation of a Quad Cities Nuclear Power Station license condition for fire protection was identified on May 3, 2007, due to the failure to adequately control transient combustible materials in a transient c
Region: III | Quad Cities | 26092 | 09/07/2007 10/10/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Delays in ECCS MOV's Due to Voltage Dips during Load Sequencing |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111117B | The inspections identified an NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that was of very low safety significance. Specifically, Motor Operated Valve (MOV) delays caused by voltage dips during load sequencing were not translated i
Region: III | Quad Cities | 26086 | 06/30/2007 07/27/2007 | 2007003-04 | NRC | NCV | Initiating Events | Green | UNQUALIFIED TARGET ROCK VALVE REPAIR |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71111.08G | On May 7, 2007, the inspectors identified a finding, and a Non-Cited Violation of 10 CFR 50.55a(g)4, for the failure to complete Code qualified weld repairs for Main Steam Safety Relief Valve 1-0203-3A. Specifically, the weld procedures for this repair we
Region: III | Quad Cities | 26087 | 06/30/2007 07/27/2007 | 2007003-05 | NRC | FIN | Mitigating Systems | Green | INADEQUATE OPERABILITY JUSTIFICATION FOR UNIT 2 4 KV BREAKERS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000265 Quad Cities 2 |  | 71111.15 | The inspectors identified a finding of very low safety significance on May 21, 2007, due to the failure to adequately document and justify the basis for continued operability of the 4 kV breakers in Unit 2 following the identification of a common mode fai
Region: III | Quad Cities | 26089 | 06/30/2007 07/27/2007 | 2007003-07 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY IMPLEMENT DRYWELL CLOSEOUT PROCEDURE |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000254 Quad Cities 1 |  | 71111.2 | The inspectors identified a finding of very low safety significance, and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V, due to the failure to effectively implement QCOS 1600-32, "Drywell/Torus Closeout," in May 2007. Corrective actions for t
Region: III | Quad Cities | 26090 | 06/30/2007 07/27/2007 | 2007003-08 | NRC | FIN | Initiating Events | Green | MANUAL REACTOR SCRAM DUE TO PLUGGED PRESSURE SENSING LINE |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A finding of very low safety significance was self-revealed on February 28, 2007, when operations personnel inserted a manual scram in response to increasing condenser back pressure. The licensee determined that blockage of an offgas system pressure sensi
Region: III | Quad Cities | 26076 | 03/31/2007 05/03/2007 | 2007002-02 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO COMPLETE HYDROSTATIC TESTS ON ALL SCBA AIR BOTTLES AT PROCEDURAL REQUIRED INTERVALS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7112103 | The inspectors identified a Green finding and a Non-Cited Violation of NRC requirements on February 8, 2007, due to the licensee's failure to complete hydrostatic tests on multiple self-contained breathing apparatus (SCBA) air bottles at the required freq
Region: III | Quad Cities | 26080 | 03/31/2007 05/03/2007 | 2007002-03 | NRC | FIN | Mitigating Systems | Green | INADQUATE OVERSIGHT AND PERFORMANCE OF TRAINING RESULTS IN TRIPPING AN OPERATING CONTROL ROOM FAN |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding was identified on January 1, 2007, when an initial license trainee tripped the "A" control room ventilation system during a training evolution. The inspectors determined that inadequate oversight of the training evolution by the ta
Region: III | Quad Cities | 26081 | 03/31/2007 05/03/2007 | 2007002-04 | NRC | NCV | Initiating Events | Green | FAILURE TO HAVE PROCEDURES APPROPRIATE TO THE CIRCUMSTANCE FOR REPLACING THE MAIN STEAM LINE LOW PRESSURE TIME DELAY RELAY |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000265 Quad Cities 2 |  | 71153 | A self-revealed finding was identified when Unit 2 experienced an unexpected half Group I containment isolation signal on January 23, 2007. The half isolation signal was caused by the licensee's failure to have procedures appropriate to the circumstance f
Region: III | Quad Cities | 26082 | 03/31/2007 05/03/2007 | 2007002-05 | NRC | NCV | Mitigating Systems | Green | REPLACING UNIT 2 PORVS WITH ERVS NOT IN ACOCRDANCE WITH 10 CFR 50.49 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000265 Quad Cities 2 |  | NONE | The team identified a finding of very low safety significance involving the replacement of an environmentally qualified (EQ) Category I component with an EQ Category II component. Specifically, a Non-Cited Violation of 10 CFR 50.49, was associated with th
Region: III | Quad Cities | 26070 | 12/31/2006 01/31/2007 | 2006007-01 | NRC | FIN | Mitigating Systems | Green | PERFORMANCE OF MAINTENANCE ACTIVITIES WITHOUT A PROCEDURE |  | H.4(a) Human Error Prevention | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71152 | The inspectors identified a Green finding due to the licensee's performance of maintenance without documented work instructions on two occasions. In one instance, the licensee failed to identify that the agitation of the 2A reactor feedwater pump minimum
Region: III | Quad Cities | 26071 | 12/31/2006 01/31/2007 | 2006007-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENTER TS 3.1.7 IN A TIMELY MANNER |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000254 Quad Cities 1 |  | 71153 | The inspectors identified a Green finding and Non-Cited Violation of Technical Specification 3.1.7 due to the licensee's failure to enter the associated limiting condition for operation upon obtaining information which challenged the continued operability
Region: III | Quad Cities | 26073 | 12/15/2006 01/29/2007 | 2006017-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO DEVELOP CORRECTIVE ACTIONS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to assure that conditions adverse to quality were promptly corrected. Specifically, the inspectors concluded that the licensee failed to develo
Region: III | Quad Cities | 26055 | 11/03/2006 11/28/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with TS SR 3.8.4.2 for 125 Vdc Battery Terminal Connection Corrosion and Resistance Measurements (Section 1R21.3.b.1) |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a Non-Cited Violation (NCV) of Technical Specification (TS) Surveillance Requirements (SR) 3.8.4.2, Amendment 199/195, having very low safety significance for failure to meet the TS SR when visible corrosion on Units 1 and 2, 125 Vdc s
Region: III | Quad Cities | 26059 | 11/03/2006 11/28/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Battery Connection Resistance Value Specified in TS SRs Insufficient to Ensure Operability (Section 1R21.3.b.2) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the failure to verify and ensure that the 125 Vdc safety-related batteries would remain operable if all the inter-cell
Region: III | Quad Cities | 26060 | 11/03/2006 11/28/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | Calculation Input Design Data Discrepancies for the Auxiliary Power Analysis and EDG Loading (Section 1R21.3.b.3) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving inadequate design review of the loading calculation for the emergency diesel generators (EDG's). Specifically, the lice
Region: III | Quad Cities | 26061 | 11/03/2006 11/28/2006 | 2006003-04 | NRC | NCV | Mitigating Systems | Green | Licensee Used Inappropriate Vortex Analysis Methodology (Section 1R21.3.b.4) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving licensee's failure to select an appropriate method for calculating the onset of vortexing at the intake of the high pre
Region: III | Quad Cities | 26062 | 11/03/2006 11/28/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | Sizing Calculation for ADS/SRV Air Accumulator Storage Tank (Section 1R21 Non-Conservative .3.b.5) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance involving the sizing calculation for the Target Rock ADS/SRV air accumulator tank. Specifically, the team identified that the lic
Region: III | Quad Cities | 26063 | 11/03/2006 11/28/2006 | 2006003-06 | NRC | NCV | Mitigating Systems | Green | Discrepant MCC Voltages Used in Degraded MOV Voltage Drop Calculations (Section 1R21.3.b.6) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance concerning the failure to use proper and most current design input for the control circuit voltage drop calculation for safety re
Region: III | Quad Cities | 26064 | 11/03/2006 11/28/2006 | 2006003-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Load Tabulation in Operations Procedure QCOP 6500-28 (Section 1R21.3.b.7) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for failing to maintain an adequate procedure for establishing an accurate load tabulation to ensure that t
Region: III | Quad Cities | 26065 | 11/03/2006 11/28/2006 | 2006003-08 | NRC | NCV | Mitigating Systems | Green | Inconsistency in Procedures for Cleaning Batteries (Section 1R21.3.b.8) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for the operations 125 Vdc safety-related battery procedure being discrepant from vendor specified instruct
Region: III | Quad Cities | 26066 | 11/03/2006 11/28/2006 | 2006003-09 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Preventive Maintenance Procedure Requirements Concerning Re-Torquing of Corroded Electrical Terminal Connections (Section 1R21.3.b.9) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for failure to follow the 125 Vdc station battery preventive maintenance procedure requirement and vendor r
Region: III | Quad Cities | 26067 | 11/03/2006 11/28/2006 | 2006003-10 | NRC | NCV | Mitigating Systems | Green | Non-Conservative HPCI Pump Test Acceptance Criteria (Section 1R21.3.b.10) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance for failure to ensure that the HPCI pump hydraulic performance tests had acceptance criteria that incorporated the acceptance limits
Region: III | Quad Cities | 26068 | 11/03/2006 11/28/2006 | 2006003-11 | NRC | NCV | Mitigating Systems | Green | Non-conservative Safety-Related Air Storage Tank Capacity Test (Section 1R21.3.b.11) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121 | The team identified a NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance involving the air drop testing for the Target Rock ADS/SRV air accumulator tank. Specifically, the team identified that the licensee
Region: III | Quad Cities | 26069 | 11/03/2006 11/28/2006 | 2006003-12 | NRC | FIN | Mitigating Systems | Green | Shift Management Failed to Adequately Document Basis for Operability Determination (Section 1R21.3.b.12) |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 7111121
Region: III | Quad Cities | 26051 | 09/30/2006 10/31/2006 | 2006006-01 | NRC | NCV | Initiating Events | Green | POOR MAINTENANCE WORK PRACTICES AND PROCEDURAL COMPLIANCE ISSUES RESULTS IN TWO FEEDWATER LEAKS AND TWO UNPLANNED POWER REDUCTIONS |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealed finding was identified due to the discovery of two separate Unit 1 feedwater leaks in July 2006. The leaks were caused by poor maintenance work practices and resulted in two unplanned power reductions. The failure to implement and maintain
Region: III | Quad Cities | 26052 | 09/30/2006 10/31/2006 | 2006006-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO CORRECT MAIN STEAM SAFETY VALVE TS ISSUES |  | P.1(b) Trend Performance CAP | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | The inspectors identified a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion XVI, due to the licensee's failure to correct a condition adverse to quality. Specifically, the licensee had not implemented timely actions to correct the repeated in
Region: III | Quad Cities | 26053 | 09/30/2006 10/31/2006 | 2006006-03 | NRC | NCV | Mitigating Systems | Green | UNEXPECTED START OF UNIT 1 EMERGENCY DIESEL GENERATOR |  | H.4(b) Procedural Compliance | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71153 | A self-revealing finding and a Non-Cited Violation of Technical Specification 5.4.1 were identified when operations performed activities which resulted in the unexpected start of the Unit 1 emergency diesel generator. The unexpected actuation was caused b
Region: III | Quad Cities | 26054 | 09/30/2006 10/31/2006 | 2006006-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EFFECTIVELY CONTROL CONDITION OF INTERNAL FLOODING PROTECTION CHECK VALVES THROUGH PERFORMANCE OF APPROPRIATE PREVENTIVE MAINTENANCE |  |  | TE?: N | 05000254 Quad Cities 1 |  | NONE | The inspectors identified a Non-Cited Violation of 10 CFR Part 50.65 due to the licensee's failure to demonstrate that the performance and condition of the turbine building internal flooding protection check valves was being effectively controlled through
Region: III | Quad Cities | 26035 | 06/30/2006 07/26/2006 | 2006005-01 | NRC | FIN | Mitigating Systems | Green | FAILURE TO EVALUATE AND ADDRESS LONG-STANDING DEGRADATION OF RHRSW SUMP PUMPS PRIOR TO IMPACTING INTERNAL FLOODING PROTECTION EQUIPMENT |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.06 | The inspectors identified a Green finding in June 2006 due to the licensee's failure to recognize and address long-standing degradation of the residual heat removal service water (RHRSW) vault sump pumps. This issue was determined to be more than mino
Region: III | Quad Cities | 26037 | 06/30/2006 07/26/2006 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE OF THE 1B CORE SPRAY PUMP TO START DUE TO BREAKER ALIGNMENT ISSUES |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealing Green finding and a Non-Cited Violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," were identified on January 4, 2006, due to the Unit 1 "B" core spray system failing to start during testing. The
Region: III | Quad Cities | 26038 | 06/30/2006 07/26/2006 | 2006005-04 | NRC | FIN | Initiating Events | Green | TURBINE/GENERATOR LOAD REJECT AND REACTOR SCRAM DUE TO MAIN POWER TRANSFORMER ISSUES |  |  | TE?: N | 05000254 Quad Cities 1 |  | 71153 | A self-revealing Green finding was identified on February 22 when the Unit 1 main turbine tripped causing a reactor scram. The licensee's post-scram efforts determined that the turbine trip was caused by degradation of the main power transformer protectiv
Region: III | Quad Cities | 26039 | 06/29/2006 07/31/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | SSMP Credited as a Redundant System for an Appendix R III.G.2 Fire Area |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a Non-cited Violation of 10 CFR Part 50, Appendix R, Section III.G.2, having very low safety significance involving the licensee's failure to ensure, in the event of a severe fire, that one redundant train of systems necessary to
Region: III | Quad Cities | 26046 | 06/29/2006 07/31/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure To Ensure One Redundant Train of RHRSW Free of Fire Damage |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a NCV of 10 CFR Part 50, Appendix R, Section III.G.2, having very low safety significance (Green) involving the licensee failure to ensure, in the event of a severe fire, that one redundant train of systems necessary to achieve a
Region: III | Quad Cities | 26047 | 06/29/2006 07/31/2006 | 2006002-03 | NRC | NCV | Mitigating Systems | Green | Procedure Included Unapproved Fuse Repair for Appedix R |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," having very low safety significance (Green) involving inadequate procedure steps. Specifically, The licensee failed to provide adequate pr
Region: III | Quad Cities | 26048 | 06/29/2006 07/31/2006 | 2006002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Acceptable Pre-Fire Plans |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a NCV of QCNPS's license condition for fire protection, having very low safety significance (Green) involving the lack of complete and accurate information in the QCNPS's fire pre-plans for various plant fire areas. Specifically,
Region: III | Quad Cities | 26049 | 06/29/2006 07/31/2006 | 2006002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Have a Calculation for Hose Stations That Did Not Meet Code Requirements to Ensure Adequate Water Pressure and Flow Rate |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a NCV of QCNPS's license condition for fire protection, having very low safety significance (Green) involving adequacy of water pressure and flow rate at standpipes with hose connections. Specifically, the licensee failed to prov
Region: III | Quad Cities | 26050 | 06/29/2006 07/31/2006 | 2006002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Meet NFPA Code Requirements for Class A Fire Extinguishers |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05T | The inspectors identified a NCV of QCNPS's license condition for fire protection, having very low safety significance (Green) involving adequacy of number of Class A fire extinguishers. Specifically, the licensee failed to have an adequate number of Class
Region: III | Quad Cities | 26027 | 05/23/2006 05/30/2006 | 2006012-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ESTABLISH MEASURES TO ENSURE THAT THE UNIT 2 ERV ACTUATORS REMAINED SUITABLE FOR OPERATION WHILE OPERATING AT EPU POWER LEVELS |  |  | TE?: N | 05000265 Quad Cities 2 |  | 71152 | A self-revealing finding of very low safety significance, and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III, Design Control, was identified on December 30, 2005, following the discovery that the Unit 2 3D ERV would not have performed its s
Region: III | Quad Cities | 26020 | 02/07/2006 03/20/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO APPLY DESIGN CONTROL MEASURES TO ENSURE ERV PILOT VALVE/ACTUATOR SUPPORT WAS ADEQUATE FOR EPU OPERATION |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion III on January 15, 2006, for failure to adequately implement design control measures to ensure that the ERV assemblies were s
Region: III | Quad Cities | 26021 | 02/07/2006 03/20/2006 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE MAINTENANCE PROCEDURE TO INSPECT ERV ACTUATORS |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion V on January 10, 2006, for failure to implement procedures appropriate to the circumstance for previous inspection and disass
Region: III | Quad Cities | 26022 | 02/07/2006 03/20/2006 | 2006009-04 | NRC | NCV | Initiating Events | Green | FAILURE TO IDENTIFY DEGRADED UNIT 2 SNUBBER AND BROKEN WELDS ON PILOT VALVE/ACTUATOR SUPPORT |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | NONE | The inspectors identified a finding of very low safety significance and a Non-Cited Violation of 10 CFR 50, Appendix B, Criterion XVI on January 17, 2006, for failure to conduct effective walkdowns during the Unit 2 and Unit 1 outages that occurred on Dec
Region: III | Quad Cities | 125170 | 07/31/2019 |  |  | LIV |  | Green | Failure to Follow Administrative Requirements for Fire Protection |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.05Q
Region: III | Quad Cities | 125781 | 10/31/2019 |  |  | LIV |  | Green | Failure to Perform Multiple Channel Functional Tests on Unit 1 and Unit 2 Service Water Radiation Monitors. |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71124.05
Region: III | Quad Cities | 126267 | 01/29/2020 |  |  | LIV |  | Green | Failure to Ensure Flood Protection for Unit 2A RHRSW Vault |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.15
Region: III | Quad Cities | 26828 | 07/22/2013 | 2013003-03 | NRC | URI | Mitigating Systems | Green | FAILURE TO ASSESS IMPACT OF RELOCATING PORTABLE PUMPS OFFSITE |  |  | TE?: N | 05000254 Quad Cities 1 05000265 Quad Cities 2 |  | 71111.07T | In April 2001, the licensee completed a 10 CFR 50.59 Safety Evaluation Screening, QC-S-2001-0026, to assess removal of the portable pumps from onsite and relocating the pumps to an offsite leasing facility located a few hours away. The licensee justified
Region: IV | Arkansas Nuclear One | 125968 | 12/31/2019 01/29/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Restore a Fire Barrier to Functional Prior to De-Posting a Fire Watch |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 | Human Performance | 71111.05Q | The inspectors identified a Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, License Condition 2.C.(8), “Fire Protection,” for the licensee’s failure to implement all provisions of the approved fire protection program. Spe
Region: IV | Arkansas Nuclear One | 126340 | 12/31/2019 01/29/2020 | 2019004-02 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Torque Temporary Power Supply Terminal Screws in accordance with Station Procedures and the Vendor Manual |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 | SSC Performance | 71153 | The inspectors reviewed a self-revealed, Green finding associated with the licensee’s failure to torque temporary power supply terminal screws in accordance with torque specifications contained in Procedure EN-MA-145, “Maintenance Standard for Torque Appl
Region: IV | Arkansas Nuclear One | 125715 | 09/30/2019 11/05/2019 | 2019003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Install Correct Component and Perform Post Maintenance Testing |  | H.14 - Conservative Bias | TE?: N | 05000368 Arkansas Nuclear 2 | Equipment Performance | 71111.19 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 2, Technical Specification 6.4.1.a, for the licensee’s failure to properly pre-plan and perform maintenance that can affect the perform
Region: IV | Arkansas Nuclear One | 125907 | 09/30/2019 11/05/2019 | 2019003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000368 Arkansas Nuclear 2 | Equipment Performance | 71152 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct conditions adverse to quality, such as
Region: IV | Arkansas Nuclear One | 125260 | 06/30/2019 08/01/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Evaluate Operability of the Unit 1 Emergency Diesel Generator 2 Room Ventilation System |  | P.4 - Trending | TE?: N | 05000313 Arkansas Nuclear 1 | Equipment Performance | 71111.15 | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to complete an adequate operability evaluation in accordance with
Region: IV | Arkansas Nuclear One | 125256 | 06/30/2019 08/01/2019 | 2019002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Procedural Steps in Sequence during Surveillance Testing |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 | Human Performance | 71153 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One Unit 1, Technical Specification 5.4.1.a, for the licensee’s failure to implement Procedure OP-1304.206, “Unit 1 EFIC Channel B Monthly Test,
Region: IV | Arkansas Nuclear One | 124445 | 03/31/2019 04/30/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate the Design Requirements into Instructions for Service Water System Sluice Gate Single Failure |  | NONE | TE?: N | 05000313 Arkansas Nuclear 1 | Procedure Quality | 71111.04Q | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to translate design requirements for the Unit 1 service water system into instructions
Region: IV | Arkansas Nuclear One | 124334 | 03/31/2019 04/30/2019 | 2019001-02 | NRC | NCV | Initiating Events | Green | Welding Programmatic Issue |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 | Human Performance | 71111.08P | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion IX, “Control of Special Processes,” for a failure to establish measures to assure that welding and nondestru
Region: IV | Arkansas Nuclear One | 124718 | 03/31/2019 04/30/2019 | 2019001-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Take Timely Corrective Actions for a Previously Identified Deficient Condition Associated with Bussmann HKA Fuse Holder Caps |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 | Human Performance | 71152 | The inspectors identified a self-revealed, Green finding associated with the licensee’s failure to take timely corrective actions for potential failures identified through industry operating experience. Specifically, the licensee identified a failure mode
Region: IV | Arkansas Nuclear One | 124720 | 03/31/2019 04/30/2019 | 2019001-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Pre-Plan Maintenance that Affected Safety-Related Equipment |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 | Human Performance | 71153 | The inspectors identified a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, Technical Specifications 5.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of sa
Region: IV | Arkansas Nuclear One | 25918 | 12/30/2018 01/23/2019 | 2018004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Fully Implement Vendor Manual Recommended Preventative Maintenance |  | NPP | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 2, Technical Specification 6.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of safet
Region: IV | Arkansas Nuclear One | 24430 | 09/30/2018 11/13/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate the Design Requirements into Instructions for Refueling Emergency Diesel Generators |  | NPP | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.04Q | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to translate current design into instructions for Unit 1 and Unit 2 diesel fuel oil tra
Region: IV | Arkansas Nuclear One | 24431 | 09/30/2018 11/13/2018 | 2018003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Welding Standard Guidance and Examination Procedures |  | H.2 - Field Presence | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.12 | The inspectors reviewed a self-revealed Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, Technical Specification 5.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of safety
Region: IV | Arkansas Nuclear One | 24432 | 09/30/2018 11/13/2018 | 2018003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Safety-Related 4160 V Breaker Operability Following Maintenance Activities |  | P.3 - Resolution | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors reviewed a self-revealed Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, Technical Specification 5.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of safety
Region: IV | Arkansas Nuclear One | 24433 | 09/30/2018 11/13/2018 | 2018003-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Main Feedwater Pump B Discharge Pressure in Band Caused a Reactor Trip |  | H.4 - Teamwork | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, Technical Specifications 5.4.1.a, for the licensee’s failure to implement Procedure OP-1102.002, “Plant Startup,” Revision 106. Spec
Region: IV | Arkansas Nuclear One | 24630 | 09/30/2018 11/13/2018 | 2018003-06 | Self - Revealed | NCV | Initiating Events | Green | Reactor Power Transient Caused by the Turbine Bypass Valve Failing Open |  | P.3 - Resolution | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors reviewed a self-revealed Green finding and associated non-cited violation of Arkansas Nuclear One, Unit 1, Technical Specifications 5.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of safet
Region: IV | Arkansas Nuclear One | 24420 | 08/31/2018 10/22/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Size the Unit 1 Emergency Diesel Generator Room Ventilation Systems |  | NPP | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.21M | Performance Deficiency: The licensee’s failure to properly size the Unit 1 Emergency Diesel Generator room ventilation systems to deliver the design flow rate of 30,000 Cubic Feet per Minute by each of its two exhaust fans, as specified in design calc
Region: IV | Arkansas Nuclear One | 24421 | 08/31/2018 10/22/2018 | 2018011-02 | NRC | NCV | Mitigating Systems | Green | Failure of Both Arkansas Nuclear One Units to Establish Adequate Corrective Actions Resulting in Excessive Instances of Damaged and Broken Internals of the Emergency Feedwater Pump Turbine Steam Admission Check Valves. |  | H.6 - Design Margins | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.21M | Performance Deficiency: The licensee’s failure to correct a condition adverse to quality related to multiple failures of safety-related emergency feedwater pump turbine steam admission check valves was a deficiency. Screening: The inspectors deter
Region: IV | Arkansas Nuclear One | 24076 | 06/30/2018 07/30/2018 | 2018002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Implement Procedural Guidance to Close Spent Fuel Pool Cooler Outlet Crosstie Valve |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors reviewed a self-revealed, Green finding and associated non-cited violation of Arkansas Nuclear One (ANO) Unit 1 Technical Specification (TS) 5.4.1.a for the licensee’s failure to implement Procedure OP-1102.015, “Filling and Draining the Fu
Region: IV | Arkansas Nuclear One | 23523 | 03/31/2018 04/25/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Criteria for Flood Seal Testing |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.01 | The inspectors identified a Green finding and associated non-cited violation of Unit 1 Technical Specification 5.4.1.a and Unit 2 Technical Specification 6.4.1.a for the licensee’s failure to establish the criteria for ensuring the necessary conditions ex
Region: IV | Arkansas Nuclear One | 23532 | 03/31/2018 04/25/2018 | 2018001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Preplan and Perform Service Water Pre-Screen Maintenance |  | H.12 - Avoid Complacency | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation and associated finding of Arkansas Nuclear One, Unit 2, Technical Specification 6.4.1.a, for the licensee’s failure to properly preplan maintenance that can affect the performance of safety-rela
Region: IV | Arkansas Nuclear One | 23460 | 12/31/2017 02/01/2018 | 2017004-02 | NRC | FIN | Mitigating Systems | Green | Failure to Properly Plan Fire Water System Maintenance |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.18 | The inspectors identified a finding for the licensee’s failure to implement work management procedure requirements while planning compensatory measures needed to minimize plant risk during firewater system maintenance associated with fire protection valve
Region: IV | Arkansas Nuclear One | 22682 | 12/31/2017 02/01/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.13 - Consistent Process | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee’s failure to promptly identify and correct weakened closing springs, a condition adverse to quality,
Region: IV | Arkansas Nuclear One | 21642 | 09/30/2017 10/25/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Service Water Train Separation |  | H.14 - Conservative Bias | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.04Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to maintain train separation between safety-related service water trains when swapping the swing high pressure injection (HPI) pump between train
Region: IV | Arkansas Nuclear One | 1476 | 08/10/2017 09/21/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct an Inadequate Design Bases Calculation |  | H.9 - Training | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.21N | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Actions,” requires, in part, that measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions,
Region: IV | Arkansas Nuclear One | 22681 | 06/30/2017 08/03/2017 | 2017002-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Fire Protection Program Procedures |  | H.4 - Teamwork | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.08P | The inspectors identified a finding and associated non-cited violation of License Conditions 2.C.(3)(b), "Fire Protection," for Arkansas Nuclear One Unit 2, associated with the failure to adequately implement the fire protection program. Specifically, the
Region: IV | Arkansas Nuclear One | 24013 | 06/30/2017 08/03/2017 | 2017002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Install Set Screw Leads to Breaker Failure |  | NPP | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | The inspectors documented a Green self-revealing finding and associated non-cited violation of Unit 2 Technical Specification 6.4.1.a, for failure to properly pre-plan and perform maintenance on the Unit 2 containment spray pump B breaker in accordance wi
Region: IV | Arkansas Nuclear One | 1475 | 06/30/2017 08/03/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with ECCS Technical Specifications |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.19 | The inspectors reviewed a Green self-revealing finding and associated non-cited violation of Unit 1 Technical Specification 3.5.2, "Emergency Core Cooling System (ECCS) - Operating," for the licensee's failure to ensure the operability of the P36A high pr
Region: IV | Arkansas Nuclear One | 1455 | 05/01/2017 05/22/2017 | 2017008-01 | NRC | FIN | Mitigating Systems | Green | Inadequate FLEX Power Supply Connections |  | H.11 Challenge the Unknown | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 2515/191 | The team identified a finding for the failure to assure that FLEX power supply connections would be reliable following all required postulated beyond design basis external events. Specifically, the team identified that one installed cable configuration co
Region: IV | Arkansas Nuclear One | 1456 | 05/01/2017 05/22/2017 | 2017008-02 | NRC | FIN | Mitigating Systems | Green | Inadequate FLEX Procedures |  | H.8 Procedure Adherence | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 2515/191 | The team identified a finding with three examples for the licensee failing to assure that FLEX procedures were adequate for implementation of the strategies credited in the licensee's Final Implementation Plan. This issue was entered into the licensee's c
Region: IV | Arkansas Nuclear One | 24012 | 03/31/2017 05/10/2017 | 2017001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Damaged Lugs |  | H.12 - Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | The inspectors documented a self-revealing finding and associated non-cited violation of Unit 1 Technical Specification 5.4.1.a, for the failure to properly perform maintenance on the Unit 1 suction valve to the emergency core cooling system B and contain
Region: IV | Arkansas Nuclear One | 1323 | 03/31/2017 05/10/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate All Required Functions for Operability |  | H.13 - Consistent Process | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | The inspectors identified a finding and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, for failure to evaluate the impact of all the required safety functions for operability when the valve
Region: IV | Arkansas Nuclear One | 1327 | 03/31/2017 05/10/2017 | 2017001-03 | NRC | NCV | Initiating Events | Green | Inadvertent Reactivity Addition |  | H.5 - Work Management | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | Inspectors documented a Green self-revealing finding and associated non-cited violation of Unit 1 Technical Specification 5.4.1.a. Specifically, the licensee failed to properly pre-plan and perform maintenance of the integrated control system equipment th
Region: IV | Arkansas Nuclear One | 1437 | 12/31/2016 02/10/2017 | 2016004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Walkdown in Controlled Manner |  | H.12 Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealed finding and associated non-cited violation of Unit 1 Technical Specification 5.4.1.a, for the failure to properly pre-plan and perform a pre-modification walkdown in the Unit 1 train A safety-related switchgear ro
Region: IV | Arkansas Nuclear One | 1438 | 12/31/2016 02/10/2017 | 2016004-02 | NRC | NCV | Initiating Events | Green | Failure to Design Pipe Support for Vibration |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealed finding and associated non-cited violation of 10 CFR 50 Appendix B Criterion III for the licensee's failure to verify that the decay heat removal (DHR) system drain piping configuration and supports could withstan
Region: IV | Arkansas Nuclear One | 1446 | 12/02/2016 02/28/2017 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Motor Operated Valve Thermal Overload Devices | EA Case: 2017017 | P.2 Evaluation | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, design control measures shall provide for verifying or checking the adequacy of design, such as by the performance of
Region: IV | Arkansas Nuclear One | 1447 | 12/02/2016 02/28/2017 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Safety Guide 9 Criteria into Surveillance Procedures | EA Case: 2017017 |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and components wil
Region: IV | Arkansas Nuclear One | 1448 | 12/02/2016 02/28/2017 | 2016008-03 | NRC | FIN | Initiating Events | Green | Failure to Monitor Startup Transformers #1, #2, and #3 Voltage Regulator/Tap Changer Function |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a Green finding for the failure to meet the surveillance standards of IEEE 308-1971, "Criteria for Class 1E Electric Systems for Nuclear Power Generating Stations," Section 5.2.3, "Preferred Power Supply." Specifically, from 2001 to
Region: IV | Arkansas Nuclear One | 1316 | 12/02/2016 02/28/2017 | 2016008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Emergency Feedwater Pump Suction Transfer Design Calculation or Testing | EA Case: 2017017 |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part that, design control measures shall provide for verifying or checking the adequacy of design, such as by the performanc
Region: IV | Arkansas Nuclear One | 1319 | 12/02/2016 02/28/2017 | 2016008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Safety Systems Would Survive Sustained Degraded Voltage Conditions | EA Case: 2017017 |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, design control measures shall provide for verifying or checking the adequacy of design, such as by the performance of
Region: IV | Arkansas Nuclear One | 1315 | 06/30/2016 07/28/2016 | 2016002-01 | NRC | FIN | Initiating Events | Green | Failure to Incorporate Vendor Guidance in Work Order |  | H.5 Work Management | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.12 | The inspectors identified a finding for the failure to incorporate vendor instructions in a work order. Specifically, the licensee exceeded the vendor specified torque values and performed the work with the component in service, contrary to vendor caution
Region: IV | Arkansas Nuclear One | 1421 | 06/30/2016 07/28/2016 | 2016002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Clean Main Feedwater Lube Oil Reservoir Leads to Reactor Power Reduction |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors documented a self-revealing finding for failure to clean the main feedwater turbine lube oil reservoir. Specifically, the main feedwater turbine lube oil reservoir had not been cleaned since 2006, causing clogged filters and low main feedwa
Region: IV | Arkansas Nuclear One | 1424 | 06/24/2016 08/04/2016 | 2016009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Loop Flow Testing |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.05XT | The team identified a non-cited violation of License Conditions 2.C.(8), "Fire Protection," for Unit 1; License Condition 2.C.(3)(b), "Fire Protection," for Unit 2; and the technical requirements manuals because the licensee did not properly test all port
Region: IV | Arkansas Nuclear One | 1425 | 06/24/2016 08/04/2016 | 2016009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Used as a Compensatory Measure |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.05XT | The team identified a non-cited violation of License Condition 2.C.(3)(b), "Fire Protection," for use of an inadequate procedure as a compensatory measure. Specifically, a procedure for providing temporary cooling to the safety parameter display system ro
Region: IV | Arkansas Nuclear One | 1430 | 06/24/2016 08/04/2016 | 2016009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that the Assumptions in the Engineering Analysis Remain Valid |  | H.3 Change Management | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.05XT | The team identified a non-cited violation of License Condition 2.C(3)(b), "Fire Protection," for the failure to establish an appropriate monitoring program in accordance with National Fire Protection Association Standard 805, Section 2.6. Specifically, th
Region: IV | Arkansas Nuclear One | 1392 | 05/12/2016 06/09/2016 | 2016007-01 | NRC | NCV | Initiating Events | Green | Failure to Complete Extent of Condition Reviews for the Stator Drop Significant Condition Adverse to Quality Event |  | P.3 Resolution | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee failed to follow procedure EN-LI-102, "Corrective Action Program," which r
Region: IV | Arkansas Nuclear One | 1393 | 05/12/2016 06/09/2016 | 2016007-02 | NRC | FIN | Initiating Events | Green | Inadequate Effectiveness Reviews for Corrective Actions to Prevent Recurrence |  | P.6 Self Assessment | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding for the licensee's failure to ensure that effectiveness reviews to assess the adequacy of corrective actions as required by procedure EN-LI-118-ANO-RC, "Cause Evaluation Process," were appropriate. Specifically, the tea
Region: IV | Arkansas Nuclear One | 1399 | 05/12/2016 06/09/2016 | 2016007-03 | NRC | FIN | Initiating Events | Green | Inadequate Operating Experience Evaluations |  | H.14 Conservative Bias | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding for the licensee's failure to evaluate operating experience as required by procedure EN-OE-100-02, "Operating Experience Evaluations." This procedure allowed taking no action for operating experience issues that were ap
Region: IV | Arkansas Nuclear One | 1400 | 05/12/2016 06/09/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Monitoring for Wall Loss in the Service Water System |  | H.14 Conservative Bias | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee failed to implement the Microbiologically Influenced Corrosion Monitoring
Region: IV | Arkansas Nuclear One | 1405 | 05/12/2016 06/09/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Include Unit 2 Service Water Pump Supports in the ASME Code Section XI Inservice Inspection Program |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR 50.55a(g)(4) for the licensee's failure to inspect Unit 2 service water pump supports in accordance with ASME Code Section XI. Specifically, the licensee failed to include
Region: IV | Arkansas Nuclear One | 1406 | 05/12/2016 06/09/2016 | 2016007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Degraded Unit 2 Train B Emergency Diesel Generator Heat Exchangers Service Water Flow and Degraded Unit 1 Containment Coatings |  | H.6 Design Margins | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified two examples of a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct conditions adverse to quality. Specifically, the licensee fa
Region: IV | Arkansas Nuclear One | 1416 | 05/12/2016 06/09/2016 | 2016007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Service Water Design Cooling to the Unit 2 High Pressure Safety Injection Pump Seal and Bearing Coolers |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the design basis service water cooling flow rates for the Unit 2 high press
Region: IV | Arkansas Nuclear One | 1417 | 05/12/2016 06/09/2016 | 2016007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Flow Monitoring of Unit 2 Service Water to Emergency Feedwater Pump Suction Supply |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a test program for the Unit 2 service water supply to emergency feedwater pump s
Region: IV | Arkansas Nuclear One | 1419 | 05/12/2016 06/09/2016 | 2016007-09 | NRC | NCV | Mitigating Systems | Green | Emergency Feedwater Pump Casing Wall Loss Not Monitored |  | H.5 Work Management | TE?: N | 05000313 Arkansas Nuclear 1 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish a test program for monitoring the Unit 1 emergency feedwater pumps casing wall t
Region: IV | Arkansas Nuclear One | 1420 | 05/12/2016 06/09/2016 | 2016007-10 | NRC | FIN | Mitigating Systems | Green | Failure to Develop an Operability Decision-Making Issue for Degraded Condition on Safety Injection Tank |  | P.6 Self Assessment | TE?: N | 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding for the licensee's failure to create an operational decision making issue document per procedure EN-OP-111, "Operability Decision Making Issue (ODMI) Process." Specifically, the licensee failed to evaluate the plant imp
Region: IV | Arkansas Nuclear One | 1071 | 05/12/2016 06/09/2016 | 2016007-11 | NRC | NCV | Mitigating Systems | Green | Pressurizer Block Valve Not Installed in the Qualified Environmental Configuration |  | P.5 Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR 50.49(f) for the licensee's failure to ensure that Unit 1 pressurizer block valve CV-1000, was installed in the qualified configuration. Specifically, the safety-related m
Region: IV | Arkansas Nuclear One | 1072 | 05/12/2016 06/09/2016 | 2016007-12 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Predictive Maintenance on Safety-Related Medium-Voltage Switchgear |  | P.1 Identification | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding for the licensee's failure to fully implement procedure EN-DC-310, "Predictive Maintenance Program," Revision 7. Specifically, the licensee failed to perform predictive maintenance-related thermography on medium-voltage
Region: IV | Arkansas Nuclear One | 1304 | 05/12/2016 06/09/2016 | 2016007-13 | NRC | NCVIV | Mitigating Systems | Green | Failure to Update Probabilistic Risk Assessment Model in a Timely Manner Results in Failure to Submit Complete and Accurate Information |  | H.1 Resources | TE?: Y SL-IV-NCVIV | 05000313 Arkansas Nuclear 1 |  | 95003 | The team identified a Green finding for the licensee's failure to update the Level 1 probabilistic risk assessment model as required by procedure EN-DC-151, "Probabilistic Safety Assessment (PSA) Maintenance and Update," Revision 5. This finding also invo
Region: IV | Arkansas Nuclear One | 1305 | 05/12/2016 06/09/2016 | 2016007-14 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement the Corrective Action Program |  | H.3 Change Management | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow corrective action program procedures. Specifically, the te
Region: IV | Arkansas Nuclear One | 1308 | 05/12/2016 06/09/2016 | 2016007-15 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Structural Design Clearances Inside the Units 1 and 2 Reactor Containment Buildings |  | P.1 Identification | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that numerous structural components located inside Units 1 and 2 reactor contain
Region: IV | Arkansas Nuclear One | 1309 | 05/12/2016 06/09/2016 | 2016007-16 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Properly Calibrate Unit 1 Reactor Building Atmospheric Particulate Radiation Monitor RE-7460 |  | H.7 Documentation | TE?: N | 05000313 Arkansas Nuclear 1 |  | 95003 | The team identified a Green finding and an associated non-cited violation of 10 CFR 20.1501(c) because the licensee failed to ensure that instruments and equipment used for quantitative radiation measurements were calibrated periodically for the radiation
Region: IV | Arkansas Nuclear One | 1381 | 03/31/2016 05/06/2016 | 2016001-01 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Hot Work Risk |  | H.4 Teamwork | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.13 | The inspectors identified a Green finding and an associated non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure to assess and manage the increase in risk due to
Region: IV | Arkansas Nuclear One | 1382 | 03/31/2016 05/06/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Design Control Requirements for Pump Seal Cooler Replacements |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | The inspectors identified a Green finding and an associated non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the suitability of materials used in safety-related equipment. Specifically, the licensee
Region: IV | Arkansas Nuclear One | 1385 | 03/31/2016 05/06/2016 | 2016001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Blocked Drain Results in Emergency Feedwater Pump Inoperability |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.19 | The inspectors documented a self-revealing Green finding with an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to verify that the floor drains in the Unit 2 turbine-driven emergency feedwater p
Region: IV | Arkansas Nuclear One | 1386 | 03/31/2016 05/06/2016 | 2016001-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Inject Service Water with Corrosion Inhibitors during Refueling Outages |  | H.12 Avoid Complacency | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors reviewed a self-revealing Green finding and an associated non-cited violation for the failure to follow Procedure OP-1052.007, "Secondary Chemistry Monitoring," Revision 040. Specifically, the licensee failed to inject corrosion inhibiting
Region: IV | Arkansas Nuclear One | 1387 | 03/31/2016 05/06/2016 | 2016001-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify and Repair Intermittent Card Failure Before Returning to Service Causes Reactor Trip |  | P.2 Evaluation | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors reviewed a self-revealing Green finding for the failure to fully understand a malfunction which resulted in putting susceptible cards back into the Unit 1 integrated control system. In 2014, a failure caused a feedwater transient, which ope
Region: IV | Arkansas Nuclear One | 1061 | 12/31/2015 01/27/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Failure to Assess Risk for Switchyard Work |  | H.13 Consistent Process | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for failure to assess the risk impact of switchyard maintenance. Specifically, the station faile
Region: IV | Arkansas Nuclear One | 1065 | 12/31/2015 01/27/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Rain Water Accumulation in the Emergency Diesel Generator System Exhausts |  | H.12 Avoid Complacency | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify a condition adverse to quality. Specifically, the licensee failed to identify rain water accumulation in the exhaust
Region: IV | Arkansas Nuclear One | 1066 | 12/31/2015 01/27/2016 | 2015004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Translate the Design Requirements for the Unit 1 Decay Heat Vault Rooms Being Sealed |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly translate the regulatory requirements and design basis into specifications, drawings, procedures, and instructions
Region: IV | Arkansas Nuclear One | 1376 | 09/30/2015 11/09/2015 | 2015003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure Results in Increased Reactor Coolant Activity |  | H.12 Avoid Complacency | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | Green. The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to follow the instructions in the chemical volume control system charging pump pulsation
Region: IV | Arkansas Nuclear One | 1380 | 09/30/2015 11/09/2015 | 2015003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality Involving Motor Control Center Bus Stabs |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | Green. The inspectors reviewed a self-revealing violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct conditions adverse to quality. Specifically, the licensee failed to promptly replace short bus stabs wi
Region: IV | Arkansas Nuclear One | 1369 | 06/30/2015 08/05/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Severe Weather Preparation |  | H.3(a) Work Planning | TE?: N | 05000313 Arkansas Nuclear 1 05000313 Arkansas Nuclear 1 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 05000368 Arkansas Nuclear 2 05000368 Arkansas Nuclear 2 |  | 71111.01 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, & Drawings," for the failure to establish appropriate procedures for preparations for severe weather. Specifically, inspectors observed
Region: IV | Arkansas Nuclear One | 1370 | 06/30/2015 08/05/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Protect Motor Control Center from Potential Pipe Spray |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.06 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to select and review equipment for suitability of application that is essential to the safety-related function of Unit 2
Region: IV | Arkansas Nuclear One | 1371 | 06/30/2015 08/05/2015 | 2015002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Verify Material Properties Prior to Installation |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.08P | The inspectors reviewed a self-revealing finding involving failure to verify that the proper material was installed in the plant during initial construction of the Unit 2 reactor coolant system (RCS) sample system. Specifically, failure to use the correct
Region: IV | Arkansas Nuclear One | 1375 | 06/30/2015 08/05/2015 | 2015002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Testing of Diesel Fuel Oil Transfer Piping |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 05000368 Arkansas Nuclear 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to establish and maintain an adequate testing program for the fuel oil transfer piping for Units 1 and 2. Specifically,
Region: IV | Arkansas Nuclear One | 1358 | 05/15/2015 06/29/2015 | 2015008-01 | NRC | NCV | Initiating Events | Green | Failure to Properly Implement Procedures for Writing Procedures Important to Safety |  | H.1 Resources | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to perform activities affecting quality as prescribed by documented procedures of a typ
Region: IV | Arkansas Nuclear One | 1359 | 05/15/2015 06/29/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Containment Spray Pump Interlock to Shutdown Cooling Heat Exchanger Room Coolers |  | P.2 Evaluation | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality. Specifically, the licensee failed to correct the containment spray pu
Region: IV | Arkansas Nuclear One | 1363 | 05/15/2015 06/29/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition Review for Risk-Significant Condition |  | H.4 Teamwork | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," that occurred because the licensee's extent of condition performed in the root cause evaluation for the Yellow flooding finding failed to i
Region: IV | Arkansas Nuclear One | 1364 | 05/15/2015 06/29/2015 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Breaker Auxiliary Switch Binding |  | H.13 Consistent Process | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to promptly correct a de
Region: IV | Arkansas Nuclear One | 1365 | 05/15/2015 06/29/2015 | 2015008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify, Document, and Mitigate Risk from Long Term Deficient Conditions |  | H.14 Conservative Bias | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to identify, document, and mitigate risk from long-term deficient conditions, as required by
Region: IV | Arkansas Nuclear One | 1357 | 03/31/2015 05/13/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Protect Safety Equipment From Potential High Energy Line Breaks |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion Ill, "Design Control," for the licensee's failure to assure that applicable regulatory requirements and the design basis were correctly translated into specifications
Region: IV | Arkansas Nuclear One | 1049 | 12/31/2014 02/13/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Adequate Guidance for Extreme Damage Mitigation |  | H.12 Avoid Complacency | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR 50.54(hh)(2) for the failure to develop mitigating strategy guidance that would successfully maintain or restore Unit 2 core cooling after the loss of large areas of the plant. Specifically, the gui
Region: IV | Arkansas Nuclear One | 1050 | 12/31/2014 02/13/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Flow Protection for Auxiliary Feedwater Pump in Emergency Operating Procedures |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.12 | Inspectors identified a noncited violation of Unit 1 Technical Specification 5.4, "Procedures," for the licensee's failure to establish adequate emergency operating procedures. Specifically, the licensee's emergency operating procedures provide minimum fl
Region: IV | Arkansas Nuclear One | 1351 | 12/31/2014 02/13/2015 | 2014005-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct Weaknesses During Drills and Exercises |  | P.2 Evaluation | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71114.07 | The inspectors identified a non-cited violation of 10 CFR Part 50.47(b)(14) for the failure to correct a deficiency identified in a 2013 simulator drill. Specifically, control room operators did not implement the procedure that describes how the site will
Region: IV | Arkansas Nuclear One | 1056 | 12/31/2014 02/13/2015 | 2014005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Ventilation Design for Vital Switchgear |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | Inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to maintain design control of the Unit 2 vital switchgear ventilation system. Specifically, the licensee failed to
Region: IV | Arkansas Nuclear One | 1032 | 09/30/2014 11/12/2014 | 2014004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Maintenance on Circuit Breaker Caused Loss of Unit 1 Decay Heat Removal Pump |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.12 | Inspectors documented a Green self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to ensure activities affecting quality were accomplished in accordance with d
Region: IV | Arkansas Nuclear One | 1044 | 09/30/2014 11/12/2014 | 2014004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance on Unit 2 Main Steam Isolation Valves |  | P.2 Evaluation | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.19 | Inspectors documented a Green self-revealing non-cited violation of Technical Specification 6.4.1.a for the licensee's failure to establish procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, Section 9, February 1978. Specifically, th
Region: IV | Arkansas Nuclear One | 1045 | 09/30/2014 11/12/2014 | 2014004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Procedural Requirements for Axial Shape Index during a Rapid Power Reduction |  | H.9 Training | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors documented a Green self-revealing non-cited violation of Technical Specification 6.4.1.a for the failure to implement procedures for changing load recommended by Regulatory Guide 1.33, Revision 2, Appendix A, Section 2.f, dated February 197
Region: IV | Arkansas Nuclear One | 1892 | 06/29/2014 08/13/2014 | 2014003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Evaluate a Spent Fuel Pool Pressure Boundary Flaw. |  | H.1 Resources | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.08P | The inspector identified a non-cited violation of 10 CFR 50.55a(g)(4) for the licensee's failure to evaluate an ASME code class piping leak in the Unit 1 spent fuel pool piping, or perform evaluation prior to returning the system to service. A through wal
Region: IV | Arkansas Nuclear One | 1893 | 06/29/2014 08/13/2014 | 2014003-02 | NRC | NCV | Initiating Events | Green | Failure to Evaluate Reactor Coolant Sample System Pressure Boundary Flaw |  | H.1 Resources | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.08P | The inspector identified a non-cited violation of 10 CFR 50.55a(g)(4) for the licensee's failure to evaluate the acceptability of the Unit 1 reactor coolant system sample cooler E30 for continued service. Specifically, when the licensee determined that th
Region: IV | Arkansas Nuclear One | 2231 | 06/29/2014 08/13/2014 | 2014003-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedures for Through Wall Leaks |  | H.9 Training | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with two examples. Criterion V, states, in part, "Activities affecting quality shall be prescribed by documented instruct
Region: IV | Arkansas Nuclear One | 2232 | 06/29/2014 08/13/2014 | 2014003-04 | NRC | FIN | Barrier Integrity | Green | Failure to Correct Through Wall Flaw in Spent Fuel Pool Piping |  | H.14 Conservative Bias | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.08P | The inspectors identified a finding for failure to follow Procedure EN-LI-102, "Corrective Action Process," Revision 23. A through wall leak in the piping of the spent fuel pool cooling (SFP) system downstream of valve SFP 23 was identified in August 2009
Region: IV | Arkansas Nuclear One | 2270 | 06/29/2014 08/13/2014 | 2014003-05 | NRC | URI | Initiating Events | Green | Proper ASME Code Classification of RCS Sample System |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.08P
Region: IV | Arkansas Nuclear One | 2271 | 06/29/2014 08/13/2014 | 2014003-06 | NRC | URI | Mitigating Systems | Green | Inservice Testing of the Diesel Fuel Oil Transfer Piping |  | H.14 Conservative Bias | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.08P
Region: IV | Arkansas Nuclear One | 1016 | 06/29/2014 08/13/2014 | 2014003-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Filling and Venting of High Pressure Injection Pump |  | P.5 Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.19 | The inspectors identified a Green non-cited violation of Unit 1 Technical Specification 5.4, "Procedures," for the licensee's failure to establish adequate instructions for filling and venting the emergency core cooling system. Specifically, an inadequate
Region: IV | Arkansas Nuclear One | 1887 | 06/29/2014 08/13/2014 | 2014003-08 | NRC | NCV | Public Radiation Safety | Green | Failure to Establish, Implement, and Maintain Appropriate Changes to the Offsite Dose Calculation Manual For Airborne Sampling |  | H.8 Procedure Adherence | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71124.07 | The inspectors identified two examples of a non-cited violation of Unit 1, Technical Specification 5.5.1, "Offsite Dose Calculation Manual (ODCM)," and Unit 2, Technical Specification 6.5.1, "Offsite Dose Calculation Manual." When changes were made to the
Region: IV | Arkansas Nuclear One | 1806 | 03/31/2014 05/09/2014 | 2014002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Correctly Install Flexible Link Bolted Connection on Phase C of 6.9 kV Bus |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Inspectors documented a self-revealing finding for the licensee's failure to correctly install the flexible link bolted connection on phase C of the 6.9 kV non segregated bus of the Unit 2 auxiliary transformer, which contributed to the explosion of the U
Region: IV | Arkansas Nuclear One | 1807 | 03/31/2014 05/09/2014 | 2014002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Land Signal Wire from Differential Relay Output to Generator Lockout Relay |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Inspectors documented a self-revealing finding for the licensee's failure to correctly land the signal wire from the Unit 2 auxiliary transformer differential relay output contacts to the main generator lockout relay, which contributed to the explosion of
Region: IV | Arkansas Nuclear One | 1815 | 03/31/2014 05/09/2014 | 2014002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Alternate ac Diesel Generator Governor |  | H.13 Consistent Process | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.22 | The inspectors documented a self-revealing non-cited violation of 10 CFR 50.63, "Loss of all alternating current power," for the licensee's failure to maintain the alternate ac diesel generator so that a power source would be available to withstand and re
Region: IV | Arkansas Nuclear One | 1021 | 03/13/2014 03/28/2014 | 2014007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Reassess the Effects of Aging |  | H.5 Work Management | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71003 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to follow procedures related to review of indications that could affect the structural integrity of the Unit 2 reac
Region: IV | Arkansas Nuclear One | 1022 | 02/10/2014 03/24/2014 | 2013012-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Develop and Implement Adequate Procedural Controls to Remediate the Anticipated Effects of Internal Flooding for Either Unit |  | H.7 Documentation | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of Unit 1 Technical Specification 5.4.1.a and Unit 2 Technical Specification 6.4.1.a, involving the licensee's failure to develop and implement procedural controls for response to internal floo
Region: IV | Arkansas Nuclear One | 1031 | 02/10/2014 03/24/2014 | 2013012-02 | Self - Revealed | FIN | Mitigating Systems | Green | Main Feedwater Regulating Valve Maintenance Practices |  | P.5 Operating Experience | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors reviewed a self-revealing finding for the licensee's failure to provide appropriate work instructions for the replacement of the main feedwater regulating valve 2CV-0748 linear variable differential transformer 2ZT-0748. Specifically, the l
Region: IV | Arkansas Nuclear One | 1868 | 02/10/2014 03/24/2014 | 2013012-03 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Required Components in the Station's Maintenance Rule Monitoring Program |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The NRC identified a non-cited violation of 10 CFR 50.65(b)(2)(i) for the licensee's failure to monitor non-safety-related structures, systems, or components that are relied upon to mitigate accidents or transients. Specifically, the Unit 1 decay heat rem
Region: IV | Arkansas Nuclear One | 1801 | 12/31/2013 02/04/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Fluorescent Light Fixture Above Emergency Feedwater Pump in Seismically Qualified Configuration |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.05Q | Inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to hang the fluorescent light fixture above the Unit 1 motor driven emergency feedwater pump in a
Region: IV | Arkansas Nuclear One | 1802 | 12/31/2013 02/04/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation Due to Failure to Characterize Weld Flaw |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | Inspectors identified a non-cited violation of 10 CFR 50.55a(b)(5), "In-Service Inspection Code Cases," for the licensee's failure to implement ASME Code Case N-513-2, "Evaluation Criteria for Temporary Acceptance of Flaws in Moderate Energy Class 2 or 3
Region: IV | Arkansas Nuclear One | 1795 | 11/19/2013 12/23/2013 | 2013009-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action For a Condition Adverse to Fire Protection |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.05T | The team identified a non-cited violation of Unit 1 License Conditions 2.C.(8), "Fire Protection," for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified that the licen
Region: IV | Arkansas Nuclear One | 1797 | 11/19/2013 12/23/2013 | 2013009-03 | NRC | FIN | Mitigating Systems | Green | Emergency Lights Satisfied their Maintenance Rule Performance Criteria |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.05T | The team identified a finding for the failure to provide an adequate testing scheme to demonstrate that the Appendix R emergency lights satisfied their maintenance rule performance criteria. The team determined that operators were provided flashlights whe
Region: IV | Arkansas Nuclear One | 1791 | 09/30/2013 11/01/2013 | 2013004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Preventive Maintenance on Plant Protection System Test Switch |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors documented a self-revealing non-cited violation of Technical Specification 6.4.1.a for the licensee's failure to implement procedures specified by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, the licensee fail
Region: IV | Arkansas Nuclear One | 1794 | 09/30/2013 11/01/2013 | 2013004-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Design Change for Main Feedwater Flow Control Valves |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors documented a self-revealing finding for the licensee's failure to adequately implement a design change to the main feedwater startup and low load feedwater control valves. As a result, the valves were inoperable for longer than their techni
Region: IV | Arkansas Nuclear One | 1014 | 06/30/2013 08/13/2013 | 2013003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Evaluate and Correct Excessive Containment Isolation Valve Leakage |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.22 | The inspectors identified a non-cited violation of Unit 2 Technical Specification 6.5.16, "Containment Leakage Rate Testing Program," for the failure to evaluate and take appropriate corrective actions to achieve acceptable performance for containment iso
Region: IV | Arkansas Nuclear One | 1789 | 06/30/2013 08/13/2013 | 2013003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Install Control Room Emergency Chiller Supply Breaker |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Inspectors documented a Green self-revealing non-cited violation of Technical Specification 6.4.1.a for the licensee's failure to implement procedures recommended by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, the licensee
Region: IV | Arkansas Nuclear One | 1783 | 03/22/2013 05/03/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Maintenance Instructions for Installation of Fluorescent Light Fixtures |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | NONE | Inspectors identified a violation of Technical Specification 5.4.1.a, which requires that the licensee establish, implement, and maintain the applicable procedures recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Paragraph 9.a
Region: IV | Arkansas Nuclear One | 1001 | 12/31/2012 02/13/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Adequate Design Change Controls for Permanent Removal of Service Water Check Valves SW-604A & SW-604B |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.07A | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that design changes, including field changes, shall be subject to design control measures commensurate with those applied
Region: IV | Arkansas Nuclear One | 1771 | 12/31/2012 02/13/2013 | 2012005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Required Examinations of Reactor Vessel Flange Seal Leak-Off Lines |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.08P | The inspectors identified a non-cited violation, with two examples, of Title 10 CFR 50.55a(g)(4), which requires that components classified as ASME Code Class 1, Class 2, and Class 3 meet the requirements set forth in Section XI of the applicable editions
Region: IV | Arkansas Nuclear One | 1775 | 12/31/2012 02/13/2013 | 2012005-03 | NRC | FIN | Initiating Events | Green | Failure to Adequately Evaluate Discolored Boric Acid on Reactor Make-up Water Pipe |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.08P | Inspectors identified a finding for the failure to perform an adequate boric acid evaluation on the reactor make-up water pipe located in the overhead of the train B charging pump room. The licensee entered this finding into their corrective action progra
Region: IV | Arkansas Nuclear One | 1776 | 12/31/2012 02/13/2013 | 2012005-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: Y SL-IV-NCVIV | 05000368 Arkansas Nuclear 2 |  | 71111.11B | The inspectors identified a [Severity Level IV] non-cited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure the integrity of Unit 2 licensed operator biennial written examinations. During the
Region: IV | Arkansas Nuclear One | 1779 | 12/31/2012 02/13/2013 | 2012005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Radiation Workers Fail to Follow High Radiological Area Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors documented a self-revealing non-cited violation of Unit 2 Technical Specification 6.4.1.a for the failure to follow station procedure EN-RP-100 "Radiation Worker Expectations", Revision 7. Specifically, when a working in a posted high radia
Region: IV | Arkansas Nuclear One | 1781 | 12/31/2012 02/13/2013 | 2012005-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide an Accurate Maintenance Tagout Results in Loss of Reactor Coolant System Inventory |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors documented a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to provide an appropriate maintenance tagout. Specifically, maintenance tagout LPSI-013-A-2SI-14C for maintenance on the Unit 2 low
Region: IV | Arkansas Nuclear One | 1780 | 12/31/2012 02/13/2013 | 2012005-07 | Self - Revealed | FIN | Initiating Events | Green | Failure to Correct a Degraded Condition Associated with the Unit 2 Condenser Vacuum Pump Solenoid Valves Results in Reactor Trip |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors documented a self-revealing finding for the failure to identify the cause and take appropriate corrective actions to address the degraded performance of the Unit 2 condenser vacuum pump solenoid valves. Specifically, from 2008 through 2012,
Region: IV | Arkansas Nuclear One | 1778 | 12/31/2012 02/13/2013 | 2012005-08 | NRC | FIN | Mitigating Systems | Green | Incorrectly Positioned Manual Jack Sleeve Results in Feedwater Regulating Valve not Fully Closing |  | H.3(b) Work Activity Coordination | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors identified a finding associated with a failure to provide sufficient work instructions to perform repairs to 2CV-0748 main feedwater regulating valve. Specifically, contrary to station procedure EN-WM-105, "Planning," Revision 10, the work
Region: IV | Arkansas Nuclear One | 987 | 09/30/2012 11/14/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality with the Unit 2 Vital Inverters |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.19 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for the licensee's failure to promptly identify and correct a condition adverse to quality associated with the Unit 2 vital inverters. Specifi
Region: IV | Arkansas Nuclear One | 991 | 09/30/2012 11/14/2012 | 2012004-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Planning Procedure Results in Short across Hand Switch in Control Room Control Panel |  | H.3(a) Work Planning | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a finding associated with a failure to implement a station procedure which resulted in not providing sufficient work instructions. Specifically, contrary to station procedure EN-WM-105, "Planning," Revision 10, the work instructi
Region: IV | Arkansas Nuclear One | 992 | 09/30/2012 11/14/2012 | 2012004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated with the Unit 1 Emergency Feedwater Initiation and Control System |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality associated with the Unit 1 emergency feedwater initiatio
Region: IV | Arkansas Nuclear One | 1770 | 06/30/2012 08/09/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Known Condition Adverse to Quality Associated with Inadequately Secured Splined Adaptors for Service Water Discharge Cross-Connect Valves |  | H.3(b) Work Activity Coordination | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI for failure to take timely corrective action to correct a condition adverse to quality. Specifically, the licensee implemented a compensatory measure for four ser
Region: IV | Arkansas Nuclear One | 986 | 06/30/2012 08/09/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Install Correct Coupling on Service Water Pump Results in Pump Failure |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion VII, Control of Purchased Material, Equipment and Services for the licensee's failure to assure that purchased material conformed to the procurement d
Region: IV | Arkansas Nuclear One | 1763 | 03/31/2012 05/11/2012 | 2012002-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Calibrate Unit 1 Effluent and Process Monitors Properly |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71124.05 | The inspectors identified a non-cited violation of 10 CFR 20.1501(b) because the licensee failed to calibrate Unit 1 effluent and process monitors properly. The Unit 1 calibration procedures did not instruct the instruments and controls technician to corr
Region: IV | Arkansas Nuclear One | 1749 | 03/16/2012 05/02/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Calibrate Unit 1 and Unit 2 480 Vac Transformer Instrumentation |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XII, "Control of Measuring and Test Equipment," which states, in part, "measures shall be established to assure that tools, gages, instruments, and other measuring a
Region: IV | Arkansas Nuclear One | 1750 | 03/16/2012 05/02/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Extreme Maximum Outside Air Temperatures into Calculations for Unit 2 Diesel Combustion Air |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis, as defined
Region: IV | Arkansas Nuclear One | 1762 | 03/16/2012 05/02/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Translate EFW Pump Runout Flow Condition into NPSH and Diesel Load Calculation |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis, as defined
Region: IV | Arkansas Nuclear One | 1737 | 12/31/2011 02/14/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Exceeded Technical Specification Allowed Outage Time for Electrical Power Systems |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | The inspectors identified a noncited violation of Unit 1 Technical Specification 3.8.4, "DC Sources-Operating," Technical Specification 3.8.7, "Inverters- Operating," and Technical Specification 3.8.9, "Distribution Systems-Operating," due to the licensee
Region: IV | Arkansas Nuclear One | 1741 | 12/31/2011 02/14/2012 | 2011005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Implement Procedure Results in Lowering Spent Fuel Pool Level by 0.6 feet |  | H.3(b) Work Activity Coordination | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealing, non-cited violation of Unit 1 Technical Specification 5.4.1.a for the failure to implement station procedure OP 1104.006 "Spent Fuel Cooling System", Revision 51. Specifically, SF-10, flow control to purificatio
Region: IV | Arkansas Nuclear One | 1742 | 12/31/2011 02/14/2012 | 2011005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Unit 1 Service Water Pump Column Protective Wrap Installation Deficiencies |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealing, noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality associated with degradation of the prote
Region: IV | Arkansas Nuclear One | 1746 | 12/31/2011 02/14/2012 | 2011005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Condition Adverse to Quality Resulted in Dropping a Fuel Bundle Approximately One Inch |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI for failure to identify and correct a condition adverse to quality. Specifically, on November 1, 2011, the licensee failed to identify and correct a condition associate
Region: IV | Arkansas Nuclear One | 1747 | 12/31/2011 02/14/2012 | 2011005-05 | Self - Revealed | FIN | Barrier Integrity | Green | Failure to Take Adequate Corrective Actions for Known Fuel Transfer System Deficiencies |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealing finding for the failure to take adequate corrective actions for known deficiencies associated with the Unit 1 fuel transfer system. Specifically, the licensee failed to investigate and correct issues that had bee
Region: IV | Arkansas Nuclear One | 1748 | 12/31/2011 02/14/2012 | 2011005-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Configuration Control Program |  | H.4(b) Procedural Compliance | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self revealing, noncited violation of Unit 1 Technical Specification 5.4.1.a for the failure to implement station procedure OP-1015.049 "Configuration Control Program", Revision 1. Specifically, on multiple occasions, station p
Region: IV | Arkansas Nuclear One | 972 | 09/30/2011 11/04/2011 | 2011004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Take Timely Corrective Actions for Invalid Local Leak Rate Test |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions" for the licensee's failure to take corrective action for an invalid local leak rate test performed on the Unit 2 escape hatch, 2C-2. Specifically,
Region: IV | Arkansas Nuclear One | 973 | 09/30/2011 11/04/2011 | 2011004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Adequate Work Instruction Results in a Main Feedwater Recirculation Valve Failing Open |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors documented a self-revealing finding for inadequate work instructions that resulted in the failure of a Unit 2 main feedwater pump A recirculation valve. Specifically, the licensee failed to provide adequate work instructions for reassemblin
Region: IV | Arkansas Nuclear One | 974 | 09/30/2011 11/04/2011 | 2011004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Adequate Work Instruction Results in Failed Bearing on Motor Generator Set |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors documented a self-revealing finding for an inadequate work instruction for the 2-02 control element motor generator set flywheel bearing replacement that resulted in a failure of that bearing. Specifically, the licensee failed to provide in
Region: IV | Arkansas Nuclear One | 977 | 09/30/2011 11/04/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of Design of Unit 1 Emergency Core Cooling Systems to Address Potential Voiding |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 2515/177 | The inspector identified a noncited violation of 10 CFR 50 Appendix B Criterion III for failure to verify and check the adequacy of design by performance of design reviews, alternate calculations, or a suitable testing program. Specifically, the licensee
Region: IV | Arkansas Nuclear One | 978 | 09/30/2011 11/04/2011 | 2011004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify the Decay Heat Removal Coolers as Potential Void Locations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 2515/177 | The inspector identified a noncited violation of 10 CFR 50 Appendix B Criterion III for failure to verify and check the adequacy of design by performance of design reviews, alternate calculations, or a suitable testing program. Specifically, when performi
Region: IV | Arkansas Nuclear One | 979 | 09/30/2011 11/04/2011 | 2011004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate the Required Minimum Level in the Borated Water Storage Tank |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 2515/177 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B Criterion III for failure to verify and check the adequacy of design by performance of design reviews, alternate calculations, or a suitable testing program. Specifically, the licensee
Region: IV | Arkansas Nuclear One | 1735 | 06/03/2011 07/29/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Compliance Work Order for Corrective Maintenance on Safety Related Equipment |  | H.4(a) Human Error Prevention | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.13 | The inspectors indentified a Green noncited violation of Unit 1 Technical Specification 5.4.1.a for a failure to perform proper placekeeping in a compliance work order for the replacement of the auto-manual pushbutton, PB-2613, emergency feedwater steam a
Region: IV | Arkansas Nuclear One | 968 | 06/03/2011 07/29/2011 | 2011003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Adequate Procedural Guidance Results in Control Element Assembly Shaft Extension Damage |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors documented a self-revealing noncited violation of Unit 2 Technical Specification 6.4.1.a for an inadequate procedure that resulted in damaging a control element assembly shaft extension. Specifically, station procedure OP-2505.007, "Unit 2
Region: IV | Arkansas Nuclear One | 1495 | 03/31/2011 05/13/2011 | 2011002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Incorporate Adequate Clearance Guidance Prevents Full Operation of the Unit 1 Emergency Control Room Ventilation Makeup Air Supply Damper |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.18 | Green. The inspectors documented a self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion III for an inadequate design package. This inadequacy led to the interference and restricted function of the Unit 1 emergency control room ventilation
Region: IV | Arkansas Nuclear One | 1496 | 03/31/2011 05/13/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Depressurizing One Emergency Core Cooling System Suction Header |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.22 | Green. The inspectors documented a self-revealing noncited violation of Unit 1 Technical Specification 5.4.1.a for the failure to follow procedure OP-1104.002 "Makeup and Purification System Operation", Revision 69. Specifically, while draining to depress
Region: IV | Arkansas Nuclear One | 1733 | 03/31/2011 05/13/2011 | 2011002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedural Guidance Results in Damaged Emergency Control Room Ventilation System Air Damper |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | Green. The inspectors documented a self-revealing noncited violation of Technical Specification 5.4.1.a for the inadequate maintenance work order and procedure that resulted in damaging the damper, CV-7910, VSF-9 makeup air supply, during planed maintenan
Region: IV | Arkansas Nuclear One | 1734 | 03/31/2011 05/13/2011 | 2011002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Action to Correct a Condition Adverse to Quality Associated with 4160 Volt Vacuum Breakers |  | H.3(a) Work Planning | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | Green. The inspectors documented a self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion XVI for the failure to take timely corrective action to correct a condition adverse to quality. Specifically, the licensee identified an issues the Si
Region: IV | Arkansas Nuclear One | 1736 | 02/18/2011 03/29/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Resolve Adverse Conditions in 120 Volt Vital Inverters in a Timely Manner |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee did not promptly identify and correct a condition adverse to quality that affected static uninterruptible power supply invert
Region: IV | Arkansas Nuclear One | 1482 | 12/31/2010 02/14/2011 | 2010005-01 | NRC | FIN | Mitigating Systems | Green | Exceeded Technical Specification Allowed Outage Time for Electrical Power Systems Due to Loss of Non-Technical Specification Supported Systems |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specifications 3.8.4, "DC Sources - Operating," Technical Specification 3.8.7, "Inverters - Operating," and Technical Specification 3.8.9, "Distribution Systems - Operating," due to the failure t
Region: IV | Arkansas Nuclear One | 1485 | 12/31/2010 02/14/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | Inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that quality control verification inspections were consistently included and correctly specified in quality-affecting procedures
Region: IV | Arkansas Nuclear One | 1486 | 12/31/2010 02/14/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement the experience and qualification requirements of the quality assurance program. As a result, the licensee
Region: IV | Arkansas Nuclear One | 1487 | 12/31/2010 02/14/2011 | 2010005-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Use Human Performance Tools Results in Two Turbine Building Roof Fires |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | NONE | The inspectors documented a self-revealing finding for contract roofers failing to use human performance tools, per Procedure EN HU 102, "Human Performance Tools," Revision 5, while performing hot work activities on Arkansas Nuclear One's turbine building
Region: IV | Arkansas Nuclear One | 1492 | 12/31/2010 02/14/2011 | 2010005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Unit 2 Refueling Water Tank and the Condensate Storage Tank Transfer Setpoints |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that design control measures shall provide for verifying or checking the adequacy of design, such as by the performance o
Region: IV | Arkansas Nuclear One | 1494 | 12/31/2010 02/14/2011 | 2010005-07 | NRC | NCV | MISC | Green | Failure to Perform Face-to-Face Supervisory Assessments Less than 4 Hours Before Individuals Began Performing Work Activities Under a Waiver |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | NONE | The inspectors identified a noncited violation of 10 CFR 26.207(a)(3), "Waivers and Exceptions," associated with the failure of supervisory personnel to appropriately perform face-to-face fatigue assessments. Specifically, supervisory personnel were perfo
Region: IV | Arkansas Nuclear One | 2409 | 09/30/2010 11/12/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Excessive Overlap of Unit 2 Written Examinations (Section 1R11) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, at Unit 2. The violation was associated with the biennial written exam overlap for the weeks four, five, and six written examinations administered by the facility d
Region: IV | Arkansas Nuclear One | 2410 | 09/30/2010 11/12/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Emergency Diesel Generators Heating, Ventilation, and Air Conditioning Ducting Susceptibility to Tornado Loadin |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to promptly identify and correct a known condition adverse to quality associated with the susceptibility of t
Region: IV | Arkansas Nuclear One | 956 | 09/30/2010 11/12/2010 | 2010004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Emergency Switchgear Chiller VCH 4A |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.18 | The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a known condition adverse to quality associated with the improper
Region: IV | Arkansas Nuclear One | 957 | 09/30/2010 11/12/2010 | 2010004-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Station Work Control Procedure Results in Unavailable Equipment |  | H.4(a) Human Error Prevention | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.19 | The inspectors documented a self-revealing finding for station electrical maintenance personnel's failure to adequately implement station Procedure EN-WM-102, "Work Implementation and Closeout," Revision 4. Specifically, station personnel performing Work
Region: IV | Arkansas Nuclear One | 958 | 09/30/2010 11/12/2010 | 2010004-05 | NRC | VIO | Mitigating Systems | Green | Failure to Adequately Implement Foreign Material Exclusion Controls | EA Case: 2010233 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement Procedure EN MA 118, "Foreign Material Exclusion," Revision 5/
Region: IV | Arkansas Nuclear One | 961 | 09/30/2010 11/12/2010 | 2010004-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Translate VCH 4B Design Requirements into Installed Plant Equipment |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.22 | The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the applicable design basis for applicable structures, systems, and components were cor
Region: IV | Arkansas Nuclear One | 962 | 09/30/2010 11/12/2010 | 2010004-07 | NRC | NCV | Public Radiation Safety | Green | Failure to Provide an Accurate Shipping Manifest |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71124.08 | The inspectors identified a noncited violation of 10 CFR 20.2006(b) for failure to ship radioactive waste with an accurate manifest. On May 19, 2009, the licensee shipped 20 Unit 2 spent fuel pool filters to a waste processor for segregation. The licensee
Region: IV | Arkansas Nuclear One | 963 | 09/30/2010 11/12/2010 | 2010004-08 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures and Generate Adequate Work Orders for Maintenance on Safety Related Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for station planning personnel's failure to adequately implement station Procedure EN FAP WM 011, "Work Planning Standard,
Region: IV | Arkansas Nuclear One | 966 | 09/30/2010 11/12/2010 | 2010004-09 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Results in Draining Unit 1 Pressurizer to Reactor Building Floor |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing noncited violation of Unit 1 Technical Specification 5.4.1.a for the failure to follow Procedure EN OP 102, "Protective and Caution Tagging," Revision 12. Specifically, a maintenance tagout holder signed off a ta
Region: IV | Arkansas Nuclear One | 1493 | 08/27/2010 10/08/2010 | 2010006-01 | NRC | FIN | Mitigating Systems | Green | Fire Protection Compensatory Measures Did Not Cover All Fire Protection Features |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.05T | The team identified a finding because the licensee did not include fire protection features in Procedure 1000.120, "ANO Fire Impairment Program," Revision 20. The approved fire protection program required implementing compensatory measures for degraded fi
Region: IV | Arkansas Nuclear One | 955 | 06/30/2010 08/05/2010 | 2010003-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Natural Emergencies Procedure to Control Site Missile Hazards During Severe Weather Warnings and Watches |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.01 | The inspectors identified a noncited violation of Technical Specification of 5.4.1.a for failure to follow Procedure OP-1203.025, "Natural Emergencies," Revision 30. Specifically, on April 23, 2010, the licensee entered Procedure OP- 1203.025 due to a tor
Region: IV | Arkansas Nuclear One | 2371 | 06/30/2010 08/05/2010 | 2010003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement Foreign Material Exclusion Controls |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement Procedure EN-MA-118, "Foreign Material Exclusion," Revision
Region: IV | Arkansas Nuclear One | 2374 | 06/30/2010 08/05/2010 | 2010003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Recognize Critical Dimension Results in Reactor Coolant Pump Seal Failure |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors documented a self-revealing finding associated with the third stage seal failure of reactor coolant pump P-32C on April 18, 2010. Specifically, during reassembly of reactor coolant pump P-32C, the licensee failed to recognize and maintain t
Region: IV | Arkansas Nuclear One | 2375 | 06/30/2010 08/05/2010 | 2010003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Requirements Into Installed Plant Configuration |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis for applicable structures, systems, and compone
Region: IV | Arkansas Nuclear One | 2376 | 06/30/2010 08/05/2010 | 2010003-05 | Self - Revealed | FIN | Initiating Events | Green | Troubleshooting in Switchyard Causes Loss of Power to Unit 1 and Unit 2 Startup Transformers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors documented a self-revealing finding for failure to implement Procedure OP-1015.033, "ANO Switchyard Controls," Revision 12. Specifically, On March 26, 2010, while performing 161 kV Breaker B1205 post-installation testing, several issues dev
Region: IV | Arkansas Nuclear One | 2379 | 06/30/2010 08/05/2010 | 2010003-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Nuclear Instrumentation Procedure Results in an Automatic Reactor Trip |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing noncited violation of Technical Specification 5.4.1.a, for failure to follow Procedure OP-1304.032, "Unit 1 Power Range Linear Amp Calibration at Power (NI Cal)," Revision 32, which resulted in a Unit 1 automatic
Region: IV | Arkansas Nuclear One | 2380 | 06/30/2010 08/05/2010 | 2010003-07 | Self - Revealed | FIN | Initiating Events | Green | Failure to Consider Failure Modes Results in Main Feedwater Pump Over Speed Trip |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors documented a self-revealing finding for the failure of the licensee to perform a thorough design change evaluation which did not recognize and address all design failure modes. Specifically, the licensee failed to address the water intrusio
Region: IV | Arkansas Nuclear One | 2329 | 03/31/2010 05/12/2010 | 2010002-01 | NRC | FIN | Initiating Events | Green | INADEQUATE ROOT CAUSE EVALUATION FAILED TO PREVENT MAIN FEEDWATER PUMP THRUST BEARING FAILURE |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | Green. The inspectors identified a Green finding for the licensee's failure to develop an adequate root cause evaluation and subsequent corrective actions to prevent reoccurrence of main feedwater pump 2P-1A thrust bearing failure. Specifically, the licen
Region: IV | Arkansas Nuclear One | 2305 | 12/31/2009 02/11/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in an Inadequate Operability Determination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawing," regarding the licensee's failure to follow the requirements of Procedure EN OP 104, "Operability Determination Proces
Region: IV | Arkansas Nuclear One | 2317 | 12/31/2009 02/11/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality Associated With Removal of a Rigid Seismic Restraint |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of licensee personnel to correct a condition adverse to quality - removal of rigid seismic restraint for valve 2CV 567
Region: IV | Arkansas Nuclear One | 2318 | 12/31/2009 02/11/2010 | 2009005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Results in a Unit 2 Loss of Shutdown Cooling |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Green. The inspectors documented a self-revealing, noncited violation of Technical Specification 6.4.1.a for the licensee's failure to follow operations Operating Procedure OP 1015.008, "Unit 2 SDC Control," Revision 30. Specifically, Unit 2 operators did
Region: IV | Arkansas Nuclear One | 2326 | 12/31/2009 02/11/2010 | 2009005-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Take Timely and Effective Corrective Action For Fish Influx and Blockage of Circulating Water Intake Structure Results in a Unit 1 Reactor Down Power |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | Green. The inspectors documented a self-revealing finding for the licensee's failure to implement timely corrective action for industry operating experience associated with intake water blockage and for failure to implement effective corrective action ste
Region: IV | Arkansas Nuclear One | 945 | 09/23/2009 11/05/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY MONITOR THE PERFORMANCE OF STATION HIGH ENERGY LINE BREAK DOOR LATCHES |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | Green. The inspectors documented a self-revealing noncited violation of 10 CFR 50.65(a)(2) associated with the licensee's failure to appropriately monitor station high energy line break doors, which are scoped into their Maintenance Rule Program, in a man
Region: IV | Arkansas Nuclear One | 946 | 09/23/2009 11/05/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN SEISMIC DESIGN BASES CONTROL |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to assure that applicable design basis for applicable structures, systems, and components were correctly translated into
Region: IV | Arkansas Nuclear One | 947 | 09/23/2009 11/05/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | INADEQUATE MAINTENANCE PROCEDURE GOVERNING REPAIRS TO UNIT 1 HIGH ENERGY LINE BREAK DOOR |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for an inadequate maintenance procedure governing repairs to a Unit 1 high energy line break door. This resulted in a condition where the door was not
Region: IV | Arkansas Nuclear One | 951 | 09/23/2009 11/05/2009 | 2009004-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO ADEQUATELY IMPLEMENT FOREIGN MATERIAL EXCLUSION CONTROLS |  | H.4(b) Procedural Compliance | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement Procedure EN MA 118, "Foreign Material Exclusion," R
Region: IV | Arkansas Nuclear One | 952 | 09/23/2009 11/05/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE THAT CONDITIONS ADVERSE TO QUALITY ARE APPROPRIATELY ENTERED INTO THE CORRECTION ACTION PROGRAM |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to have adequate measures established to assure that, when a condition adverse to quality was identified, i
Region: IV | Arkansas Nuclear One | 2283 | 09/23/2009 11/05/2009 | 2009004-06 | Self - Revealed | FIN | Initiating Events | Green | FAILURE TO IMPLEMENT TROUBLESHOOTING PROCEDURE DURING TROUBLESHOOTING ACTIVITIES |  | H.4(b) Procedural Compliance | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | Green. The inspectors documented a self-revealing finding for failure to follow Procedure EN MA 125, "Troubleshooting," Revision 3. Specifically, the procedure was not implemented, as work conditions dictated, and failed to prevent maintenance from blowin
Region: IV | Arkansas Nuclear One | 2284 | 09/23/2009 11/05/2009 | 2009004-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO CONTROL ACCESS TO A HIGH RADIATION AREA WITH DOSE RATES IN EXCESS OF 1.0 R/HR |  | H.3(a) Work Planning | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7112101 | Green. The inspector reviewed a self-revealing noncited violation of Technical Specification 6.7.2 for failure to control a high radiation area with dose rates in excess of 1.0 R/hr. On September 12, 2009, a radiological barrier was removed by a work crew
Region: IV | Arkansas Nuclear One | 2290 | 07/31/2009 09/11/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Class 1E Batteries and Battery Racks |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7111121 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that design changes, including field changes, shall be subject to design control measures commensurate with those applie
Region: IV | Arkansas Nuclear One | 2408 | 06/30/2009 08/14/2009 | 2009008-01 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure to Obtain OSRC Review Prior to Restart |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 95001 | A Green NRC-identified finding was identified for the failure of operations personnel to follow procedures to obtain an Operational Safety Review Committee review and approval prior to restart of the unit where the cause of the trip had not been positivel
Region: IV | Arkansas Nuclear One | 2267 | 06/23/2009 08/05/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure and Perform Postmaintenance Testing Prior to Declaring Equipment Operable |  | H.3(b) Work Activity Coordination | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with licensee personnel's failure to follow station procedures. Specifically, following work completed on high
Region: IV | Arkansas Nuclear One | 2268 | 06/23/2009 08/05/2009 | 2009003-02 | NRC | FIN | Initiating Events | Green | Failure to Follow Station Planning Procedure Results in an Inadequate Work Instruction |  | H.4(b) Procedural Compliance | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a finding associated with a station planner's failure to follow procedure which resulted in inadequate work instructions. This is not a violation because the isophase blower is not safety related equipment. Specifically, contrary
Region: IV | Arkansas Nuclear One | 2269 | 06/23/2009 08/05/2009 | 2009003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Appropriately Identify and Implement Adequate Corrective Actions to Correct a Condition Adverse to Quality Associated with the Material Control System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts or Components," associated with the licensee's failure to properly control nonconforming components. Specifically, in 1997 the lice
Region: IV | Arkansas Nuclear One | 944 | 06/23/2009 08/05/2009 | 2009003-04 | Self - Revealed | FIN | Initiating Events | Green | Trip of a Main Feed Pump Due to Electromagnetic Interference |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors documented a self-revealing finding associated with the trip of main feed pump P 1B on April 9, 2009. Specifically, the main feed pump tripped due to an intermittent electromagnetic interference signal. This interference caused the digital
Region: IV | Arkansas Nuclear One | 2254 | 03/24/2009 05/06/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Reactor Protection System Maintenance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for an inadequate maintenance procedure governing reactor protection system Channel A flux/delta flux/flow trip circuit. Specifically, the instructions did no
Region: IV | Arkansas Nuclear One | 2255 | 03/24/2009 05/06/2009 | 2009002-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Service Air Compressor Torque Value Led to Loss of Control Rod Drive Cooling and Manual Reactor Trip |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors documented a self-revealing finding associated with the Unit 1 February 5, 2009, manual reactor trip. The unit was manually tripped because control rod drive mechanism cooling was lost when the head gasket on Service Air Compressor C 3A fai
Region: IV | Arkansas Nuclear One | 2261 | 03/24/2009 05/06/2009 | 2009002-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure for Use of a Torque Amplifying Device on a Valve in the Generator Hydrogen System |  | H.4(a) Human Error Prevention | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors documented a self revealing finding because an auxiliary operator failed to follow procedure instructions that prohibited the use of torque amplifying devices on plant valves. The operators used such a device on a main generator hydrogen sk
Region: IV | Arkansas Nuclear One | 2262 | 03/24/2009 05/06/2009 | 2009002-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure for Flow Accelerated Corrosion Program |  | P.2(b) Implementing Operating Experience | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors documented a self-revealing finding for the failure to properly implement the flow accelerated corrosion control program. Consequently, a nonsafety related extraction steam drain line failed because of flow accelerated corrosion. Engineers
Region: IV | Arkansas Nuclear One | 2236 | 12/31/2008 02/12/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Risk Assessment when Disabling a Station High Energy Line Break Barrier |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to perform an adequate risk assessment for planned mainten
Region: IV | Arkansas Nuclear One | 2243 | 12/31/2008 02/12/2009 | 2008005-02 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Reactor Vessel Head Lift |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | While performing a review in accordance with Operating Experience Smart Sample FY2007 03, "Crane and Heavy Lift Inspection, Supplemental Guidance for Inspection Procedure 71111.20," the inspectors identified a noncited violation of Technical Specification
Region: IV | Arkansas Nuclear One | 2244 | 12/31/2008 02/12/2009 | 2008005-03 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement Foreign Material Exclusion Controls |  | H.4(b) Procedural Compliance | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement Station Procedure EN MA 118, Revision 4, "Foreign Material
Region: IV | Arkansas Nuclear One | 2245 | 12/31/2008 02/12/2009 | 2008005-04 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustible Material in the Auxiliary Building |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1, "Procedures," associated with the licensee's failure to adequately implement the fire protection program. Specifically, again on multiple occasions station personnel ex
Region: IV | Arkansas Nuclear One | 2253 | 12/31/2008 02/12/2009 | 2008005-05 | NRC | NCV | Initiating Events | Green | Failure to Correct and Prevent Recurrence of a Significant Condition Adverse to Quality Associated with Fires |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with a fire that occurred in the Arkansas Nuclear One switchyard while Entergy Arkansas contractors performed welding activities.
Region: IV | Arkansas Nuclear One | 942 | 09/23/2008 11/07/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENTER CONDITIONS ADVERSE TO QUALITY INTO THE CORRECTIVE ACTION PROGRAM |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to implement required measures to ensure that conditions adverse to quality were promptly identified and corrected. Specifica
Region: IV | Arkansas Nuclear One | 943 | 09/23/2008 11/07/2008 | 2008004-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY IDENTIFY AND CORRECT A CONDITION ADVERSE TO QUALITY ASSOCIATED WITH EMERGENCY SWITCH GEAR CHILLER VALVE VCH-4B |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of licensee personnel to promptly identify and correct a condition adverse to quality - chill water expansion tank corrosion
Region: IV | Arkansas Nuclear One | 2234 | 09/23/2008 11/07/2008 | 2008004-03 | Self - Revealed | FIN | Initiating Events | Green | FAILURE OF FEEDWATER HEATER HIGH LEVEL DRAIN VALVE DUE TO MAINTENANCE |  | H.4(a) Human Error Prevention | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | Inspectors documented a self-revealing finding for the failure to follow Procedure EN-HU-102, "Human Performance Tools," Revision 4, which required that workers perform self checks and peer checks to ensure that the correct work was being performed on the
Region: IV | Arkansas Nuclear One | 2235 | 09/23/2008 11/07/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ADEQUATELY MONITOR THE PERFORMANCE OF THE UNIT 1 AUXILIARY BUILDING ROOF DRAINS |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(1) for the licensee's failure to monitor Unit 1 auxiliary building roof drains performance in a manner to provide reasonable assurance that the roof drains were capable of fulfilling their
Region: IV | Arkansas Nuclear One | 941 | 09/11/2008 10/21/2008 | 2008006-01 | NRC | NCV | Barrier Integrity | Green | B.5.b. Phase 2 and 3 Mitigating Strategy |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: IV | Arkansas Nuclear One | 1863 | 06/23/2008 08/07/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to adequately monitor the performance of the alternate AC diesel generator |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65 (a)(2) for the licensee's failure to demonstrate that alternate AC diesel generator performance was being effectively controlled through preventative maintenance. The licensee maintained the d
Region: IV | Arkansas Nuclear One | 1864 | 06/23/2008 08/07/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequtely monitor the performance of the Unit 2 service water intake structure roof drains |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65 (a)(2) for the licensee's failure to demonstrate that Unit 2 service water intake structure roof drains performance was being effectively controlled through preventive maintenance. Specificall
Region: IV | Arkansas Nuclear One | 1865 | 06/23/2008 08/07/2008 | 2008003-03 | NRC | FIN | Mitigating Systems | Green | Failure to follow station procedures while troubleshooting |  | H.3(b) Work Activity Coordination | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.13 | The inspectors identified a finding because the "Fix-it-Now" team failed to follow site procedures when working on high energy line break barrier Door 62, which protected one train of the Unit 1 emergency switchgear. While performing troubleshooting activ
Region: IV | Arkansas Nuclear One | 1866 | 06/23/2008 08/07/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Low pressure safety injection check valve failure due to inadequate maintenance procedures |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors documented a self-revealing noncited violation of Technical Specification 6.4.1.a, "Procedures," for an inadequate Unit 2 low pressure safety injection discharge check valve assembly procedure. Specifically, during Refueling Outage 2R18 (Fa
Region: IV | Arkansas Nuclear One | 1867 | 06/23/2008 08/07/2008 | 2008003-05 | NRC | NCV | Barrier Integrity | Green | Failure to maintain containment closure capability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | The inspectors identified a Green noncited violation of Unit-2 Technical Specification 6.4.1.a, "Procedures," associated with the licensee's failure to maintain containment closure capability as required by Station Procedure OP 1015.008, "Unit 2 SDC Contr
Region: IV | Arkansas Nuclear One | 936 | 06/23/2008 08/07/2008 | 2008003-07 | NRC | NCV | Mitigating Systems | Green | Failure to adequately monitor the performance of the Unit 1 emergency switchgear chillers |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | The inspectors identified a noncited violation involving the licensee's failure to adequately monitor the performance of the emergency switchgear chillers in accordance with 10 CFR 50.65 (a)(2). Specifically, while re-evaluating the systems' performance f
Region: IV | Arkansas Nuclear One | 937 | 06/23/2008 08/07/2008 | 2008003-08 | NRC | FIN | Initiating Events | Green | Loss of 500 kV power line due to switchyard maintenance |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71153 | The inspectors documented a self-revealing finding for emergent work performed outside of the original work scope that led to the loss of the Pleasant Hills 500 kV power line. Entergy switchyard technicians, while working on a switchyard breaker, stepped
Region: IV | Arkansas Nuclear One | 938 | 06/23/2008 08/07/2008 | 2008003-09 | NRC | NCV | Mitigating Systems | Green | Inadequate preventive maintenance activities result in emergency light failures |  | H.3(b) Work Activity Coordination | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix R, Section III.J, with two examples for inadequate preventive maintenance activities that resulted in 90 emergency light failures between January 2005 and December 2007. The first
Region: IV | Arkansas Nuclear One | 1861 | 04/04/2008 05/02/2008 | 2008002-01 | Self - Revealed | NCV | Barrier Integrity | Green | SCAFFOLDING RENDERED CONTAINMENT ISOLATION VALVE INOPERABLE |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.22 | Green. The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow a site scaffolding procedure, in that operators and the scaffolding certif
Region: IV | Arkansas Nuclear One | 1862 | 04/04/2008 05/02/2008 | 2008002-02 | NRC | NCV | Barrier Integrity | Green | INADEQUATE CONTAINMENT AIR LOCK LEAKAGE TESTING |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.22 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," involving unacceptable preconditioning during Unit 2 containment escape hatch outer door local leakage rate testing. Specifically, the test
Region: IV | Arkansas Nuclear One | 935 | 03/28/2008 08/07/2008 | 2008003-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to follow procedure when exiting the RCA |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7112101 | The inspectors identified a noncited violation of Technical Specification 6.4.1 which resulted from workers failing to follow procedural requirements. On March 25, 2008, two workers entered the radiologically controlled area, dressed in protective clothin
Region: IV | Arkansas Nuclear One | 934 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Initiating Events | Green | Failure to Maintain Fire Barrier for Emergency Feedwater Pump A |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.05Q | Green. The inspectors identified a Green noncited violation of Technical Specification 6.4.1.c, "Procedures," associated with the licensee's failure to adequately implement the fire protection program. Specifically, station personnel breached the fire bar
Region: IV | Arkansas Nuclear One | 1852 | 12/31/2007 02/11/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of the Emergency Switchgear Room Chillers |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.12 | Green. The inspectors identified a Green noncited violation involving the licensee's failure to adequately monitor the performance of the emergency switchgear chillers in accordance with 10 CFR 50.65(a)(2). Specifically, while evaluating the system for 10
Region: IV | Arkansas Nuclear One | 1853 | 12/31/2007 02/11/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of EFW Flow Control Valve Prior to Inservice Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.19 | Green. The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the unacceptable preconditioning of Unit 1 EFW Flow Control Valve CV-2647 prior to inservice testing. Maintenance was conducted on the valve whic
Region: IV | Arkansas Nuclear One | 1855 | 12/31/2007 02/11/2008 | 2007005-06 | NRC | NCV | Initiating Events | Green | Failure to Control Combustible Material Brought Into the Auxiliary Building |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | Green. The inspectors identified a Green NCV of TS 5.4.1, "Procedures," associated with the licensee's failure to adequately implement the fire protection program. Specifically, on multiple occasions station personnel exceeded the transient combustible li
Region: IV | Arkansas Nuclear One | 1857 | 12/31/2007 02/11/2008 | 2007005-08 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Inadequate Stroke Time Testing of EFW Flow Control Valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71152 | Green. The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a practice of inadequate stroke time testing during ASME Code Inservice Testing of
Region: IV | Arkansas Nuclear One | 1858 | 11/09/2007 02/27/2008 | 2007009-01 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE MAINTENANCE PROCEDURE FOR MOTOR CONTROL CENTER BREAKERS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000368 Arkansas Nuclear 2 |  | 93812 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified associated with the licensee's failure to implement adequate corrective actions to prevent recurrence of a significant condition adverse
Region: IV | Arkansas Nuclear One | 1859 | 11/09/2007 02/27/2008 | 2007009-02 | NRC | NCV | Initiating Events | Green | FAILURE TO IDENTIFY, CORRECT AND PREVENT RECURRENCE OF A SIGNIFICANT CONDITION ADVERSE TO QUALITY |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 93812 | A self-revealing noncited violation was identified associated with the licensees' failure to comply with Unit 2 Technical Specifications, Section 6.4.1, "Procedures," for the failure to ensure adequate procedures were available for maintenance that was co
Region: IV | Arkansas Nuclear One | 1860 | 11/09/2007 02/27/2008 | 2007009-03 | NRC | NCV | Initiating Events | Green | INADEQUATE IMPLEMENTATION OF CORRECTIVE ACTIONS FAIL TO CORRECT A CONDITION ADVERSE TO QUALITY |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions in response to a Motor Control Center fire that occurred on October 24, 2000.
Region: IV | Arkansas Nuclear One | 932 | 10/19/2007 12/03/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN ADEQUATE FIRE BRIGADE STAFFING DURING ALTERNATE SHUTDOWN |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.05T | The team identified a noncited violation of License Conditions 2.C.(8) for Unit 1 and 2.C.(3)(b) for Unit 2 for failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to mainta
Region: IV | Arkansas Nuclear One | 1850 | 09/23/2007 10/24/2007 | 2007004-01 | NRC | NCV | Initiating Events | Green | FAILURE TO PERFORM A RISK ASSESSMENT WHEN REQUIRED BY 10 CFR 50.65(a)(4) FOR MOBILE CRANE USE IN THE VICINITY OF SAFETY-RELATED EQUIPMENT |  | H.3(a) Work Planning | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.13 | The inspectors identified a noncited violation (NCV) of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," involving the failure of the licensee to perform a risk assessment prior to mobile crane ac
Region: IV | Arkansas Nuclear One | 1851 | 09/23/2007 10/24/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | LOSS OF FUNCTION OF EMERGENCY SWITCHGEAR CHILLER DUE TO INADEQUATE MAINTENANCE PROCEDURE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | A self-revealing noncited violation of Unit 1 Technical Specification 5.4.1.a was identified for the licensee's failure to provide adequate instructions for conducting maintenance on the north emergency switchgear chiller hot gas bypass valve. The failure
Region: IV | Arkansas Nuclear One | 924 | 09/23/2007 10/24/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | INDICATING LAMP FAULT RESULTS IN LOSS OF CONTROL POWER TO STEAM DRIVEN EMERGENCY FEEDWATER PUMP |  | P.2(b) Implementing Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.15 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the licensee's failure to take adequate corrective actions in response to a loss of control power to the Unit 1 turbine-driven
Region: IV | Arkansas Nuclear One | 929 | 09/23/2007 10/24/2007 | 2007004-04 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE WORK PROCEDURES FOR EDG 2K-4A RESULTS IN A FIRE |  | P.2(b) Implementing Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 6.4.1, "Procedures," was identified associated with the failure to ensure that adequate procedures were available for maintenance conducted on the Unit 2 Emergency Diesel Generator (EDG) 2K-4A
Region: IV | Arkansas Nuclear One | 930 | 09/21/2007 11/05/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | NONCONSERVATIVE ERRORS IN UNIT 2 FUEL OIL CONSUMPTION CALCULATION |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7111121 | The team identified a non-cited violation of 10 CFR 50 Appendix B, Criterion III, Design Control for the failure to recognize multiple non-conservative errors in a Unit 2 emergency diesel generator fuel oil consumption calculation. The errors were a resul
Region: IV | Arkansas Nuclear One | 1837 | 06/23/2007 08/03/2007 | 2007003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify the Preconditioning of Reactor Building Spray Pumps |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to prompty identify and correct a practice of unacceptable preconditioning prior to American Society of Mechanical
Region: IV | Arkansas Nuclear One | 1839 | 06/23/2007 08/03/2007 | 2007003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post a Radiation Area |  | H.4(a) Human Error Prevention | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7112101 | The inspectors identified a noncited violation of 10 CFR 20.1902(a) because the licensee failed to conspicuously post a radiation area. On May 2, 2007, during a tour of the auxiliary building, the inspectors observed that the radiological posting to the e
Region: IV | Arkansas Nuclear One | 1840 | 06/23/2007 08/03/2007 | 2007003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to use an Engineering Control as Required by a Radiation Work Permit |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a. because of a failure to use an engineering control as required by a radiation work permit. On April 25, 2007, four workers were unable to clear the personnel c
Region: IV | Arkansas Nuclear One | 1841 | 06/23/2007 08/03/2007 | 2007003-04 | Self - Revealed | FIN | Initiating Events | Green | Complete Loss of Component Cooling Water Flow During maintenance Operations |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71152 | A self-revealing finding was identified when Unit 2 experienced a complete loss of component cooling water flow due to the loss of the Train B component cooling water Pump 2P-33B on February 21, 2007. Specifically, the loss of component cooling water occu
Region: IV | Arkansas Nuclear One | 1846 | 06/23/2007 08/03/2007 | 2007003-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Evaluation of Non-Routine Hot Work Activities Resulted in a Failure to Maintain Fire Watch for Required Amount of Time |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | A self-revealing noncited violation of Unit 2 Technical Specification 6.4.1.c, "Fire Protection Program Implementation," was identified for the licensee's failure to provide training and qualification for fire protection designees which resulted in non-ro
Region: IV | Arkansas Nuclear One | 1847 | 06/23/2007 08/03/2007 | 2007003-06 | Self - Revealed | NCV | Initiating Events | Green | Ineffective Corrective Actions Fail to Identify and Correct a Condition Adverse to Quality |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified associated with the exhaust manifold lagging fire that occurred on Unit 2 Emergency Diesel Generator 2K-4A on May 11, 2007. Specifically,
Region: IV | Arkansas Nuclear One | 1848 | 06/23/2007 08/03/2007 | 2007003-07 | Self - Revealed | NCV | Initiating Events | Green | Improperly Rated Material Results in Small Flash Fires |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified associated with small flash fires that occurred on the Unit 2 Emergency Diesel Generator 2K-4A on April 15, 2007. Specifically, the licensee
Region: IV | Arkansas Nuclear One | 1825 | 03/24/2007 05/03/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | NONCONSERVATIVE BATTERY INTERCELL CONNECTION RESISTANCE VALUE SPECIFIED IN TS SR |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | An NRC identified noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure of the licensee to ensure that the 125 Vdc safety-related batteries would remain operable if all the intercell and terminal
Region: IV | Arkansas Nuclear One | 1826 | 03/24/2007 05/03/2007 | 2007002-02 | Self - Revealed | NCV | Barrier Integrity | Green | INADEQUATE MODIFICATION CONTRIBUTES TO FAILURE OF CONTROL ROOM ISOLATION DAMPER |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7111117A | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified associated with the failure of the Unit 1 control room Damper CV-7907 to close on December 18, 2006. The licensee failed to control critical
Region: IV | Arkansas Nuclear One | 1835 | 03/24/2007 05/03/2007 | 2007002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO POSSESS A RADIATION MONITORING DEVICE THAT APPROPRIATELY ALARMS IN A HIGH RADIATION AREA |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of Technical Specification 6.7.1.d because a worker entered a high radiation area without possessing a radiation monitoring device that appropriately alarmed when the device's set point was reache
Region: IV | Arkansas Nuclear One | 1836 | 03/24/2007 05/03/2007 | 2007002-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW WORK MANAGEMENT PROCEDURES WHILE ADJUSTING REACTOR PROTECTION SYSTEM PARAMETERS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71153 | An NRC identified noncited violation of Unit 2 Technical Specification 6.4.1.a, "Procedures," was identified for the failure of operations personnel to follow applicable work management procedures while conducting instrumentation and control maintenance.
Region: IV | Arkansas Nuclear One | 1824 | 03/08/2007 04/20/2007 | 2007007-01 | Self - Revealed | NCV | Mitigating Systems | Green | INEFFECTIVE CORRECTIVE ACTIONS RESULTS IN A FIRE IN MOTOR CONTROL CENTER 2B-53 |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | NONE | The team reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure of the licensee to take effective corrective action for earlier events in 1991 and 2001. This failure to ensure positive engagement of 480 volt
Region: IV | Arkansas Nuclear One | 919 | 12/31/2006 02/14/2007 | 2006005-01 | Self - Revealed | NCV | Initiating Events | Green | FIRE DURING HOT WORK ACTIVITIES ON THE CONTAINMENT SUMP STRAINER |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | NONE | A self-revealing noncited violation of Unit 2 Technical Specification 6.4.1.c, Fire Protection Program Implementation, was identified for the failure of maintenance personnel to follow Procedure EN-DC-127, "Control of Hot Work and Ignition Sources," while
Region: IV | Arkansas Nuclear One | 920 | 12/31/2006 02/14/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO PERFORM MODIFICATION RESULTED IN AN INOPERABLE REACTOR COOLANT PUMP OIL COLLECTION SYSTEM |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.15 | A self-revealing noncited violation of ANO Unit 2 License Condition 2.C.(3)(b), "Fire Protection," was identified for failure of the licensee to maintain the lube oil collection system for reactor coolant Pumps C and D in an operable condition. Specifical
Region: IV | Arkansas Nuclear One | 921 | 12/31/2006 02/14/2007 | 2006005-03 | Self - Revealed | NCV | Initiating Events | Green | INADVERTENT REACTOR COOLANT SYSTEM DRAINING WHILE IN MODE 5 |  | H.4(a) Human Error Prevention | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | A self-revealing noncited violation of Unit 2 Technical Specification 6.4.1.a, "Procedures," was identified when an operator failed to close Valve 2DCH-11, resin sluice header drain valve, when securing from a resin transfer as required by procedure. One
Region: IV | Arkansas Nuclear One | 922 | 12/31/2006 02/14/2007 | 2006005-04 | Self - Revealed | FIN | Initiating Events | Green | UNPLANNED INCREASE IN TIME WITH REACTOR VESSEL WATER LEVEL AT FLANGE LEVEL |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71111.2 | A self-revealing finding was identified associated with the licensee's practice of using a hammer to remove the main hook pin on the Unit 2 polar crane. Specifically, this practice resulted in both the polar crane main hook pin and the load cell pin being
Region: IV | Arkansas Nuclear One | 923 | 12/31/2006 02/14/2007 | 2006005-05 | Self - Revealed | FIN | Initiating Events | Green | TRIP OF MAIN FEEDWATER PUMP DUE TO INADEQUATE DESIGN CONTROL |  | P.2(b) Implementing Operating Experience | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | A self-revealing finding was identified when the Unit 1 main feedwater Pump A tripped, resulting in a plant run back to 40 percent reactor power. The trip occurred due to electromagnetic interference from an air conditioning unit recently installed on top
Region: IV | Arkansas Nuclear One | 918 | 09/23/2006 11/02/2006 | 2006004-01 | NRC | FIN | Initiating Events | Green | LOSS OF RUNNING INTERMEDIATE COOLING WATER PUMP DUE TO HIGH AMBIENT TEMPERATURES IN THE TURBINE BUILDING |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.01 | The inspectors reviewed a self-revealing finding associated with inadequate turbine building ventilation procedures which failed to maintain design temperatures within the turbine building. As a result, on July 19, 2006, Unit 1 experienced a trip of the t
Region: IV | Arkansas Nuclear One | 1821 | 06/23/2006 08/07/2006 | 2006003-02 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO MEET IMMEDIATE NOTIFICATION REQUIREMENTS DURING TRANSIENT EVENTS |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71114.01 | A noncited violation of 10 CFR 50.54(q), 10 CFR 50.47(b)(5), and 10 CFR 50, Appendix E.IV.D.3. was identified for programmatic and procedure inadequacies that allow the licensee to not make immediate offsite notifications for certain situations after a va
Region: IV | Arkansas Nuclear One | 1822 | 06/23/2006 08/07/2006 | 2006003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO FOLLOW WRITTEN CHEMISTRY PROCEDURES |  | H.4(b) Procedural Compliance | TE?: N | 05000313 Arkansas Nuclear 1 |  | 7112101 | The inspector reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a., resulting from a chemistry technician's failure to follow written procedures. On November 8, 2005, while performing an annual liquid alpha cross-check of Am-2
Region: IV | Arkansas Nuclear One | 1820 | 06/23/2006 08/07/2006 | 2006003-04 | Self - Revealed | NCV | Barrier Integrity | Green | MOVEMENT OF IRRADIATED FUEL WITH LESS THAN REQUIRED SOURCE RANGE INSTRUMENTS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | A noncited violation of Technical Specification 3.9.2 was identified for movement of irradiated fuel assemblies with less than the two required operable source range instruments. On December 1, 2005, the licensee loaded four fuel assemblies into the react
Region: IV | Arkansas Nuclear One | 1819 | 06/23/2006 08/07/2006 | 2006003-05 | Self - Revealed | FIN | Initiating Events | Green | REACTOR TRIP DUE TO AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM ON MAIN TURBINE TRIP AND INVALID ACTUATION OF THE EMERGENCY FEEDWATER SYSTEM |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71153 | The inspectors reviewed a self-revealing finding for an inadequate maintenance procedure which did not include vendor recommended maintenance for the Unit 1 main turbine lube oil ejector dischage check valve. On December 26, 2005, Unit 1 experienced an au
Region: IV | Arkansas Nuclear One | 1817 | 03/24/2006 05/05/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO ENSURE FIRE DOORS WERE LATCHED |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71111.05A | Four examples of an NRC identified noncited violation of Unit 1 License Condition 2.C.(8), "Fire Protection," and ANO Unit 2 License Condition 2.C.(3)(b), "Fire Protection," were identified for the failure of licensee personnel to ensure fire doors were l
Region: IV | Arkansas Nuclear One | 24394 | 10/22/2018 |  | Licensee - Identified | NCV |  | Green | Failure to document the implementation of required cyber security controls |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71130.10P | ***Security-Related Information*** The licensee identified multiple examples in which they failed to document the implementation of cyber security controls, adversely impacting the establishment of defense-in-depth protective strategies. Specifically
Region: IV | Arkansas Nuclear One | 124969 | 08/01/2019 |  |  | LIV |  | Green | Failure to Follow Radiation Protection Procedures Resulting in Uncontrolled Radioactive Material |  |  | TE?: N | 05000368 Arkansas Nuclear 2 |  | 71124.02
Region: IV | Arkansas Nuclear One | 125763 | 10/17/2019 |  | Licensee - Identified | LIV |  | Green | (OUO-SRI) Inattentive security armed responder. |  |  | TE?: N | 05000313 Arkansas Nuclear 1 05000368 Arkansas Nuclear 2 |  | 71130.02
Region: IV | Arkansas Nuclear One | 126602 | 01/29/2020 |  |  | LIV |  | Green | Failure to Verify Emergency Diesel Generator Crankcase Pressure Device in the Tripped Condition |  |  | TE?: N | 05000313 Arkansas Nuclear 1 |  | 71111.04Q
Region: IV | Callaway | 126488 | 12/31/2019 01/30/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate Acceptance Limits into Test Procedures |  | NPP | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the licensee’s failure to assure that testing required to demonstrate that the solid state protection system will perform
Region: IV | Callaway | 126489 | 12/31/2019 01/30/2020 | 2019004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Verify or Check the Adequacy of Design for the Control Room Filtration Fan |  | H.7 - Documentation | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to ensure design changes were subject to design control measures commensurate with those applied
Region: IV | Callaway | 126178 | 11/07/2019 11/22/2019 | 2019011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Environmentally Qualify Electrical Components in Containment to Most Severe Chemical Environment |  | NPP | TE?: N | 05000483 Callaway |  | 71111.21N | The inspectors identified a Green finding and associated non-cited violation of 10 CFR 50.49(e)(3) when the licensee failed to environmentally qualify all 10 CFR 50.49 electrical equipment for the most severe chemicals effects expected in containment.
Region: IV | Callaway | 125815 | 09/30/2019 11/05/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Butterfly Valve Issues |  | P.5 - Operating Experience | TE?: N | 05000483 Callaway | Equipment Performance | 71152 | The inspectors reviewed a self-revealed, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct a condition adverse to quality, identified several times bet
Region: IV | Callaway | 125816 | 09/30/2019 11/05/2019 | 2019003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Turbine Startup Procedure Caused Elevated Main Generator Vibration |  | NONE | TE?: N | 05000483 Callaway | Procedure Quality | 71152 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to establish, implement, and maintain a procedure for turbine startup and synchronization of the generator. Sp
Region: IV | Callaway | 125817 | 09/30/2019 11/05/2019 | 2019003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Maintenance Procedures for Switchyard Maintenance and Modifications |  | H.12 - Avoid Complacency | TE?: N | 05000483 Callaway | Design Control | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to establish, implement, and maintain procedures for switchyard maintenance and modifications. Specifically, a
Region: IV | Callaway | 125826 | 09/30/2019 11/05/2019 | 2019003-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Reactor Startup Procedures |  | H.2 - Field Presence | TE?: N | 05000483 Callaway | Human Performance | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to monitor all critical parameters during a reactor startup. Specifically, licensed operators failed to bypass
Region: IV | Callaway | 124538 | 03/31/2019 05/10/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality When Performing Essential Service Water System Flow Balance Tests |  | H.12 - Avoid Complacency | TE?: N | 05000483 Callaway | Equipment Performance | 71111.07T | The inspectors identified two examples of a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for failure to identify a condition adverse to quality during past essential service water system flow balance tests.
Region: IV | Callaway | 25896 | 12/31/2018 01/28/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Fuel Oil Filtration Renders Emergency Diesel Generator Inoperable |  | NPP | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a Green, non-cited violation of Technical Specification 3.8.1, “AC Sources – Operating,” for the licensee’s failure to take required actions for an inoperable emergency diesel generator. Specifically, the licensee connected a non
Region: IV | Callaway | 24068 | 06/30/2018 08/08/2018 | 2018002-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess and Manage Risk Associated with Switchyard Relay Work During a Planned Risk Significant Turbine-driven Auxiliary Feedwater Pump Equipment Outage |  | H.12 - Avoid Complacency | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors identified a Green, non-cited violation of 10 CFR 50.65(a)(4), “Requirements for monitoring the effectiveness of maintenance at nuclear power plants,” for the licensee’s failure to adequately assess and manage risk associated with switchyar
Region: IV | Callaway | 24069 | 06/30/2018 08/08/2018 | 2018002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Establish Maintenance Procedures for Doors that Provide Safety-Related Functions |  | H.4 - Teamwork | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to establish, implement, and maintain procedures associated with door maintenance. Specifically, the licensee failed to est
Region: IV | Callaway | 24046 | 06/30/2018 08/08/2018 | 2018002-03 | NRC | NCV | Emergency Preparedness | Green | Failure to critique an inaccurate emergency classification during a simulator training scenario |  | P.6 - Self-Assessment | TE?: N | 05000483 Callaway |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.47(b)(14) for the licensee’s failure to critique an inaccurate emergency classification made during licensed operator training. Performance Assessment: Performance Deficiency: The fail
Region: IV | Callaway | 24047 | 06/30/2018 08/08/2018 | 2018002-04 | NRC | NCV | Emergency Preparedness | Green | Failure of an Analysis of the Impact of Changes to Emergency Action Levels to Demonstrate the Changes did not Reduce the Effectiveness of the Emergency Plan |  | H.14 - Conservative Bias | TE?: N | 05000483 Callaway |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(3), for the failure of an analysis of the impact of changes to licensee emergency action levels to demonstrate that the changes did not reduce the effectiveness of the emergency plan. Per
Region: IV | Callaway | 23506 | 03/31/2018 05/03/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Emergency Operating Procedures |  | H.3 - Change Management | TE?: N | 05000483 Callaway |  | 71111.11Q | The inspectors identified a Green, non-violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to maintain emergency operating procedures for aligning auxiliary feedwater suction sources. Specifically, the licensee added con
Region: IV | Callaway | 22368 | 12/31/2017 01/28/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Design Control of the Ultimate Heat Sink Cooling Tower |  | H.12 - Avoid Complacency | TE?: N | 05000483 Callaway |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee’s failure to provide design control measures for verifying or checking the adequacy of the design of the ultimate heat sink co
Region: IV | Callaway | 22369 | 12/31/2017 01/28/2018 | 2017004-02 | NRC | NCV | Mitigating Systems | Green | Incorrect Safety Injection Pumps and Centrifugal Charging Pumps Mission Time |  | NPP | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee’s failure to assure that applicable regulatory requirements and the design basis were correctly translated into procedures for
Region: IV | Callaway | 21665 | 10/06/2017 10/06/2017 | 2017007-01 | NRC | NOV | Mitigating Systems | Green | Not Verifying the Operation and Timing of the Engineered Safety Feature Transformer XNB01 Load Tap Changer |  | H.5 - Work Management | TE?: N | 05000483 Callaway |  | 71111.21M | Closed in 2018001. The team identified a Green, cited violation of Technical Specification 5.4.1.a which requires, in part, that written procedures shall be established, implemented, and maintained covering the applicable procedures recommended in R
Region: IV | Callaway | 21621 | 09/30/2017 10/31/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Spurious Containment Spray Pump Start |  | P.3 - Resolution | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to implement Preventative Maintenance Basis document IC-LSELS, “Load Shed and Emergency Load Sequencer (LSELS),” Revi
Region: IV | Callaway | 21666 | 08/28/2017 10/06/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Safety Injection Piggyback Valve EJ-HV-8804A Valve Interlocks Not Tested |  |  | TE?: N | 05000483 Callaway |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” which requires, in part, that a test program shall be established to assure that all testing required to demonstrate that structures, systems, an
Region: IV | Callaway | 21667 | 08/28/2017 10/06/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Inputs to Internal Flooding Calculations Not Translated |  |  | TE?: N | 05000483 Callaway |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” which requires, in part, that measures shall be established to assure that the design basis is correctly translated into procedures and instru
Region: IV | Callaway | 17588 | 06/30/2017 07/26/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Motor Control Center Procedure |  | H.11 Challenge the Unknown | TE?: N | 05000483 Callaway |  | 71111.19 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow Procedure MPE-ZZ-QS001, "Cleaning and Inspection of Motor Control Centers," Revision 34. On May 2, 2017, th
Region: IV | Callaway | 17562 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Simulator Fidelity |  |  | TE?: N | 05000483 Callaway |  | 71111.11A | The inspectors identified a non-cited violation of 10 CFR 55.46(c), "Plant-Referenced Simulators," for failure of the licensee to ensure that the plant-referenced simulator demonstrated expected plant response to transient and accident conditions to which
Region: IV | Callaway | 17547 | 06/30/2016 08/12/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Water Hammer Stresses in Essential Service Water System Calculations |  | H.14 Conservative Bias | TE?: N | 05000483 Callaway |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to account for the essential service water pipe stresses caused by pressure fluctuations of the known column closure
Region: IV | Callaway | 17553 | 06/30/2016 08/12/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Applicable ASME Code Requirements for Repairs to Components in the Essential Service Water System |  | H.9 Training | TE?: N | 05000483 Callaway |  | 71111.07A | The inspectors identified a non-cited violation of 10 CFR 50.55a, "Codes and Standards," for the licensee's failure to repair various ASME Code Class 3 components in accordance with ASME Code, Section XI requirements. Specifically, the licensee did not fo
Region: IV | Callaway | 17554 | 06/30/2016 08/12/2016 | 2016002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Operability for a Degraded Condition |  | H.14 Conservative Bias | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate operability assessment when a degraded or nonconforming condition was i
Region: IV | Callaway | 17559 | 06/30/2016 08/12/2016 | 2016002-04 | NRC | VIO | Mitigating Systems | Green | Failure to Promptly Correct Conditions Adverse to Quality |  | H.1 Resources | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to take timely corrective action for a previously identified condition adverse to quality. Specifically,
Region: IV | Callaway | 17560 | 06/30/2016 08/12/2016 | 2016002-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Plant Foreign Material Exclusion Procedure |  | H.9 Training | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealed finding for the licensee's failure to follow the plant procedure for foreign material exclusion. Specifically, after finding foreign material (broken cable ties) within the main generator excitation transformer, est
Region: IV | Callaway | 17546 | 03/31/2016 05/09/2016 | 2016001-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Degraded Flood Mitigation Capability in Piping Penetration Room |  | H.4 Teamwork | TE?: N | 05000483 Callaway |  | 71111.06 | The inspectors identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate operability determination for safety related components located in the
Region: IV | Callaway | 17533 | 12/31/2015 02/11/2016 | 2015004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Promptly Correct a Condition Adverse to Quality on the Reactor Coolant System |  | H.5 Work Management | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality. Specifically, after identifying boric acid deposits on t
Region: IV | Callaway | 17537 | 12/31/2015 02/11/2016 | 2015004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Properly Establish and Maintain a Plant Procedure for Preparation for Refueling Outages |  |  | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1, "Procedures," for the licensee's failure to establish, implement, and maintain a procedure recommended in Regulatory Guide 1.33, Revision 2, Appendix A, Februa
Region: IV | Callaway | 17538 | 12/31/2015 02/11/2016 | 2015004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Plant Procedure for Unit Reliability Team |  | H.4 Teamwork | TE?: N | 05000483 Callaway |  | 71152 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow plant procedures for the unit reliability team. Specifically, after delaying a modification to the plant's turbine control system, no compensatory measures were implemen
Region: IV | Callaway | 17514 | 11/30/2015 01/13/2016 | 2015009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Suitability of the Design of the Reverse-Engineered Replacement Controller Cards for the Auxiliary Feedwater Flow Control Valves |  | H.4 Teamwork | TE?: N | 05000483 Callaway |  | NONE | The team identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the design of the replacement reverse engineered Modutronics controller cards for the auxiliary feedwater c
Region: IV | Callaway | 17515 | 11/30/2015 01/13/2016 | 2015009-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have an Adequate Procedure for Calibration of the Auxiliary Feedwater Pump Flow Control Valve Potentiometer |  |  | TE?: N | 05000483 Callaway |  | NONE | The team reviewed a self revealing non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to prescribe activities affecting quality using procedures appropriate to the circumstances. Specifica
Region: IV | Callaway | 17519 | 11/30/2015 01/13/2016 | 2015009-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have an Adequate Post-Maintenance Test for Setting the Motor-Driven Auxiliary Feedwater Flow Control Valve Modutronics Potentiometer |  |  | TE?: N | 05000483 Callaway |  | NONE | The team reviewed a self revealing non cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to ensure that testing demonstrated that structures, systems, and components will perform satisfactorily in service. Specifical
Region: IV | Callaway | 17520 | 11/30/2015 01/13/2016 | 2015009-04 | NRC | NCV | Mitigating Systems | Green | Two Examples of a Failure to Properly Designate the Significance Level of Callaway Action Requests |  | H.14 Conservative Bias | TE?: N | 05000483 Callaway |  | NONE | The team identified two examples of a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to implement their corrective action program procedure. Specifically: (1) on Novembe
Region: IV | Callaway | 17523 | 11/30/2015 01/13/2016 | 2015009-05 | NRC | NCV | Mitigating Systems | Green | Failure to Determine the Cause and Take Corrective Action to Preclude Repetition for the Inadequate Design of Auxiliary Feedwater Flow Control Valve Modutronics Cards |  | H.13 Consistent Process | TE?: N | 05000483 Callaway |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to determine the cause and take corrective action to preclude repetition for a significant condition adverse to quality
Region: IV | Callaway | 17524 | 11/30/2015 01/13/2016 | 2015009-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have an Adequate Procedure for Testing the Torque and Thrust Values for the Auxiliary Feedwater Pump Flow Control Valves |  | H.11 Challenge the Unknown | TE?: N | 05000483 Callaway |  | NONE | The team reviewed a self revealing non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to provide a procedure appropriate to the circumstances. Specifically, on March 4, 2014, the licensee
Region: IV | Callaway | 17532 | 11/30/2015 01/13/2016 | 2015009-07 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Additonal Undersized Components on Auxiliary Feedwater System Flow Control Valve Modified Modutronics Controller Cards |  | H.12 Avoid Complacency | TE?: N | 05000483 Callaway |  | NONE | The team identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct a condition adverse to quality. Specifically, as of September 23, 2015, the licensee had not ta
Region: IV | Callaway | 17503 | 09/30/2015 11/02/2015 | 2015003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Conduct Simulator Testing and Maintenance In Accordance with ANSI/ANS-3.5-2009 |  |  | TE?: N | 05000483 Callaway |  | 71111.11B | The inspectors identified a finding with four examples for failing to conduct and evaluate simulator performance testing in accordance with the standards of ANSI/ANS-3.5-2009. Specifically, the licensee failed to do the following: - set the instantaneous
Region: IV | Callaway | 17507 | 09/30/2015 11/02/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Operability Determination Procedure |  | H.11 Challenge the Unknown | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow their operability determination procedure. Specifically, when an auxiliary feedwater
Region: IV | Callaway | 17508 | 09/30/2015 11/02/2015 | 2015003-03 | NRC | NCV | Occupational Radiation Safety | Green | Unauthorized Non-Routine Maintenance on a Sealed Source Device |  | H.14 Conservative Bias | TE?: N | 05000483 Callaway |  | NONE | The inspectors identified a non-cited violation of Callaway Plant's License No. NPF-25, Condition 2.B.(3), for the licensee performing non-routine maintenance on a J.L. Shepherd calibrator without license authorization. The licensee documented this issue
Region: IV | Callaway | 17490 | 06/20/2015 08/03/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Compensatory Actions as Directed by Operability Evaluation |  | H.11 Challenge the Unknown | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to properly implement procedure directed compensatory actions necessary for operability of s
Region: IV | Callaway | 17502 | 06/20/2015 08/03/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation When Taking Emergency Diesel Generator Support Equipment Out of Service |  | H.5 Work Management | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate operability evaluation on the train A emergency diesel generator when
Region: IV | Callaway | 17489 | 05/31/2015 06/23/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate all Targets Within the Zone of Influence of Ignition Sources |  |  | TE?: N | 05000483 Callaway |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.48(c) and National Fire Protection Association Standard 805 for the licensee's failure to address the effects of fire damage to risk-significant circuits impacted by an analyzed fire scenario. S
Region: IV | Callaway | 17482 | 03/21/2015 04/24/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Post-maintenance Testing on Safety-related Equipment Prior to Declaring it Operable |  | H.5 Work Management | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to conduct post-maintenance testing after maintenance on safety-related equipment prior to
Region: IV | Callaway | 17481 | 12/31/2014 02/04/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality on Safety Related Equipment |  | P.2 Evaluation | TE?: N | 05000483 Callaway |  | 71111.12 | Inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," involving the licensee's failure to correct a condition adverse to quality. Specifically, an extent of condition review for a fail
Region: IV | Callaway | 17459 | 09/27/2014 10/29/2014 | 2014004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Nondestructive Testing on Essential Service Water Piping in Accordance with Procedures |  | H.8 Procedure Adherence | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform nondestructive testing on portions of the essential service water syst
Region: IV | Callaway | 17460 | 09/27/2014 10/29/2014 | 2014004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Verify Material Properities Prior to Installation |  | H.12 Avoid Complacency | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors reviewed a self-revealing finding involving failure to verify the proper material was installed in the plant during a modification to the circulating water pumps. Specifically, Request for Resolution 201300416 specified the use of ASTM A276
Region: IV | Callaway | 17464 | 08/29/2014 11/06/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.5 Work Management | TE?: N | 05000483 Callaway |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to assess operability in accordance with Station Procedure APA-ZZ-00500 Appendix 1, "Ope
Region: IV | Callaway | 17465 | 08/29/2014 11/06/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze for Tornado Missile Strike on Turbine Driven Auxiliary Feedwater Steam Exhaust Piping |  | P.2 Evaluation | TE?: N | 05000483 Callaway |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to verify the adequacy of the design of the turbine-driven auxiliary feedwater pump exhaust stack to be ab
Region: IV | Callaway | 13852 | 07/02/2014 07/31/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Testing the Load Tap Changers on Transformers XNB01 and XNB02. |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of Technical Specification 5.4.1, which states, in part, "Written procedures shall be established, implemented, and maintained covering the following activities: Part a. The applicable procedures recommende
Region: IV | Callaway | 13855 | 07/02/2014 07/31/2014 | 2014007-02 | NRC | NCVIV | Mitigating Systems | Green | 10 CFR 50.59 Screen for the Auxiliary Feedwater Motor Operated Control Valves Thermal Overload Relays. |  |  | TE?: Y SL-IV-NCVIV | 05000483 Callaway |  | 7111121 | The team identified a Severity Level IV, non-cited violation of 10 CFR Part 50.59, "Changes, Tests and Experiments," which states, in part, "A licensee may make changes in the facility as described in the final safety analysis report, make changes in th
Region: IV | Callaway | 13871 | 07/02/2014 07/31/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures by Not Identifying a Conflict Between Two Procedures |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Callaway | 13872 | 07/02/2014 07/31/2014 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Essential Service Water Pump House Supply Fan Testing. |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and comp
Region: IV | Callaway | 13878 | 07/02/2014 07/31/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Analyze Maximum Electrical Equipment Temperatures Resulting from the Single Failure of Control Building Heating Ventilation/Air Conditioning. |  | P.1 Identification | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, are correctly tr
Region: IV | Callaway | 13879 | 07/02/2014 07/31/2014 | 2014007-06 | NRC | NCV | Mitigating Systems | Green | Failure To Review Motor Operated Valve (MOV) Data and Complete Analysis of the Data in a Timely Manner. |  | H.1 Resources | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Callaway | 13886 | 07/02/2014 07/31/2014 | 2014007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Account for Motor Operated Valve Unseating Torque in Torque Calculation. |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and componen
Region: IV | Callaway | 13887 | 07/02/2014 07/31/2014 | 2014007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Cooling Instrumentation During a Station Blackout Event. |  | H.3 Change Management | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50.63(a)(2) which states, in part, "The reactor core and associated coolant, control, and protection systems, including station batteries and any other necessary support systems, must provide
Region: IV | Callaway | 13840 | 06/30/2014 08/04/2014 | 2014003-01 | NRC | FIN | Barrier Integrity | Green | Plastic Shipping Plug in Rosemount Transmitter |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a finding for the licensee's failure to properly install a flow transmitter for the containment spray system. Specifically, since construction, Rosemount Transmitter ENFT0005, which provides a signal for containment spray train A
Region: IV | Callaway | 13851 | 06/30/2014 08/04/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Condition Review |  | H.14 Conservative Bias | TE?: N | 05000483 Callaway |  | 2515/182 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate extent of condition assessment. While performing an evaluation of pitti
Region: IV | Callaway | 13831 | 03/28/2014 05/05/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Scoffold Procedue to Ensue Nearb Equipment is Not Impacted |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide an adequate procedure for construction and disassembly of scaffolding. Specifically
Region: IV | Callaway | 13832 | 03/28/2014 05/05/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions to Preclude Repetition |  |  | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," involving the licensee's failure to prevent repetition of a significant condition adverse to quality. Specifically, the licensee failed to
Region: IV | Callaway | 13839 | 03/28/2014 05/05/2014 | 2014002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Correct a Design Deficiency in Main Generator Bus Duct Cooling System |  | H.13 Consistent Process | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealing finding involving the failure to correct a design deficiency known to represent s single point plant trip vulnerability. Specifically, Procedure EDP-ZZ-01131, "Callaway Plant Health Program," required documenting a
Region: IV | Callaway | 13824 | 12/31/2013 02/06/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Ultimate Heat Sink Cooling Tower - Incorrect Action Criteria in Control Room Evacuation Procedure |  |  | TE?: N | 05000483 Callaway |  | 71111.17T | The inspectors identified a non-cited violation of Technical Specification 5.4.1(d), "Procedures," which states, in part, that written procedures shall be established, implemented, and maintained covering fire protection program implementation. Specifical
Region: IV | Callaway | 13825 | 12/31/2013 02/06/2014 | 2013005-03 | NRC | NCV | Mitigating Systems | Green | Failue to Correct Non-conservative Safety Related Equipment Oil Leakage Criteria |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000483 Callaway |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for a failure to correct a condition adverse to quality. Specifically, the licensee's calculations to determine acceptable oil leak rates of
Region: IV | Callaway | 13826 | 12/31/2013 02/06/2014 | 2013005-04 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Class and Describe a Radioactive Material Shipment Correctly and Failue to Include all Required Hazard Communication Information in a Radioactive Shipment Document |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | NONE | Inspectors reviewed a self-revealing non-cited violation of 10 CFR 71.5(a) because the licensee failed to class and describe a radioactive material shipment correctly and failed to include all required hazard communication information in a radioactive shi
Region: IV | Callaway | 13822 | 09/27/2013 11/07/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adminiser a Compehensive Requalification Operating Test |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR 55.59, "Requalification," for failure to administer a comprehensive annual requalification operating test to one crew. After a quality review by NRC inspectors, it was determined that the job perfo
Region: IV | Callaway | 13803 | 06/30/2013 08/13/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor and Maintain Emergency Core Cooling System Room Coolers |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000483 Callaway |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65, involving the licensee's failure to monitor performance of structures, systems, or components in a manner sufficient to provide reasonable assurance that these structures, systems, or compon
Region: IV | Callaway | 13804 | 06/30/2013 08/13/2013 | 2013003-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Appropriately Pre-plan and Perform Maintenance on the Unit Auxiliary Transformer |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors reviewed a self-revealing non-cited violation of Technical Specifications 5.4.1 and Regulatory Guide 1.33, "Quality Assurance Program Requirements (Operation)," involving the failure to appropriately pre-plan and perform maintenance on equi
Region: IV | Callaway | 13805 | 06/30/2013 08/13/2013 | 2013003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Appropriately Pre-plan and Perform Maintenance on Safeguards Transformer B |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000483 Callaway |  | 71152 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1 and Regulatory Guide 1.33, "Quality Assurance Program Requirements (Operation)," involving the failure to appropriately pre-plan and perform maintenance on equip
Region: IV | Callaway | 13808 | 06/30/2013 08/13/2013 | 2013003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Screen Repetitive Equipment Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to perform activities affecting quality in accordance with procedures. Specifically, the licens
Region: IV | Callaway | 13797 | 12/31/2012 02/13/2013 | 2012005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Technical Specification Surveillance Requirements on the Control Room Air Conditioning System |  |  | TE?: N | 05000483 Callaway |  | 71111.07A | The inspectors identified a non-cited violation of Technical Specification 3.7.11, "Control Room Air Conditioning System (CRACS)," for failure to perform the surveillance requirements specified for the control room air conditioning system. Surveillance Re
Region: IV | Callaway | 13794 | 09/25/2012 11/05/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct an Adverse Condition on an Emergency Diesel Generator |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving the licensee's failure to correct an adverse condition on a safety related system. Specifically, when a low oil condition was iden
Region: IV | Callaway | 13795 | 09/25/2012 11/05/2012 | 2012004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, because a worker did not follow radiation work permit - 3 - instructions. Specifically, an individual entered an area with radiation dose rates significantl
Region: IV | Callaway | 13783 | 07/15/2012 09/11/2012 | 2012008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to identify and correct the failure mode of an essential service water pump |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71152B | The team reviewed a Green self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. During troubleshooting, the license
Region: IV | Callaway | 13784 | 07/15/2012 09/11/2012 | 2012008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to provide adequate maintenance instruction |  |  | TE?: N | 05000483 Callaway |  | 71152B | The team reviewed a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to provide maintenance instructions appropriate for repair of the Train B emergency diesel generator supply fan. These inadequate instruct
Region: IV | Callaway | 13785 | 07/15/2012 09/11/2012 | 2012008-03 | NRC | NCV | Mitigating Systems | Green | Failure to initiate a corrective action document. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure, upon discovery of an adverse condition, to initiate a Callaway Action Request, to notify the shift
Region: IV | Callaway | 13792 | 07/15/2012 09/11/2012 | 2012008-04 | NRC | NCV | Mitigating Systems | Green | Failure to fully implement fl uid leak management program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to fully implement the requirements of its fluid leak management procedure. The team identifie
Region: IV | Callaway | 13776 | 06/26/2012 08/02/2012 | 2012003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate Operating Experience for a 10 CFR 50.65(a)(3) Assessment |  |  | TE?: N | 05000483 Callaway |  | 71111.06 | The inspectors identified a finding for failure to ensure that a system credited in the Final Safety Analysis Report for mitigating internal flooding was available and reliable. On May 1, 2012, the licensee discovered the floor drains in the engineered sa
Region: IV | Callaway | 13777 | 06/26/2012 08/02/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Declare Component Cooling Water Train A Inoperable Due to Voids |  | P.2(b) Implementing Operating Experience | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, involving the licensee's failure to properly assess the operability of component cooling water train A when voids were recognized during a post-maintenance
Region: IV | Callaway | 13775 | 05/04/2012 06/07/2012 | 2012007-01 | NRC | FIN | Mitigating Systems | Green | Failure to establish preventive maintenance for equipment used to achieve post-fire safe shutdown. |  |  | TE?: N | 05000483 Callaway |  | 71111.05T | The team identified a finding for the failure to establish preventive maintenance of local transfer/isolation switch JEHS0021A, "B D/G Fuel Oil Transfer Pump Iso/Run" for the train B emergency diesel generator fuel oil transfer pump in procedures covering
Region: IV | Callaway | 13774 | 03/27/2012 04/23/2012 | 2012002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Evaluate the Design of Steam Generator Drain Plugs |  |  | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after the licensee failed to ensure that testing used to verify the adequacy of a steam generator drain plug was conducted under expected design
Region: IV | Callaway | 13760 | 12/31/2011 02/07/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Ensure Separation of Stainless Steel and Carbon Steel Hand Files and Wire Brushes |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, for the failure to have procedures that ensured that hand files and wire brushes designated for stainless steel weld preparation were stored separately from hand files
Region: IV | Callaway | 13761 | 12/31/2011 02/07/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Simulator Fidelity |  |  | TE?: N | 05000483 Callaway |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR Part 55.46(c), "Plant-Referenced Simulators," for failure of the licensee to ensure that the plant-referenced simulator demonstrated expected plant response to transient and accident conditions to
Region: IV | Callaway | 13762 | 12/31/2011 02/07/2012 | 2011005-03 | NRC | FIN | Mitigating Systems | Green | Failure to Conduct Simulator Testing in Accordance with ANSI/ANS 3.5-1998 |  |  | TE?: N | 05000483 Callaway |  | 71111.11B | The inspectors identified a finding associated with the conduct of simulator performance testing because the licensee was not testing in accordance with the standards of ANSI/ANS 3.5-1998. Specifically, the licensee did not include relief valve flow in th
Region: IV | Callaway | 13766 | 12/31/2011 02/07/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess and Manage Outage Risk Associated with Significant Switchyard Work |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," involving the licensee's failure to assess and manage outage risk related to significant switchy
Region: IV | Callaway | 13767 | 12/31/2011 02/07/2012 | 2011005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Ground and Test Device Damages Residual Heat Removal Pump Switchgear |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000483 Callaway |  | 71111.19 | The inspectors reviewed a Green self-revealing non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Procedures," involving the licensee's failure to correctly install a ground test device for the train A safety-related 4160 volt switchgear, NB0
Region: IV | Callaway | 13768 | 12/31/2011 02/07/2012 | 2011005-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Isolate Control Room Air Comditining Unite SGK04A for Maintenance |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a Green self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," involving the failure to isolate an electrical power supply during maintenance on control room air conditioning system train A. Specifical
Region: IV | Callaway | 13773 | 12/31/2011 02/07/2012 | 2011005-07 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Implement Plant Maintenance Procdures |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," involving the failure to ensure compliance with relay test maintenance procedures associated with electrical switchyard work that affected the p
Region: IV | Callaway | 13521 | 09/23/2011 11/03/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Implement Plant Maintenance Procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to correctly follow maintenance procedures which resulted in a failure of motor-operated valve EFHV0065 associated wit
Region: IV | Callaway | 13755 | 09/23/2011 11/03/2011 | 2011004-02 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Evaluate Breaker Relay Settings Results in Partial Loss of Station Blackout Response Capability |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71153 | The inspectors reviewed a self-revealing finding for the failure of AmerenUE engineering personnel to correctly establish the relay settings for the alternate emergency power supply diesel output breakers. On August 21, 2011, Callaway Plant experienced a
Region: IV | Callaway | 13491 | 06/23/2011 07/18/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Flooding Analysis for Room 3101 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after the licensee failed to provide adequate design control measures for verifying the adequacy of the flooding analysis associated with the 20
Region: IV | Callaway | 13492 | 06/23/2011 07/18/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Refueling Water Storage Tank Level Transmitters for High-Energy Line Break |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to adequately evaluate a potential high-energy line break in nonseismically qualified auxiliary steam piping in the r
Region: IV | Callaway | 13496 | 06/23/2011 07/18/2011 | 2011003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Establish Test Program for Isolation Valves in Post-LOCA Recirculation Flowpath |  |  | TE?: N | 05000483 Callaway |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to adequately demonstrate that the seat leakage of centrifugal charging pump and safety injection pump suction isolation valves remaine
Region: IV | Callaway | 13490 | 06/23/2011 07/18/2011 | 2011003-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correctly Implement a Plant Safety System Test Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified when the licensee's failure to correctly follow a test procedure resulted in a negative reactivity excursion due to excessive boration. On May 27, 2011, w
Region: IV | Callaway | 13497 | 05/27/2011 07/18/2011 | 2011003-04 | NRC | NCV | Public Radiation Safety | Green | Failure to Verify Recipient's License Conditions Prior to shipping Special Nuclear Material |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71124.08 | The inspectors identified a noncited violation of 10 CFR 70.42 (c) for failure to verify that a recipient of special nuclear material was authorized to receive the quantity of material shipped. This finding was determined to be of very low safety signific
Region: IV | Callaway | 13475 | 03/24/2011 05/04/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Document Reasonable Expectation of Operability for Equipment Supported b y the Class 1E Air Conditioning Units |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for failure to adequately evaluate past operability associated with the Class 1E electrical equipment air conditionin
Region: IV | Callaway | 13482 | 03/24/2011 05/04/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Containment Spray Test Procedure Potentially Creates an Unanalyzed Condition |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for failure to provide adequate procedural guidance for testing of containment spray pumps. The inspectors reviewed a licen
Region: IV | Callaway | 13483 | 03/24/2011 05/04/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Scaffolding Installation Inadequacy |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for failure to properly implement Procedure MDP-ZZ-S0001, "Scaffolding Installation and Evaluation," Revision 26, when scaffolding was erected near or in contact with equipm
Region: IV | Callaway | 13473 | 03/18/2011 04/26/2011 | 2011006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Design the Emergency Diesel Generator Ground Fault Protection Circuitry |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly
Region: IV | Callaway | 13474 | 03/18/2011 04/26/2011 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Residual Heat Removal Flow Alarm Setpoint |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly
Region: IV | Callaway | 13501 | 02/08/2011 05/06/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure in the Establishment of a Turbine Driven Auxiliary Feedwater Pump Postmaintenance Test Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a involving a failure to follow procedures in the development of Procedure OTS-FC-0006, "TDAFW Pump Post-Maintenance Test Run on Aux Steam." Specifically, the licensee fail
Region: IV | Callaway | 13502 | 02/08/2011 05/06/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Turbine-Driven Auxiliary Feedwater Pump Postmaintenance Testing |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a involving five examples of failure to follow 2 Enclosure Procedure OTS-FC-0006, "TDAFW Pump Post-Maintenance Test Run on Aux Steam." Specifically, operators failed to fo
Region: IV | Callaway | 13503 | 02/08/2011 05/06/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Past Operability Determination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure APA-ZZ-00500, Appendix 3, "Past Operability a
Region: IV | Callaway | 13507 | 02/08/2011 05/06/2011 | 2011007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Calculate and Implement Conservative Safety Related Equipment Oil Leakage Operability Criteria |  |  | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for a failure to adequately determine safety related equipment oil leakage acceptance criteria that was used in operator logs. Specifically,
Region: IV | Callaway | 13508 | 02/08/2011 05/06/2011 | 2011007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance Schedule to Protect Safety-Related Equipment from Undetected Degraded Conditions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1 for a failure to adequately establish and implement procedures required by Regulatory Guide 1.33, Appendix A, Section 9, "Procedures for Performing Maintenance." Specifical
Region: IV | Callaway | 13509 | 02/08/2011 05/06/2011 | 2011007-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Extent of Cause Results in Missed Safety-Related Pump Overhaul |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix 8, Criterion XVI, "Corrective Action," associated with the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee reduced
Region: IV | Callaway | 13465 | 12/31/2010 01/26/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for failure to follow Procedure APA ZZ 00500, Appendix 1, "Operability and Functionality Determinations." On the morning of
Region: IV | Callaway | 13466 | 12/31/2010 01/26/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate, Untimely Corrective Actions for a Containment Spray System Condition Adverse to Quality |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to promptly identify and correct a boric acid leak on the containment spray system, a condition advers
Region: IV | Callaway | 13467 | 12/31/2010 01/26/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Condition Adverse to Quality Associated with Emergency Diesel Generator Jacket Water Keep Warm Pump into the Corrective Action Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow the requirements of Callaway Procedure APA ZZ 00500, "Corrective Action Program,"
Region: IV | Callaway | 13459 | 11/05/2010 12/17/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Degraded Conditions in Essential Service Water System in a Timely Manner |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000483 Callaway |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to correct in a timely manner degraded conditions affecting the essential service water system. Specifically, the licensee failed to resolve
Region: IV | Callaway | 13463 | 11/05/2010 12/17/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Repetitive Failures in Steam Generator Atmospheric Dump Valves in a Timely Manner |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000483 Callaway |  | 71152B | The team identified a green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, involving the failure to promptly correct deficiencies affecting the steam generator atmospheric steam dump valves. In 2002, system engineers identified that the
Region: IV | Callaway | 13464 | 11/05/2010 12/17/2010 | 2010006-03 | NRC | FIN | Mitigating Systems | Green | Failure to Follow the Corrective Action Program Procedure |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000483 Callaway |  | 71152B | The team identified a finding involving the licensee's failure to follow the corrective action program procedure for assigning significance levels to Callaway action requests. This deficiency resulted in the licensee's failure to adequately evaluate the c
Region: IV | Callaway | 13455 | 09/23/2010 11/02/2010 | 2010004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Adequate Administration Controls for Failed Containment Isolation Valve |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a green noncited violation of Technical Specification 3.6.3, "Containment Isolation Valves," after the licensee failed to implement adequate administrative controls following the failure of valve EGHV0059. On August 10, 2010, con
Region: IV | Callaway | 13457 | 09/03/2010 11/09/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Lack of Maintenance as Cause of Diesel Generator Failure |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000483 Callaway |  | 95001 | The inspectors identified a Green noncited violation of 10 Part 50, Appendix B, Criterion V, for the failure to accomplish a root cause evaluation in accordance with station procedures. Specifically, the licensee failed to identify and document that imple
Region: IV | Callaway | 13446 | 06/23/2010 07/29/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Procedure to Verify and Maintain Emergency Core Cooling System Operable |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.04Q | The inspectors identified a noncited violation of Technical Specification 3.5.2, "Emergency Core Cooling Systems." Specifically Technical Specifications Surveillance Requirement 3.5.2.3, "Verify the ECCS piping is full of water," was not being met by lice
Region: IV | Callaway | 13447 | 06/23/2010 07/29/2010 | 2010003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Two Operable Source Range Channels During Core Alterations |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71111.2 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," when the licensee's inadequate procedure and failure to control work activities during a reload of the reactor vessel fuel assemblies resulted
Region: IV | Callaway | 13448 | 06/23/2010 07/29/2010 | 2010003-03 | NRC | FIN | Initiating Events | Green | Failure to Ensure Completion of Corrective Actions for Degraded Chemical and Volume Control System Valves |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a finding associated with AmerenUE's failure to take prompt corrective actions for leaking boundary valves in the chemical and volume control system. On April 13, 2010, an attempt to place the train A chemical and volume control
Region: IV | Callaway | 13454 | 06/23/2010 07/29/2010 | 2010003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Fabricate Replacement Gasket for Emergency Diesel Generator TrainA |  |  | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after the licensee failed to adequately select suitable replacement gaskets essential to the operation of emergency diesel genera
Region: IV | Callaway | 13439 | 03/24/2010 04/19/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.15 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for failure to follow Procedure APA-ZZ-00500, Appendix 1, "Operability and Functionality Determinations." The inspectors determine
Region: IV | Callaway | 13440 | 03/24/2010 04/19/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Suitable Replacement Parts Essential for the Operation of the Component Cooling Water System |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after the licensee failed to adequately select suitable replacement gaskets essential to the operation of the component cooling water system heat excha
Region: IV | Callaway | 13441 | 03/24/2010 04/19/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Failure to M aintain an Adequare Ultimate Heat Sink Thermal Performance Analysis |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after AmerenUE failed to provide adequate design control measures for verifying the adequacy of the ultimate heat sink thermal performance analysis eva
Region: IV | Callaway | 13432 | 12/31/2009 01/20/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain and Adequate Flooding Analysis |  |  | TE?: N | 05000483 Callaway |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after AmerenUE failed to provide adequate design control measures for verifying the adequacy of flooding analysis for the auxiliary feedwater pi
Region: IV | Callaway | 13435 | 12/31/2009 01/20/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Two Examples of Failure to Follow Operability Determination Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.15 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for two examples of failure to follow Procedure APA-ZZ-00500, Appendix 1, "Operability and Functionality Determinations." The firs
Region: IV | Callaway | 13436 | 12/31/2009 01/20/2010 | 2009005-03 | Self - Revealed | NCV | Initiating Events | Green | Plant Transient Caused by Human Error During Power Range Nuclear Instrument Surveillance |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 71111.22 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after maintenance on power range nuclear instrument N41 resulted in an unanticipated plant transient. On October 6, 2009, the licensee performed
Region: IV | Callaway | 13417 | 09/30/2009 09/30/2009 | 2009009-01 | NRC | NCV | Mitigating Systems | Green | Turbine-driven auxiliary feedwater pump inoperable due to inadequately lubricated trip throttle valve |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 93812 | The team identified a self-revealing apparent violation of Technical Specification 3.7.5, "Auxiliary Feedwater System," due to the failure to adequately lubricate turbine-driven auxiliary feedwater pump trip throttle valve FCHV0312. During May 25, 2009, s
Region: IV | Callaway | 13418 | 09/30/2009 09/30/2009 | 2009009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Lubrication Procedure for Valve FCHV0312 |  |  | TE?: N | 05000483 Callaway |  | 93812 | The team identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for the failure to provide adequate procedural guidance for the lubrication of auxiliary feedwater pump turbine trip throttle valve FCHV0312. The inspectors found t
Region: IV | Callaway | 13423 | 09/30/2009 09/30/2009 | 2009009-03 | NRC | NCV | Mitigating Systems | Green | Failure to adequately evaluate the use of Mobile 28 grease for the turbine-driven auxiliary feedwater pump trip throttle valve. |  |  | TE?: N | 05000483 Callaway |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to adequately evaluate the use of Mobile 28 grease for the turbine-driven auxiliary feedwater pump trip throttle valve. The licensee's
Region: IV | Callaway | 13424 | 09/30/2009 09/30/2009 | 2009009-04 | NRC | NCV | Mitigating Systems | Green | Failure to enter conditions adverse to quality associated with the turbine-driven auxiliary feedwater pump trip throttle valve into the corrective action program. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Callaway Procedure APA-ZZ-00500, "Corrective Action Program." Spe
Region: IV | Callaway | 13425 | 09/30/2009 09/30/2009 | 2009009-05 | NRC | NCV | Mitigating Systems | Green | Failure to ensure turbine-driven auxiliary feedwater pump is operable prior to entry into Mode 3. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 93812 | The team identified a noncited violation of Technical Specification Limiting Condition for Operation 3.0.4 for entering Mode 3 with the turbine-driven auxiliary feedwater pump inoperable. Specifically, on November 3, 2008, while in Mode 4 for Refueling Ou
Region: IV | Callaway | 13430 | 09/23/2009 10/21/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Essential Service Water Pump Cable Underground Electrical Vault Seals |  |  | TE?: N | 05000483 Callaway |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to take prompt corrective actions to prevent continuous submergence of essential service water pump ke
Region: IV | Callaway | 13414 | 06/23/2009 07/28/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Controls of Crane Work Above the Protected Train of Essential Service Water |  | H.3(a) Work Planning | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) associated with the licensee's failure to adequately assess and manage risk associated with crane work over the essential service water system Train A. On March 31, 2009, the licensee pe
Region: IV | Callaway | 13415 | 06/23/2009 07/28/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate, At Power, Risk Assessment for Maintenance Activities on One Train of Essential Service Water and Emergency Diesel Generator |  | H.3(a) Work Planning | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) associated with the licensee's failure to perform an adequate risk assessment for planned maintenance on the emergency diesel generator Train A and essential service water pump Train A.
Region: IV | Callaway | 13416 | 06/23/2009 07/28/2009 | 2009003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply with Radiation Work Permit Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a, which resulted from a failure to comply with radiation work permit instructions. Specifically, on November 2, 2008, during a change out of the chemical and vo
Region: IV | Callaway | 13412 | 04/30/2009 06/01/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Suitable Replacement Parts Essential for Emergency Diesel Generator Train B |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identifed a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" after the licensee failed to adequately select suitable replacement parts essential to the operation of emergency diesel generator Train B. On Dec
Region: IV | Callaway | 13400 | 03/24/2009 04/28/2009 | 2009002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Response to Feedwater Transient Results in Reactor Trip |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after operator response to an electrical fault on the condensate Pump C motor resulted in an unplanned and unnecessary reactor trip, feedwater
Region: IV | Callaway | 13401 | 03/24/2009 04/28/2009 | 2009002-02 | Self - Revealed | NCV | Initiating Events | Green | Intermediate Range Hi Flux Reactor Protection System Actuation W hile Shutdown |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after maintenance on intermediate range nuclear Instrument N36 resulted in an unanticipated reactor trip signal and feedwater isolation. On Dec
Region: IV | Callaway | 13396 | 02/27/2009 04/09/2009 | 2009006-01 | NRC | NCV | Initiating Events | Green | Failure to Correct Problems with Fire Protection Impairment Permits |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 71111.05T | An NRC identified violation of License Condition 2.C.(5), "Fire Protection," was identified for failing to effectively correct problems with the issuance and establishment of Fire Protection Impairment Permits. After problems were identified in 2006 and 2
Region: IV | Callaway | 13381 | 12/31/2008 02/04/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate shutdown risk assessment for maintenance activities in the reactor building. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), for failure to adequately assess and manage shutdown risk associated with maintenance activities in the reactor building. Specifically, on October 15, 2008, the inspectors found foreign
Region: IV | Callaway | 13382 | 12/31/2008 02/04/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to ensure the suitability of the design of the resideual heat removal Train A pump room cooler |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71111.19 | The inspectors identified a self-revealing Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after a trip of the residual heat removal Train A room cooler fan revealed that AmerenUE had not adequately selected and re
Region: IV | Callaway | 13383 | 12/31/2008 02/04/2009 | 2008005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate maintenance procedure resulted in residual heat removal mechanical seal failure |  |  | TE?: N | 05000483 Callaway |  | 71111.19 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1a, "Procedures," for inadequate procedural guidance that resulted in the failure of the residual heat removal Train A pump mechanical seal. On October 22, 2008,
Region: IV | Callaway | 13386 | 12/31/2008 02/04/2009 | 2008005-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to maintain an adequate plant shutdown procedure |  | H.1(c) Communication of Decisions | TE?: N | 05000483 Callaway |  | 71111.2 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after improper isolation of the main steam isolation valves by the Callaway control room operators resulted in a reactor trip signal and auxili
Region: IV | Callaway | 13387 | 12/31/2008 02/04/2009 | 2008005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to adequately implement plant equipment control tagout procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 71111.2 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after improper restoration of the essential service water supply to the emergency diesel generator Train A lubricating oil cooler resulted in s
Region: IV | Callaway | 13388 | 12/31/2008 02/04/2009 | 2008005-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to comply wity high radiation area entry requirements. |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.7.1, which resulted from a failure of three individuals to comply with high radiation area entry requirements. Specifically, on October 20, 2008, three engineers tou
Region: IV | Callaway | 13394 | 12/31/2008 02/04/2009 | 2008005-07 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to terminate refueling water storage tank recirculation results in inadvertent loss of spent fuel pool inventory |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1a, "Procedures," for the failure to close Valve BNV0002 during a fill of the spent fuel pool resulting in approximately 2000 gallons of water being inadvertently
Region: IV | Callaway | 13395 | 12/31/2008 02/04/2009 | 2008005-08 | Self - Revealed | FIN | Initiating Events | Green | Failure to evaluate material equivalencies leads to a manual reactor trip |  |  | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a self-revealing finding for failure of the engineering department to perform a material equivalency evaluation to ensure replacement components do not adversely affect plant operations. On November 11, 2008, Callaway Plant exper
Region: IV | Callaway | 13372 | 09/24/2008 10/29/2008 | 2008004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Boric Acid Corrosion Control Procedures |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to perform a corrosion evaluation of boric acid leakage from containment spray Valve ENHV0006 in accordance wi
Region: IV | Callaway | 13374 | 08/22/2008 12/05/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Safety Related 125 Vdc Station Battery NK11 Inadequate Battery Sizing Calculation |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a non-cited violation 10 CFR 50, Appendix B, Criterion III, "Design Control," for failure to verify the adequacy of design and for failure to correctly translate the 125 Vdc system design basis into instructions, procedures, and drawin
Region: IV | Callaway | 13375 | 08/22/2008 12/05/2008 | 2008008-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative Pipe Break Location for the Condensate Stoarge Tank Supply to Auxiliary Feedwater Pumps |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for not verifying the adequacy of the design. Specifically, an incorrect pipe break location in the analysis for loss of the condensate storage tank f
Region: IV | Callaway | 13376 | 08/22/2008 12/05/2008 | 2008008-03 | NRC | NCV | Mitigating Systems | Green | Auxiliary Feedwater Turbine Digital Control Panel FC219 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawing" for the failure to follow Procedure APA-ZZ-00500, Appendix 1, Revision 6, "Operability Determination." The evaluation did not inc
Region: IV | Callaway | 13352 | 06/24/2008 08/05/2008 | 2008003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure the Suitability of the Design of the Containment Air Cooler Control Circuitry |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified after determining that the licensee had not adequately selected and reviewed the suitability of the design of the containment air cooler con
Region: IV | Callaway | 13353 | 06/24/2008 08/05/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Procedure Resulted in an Inaperable Emergency Core Cooling System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 3.5.2, "Emergency Core Cooling Systems," after an inadequate surveillance procedure resulted in the licensee failing to maintain the emergency core cooling system full of water as r
Region: IV | Callaway | 13363 | 06/24/2008 08/05/2008 | 2008003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality for Diesel Generator Jacket Water O-Rings |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71111.19 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified after the licensee failed to promptly correct leakage from diesel generator jacket water o-rings. On February 20, 2008, during a normal s
Region: IV | Callaway | 13364 | 06/24/2008 08/05/2008 | 2008003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain an Adequate Technical Specificaion Bases Change Process |  | H.1(c) Communication of Decisions | TE?: N | 05000483 Callaway |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," after Callaway control room operators improperly entered a wrong Technical Specification action statement due to the failure to maintain the Technical Specifi
Region: IV | Callaway | 13371 | 06/24/2008 08/05/2008 | 2008003-05 | NRC | VIO | Mitigating Systems | Green | Failure to Prevent Recurrence of Voids in Emergency Core Cooling System Cold Leg Recirculation Piping | EA Case: 2008190 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee failed to restore compliance within a reasonable time by establishing measures to prevent void formation in emergency core coolin
Region: IV | Callaway | 13345 | 03/14/2008 04/21/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Nonconservative Technical Specification for Battery Inter-cell Connection Resistances |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000483 Callaway |  | 71152B | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because the licensee failed to ensure that Technical Specification Surveillance Requirements for the NK11 and NK14 safety related batteries esta
Region: IV | Callaway | 13339 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Needed Test Conditions to Satisfy Technical Specification Surveillance Requirement 3.8.1.18 |  |  | TE?: N | 05000483 Callaway |  | 71111.04Q | The inspectors identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," after AmerenUE confirmed that the load shedding emergency load sequencing test could not demonstrate that component cooling water pump breakers wo
Region: IV | Callaway | 13340 | 12/31/2007 02/11/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage Increased Risk During a Maintenance Activity |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4) after AmerenUE operating personnel failed to implement prescribed risk management actions associated with maintenance on the Train B emergency diesel generator. NRC inspectors perf
Region: IV | Callaway | 13341 | 10/05/2007 02/11/2008 | 2007005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Adhere to a Radiation Work Permit Requirement |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of a Technical Specification 5.4.1.a. required procedure that resulted in the external contamination of a work group with two of the four workers receiving internal contamination. Specifically,
Region: IV | Callaway | 13342 | 10/05/2007 02/11/2008 | 2007005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to notify radiation protection of an electronic dosimeter alarm. |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of a Technical Specification 5.4.1.a. required procedure that resulted when mechanical maintenance workers did not report electronic dosimeter alarms when received. Specifically, during troubles
Region: IV | Callaway | 12561 | 09/22/2007 10/26/2007 | 2007004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality for Train B Motor-driven Auxiliary Feedwater Pump |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152 | A self-revealing Green noncited violation of 10 CFR 50, Appendix B, Criteria XVI, "Corrective Action," was identified after the licensee allowed the Train B motor-driven auxiliary feedwater pump to be returned to service even though maintenance personnel
Region: IV | Callaway | 13338 | 09/22/2007 10/26/2007 | 2007004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Maintenance Instructions Affecting the Letdown Backpressure Control Valve. |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 71153 | A self-revealing Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified after the licensee failed to follow reassembly procedures for the letdown system backpressure control valve. In
Region: IV | Callaway | 13343 | 08/10/2007 02/11/2008 | 2007005-05 | NRC | NCV | Emergency Preparedness | Green | Licensee Practices Allow Protective Action Recommendations for Areas Where Protective Action Guides are not Exceeded. |  |  | TE?: N | 05000483 Callaway |  | NONE | The inspectors identified a noncited violation of 10 CFR 50.54(q), 50.47(b)(10), and 10 CFR Part 50, Appendix E, IV(B), for practices that require licensee protective action recommendations to be made for areas offsite that are not affected by the radiolo
Region: IV | Callaway | 12555 | 06/23/2007 08/02/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Ineffective Corrective Actions to Evaluate the Design Basis for an Ultimate Heat Sink Workaround |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," after AmerenUE failed to implement effective corrective actions to correct discrepancies in the ultimate heat sink design basis. The system d
Region: IV | Callaway | 12558 | 06/23/2007 08/02/2007 | 2007003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Foreign Material Controls for the Refueling Cavity with Reactor Head Removed |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after refueling personnel did not maintain procedurally required foreign material exclusion barriers. AmerenUE's foreign materi
Region: IV | Callaway | 12559 | 06/23/2007 08/02/2007 | 2007003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Essential Service Water Pipe Wall Thinning |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," after AmerenUE's past corrective actions were inadequate to identify and correct essential service water piping degradation due to corrosion.
Region: IV | Callaway | 12552 | 03/24/2007 05/02/2007 | 2007002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inoperable Auxiliary Feedwater Pump due to an Inadequae Surveillance Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.22 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified after an inadequate surveillance procedure resulted in the inadvertent defeat of the Train B turbine-driven auxiliary feedwater pump automatic start featu
Region: IV | Callaway | 12553 | 03/24/2007 05/02/2007 | 2007002-02 | NRC | FIN | Initiating Events | Green | Inadequate Management of an Operator Workaround Resulted in Unplanned Loss of Voume Control Tank Inventory |  | H.3(b) Work Activity Coordination | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a finding after volume control tank inventory was inadvertently diverted from the reactor coolant system due to inadequate management of an operator workaround. On January 19 and March 22, 2007, operators had isolated the volume
Region: IV | Callaway | 12554 | 03/24/2007 05/02/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Preserve Essential Service Water System Material Condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, after past corrective actions were inadequate to preclude recurrence of essential service water piping degradation due to corrosion. On March 14 and 23, 2007, plan
Region: IV | Callaway | 12541 | 01/12/2007 02/23/2007 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Refueling Water Storage Tank Vent Sizing Calculation |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for an inadequate refeuling water storage tank vent sizing calculation. The calculation assumed that only one low head safety injection pump would opera
Region: IV | Callaway | 12542 | 01/12/2007 02/23/2007 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Diesel Generator Fuel Oil Verification |  | H.4(a) Human Error Prevention | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of Technical Specifications Surveillance Requirement 3.8.3.3 for the failure to verify that fuel oil testing results were within the specified limits. Consequently, fuel oil that was transferred to the Train A stor
Region: IV | Callaway | 12543 | 01/12/2007 02/23/2007 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Diesel Generator Heat Exchanger Tube Plugging Calculation |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to properly calculate the tube plugging limit for the emergency diesel generator intercooler, jacket water, and lube oil cooler heat exc
Region: IV | Callaway | 12549 | 01/12/2007 02/23/2007 | 2006009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Essential Service Water Cooling Tower Design Basis Information into Specifications and Procedures. |  |  | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to properly translate design requirements into procedures and instructions. Specifically, the cooling tower sizing calculation specified
Region: IV | Callaway | 12550 | 01/12/2007 02/23/2007 | 2006009-05 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Action for Refueling Water Storage Tank Vortexing Concerns |  | P.2(b) Implementing Operating Experience | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Action) for the failure to take adequate corrective actions following the identification of a condition adverse to quality. Specifically, the licensee had id
Region: IV | Callaway | 12551 | 01/12/2007 02/23/2007 | 2006009-06 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate an Operability Evaluation for Water Hammer Concerns. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, Procedures, for the failure to follow Callaway Plant procedure requirements associated with operability determinations. Specifically, engineers had identified that a wate
Region: IV | Callaway | 12517 | 12/31/2006 02/06/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Degraded Fire Barrier |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71111.05Q | On November 21, 2006, the inspectors identified a noncited violation of Technical Specification 5.4.1.d, "Fire Protection Program," after AmerenUE failed to identify and correct a degraded auxiliary building fire door. The inspectors identified that the l
Region: IV | Callaway | 12518 | 12/31/2006 02/06/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Categorize a Maintenance Preventable Functional Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2) after AmerenUE failed to categorize the failure of motor-operated valve auxiliary contacts as a maintenance preventable functional failure and to monitor the component as required by 10
Region: IV | Callaway | 12525 | 12/31/2006 02/06/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage Increased Risk During a Maintenance Activity |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000483 Callaway |  | 71111.13 | On September 26, 2006, the inspectors identified a noncited violation of 10 CFR 50.65(a)(4) after AmerenUE failed to adequately manage the risk associated with maintenance on the turbine-driven auxiliary feedwater pump. AmerenUE removed the turbine-driven
Region: IV | Callaway | 12535 | 12/31/2006 02/06/2007 | 2006005-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of an Operator Workaround Resulted in an Inoperable Safety Injection Accumulator |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," after the licensee failed to adequately evaluate and promptly correct an operator workaround that resulted in the loss of nitrogen pressure o
Region: IV | Callaway | 12504 | 11/30/2006 12/26/2006 | 2006012-01 | NRC | NCV | Mitigating Systems | Green | Failure to initiate Callaway Action Request |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to initiate Callaway Action Requests for conditions adverse to quality that affected the reliability of mitigating systems. Specifically, on August 17, 2005
Region: IV | Callaway | 12507 | 11/30/2006 12/26/2006 | 2006012-02 | NRC | NCV | Mitigating Systems | Green | Failure to identify conditions adverse to quality |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, and the corrective action program because licensee personnel failed to recognize and to identify two separate examples as conditions adverse to quality. Specifically, on
Region: IV | Callaway | 12508 | 11/30/2006 12/26/2006 | 2006012-03 | NRC | NCV | Barrier Integrity | Green | Inadequate operability determination of a degraded main steam isolation valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152B | The team identified a noncited violation of Technical Specification 3.7.2, after operations personnel failed to enter and implement required Technical Specification 3.7.2 actions. Specifically, the licensee had performed an inadequate operability determin
Region: IV | Callaway | 12509 | 11/30/2006 12/26/2006 | 2006012-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to effectively implement actions to prevent recurrence |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71152B | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, resulted from the failure to correct, and preclude repetition of (evaluate extent of condition), a significant condition adverse to quality related to identification of high
Region: IV | Callaway | 12516 | 11/30/2006 12/26/2006 | 2006012-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to promptly correct a condition adverse to quality. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71152B | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI resulted after operations personnel failed to implement corrective actions. Specifically, the licensee failed to modify Procedure OSP-AL-V0003, "Auxiliary Feedwater Pump Disc
Region: IV | Callaway | 12495 | 09/23/2006 10/31/2006 | 2006004-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Equipment Control Procedur Resulted in Loss of Volume Control Tank Inventory |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified following two unplanned 50 gallon per minute volume control tank loss of inventory events. Both events occurred due to an inadequate equipment control pro
Region: IV | Callaway | 12501 | 09/23/2006 10/31/2006 | 2006004-03 | NRC | NCV | Emergency Preparedness | Green | Program Failure to Ensure Emergency Action Level Entered when Meeting the Defined Limit for Hazardous Atmosphere |  | H.1(c) Communication of Decisions | TE?: N | 05000483 Callaway |  | 71153 | The inspectors identified a Green noncited violation of 10 CFR 50.54(q) for a failure to adequately implement the emergency plan. The licensee failed to declare an ALERT when conditions existed that met Emergency Action Level 3J, "Hazards Affecting Plant
Region: IV | Callaway | 12502 | 09/23/2006 10/31/2006 | 2006004-04 | Self - Revealed | NCV | Initiating Events | Green | Review Adequacy of Procedure and Operator Response to a Turbine Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | NONE | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified after an inadequate turbine trip procedure resulted in an unplanned manual reactor trip. On May 12, 2006, the inadequate procedure lead to a steam generat
Region: IV | Callaway | 12503 | 09/23/2006 10/31/2006 | 2006004-05 | NRC | FIN | Initiating Events | Green | Review of Less Than Adequate Post Reactor Trip Evaluation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | NONE | An NRC identified finding was identified after AmerenUE restarted the reactor on May 12, 2006, without completing an adequate reactor posttrip evaluation. The licensee did not adequately address discrepancies between expected and actual plant response dur
Region: IV | Callaway | 12479 | 06/23/2006 08/07/2006 | 2006003-01 | NRC | NCV | Barrier Integrity | Green | Less Than Adequate Evaluation of Containment Heat Exchanger Postmodification Tests Results and self Assessment Recommendations |  |  | TE?: N | 05000483 Callaway |  | 71111.07A | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," after containment heat exchanger postmodification tests, conducted in Refuel Outages 11 (May 2001) and 12 (November 2002), failed to demonstrate that th
Region: IV | Callaway | 12480 | 06/23/2006 08/07/2006 | 2006003-02 | NRC | NCV | Barrier Integrity | Green | Less Than Adequate Evaluation of Containment Heat Exchanger Performance Monitoring Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.07A | The inspectors identified a noncited violation of Technical Specification 3.6.6, "Containment Spray and Cooling Systems," after AmerenUE failed to perform Surveillance Requirement 3.6.6.7 to verify minimum cooling water was provided to each containment co
Region: IV | Callaway | 12481 | 06/23/2006 08/07/2006 | 2006003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedures Resulted in a Main Steam Line Water Hammer |  | H.4(b) Procedural Compliance | TE?: N | 05000483 Callaway |  | 7111114 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified after a water hammer transient occurred because plant operators failed to follow a procedure. On May 31, 2006, a main steam line water hammer occurred aft
Region: IV | Callaway | 12491 | 06/23/2006 08/07/2006 | 2006003-05 | Self - Revealed | FIN | Mitigating Systems | Green | An Inadequate Switchyard Restoration Procedure Resulted in a Partial Loss of Off-Site Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000483 Callaway |  | 7111114 | A self-revealing finding was identified after an inadequate switchyard maintenance procedure resulted in the loss of power to a safety-related bus. On June 6, 2006, off-site power was lost to a plant safety-related bus when electricians restored the "brea
Region: IV | Callaway | 12492 | 06/23/2006 08/07/2006 | 2006003-06 | NRC | NCV | Barrier Integrity | Green | Less than adequate Operability Determination of a Degraded Containment Heat Exchanger |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," after AmerenUE failed to properly evaluate a degraded containment cooling train. The inspectors identified that between August 16 and Septemb
Region: IV | Callaway | 12475 | 04/14/2006 07/14/2006 | 2006011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize and Correct Inadequate Emergency Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to take adequate corrective action to prevent recurrence of a significant condition adverse to quality. Specifically, AmerenUE failed to correct t
Region: IV | Callaway | 12476 | 04/14/2006 07/14/2006 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Result in Possible CCW Runout Conditions |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000483 Callaway |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for AmerenUE's failure to implement appropriate corrective actions for maintaining component cooling water flow consistent with design basis requirements. On Apri
Region: IV | Callaway | 12474 | 03/24/2006 05/05/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Degraded Plant Equipment |  |  | TE?: N | 05000483 Callaway |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," after the licensee failed to promptly identify, evaluate, and correct a degraded control building air conditioning unit compressor. The compr
Region: IV | Callaway | 124721 | 05/10/2019 |  |  | LIV |  | Green | This violation of very low safety significance was identified by the licensee and has been entered into the licensee's corrective action program and is being treated as a non-cited violation, consistent with Section 2.3.2 of the Enforcement Policy. |  |  | TE?: N | 05000483 Callaway |  | 71111.12
Region: IV | Callaway | 124781 | 05/10/2019 |  |  | LIV |  | Green | This violation of very low safety significance was identified by the licensee and has been entered into the licensee's corrective action program and is being treated as a non cited violation, consistent with Section 2.3.2 of the Enforcement Policy. |  |  | TE?: N | 05000483 Callaway |  | 71111.04Q
Region: IV | Callaway | 126499 | 01/30/2020 |  | Licensee - Identified | LIV |  | Green | Technical Specification Surveillance Intervals Exceeded |  |  | TE?: N | 05000483 Callaway |  | 71111.12
Region: IV | Columbia Generating Station | 126335 | 12/31/2019 01/22/2020 | 2019004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Loss of Diesel Starting Air Results in High Pressure Core Spray Inoperability |  | P.5 - Operating Experience | TE?: N | 05000397 Columbia Generating Station | Configuration Control | 71111.15 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to perform maintenance in accordance with written procedures appropriate to the circumstances. Specifically, Procedure SOP-D
Region: IV | Columbia Generating Station | 126217 | 12/31/2019 01/22/2020 | 2019004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Periodically Calibrate Radiation Monitors |  | H.3 - Change Management | TE?: N | 05000397 Columbia Generating Station | Facilities and Equipment | 71124.05 | The inspectors identified a Green non-cited violation (NCV) of 10 CFR 20.1501(c) for failure to periodically calibrate installed radiation monitoring equipment used to perform dose rate measurements. Specifically, beginning May 31, 2013, the licensee has
Region: IV | Columbia Generating Station | 126204 | 12/31/2019 01/22/2020 | 2019004-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Follow Radioactive Material Control Procedures |  | H.12 - Avoid Complacency | TE?: N | 05000397 Columbia Generating Station | Program & Process | 71124.08 | The inspectors documented a self-revealing Green non-cited violation (NCV) of Technical Specification 5.4.1.a. for the failure to follow radiologically controlled area material release procedure GEN-RPP-04, “Entry Into, Conduct In, and Exit from Radiologi
Region: IV | Columbia Generating Station | 126280 | 12/31/2019 01/22/2020 | 2019004-04 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure of 10 CFR 61.56(b)(3) to Ensure the Void Space Within a Waste Package was Reduced to the Extent Practicable |  | H.8 - Procedure Adherence | TE?: N | 05000397 Columbia Generating Station | Program & Process | 71124.08 | The inspectors documented a self-revealing Green non-cited violation (NCV) of 10 CFR 61.56(b)(3) for failure to ensure the void space within a waste package was reduced to the extent practicable. Specifically, on September 4, 2019, a shipment of resin sen
Region: IV | Columbia Generating Station | 125637 | 09/30/2019 10/30/2019 | 2019003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure Results in Open Current Transformer |  | NPP | TE?: N | 05000397 Columbia Generating Station | Configuration Control | 71111.18 | The inspectors reviewed a self-revealed, Green finding for the licensee's failure to follow plant procedure 10.25.19, "Termination and Splicing Instruction," that ensures wire and cable terminations, splices, and insulation are properly controlled. Speci
Region: IV | Columbia Generating Station | 125142 | 06/30/2019 08/01/2019 | 2019002-01 | Self - Revealed | FIN | Initiating Events | Green | Packing Failure Results in Unit Downpower |  | H.11 - Challenge the Unknown | TE?: N | 05000397 Columbia Generating Station | Equipment Performance | 71111.19 | The inspectors reviewed a self-revealed, Green finding for the licensee’s failure to follow station procedure, Plant Procedures Manual (PPM) 10.2.79, “Valve Packing and Live Loading,” Revision 17, Step 4.13, for maintaining proper clearances of Chesterton
Region: IV | Columbia Generating Station | 124635 | 03/31/2019 05/06/2019 | 2019001-01 | NRC | FIN | Initiating Events | Green | Failure to Enter the Operational Decision Making Process for a Condition Reducing Operating Margin in Accordance with Station Procedures |  | H.14 - Conservative Bias | TE?: N | 05000397 Columbia Generating Station | Equipment Performance | 71111.13 | The inspectors identified a Green finding for the licensee’s failure to adhere to station procedure, Plant Procedures Manual 1.3.67, “Operational Decision-Making Process,” Revision 17, Step 6.1, for a condition that creates an actual or potential reductio
Region: IV | Columbia Generating Station | 25957 | 12/31/2018 01/28/2019 | 2018004-01 | Self - Revealed | FIN | Mitigating Systems | Green | Licensed Operator Failure Rate |  | H.1 - Resources | TE?: N | 05000397 Columbia Generating Station | Human Performance | 71111.11B | The inspectors reviewed a self-revealed, Green finding associated with licensed operator performance on the biennial requalification exam. Specifically, 15 of 51 operators failed at least one portion of the biennial requalification examinations and 2 of 8
Region: IV | Columbia Generating Station | 8 | 12/31/2018 01/28/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Hourly Fire Tours as Required by the Fire Protection Program |  | H.4 - Teamwork | TE?: N | 05000397 Columbia Generating Station | Protection Against External Factors | 71152 | The inspectors identified a Green, non-cited violation of Columbia Generating Station Operating License Condition 2.C(14), “Fire Protection Program (Generic Letter 86-10),” because the licensee failed to perform hourly compensatory fire tours as required
Region: IV | Columbia Generating Station | 24661 | 09/30/2018 10/31/2018 | 2018003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiologically Controlled Area Procedures |  | H.12 - Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71124.01 | The inspectors reviewed a self-revealed Green, non-cited violation of Technical Specification 5.4.1(a) when the licensee failed to implement radiation control procedures. Performance Deficiency: Failure to follow station procedures for entry into a r
Region: IV | Columbia Generating Station | 24663 | 09/30/2018 10/31/2018 | 2018003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Workers in a High Radiation Area (>1.0 rem per hour) |  | H.4 - Teamwork | TE?: N | 05000397 Columbia Generating Station |  | 71124.01 | The inspectors reviewed a self-revealed Green, non-cited violation of Technical Specification 5.7.2 (b) and (e) when the licensee failed to control worker activities in a locked high radiation area in accordance with the requirements of the RWP and failed
Region: IV | Columbia Generating Station | 24409 | 09/30/2018 10/31/2018 | 2018003-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Adequately Control Work Hours for Covered Personnel |  | H.5 - Work Management | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR 26.205 associated with the licensee’s failure to adequately schedule and control work hours for personnel subject to work hour controls. Specifically, the licensee failed to appropriately sc
Region: IV | Columbia Generating Station | 24066 | 06/30/2018 07/24/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control in the Diesel Generator 2 Diesel Cooling Water System |  | H.12 - Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to perform maintenance in accordance with written procedures appropriate to the circumstances. Specifically, on April 9, 2018
Region: IV | Columbia Generating Station | 23507 | 03/31/2018 04/25/2018 | 2018001-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Leads to Loss of Secondary Containment |  | H.5 - Work Management | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1a for the licensee's failure to perform maintenance in accordance with documented instructions appropriate to the circumstances. Specifically, on September
Region: IV | Columbia Generating Station | 22378 | 12/31/2017 02/05/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Loss of Configuration Control Results in Emergency Diesel Generator Inoperability |  | NPP | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee’s failure to maintain the configuration of the division 2 emergency diesel generator test mode relays. Specifical
Region: IV | Columbia Generating Station | 22597 | 12/31/2017 02/05/2018 | 2017004-02 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Follow Procedure Results in Isolation of Reactor Feedwater Minimum Flow Lines |  | H.7 - Documentation | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors reviewed a self-revealed finding for the licensee’s failure to follow plant Procedure 1.3.64, "Plant Clearance Order," that ensures equipment status is properly controlled. Specifically, during Refueling Outage R23, the licensee removed the
Region: IV | Columbia Generating Station | 22598 | 12/31/2017 02/05/2018 | 2017004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instructions Result in Reactor Core Isolation Cooling System Inoperability |  | H.11 - Challenge the Unknown | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee’s failure to perform maintenance with documented instructions appropriate to the circumstances. Specifically, on June 10, 2017, the licensee
Region: IV | Columbia Generating Station | 22599 | 12/31/2017 02/05/2018 | 2017004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Leads to Loss of Secondary Containment |  | H.13 - Consistent Process | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee’s failure to follow procedure SYS-2-25, "Procedure PM Template Preparation and Review," Revision 2. Specifically, the licensee
Region: IV | Columbia Generating Station | 22600 | 12/31/2017 02/05/2018 | 2017004-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Single Point Vulnerability Review Process for Components Results in Reactor Scram |  | NPP | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealed finding for the licensee’s failure to follow plant Procedure EGM-1-9, "Single Point Vulnerability Review Process," that establishes the licensee’s requirements for performing single point vulnerability reviews by id
Region: IV | Columbia Generating Station | 21630 | 09/30/2017 10/26/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate High Pressure Core Spray Fill and Vent Procedure |  | H.12 - Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee’s failure to have a high pressure core spray system fill and vent procedure appropriate to the circumstances. The licensee entered this issue
Region: IV | Columbia Generating Station | 21684 | 09/15/2017 10/25/2017 | 2017010-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Transfer Byproduct Material to a Disposal Facility in Accordance with the Terms of the Facility’s License |  | H.1 - Resources | TE?: N | 05000397 Columbia Generating Station |  | 71124.08 | The inspectors reviewed a self-revealed non-cited violation of 10 CFR 30.41(b)(5) for the failure to transfer byproduct material to an authorized waste disposal facility in accordance with the terms of the facility’s license. Specifically, License Conditi
Region: IV | Columbia Generating Station | 21685 | 09/15/2017 10/25/2017 | 2017010-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Control a High Radiation Area with Dose Rates Greater Than 1000 Millirem Per Hour at 30 Centimeters |  | H.2 - Field Presence | TE?: N | 05000397 Columbia Generating Station |  | 71124.01 | The inspectors identified a non-cited violation of Technical Specification 5.7.2 for the failure to control a high radiation area with dose rates greater than 1000 millirem per hour at 30 centimeters. Specifically, equipment boxes placed adjacent to high
Region: IV | Columbia Generating Station | 21613 | 06/30/2017 08/10/2017 | 2017002-01 | Self - Revealed | FIN | Initiating Events | Green | Mechanism Operated Cell Switch Failure |  | H.13 Consistent Process | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | The inspectors reviewed a self-revealed finding for the licensee's failure to follow plant Procedure SWP-CAP-01, "Corrective Action Program," that ensures corrective actions are timely. As a corrective action for failures associated with mechanism operate
Region: IV | Columbia Generating Station | 21614 | 06/30/2017 08/10/2017 | 2017002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Conduct Adequate Surveys of Spent Filters Moved from the Spent Fuel Pool |  | H.5 Work Management | TE?: N | 05000397 Columbia Generating Station |  | 71124.01 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR 20.1501 resulting from the licensee's failure to conduct radiation surveys necessary to establish appropriate controls to support movement of spent filters from the spent fuel pool to
Region: IV | Columbia Generating Station | 21615 | 06/30/2017 08/10/2017 | 2017002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Causes Failure of HPCS Room Normal Supply Fan |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct a condition adverse to quality. Specifically, since 2012, the licensee failed to i
Region: IV | Columbia Generating Station | 19434 | 04/06/2017 04/06/2017 | 2017008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Operators Fail to Follow Reactor Scram Procedure |  | H.9 Training | TE?: N | 05000397 Columbia Generating Station |  | NONE | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow Procedure 3.3.1, "Reactor Scram," Revision 62. Specifically, the licensee failed to trip the main generator
Region: IV | Columbia Generating Station | 19435 | 04/06/2017 04/06/2017 | 2017008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Operators Fail to Follow Procedure Causes RCIC Overspeed Trip |  | H.9 Training | TE?: N | 05000397 Columbia Generating Station |  | NONE | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow Procedure SOP-RCIC-INJECTION-QC, "RCIC RPV Injection - Quick Card," Revision 5. During a complicated reacto
Region: IV | Columbia Generating Station | 19436 | 04/06/2017 04/06/2017 | 2017008-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Causes Failure of HPCS Restricting Orifice Gasket |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct a condition adverse to quality. Specifically, since 2009, the licensee failed to i
Region: IV | Columbia Generating Station | 19441 | 03/17/2017 04/10/2017 | 2016009-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Conduct Adequate Surveys of a Solid Radwaste Shipment |  | H.7 Documentation | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team reviewed three examples of a self-revealed, non-cited violation of 10 CFR 20.1501 associated with the failure to conduct adequate surveys of the solid radwaste contents of a shipment that was packaged and transported for ultimate disposal. As a r
Region: IV | Columbia Generating Station | 19442 | 03/17/2017 04/10/2017 | 2016009-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Label or Provide Written Information for Items Stored in the Spent Fuel Pool |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team identified a non-cited violation of 10 CFR 20.1904 associated with the licensee's failure to ensure that each container of licensed material in the spent fuel was conspicuously marked commensurate with the radiological hazard or that the conten
Region: IV | Columbia Generating Station | 19443 | 03/17/2017 04/10/2017 | 2016009-04 | NRC | NCV | Public Radiation Safety | Green | Failure to Provide an Accurate Shipping Manifest |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team identified a non-cited violation of 10 CFR 20.2006(b) for the licensee's failure to ship radwaste with an accurate shipping manifest. Specifically, the licensee failed to provide the correct identification number and proper shipping name, radionu
Region: IV | Columbia Generating Station | 19446 | 03/17/2017 04/10/2017 | 2016009-05 | NRC | NCV | Public Radiation Safety | Green | Failure of the QA Program to Assure Compliance with 10 CFR 61.55 and 10 CFR 61.56 |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team identified a non-cited violation of 10 CFR Part 20, Appendix G, for the failure to manage a quality assurance program to ensure compliance with 10 CFR 61.55 and 10 CFR 61.56. Additionally, licensee management failed to effectively evaluate the si
Region: IV | Columbia Generating Station | 19448 | 03/17/2017 04/10/2017 | 2016009-07 | NRC | FIN | Public Radiation Safety | Green | Failure to Follow Procedure and Perform a Root Cause Evaluation to Assess the Causes of a Radwaste Shipping Event |  | P.2 Evaluation | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team identified a finding for the failure to follow the requirements of Procedure SWP-CAP-06, "Condition Report Review," when determining the type of cause evaluation required to assess the causes of the higher than expected dose rates on a radwaste
Region: IV | Columbia Generating Station | 19455 | 03/17/2017 04/10/2017 | 2016009-08 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Transfer Byproduct Material to a Disposal Facility in Accordance with the Terms of the Facility's License |  | H.14 Conservative Bias | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team reviewed a self-revealed non-cited violation of 10 CFR 30.41(b)(5) for the failure to transfer byproduct material to an authorized waste disposal facility in accordance with the terms of the facility's license. Specifically, License Condition No.
Region: IV | Columbia Generating Station | 21612 | 03/17/2017 04/10/2017 | 2016009-09 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Minimize Void Spaces in a Radioactive Waste Package |  | H.4 Teamwork | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The team reviewed a self-revealed non-cited violation of 10 CFR 61.56(a)(3) for the licensee's failure to assure that void spaces within the waste packages were reduced to the extent practicable. Specifically, a shipment of dry active waste sent to US Eco
Region: IV | Columbia Generating Station | 19437 | 03/01/2017 04/06/2017 | 2017007-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate and Control Nonconforming SSCs |  | H.14 Conservative Bias | TE?: Y SL-IV-NCVIV | 05000397 Columbia Generating Station |  | NONE | The team identified a Green, Severity Level IV non-cited violation of 10 CFR Part 50 Appendix B Criteria VII and XV, for the licensee's failure to ensure materials intended for installation in safety-related applications conformed to procurement requireme
Region: IV | Columbia Generating Station | 19422 | 12/31/2016 02/03/2017 | 2016004-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.1 Resources | TE?: Y SL-IV-NCVIV | 05000397 Columbia Generating Station |  | 71111.11B | The inspectors identified a Severity Level IV, non-cited violation of 10 CFR 55.49, "Integrity of Examinations and Tests," associated with a Green finding, for the failure to ensure the integrity of simulator scenario tests, given as part of the 2015 lice
Region: IV | Columbia Generating Station | 19423 | 12/31/2016 02/03/2017 | 2016004-02 | Self - Revealed | NCV | Mitigating Systems | Green | RCIC Trips After Surveillances |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of design of the reactor core isolation cooling (RCIC) system. Specifically, in
Region: IV | Columbia Generating Station | 19429 | 12/31/2016 02/03/2017 | 2016004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Flow Indicating Switch Adjustment |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement adequate work instructions for performing maintenance on residual heat removal flow indicating switch RH
Region: IV | Columbia Generating Station | 19418 | 09/30/2016 10/28/2016 | 2016003-01 | Self - Revealed | FIN | Initiating Events | Green | Ineffective System Performance Monitoring Program For Plant Service Water Piping Fouling |  | H.11 Challenge the Unknown | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow plant procedure SYS-4-31, "System and Equipment Performance Monitoring and Trending Program," revision 11, that ensures system and component performance to permit early
Region: IV | Columbia Generating Station | 19415 | 06/30/2016 07/20/2016 | 2016002-01 | Self - Revealed | NCV | Initiating Events | Green | Loss of RCC Cooling Requiring a Reactor Scram |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow procedure OI-41, "Operations Work Control Expectations," Revision 59. Specifically, the licensee incorrectl
Region: IV | Columbia Generating Station | 19419 | 06/24/2016 08/05/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Programmatic Concern Pertaining to Columbia Generating Stations Procedures |  | H.1 Resources | TE?: N | 05000397 Columbia Generating Station |  | 71111.21M | The team identified a Green, non-cited violation of Technical Specification 5.4, Procedures, Section 5.4.1, which states, in part, "Written procedures shall be established, implemented, and maintained covering the following activities: a. The applicable p
Region: IV | Columbia Generating Station | 19411 | 12/31/2015 01/29/2016 | 2015004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Incorrect Electrical Component Operated During Maintenance |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.04S | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement Work Order 02048855 during maintenance on a safety-related power panel. Specifically, the licensee opera
Region: IV | Columbia Generating Station | 19416 | 10/01/2015 11/03/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Acceptance Criteria in Fire Main Surveillance Testing |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.14, "Fire Protection Program (Generic Letter 86-10)," for the failure to establish procedural guidance for validating the underground fire main condition to ensure the required fire suppre
Region: IV | Columbia Generating Station | 19417 | 10/01/2015 11/03/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.4, "Procedures," for the failure to provide adequate procedures to implement the fire protection program. Specifically, the alternative shutdown procedure failed to assure operator act
Region: IV | Columbia Generating Station | 19398 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Maintain Seismic Instrumentation Functional to Alert Plant Operators of Ground Motions Exceeding the Operating Basis Earthquake |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | The inspectors identified a finding associated with the licensee's failure to maintain seismic instrumentation functional as required by Licensee Controlled Specification 1.3.7.2, "Seismic Monitoring Instrumentation." Specifically, because of inadequate c
Region: IV | Columbia Generating Station | 19399 | 09/30/2015 11/12/2015 | 2015003-02 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Shutdown Criteria in Earthquake Abnormal Procedure |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the failure to maintain an adequate abnormal procedure for earthquakes. Specifically, the licensee failed to establish appropriate shutdown criteria for
Region: IV | Columbia Generating Station | 19408 | 09/30/2015 11/12/2015 | 2015003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Design Control Measures for Control Room Emergency Chillers |  | P.2 Evaluation | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of the design of the control room HVAC system. Specifically, the licensee failed to demonstrate th
Region: IV | Columbia Generating Station | 19409 | 09/30/2015 11/12/2015 | 2015003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedures to Ensure Availability of Safe Shutdown Personnel |  | H.4 Teamwork | TE?: N | 05000397 Columbia Generating Station |  | 71111.11Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to ensure operators could perform time-critical steps for fire events. Specifically, on July 4, 2015, the licensee failed to imple
Region: IV | Columbia Generating Station | 19370 | 06/30/2015 08/07/2015 | 2015002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures Associated with Operation of the Fuel Pool Cooling System |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71111.2 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow procedures associated with operation of the fuel pool cooling system. Specifically, on May 12, 2015, the li
Region: IV | Columbia Generating Station | 19371 | 06/30/2015 08/07/2015 | 2015002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Barricade a High Radiation Area |  | H.12 Avoid Complacency | TE?: N | 05000397 Columbia Generating Station |  | 71124.01 | The inspectors identified a non-cited violation of Technical Specification 5.7.1.a for the failure to barricade a high radiation area. Specifically, the high radiation area entry gate in the 572-foot "A" RHR Heat Exchanger Room was found in the open posit
Region: IV | Columbia Generating Station | 19372 | 06/30/2015 08/07/2015 | 2015002-03 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Maintain Doses ALARA for the Alternate Fuel Pool Cooling Modification Job |  | H.2 Field Presence | TE?: N | 05000397 Columbia Generating Station |  | 71124.02 | The inspectors identified a finding associated with the licensee's failure to maintain doses as low as reasonably achievable (ALARA) while performing the Alternate Fuel Pool Cooling Modification job. Specifically, the licensee failed to effectively apply
Region: IV | Columbia Generating Station | 19394 | 06/30/2015 06/30/2015 | 2015301-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Simulator Fidelity with Two Examples |  | H.9 Training | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. Title 10 CFR Part 55.46(c), "Plant-referenced Simulators," states, in part, that a "plant-referenced simulator used for the administration of the operating test or to meet experience requirements in º 55.31(a)(5) must demonstrate expected plant res
Region: IV | Columbia Generating Station | 19379 | 04/03/2015 05/13/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Report for a Degraded Condition Outside the Scope of Maintenance Work Order |  | H.13 Consistent Process | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to initiate a condition report in accordance with SWP-CAP-01, "Corrective Action Program," Rev
Region: IV | Columbia Generating Station | 19380 | 04/03/2015 05/13/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control of Ventilation Systems Needed for Station Blackout |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green, non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current Power," for the licensee's failure to maintain appropriate quality assurance requirements for components needed to cope with a station blackout event. Speci
Region: IV | Columbia Generating Station | 19388 | 04/03/2015 05/13/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate the Operability of a Nonconforming Condition Involving Molded Case Circuit Breakers |  | H.6 Design Margins | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to identify a nonconforming condition involving molded case circuit breakers. Consequently, op
Region: IV | Columbia Generating Station | 19389 | 04/03/2015 05/13/2015 | 2015007-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Maintenance Procedures for Temperature Control Valve Electro-Hydraulic Operators |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team reviewed a self-revealing Green, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to provide adequate work instructions for performing maintenance on service water temperature control valve electro-
Region: IV | Columbia Generating Station | 19390 | 04/03/2015 05/13/2015 | 2015007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis into Component Classification Evaluation Records |  | P.3 Resolution | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the design basis into specifications. Specifically, the team identified five instances where the licen
Region: IV | Columbia Generating Station | 19393 | 04/03/2015 05/13/2015 | 2015007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Report for Operating Experience that Impacts Molded Case Circuit Breakers |  | P.2 Evaluation | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to initiate a condition report as required by the operating experience program. Specifically, t
Region: IV | Columbia Generating Station | 19364 | 03/31/2015 04/29/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with ECCS Technical Specifications |  | H.8 Procedure Adherence | TE?: N | 05000397 Columbia Generating Station |  | 71111.06 | The inspectors identified a non-cited violation of Technical Specification 3.5.1, "ECCS - Operating," for the licensee's failure to maintain the low-pressure coolant injection system operable. Specifically, the licensee failed to implement adequate compen
Region: IV | Columbia Generating Station | 19365 | 03/31/2015 04/29/2015 | 2015001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Work Instructions for 480-Volt Motor Control Center Starters |  | H.1 Resources | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to provide adequate work instructions for performing maintenance on 480-volt motor control center starter PRA-42-8AA4
Region: IV | Columbia Generating Station | 19366 | 03/31/2015 04/29/2015 | 2015001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Program Procedures |  | H.2 Field Presence | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures and Drawings," associated with the licensee's failure to initiate condition reports for conditions adverse to quality as required by stati
Region: IV | Columbia Generating Station | 19410 | 10/27/2014 11/12/2015 | 2015003-05 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Reduce the Free Water in a Class A Unstable Resin Disposal Package to Less than 0.5 Percent of Water Volume |  | H.6 Design Margins | TE?: N | 05000397 Columbia Generating Station |  | 71124.08 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to follow their Process Control Program as implemented by their solid radioactive waste system procedures. Specifica
Region: IV | Columbia Generating Station | 16939 | 09/21/2014 10/30/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Ultimate Heat Sink Technical Specification Level Requirements |  | P.6 Self Assessment | TE?: N | 05000397 Columbia Generating Station |  | 71111.01 | The inspectors identified a non-cited violation of Technical Specification 3.7.1, "Standby Service Water (SW) System and Ultimate Heat Sink (UHS)," for the licensee's failure to take the required actions for an inoperable ultimate heat sink. Specifically,
Region: IV | Columbia Generating Station | 16965 | 09/21/2014 10/30/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance Schedules for Fuel Oil Tank Vents |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to establish preventative maintenance schedules for the emergency diesel generator fuel oil storage and day tank flame arrestor ve
Region: IV | Columbia Generating Station | 19396 | 06/26/2014 05/07/2015 | 2015502-01 | NRC | FIN | Emergency Preparedness | Green | Failure to follow an emergency plan requirement to not delegate responsibility for protective action recommendations |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | The NRC identified three examples in which Columbia Generating Station failed to follow an emergency plan meeting the requirements of 10 CFR 50.47(b) as required by 10 CFR 50.54(q)(2). Specifically, the licensee failed to follow Sections 2.1 and 5.5 of Em
Region: IV | Columbia Generating Station | 19356 | 06/22/2014 08/06/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Corrective Actions to Address Extent of Cause for Service Water Pump Coupling Failures |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions" for the licensee's failure to implement corrective actions to address identified weaknesses in the preventative maintenance program. Specifi
Region: IV | Columbia Generating Station | 19357 | 06/22/2014 08/06/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedures That Ensure Operators Could Perform Time Critical Steps For Fire Events |  | H.3 Change Management | TE?: N | 05000397 Columbia Generating Station |  | 71111.11Q | The inspectors identified a green non-cited violation of Columbia Generating Station Technical Specification 5.4.1.a for the failure of the licensee to implement procedures that ensure operators could perform time critical steps for fire events. The licen
Region: IV | Columbia Generating Station | 19359 | 06/22/2014 08/06/2014 | 2014003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to implement high radiation area controls in an area with a dose rate greater than 1 rem/hour. |  | H.5 Work Management | TE?: N | 05000397 Columbia Generating Station |  | 71124.02 | The inspectors reviewed a Green, self-revealing, non-cited violation of Technical Specification 5.7.2, which was caused by licensee personnel's failure to control a high radiation area with radiation levels greater than 1 rem/hour when lifting the moistur
Region: IV | Columbia Generating Station | 19360 | 06/22/2014 08/06/2014 | 2014003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Procedures For a Design Basis Ashfall Event |  | P.1 Identification | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors identified a green non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to maintain procedures for mitigating a design-basis volcanic ashfall event. The licensee restored compliance by initiating AR 304380 and m
Region: IV | Columbia Generating Station | 19361 | 06/22/2014 08/06/2014 | 2014003-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform Adequate Verification of Breaker Cubicle Fit Results in Loss of Reactor Recirculation Pump |  | H.1 Resources | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors reviewed a self-revealing Green finding for the licensee's failure to verify that circuit breaker E-CB-S5 was properly installed in accordance with procedure SOP-ELEC-BKR-OPS, "AC Electrical Breaker Racking," Revision 10. The improper insta
Region: IV | Columbia Generating Station | 19362 | 06/22/2014 08/06/2014 | 2014003-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Configuration Control of Reactor Building Ventilation Differential Pressure Controllers |  | P.2 Evaluation | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealing Green non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to properly pre-plan calibrations of differential pressure controllers used to maintain secondary containment p
Region: IV | Columbia Generating Station | 19353 | 03/23/2014 05/07/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Subject Diesel Generator Intake Air Pre-Filters to the Controls of the Quality Assurance Program |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.01 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the licensee's failure to apply the applicable quality assurance requirements of 10 CFR 50, Appendix B, "Quality Assurance Crite
Region: IV | Columbia Generating Station | 19355 | 03/23/2014 05/07/2014 | 2014002-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Operability Evaluation of Degraded Reactor Core Isolation Cooling Valve |  | H.11 Challenge the Unknown | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of the licensee to perform a detailed examination of a degraded condition associated with the reactor core
Region: IV | Columbia Generating Station | 19350 | 12/31/2013 01/30/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Internal Flooding Design into Station Procedures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.06 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the design of water resistant doors used to protect emergency core cooling rooms from internal f
Region: IV | Columbia Generating Station | 19351 | 12/31/2013 01/30/2014 | 2013005-02 | NRC | NCV | Barrier Integrity | Green | Non-Conservative Error in Control Room Boundary Breach Specification. |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," for the licensee's failure to translate the results of calculation NE-02-02-01, "Control Room Boundary Leakage Limitation" into allowed breach
Region: IV | Columbia Generating Station | 19337 | 11/21/2013 12/24/2013 | 2013010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Determine Cause for a Significant Condition Adverse to Quality |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to perform a cause evaluation for a significant condition adverse to quality. Specifically, the licensee failed t
Region: IV | Columbia Generating Station | 19338 | 11/21/2013 12/24/2013 | 2013010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability of System Wide Anode Degradation in the Service Water System |  | P.1(b) Trend Performance CAP | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow Procedure PPM 1.3.66, "Operability and Functionality Evaluation," Revision 25-27. Sp
Region: IV | Columbia Generating Station | 19343 | 11/21/2013 12/24/2013 | 2013010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Testing of the Service Water Supplied Room Coolers |  | P.2(b) Implementing Operating Experience | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to maintain an adequate test program that demonstrates safety-related room coolers will perform satisfactorily in servi
Region: IV | Columbia Generating Station | 19344 | 11/21/2013 12/24/2013 | 2013010-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures when Installing Roll-filters in Safety-related Air Handling Units |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," associated with the failure of the licensee to install roll-filters in safety-related room coolers in accordance with station procedures. Consequently, the r
Region: IV | Columbia Generating Station | 19345 | 11/21/2013 12/24/2013 | 2013010-05 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Plant Technical Specifications for Control Room Air Conditioning System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 93812 | The inspectors identified a non-cited violation of Technical Specification 3.7.4, "Control Room Air Conditioning (AC) System," involving the licensee's failure to adequately test and maintain the control room heating, ventilation, and air conditioning (HV
Region: IV | Columbia Generating Station | 19336 | 09/21/2013 10/31/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Improperly Installed Jumper Results in Inoperable Remote Transfer Switch |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 3.3.3.2, "Remote Transfer System," involving the licensee's failure to remove a jumper in the 480 volt motor control center starter for residual heat removal suppression pool spray
Region: IV | Columbia Generating Station | 19326 | 08/22/2013 10/02/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Independence Requirements of IEEE 308-1974 for Divisions 1 and 2 Vital Instrumentation and Control Power Systems |  |  | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as by the performanc
Region: IV | Columbia Generating Station | 19333 | 08/22/2013 10/02/2013 | 2013007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze the Effect of System, Test Source, and Transient Harmonics on Proper Operation of Undervoltage Relays |  |  | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as by the performanc
Region: IV | Columbia Generating Station | 19334 | 08/21/2013 10/02/2013 | 2013007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Include ECCS Pumps' NPSH Limits in the Emergency Operating Procedures |  |  | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of Technical Specification 5.4.1(b) which states, in part, "Written procedures shall be established, implemented, and maintained covering the following activities: The emergency operating procedures r
Region: IV | Columbia Generating Station | 19335 | 08/21/2013 10/02/2013 | 2013007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality with Emergency Operating Procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, defici
Region: IV | Columbia Generating Station | 19329 | 08/20/2013 10/02/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Technical Basis for Assuming Turbulent Mixing of Diesel Combustion Air |  |  | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as by the
Region: IV | Columbia Generating Station | 19327 | 08/07/2013 10/02/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Emergency Procedures for Filling and Venting Diesel Fuel Oil Tanks after Tornado Damage |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of Technical Specification 5.4.1(a), "Procedures" which requires, "Written procedures shall be established, implemented, and maintained covering the following activities: (a) The applicable procedures
Region: IV | Columbia Generating Station | 19325 | 08/06/2013 10/02/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Support the Ability to Restore Class 1E Diesel Generator Standby Power and Recover from Station Blackout (SBO) Conditions |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000397 Columbia Generating Station |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current Power," which states, in part, that each light-water-cooled nuclear power plant licensed to operate under this part must be able to withstand for a sp
Region: IV | Columbia Generating Station | 19308 | 07/12/2013 08/22/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Programmatic Failure to Promptly Evaluate Safety Impact of Degraded Conditions |  | H.4(b) Procedural Compliance | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures and Drawings." This violation involved multiple examples of the licensee's failure to follow station operability and functionality evaluat
Region: IV | Columbia Generating Station | 19309 | 07/12/2013 08/22/2013 | 2013008-02 | NRC | FIN | Mitigating Systems | Green | Failure to Classify Condition Reports in Accordance with Procedures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green finding involving six examples of the licensee's failure to follow its corrective action program procedures. This resulted in condition reports not being appropriately prioritized in accordance with procedure SWP-CAP-06, "Condi
Region: IV | Columbia Generating Station | 19318 | 07/12/2013 08/22/2013 | 2013008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Environmental Qualification Deficiency |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Following discovery of non-environmentally quali
Region: IV | Columbia Generating Station | 19319 | 07/12/2013 08/22/2013 | 2013008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Control Inadequate Surveillance Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a Green non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to follow its procedure-control procedure. Following discovery of an inadequate surveillance procedure for a high-pressure core spray instrument,
Region: IV | Columbia Generating Station | 19320 | 07/12/2013 08/22/2013 | 2013008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedure for Age Management of Electrolytic Capacitors |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 71152B | The team identified a green non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement its procedure for age management of electrolytic capacitors. The licensee had established the procedure in December 2
Region: IV | Columbia Generating Station | 17053 | 06/22/2013 07/25/2013 | 2013003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Corrective Action Program Procedures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the corrective action program procedure by prompt
Region: IV | Columbia Generating Station | 17056 | 06/22/2013 07/25/2013 | 2013003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedures for Inoperable Control Room Ventilation Boundary Damper |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," associated with the licensee's failure to follow station procedure PPM 1.3.57, "Barrier Impairments", Revision 29.
Region: IV | Columbia Generating Station | 17043 | 03/23/2013 04/23/2013 | 2013002-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: Y SL-IV-NCVIV | 05000397 Columbia Generating Station |  | 71111.11B | -Severity Level IV. The inspectors identified a non-cited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," and an associated Green finding, for the failure of the licensee to ensure the integrity of remedial tests given as part of th
Region: IV | Columbia Generating Station | 17044 | 03/23/2013 04/23/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that All License Conditions are Met for Licensed Operators |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.11B | Green. The inspectors identified a non-cited violation of 10 CFR 55.53, "Conditions of License," for the failure of the licensee to ensure that licensed operators met all the conditions of their licenses in order to be considered an active watch stander.
Region: IV | Columbia Generating Station | 17051 | 03/23/2013 04/23/2013 | 2013002-03 | NRC | FIN | Mitigating Systems | Green | Failure to Address Noticeable Differences in the Simulator in Accordance with ANSI/ANS 3.5-1998 and -2009 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.11B | Green. The inspectors identified a finding associated with addressing noticeable differences between the simulator and the plant in accordance with the standards of ANSI/ANS 3.5-1998 and -2009. Specifically, there was a failure to correct a difference in
Region: IV | Columbia Generating Station | 17035 | 12/31/2012 02/08/2013 | 2012005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Maintenance Procedures for Control Room Emergency Ventilation System Dampers |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for failure to provide suitable work instructions for maintenance on control room emergency ventilation system dampers. On November 11, 2
Region: IV | Columbia Generating Station | 17036 | 12/31/2012 02/08/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Correct Technical Specification Action Statements When Authorizing Work |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a non-cited violation of Technical Specification, 5.4.1.a, "Procedures," for the failure to follow Procedure OI-09, "Operations Standards and Expectations," Revision 56, when authorizing work on emergency core cooling syst
Region: IV | Columbia Generating Station | 17037 | 12/31/2012 02/08/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Condition Report upon Identification of Degraded Lubrication in Safety-Related Equipment |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow Procedure SWP-CAP-01, "Corrective Action Program," Revision 24. Specifically,
Region: IV | Columbia Generating Station | 17038 | 12/31/2012 02/08/2013 | 2012005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Adequate Surveillance Testing of the Control Room Air Conditioning System |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure of the licensee to perform required surveillance testing of the control room heating, ventilation and air conditioning (HVA
Region: IV | Columbia Generating Station | 17039 | 12/31/2012 02/08/2013 | 2012005-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Shutdown Cooling Isolation Logic Bypass Procedures Results in Loss of Safety Function |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's human performance associated with operation of the residual heat removal system shutdown cooling isolation logic. On October 1, 201
Region: IV | Columbia Generating Station | 17019 | 09/21/2012 10/29/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Applicable LCO for Offsite Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | Green. The inspectors identified a non-cited violation of Technical Specification 3.8.1, "AC Sources - Operating," for the licensee's failure to enter and take required actions contained in Technical Specification 3.8.1, Condition A, when removing startup
Region: IV | Columbia Generating Station | 17018 | 09/21/2012 10/29/2012 | 2012004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Develop Preventive Maintenance Schedule for Safety-Related 480V Starter Coils |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement preventive maintenance schedules for safety-related 480V starter coils. On June 16, 2012, fuel po
Region: IV | Columbia Generating Station | 17022 | 09/21/2012 10/29/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Procedural Guidance for critical Switchgear Ventilation Systems |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to maintain adequate procedures associated with critical switchgear ventilation systems. Specifically, licensee Procedure A
Region: IV | Columbia Generating Station | 17023 | 09/21/2012 10/29/2012 | 2012004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Adequate Work Instructions |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors reviewed a self-revealing Green non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide work instructions appropriate for performing maintenance o
Region: IV | Columbia Generating Station | 17024 | 09/21/2012 10/29/2012 | 2012004-05 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Dose ALARA due to Poor Job Execution |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000397 Columbia Generating Station |  | 71124.02 | Green. The inspector reviewed a self-revealing finding for failure to maintain doses as low as is reasonably achievable (ALARA) due to poor job execution. The licensee estimated that ALARA Task 11748210101 attached to Radiation Work Permit 30002666, "R20
Region: IV | Columbia Generating Station | 17025 | 09/21/2012 10/29/2012 | 2012004-06 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Maintain Dose ALARA due to Inadequate Job Planning |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71124.02 | Green. The inspector reviewed a self-revealing finding, with two examples, for failure to maintain doses as low as is reasonably achievable (ALARA) due to inadequate job planning. In the first example, the licensee estimated that Radiation Work Permit 300
Region: IV | Columbia Generating Station | 17026 | 09/21/2012 10/29/2012 | 2012004-07 | NRC | NCV | Emergency Preparedness | Green | Failure to Identify a Performance Weakness During a Drill |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000397 Columbia Generating Station |  | 71151 | Green. A non-cited violation of 10 CFR 50.47(b)(14) was identified for the licensee's failure to identify a deficiency occurring during a drill to ensure correction. Specifically, the licensee did not identify a failure to provide accurate information in
Region: IV | Columbia Generating Station | 17027 | 09/21/2012 10/29/2012 | 2012004-08 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Establish Conservative Electronic Dosimeter Alarm Set-points |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. A non-cited violation of Technical Specification 5.4.1a was identified for the failure to follow station procedures and establish conservative electronic dosimeter set-points prior to entering the radiologically controlled area during emergency pre
Region: IV | Columbia Generating Station | 17028 | 09/21/2012 10/29/2012 | 2012004-09 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements to Inform Workers about Radiological Conditions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. A non-cited violation of Technical Specification 5.4.1.a was identified for the failure to follow radiation work permit requirements to brief workers on the radiological conditions in the work area and to provide workers current radiological survey
Region: IV | Columbia Generating Station | 17017 | 06/29/2012 08/02/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Post Fire Safe Shutdown Circuitry for Isolation for a Control Room Fire |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71111.05T | Green. The inspectors identified a non-cited violation for the failure to ensure that material, parts, and equipment specified met or exceeded the design criteria as required by License Condition 2.C.14, "Fire protection Program (Generic Letter 86-10)." S
Region: IV | Columbia Generating Station | 17009 | 06/22/2012 07/24/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability Associated with Residual Heat Removal Pump B |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of the licensee to perform a required operability determination for a degraded condition associated
Region: IV | Columbia Generating Station | 17010 | 06/22/2012 07/24/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Postmaintenance Tests for Replacement of Division 3 Safety Related Batteries |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure of the licensee to perform a required postmaintenance test of the division 3 safety-related batteries prior to system resto
Region: IV | Columbia Generating Station | 17011 | 06/22/2012 07/24/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Control High Energy Line Break Barriers |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of the licensee to control impairment of high energy line break barriers in accordance with Procedu
Region: IV | Columbia Generating Station | 16994 | 03/23/2012 05/04/2012 | 2012002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Corrective Actions to Address Hardened Lubricant Safety-Related Disconnect Switches |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | Green. The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to take corrective actions to address hardened lubricant in safety-related 480V disconnect s
Region: IV | Columbia Generating Station | 16993 | 03/23/2012 05/04/2012 | 2012002-02 | NRC | NCV | Initiating Events | Green | Failure to Update Combustible Loading Calculation |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | 71111.05Q | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.d, "Procedures," for the licensee's failure to implement Procedure PPM 1.3.10C, "Control of Transient Combustibles," Revision 13, which required the reactor building c
Region: IV | Columbia Generating Station | 17003 | 03/23/2012 05/04/2012 | 2012002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Validate Compensatory Measures During Maintenance |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors identified a non-cited violation of Technical Specification 3.7.3, "Control Room Emergency Filtration (CREF) System," for the licensee's failure to provide adequate compensatory measures during maintenance on the control room emergen
Region: IV | Columbia Generating Station | 17004 | 03/23/2012 05/04/2012 | 2012002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Unauthorized Entry into a High Radiation Area |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.7, "High Radiation Area," when a mechanic entered into a high radiation area without authorization and using required controls on March 7, 2012. Specifically,
Region: IV | Columbia Generating Station | 17005 | 03/23/2012 05/04/2012 | 2012002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Reportability Associated with Division 3 Diesel Generator Inoperability |  | H.1(c) Communication of Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow procedure SWP-CAP-01, "Corrective Action Program," Revision 21, when evaluatin
Region: IV | Columbia Generating Station | 16988 | 12/31/2011 02/13/2012 | 2011005-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Work Instructions when Fabricating a Gagging Device for Main Condenser Hotwell Surge Bypass Valve |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors reviewed a self-revealing finding for the licensee's failure to follow work instructions. Specifically, mechanics failed to properly implement Work Order 01188696, Task 7, when fabricating the gagging device used to maintain main con
Region: IV | Columbia Generating Station | 16989 | 12/31/2011 02/13/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Acceptance Criteria in Offsite Power Alignment Procedure |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to include appropriate steps in a surveillance test procedure. Specifically, Procedure OSP-ELEC-W101, "Offsite Station Power Alignment Ch
Region: IV | Columbia Generating Station | 16990 | 12/31/2011 02/13/2012 | 2011005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Missed Procedural Step Results in Secondary Containment Pressure Excursion |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to follow procedures. Specifically, on November 2, 2011, operators failed to follow Procedure SOP-HVAC/RB-START, "Reactor Bu
Region: IV | Columbia Generating Station | 16991 | 12/31/2011 02/13/2012 | 2011005-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Follow Earthquake Abnormal Procedure |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to follow the abnormal procedure for earthquakes. Specifically, the licensee failed to follow Procedure "ABN-Earthquake," Revision 6, by n
Region: IV | Columbia Generating Station | 16985 | 09/30/2011 12/15/2011 | 2011008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Clearance Order Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team documented a Green self-revealing violation of Technical Specification 5.4.1(a), Procedures, because operators failed to meet the conditions of a plant clearance order before opening main steam line drain valves. Consequently, operators in
Region: IV | Columbia Generating Station | 16986 | 09/30/2011 12/15/2011 | 2011008-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Suppression Pool Cooling Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team documented a Green self-revealing violation of Technical Specification 5.4.1(a), because operators failed to properly align the train B residual heat removal system prior to starting the pump. Consequently, approximately 269 gallons of wat
Region: IV | Columbia Generating Station | 16987 | 09/30/2011 12/15/2011 | 2011008-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Control Rod Drvie System Lineup |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team documented a Green self-revealing violation of Technical Specification 5.4.1(a), because operators failed follow the control rod drive scram testing procedure, in that they failed to verify that no conflicting activities were in progress.
Region: IV | Columbia Generating Station | 16966 | 09/24/2011 11/02/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Reactor Core Isolation Cooling Surveillance Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure of the licensee to maintain an adequate reactor core isolation cooling pump surveillance procedure. Specifically, Procedure OSP-RCIC/IST-B501, "RCIC L
Region: IV | Columbia Generating Station | 16967 | 09/24/2011 11/02/2011 | 2011004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Maintenance and Lubrication Procedures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green . The inspectors identified a noncited violation of Technical Specification 5.4.1.a for failure to follow Procedure PPM 10.2.80, "CVB and CSP Valve Air Operator Seal Replacement," Revision 4. On May 28, 2011, containment vacuum breaker valve CVB-V-1
Region: IV | Columbia Generating Station | 16968 | 09/24/2011 11/02/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Test Emergency Diesel Generator Critical Trips |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. The inspectors identified a noncited violation of Technical Specification 3.8.1, "AC Sources - Operating," for the licensee's failure to meet testing requirements of Surveillance Requirement 3.8.1.13. Specifically, the inspectors determined the lic
Region: IV | Columbia Generating Station | 16964 | 09/24/2011 11/02/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Seismic Storage Requirements Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000397 Columbia Generating Station |  | 71111.17T | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to accomplish activities affecting quality. From July 13, 2011, to July 19, 2011, the licensee failed to accomplish the storage of transient equi