Region: IV | Columbia Generating Station | 16971 | 09/24/2011 11/02/2011 | 2011004-05 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure Main Steam Isolation Valve Setpoint Change is Adequate |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspectors reviewed a self revealing violation of 10 CFR Part 50 Appendix B, Criterion III for the licensee's failure to perform an adequate review of a design modification that changed the isolation logic for the main steam isolation valves fr
Region: IV | Columbia Generating Station | 16972 | 09/16/2011 10/25/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Degraded Flood Barriers |  | H.1(c) Communication of Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. The team identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because Energy Northwest failed to promptly identify and correct degraded flood barrier floor coatings, which protected the Division 2 safe
Region: IV | Columbia Generating Station | 16983 | 09/16/2011 10/25/2011 | 2011006-02 | NRC | NCV | Mitigating Systems | Green | Three Examples of a Failure to Follow Procedures Results in Unsecured Transient Equipment and Ineffective Corrective Actions |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. The team identified three examples of a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow station procedures. The licensee entered these examples into the correc
Region: IV | Columbia Generating Station | 16984 | 09/16/2011 10/25/2011 | 2011006-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Survey |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. The team reviewed a self-revealing noncited violation of 10 CFR Part 20.1501(a), for the failure to survey the residual heat removal pump A room after it was secured from service. Specifically, on August 29, 2011, during a tour with the NRC inspect
Region: IV | Columbia Generating Station | 16963 | 06/25/2011 07/27/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Loss of Reactor Coolant System Inventory during Reactor Pressure Vessel Flood-up |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.2 | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the licensee's failure to provide procedures appropriate to the circumstances to perform flood-up. Specifically, operators inadvertently drained 4000 gallons wate
Region: IV | Columbia Generating Station | 16962 | 03/26/2011 05/10/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Unacceptable Preconditioning is Considered During the Work Management Process |  | H.4(b) Procedural Compliance | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors identified a noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to consider the impact of preconditioning on the emergency core cooling systems during ma
Region: IV | Columbia Generating Station | 16943 | 12/31/2010 02/08/2011 | 2010005-01 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment During Lifting Activities |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.13 | Green. The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) for the licensee's failure to perform a risk assessment during lifting activities in the circulating water pump house. Specifically, licensee personnel failed to assess the increa
Region: IV | Columbia Generating Station | 16944 | 12/31/2010 02/08/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Acceptance Criteria |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to include acceptance criteria appropriate to the circumstance in surveillance testing p
Region: IV | Columbia Generating Station | 16956 | 12/31/2010 02/08/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with both Trains of Control Room Emergency Chillers |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct a condition adverse to quality involving both trains of control room emergency chille
Region: IV | Columbia Generating Station | 16957 | 12/31/2010 02/08/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Engineering Evaluation to Determine Seismic Qualification of Safety-related Equipment |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure PPM 10.2.53, "Seismic Requirements for Scaffolding, Ladders, Man-Lifts, Tool Ga
Region: IV | Columbia Generating Station | 16942 | 09/25/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment Associated with Planned Surveillance Activities |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.13 | Green. The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4) for the licensee's failure to perform an adequate risk assessment during surveillance testing. Specifically, licensee personnel failed to input the appropriate variable for
Region: IV | Columbia Generating Station | 16936 | 06/26/2010 08/04/2010 | 2010003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Translate Appropriate Acceptance Critereia |  | P.3(a) Self-Assessment | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | -Green. The inspectors reviewed a Green self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" for Energy Northwest's failure to include acceptance criteria appropriate to the circumstances i
Region: IV | Columbia Generating Station | 16937 | 06/11/2010 09/09/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Emergency Diesel Generator Air Filters During an Ashfall Event |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which requires, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tr
Region: IV | Columbia Generating Station | 16940 | 06/11/2010 09/09/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Offsite Electrical Power Capability to Safety-Related Emergency Core Cooling System Equipment During a Design Basis Event with Offsite Power Available |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which requires, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performance of
Region: IV | Columbia Generating Station | 16941 | 06/11/2010 09/09/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Inappropriate Extension of Qualified Service Life of Agastat Relays |  | P.2(b) Implementing Operating Experience | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which requires, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performance of
Region: IV | Columbia Generating Station | 16932 | 03/27/2010 05/10/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Reactor Core Isolation Cooling Turbine Bearing Oil Level in Accordance with the Applicable Operating Procedure Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a for a failure to maintain reactor core isolation cooling turbine bearing oil level in the proper band in accordance with procedural requirements. Not documenting oil
Region: IV | Columbia Generating Station | 6324 | 03/27/2010 05/10/2010 | 2010002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Adequate Acceptance Criteria |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors reviewed a self revealing non-cited violation of Technical Specification 5.4.1a for a failure to provide procedures appropriate to the circumstance for rebuilding hydraulic control unit directional control valves. The failure to prov
Region: IV | Columbia Generating Station | 16897 | 12/31/2009 02/04/2010 | 2009005-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Classify a Notification of Unusual Event During a Toxic Gas Event |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000397 Columbia Generating Station |  | 71114.05 | Green. The inspectors identified a noncited violation of 10 CFR 50.47(b)(4) for the failure to classify an emergency condition during a toxic gas event. The licensee's failure to classify a Notification of Unusual Event on May 20, 2009, after being inform
Region: IV | Columbia Generating Station | 16924 | 12/31/2009 02/04/2010 | 2009005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a resulting from a worker's failure to follow radiation protection requirements. The worker failed to ensure he was on the correct radiation work permit,
Region: IV | Columbia Generating Station | 16925 | 12/31/2009 02/04/2010 | 2009005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Notify Radiological Planning Personnel of a Work Plan Deviation |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | 7112102 | Green. The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a resulting from a work group's deviation from an established work plan. The original dose estimate for the refurbishment of the containment recirculation
Region: IV | Columbia Generating Station | 16926 | 12/31/2009 02/04/2010 | 2009005-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Submit An Outage Job To The Senior Site ALARA Committee For Review |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 7112102 | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a because the licensee failed to submit an outage job to the Senior Site ALARA Committee for review. The original dose estimate for turbine building general access was
Region: IV | Columbia Generating Station | 16923 | 12/31/2009 02/04/2010 | 2009005-05 | Self - Revealed | FIN | Initiating Events | Green | Digital Electro-Hydraulic Leak Results in Reactor Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspectors reviewed a self-revealing finding for the failure of the licensee to provide an adequate procedure for the installation of an o-ring in the digital electro-hydraulic system. Specifically, failure to provide the methods and details fo
Region: IV | Columbia Generating Station | 16919 | 11/21/2009 11/25/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct an Adverse Trend in Keep Fill Pump Performance |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which occurred when the licensee failed to promptly correct an identified condition adverse to quality. Specifically, in 1998, the licensee
Region: IV | Columbia Generating Station | 16920 | 11/21/2009 11/25/2009 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Suitability of Class 1E Electrical Components |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. A noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was revealed on April 7, 2007, when overheating of a Class 1E power conditioning transformer resulted in a fire. The licensee determined that the failed transforme
Region: IV | Columbia Generating Station | 16921 | 11/21/2009 11/25/2009 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Housekeeping Program Requirements |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000397 Columbia Generating Station |  | 71152B | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to properly implement housekeeping procedures to control transient equipment and materials. Specifically,
Region: IV | Columbia Generating Station | 16930 | 09/30/2009 11/23/2009 | 2009010-01 | Self - Revealed | FIN | Mitigating Systems | Green | Inadquate Technical Review of Design Change Packages |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The inspectors reviewed two examples of a self-revealing finding for the failure to follow Procedure SWP-DES-01, "Plant Modification & Configuration Control," Revision 11, for the modifications to the digital electrohydraulic control system and the
Region: IV | Columbia Generating Station | 16931 | 09/30/2009 11/23/2009 | 2009010-02 | NRC | FIN | Initiating Events | Green | Failure to Perform Inspections Resulted in Bus Failure and Reactor Scram |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The inspectors reviewed a self-revealing finding for the failure to follow Procedure PPM 1.5.13, "Preventive Maintenance Optimization Living Program," Revision 16, for not evaluating the scope changes for the preventive maintenance inspections on t
Region: IV | Columbia Generating Station | 16912 | 09/26/2009 11/03/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Requirements of Procedure SOP-ENTRY-DW |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.2 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for Energy Northwest's failure to effectively implement procedure SOP-ENTRY-DW, "Personnel Entry into Drywell." Ene
Region: IV | Columbia Generating Station | 16913 | 09/26/2009 11/03/2009 | 2009004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform Back-up Monitoring |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspectors reviewed a self-revealing finding for the failure of Energy Northwest to implement the standards and guidance provided in Operations Instruction OI-09, "Operations Standards and Expectations," Revision 24. As a result, an operator fa
Region: IV | Columbia Generating Station | 16911 | 08/28/2009 09/15/2009 | 2009009-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide Adequate Respiratory Protection Equipment for Emergency Response |  | H.2(d) Facilities & Equipment | TE?: N | 05000397 Columbia Generating Station |  | 7112103 | Green. The inspectors identified a non-cited violation of 10 CFR 50.47(b)(10) for the failure to provide adequate respiratory protection equipment for emergency response, compromising the protective actions developed for the plume exposure pathway for eme
Region: IV | Columbia Generating Station | 16908 | 06/27/2009 08/10/2009 | 2009003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Barricade and Conspicuously Post a High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | A self-revealing noncited violation of Technical Specification 5.7.1 was identified for failure to barricade and conspicuously post a high radiation area. On April 14, 2009, equipment drain radioactive tank 5 was completely drained which created an unpost
Region: IV | Columbia Generating Station | 16909 | 05/08/2009 08/10/2009 | 2009003-02 | Self - Revealed | FIN | Initiating Events | Green | Reactor Scram Due to Seal Oil Leak for Main Generator |  | P.2(b) Implementing Operating Experience | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealing finding for the failure of Energy Northwest to implement the standards and guidance provided in Site Wide Procedure SWP-CAP-01, "Corrective Action Program," Revision 17. Specifically, Energy Northwest failed to tak
Region: IV | Columbia Generating Station | 16907 | 03/28/2009 04/30/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform engineering evaluation to determine seismic qualificaiton of safety-related equipment |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for Energy Northwest's failure to follow procedure PPM 10.2.53, "Seismic Requirements for Scaffolding, Ladders, Man-Lifts,
Region: IV | Columbia Generating Station | 16906 | 02/08/2009 04/30/2009 | 2009002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform an Adequate Site Acceptance Test |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71153 | The inspectors reviewed a self-revealing finding for the failure of Energy Northwest to perform an adequate site acceptance test of the digital electro-hydraulic system. Specifically, Energy Northwest failed to verify that the quad voter solenoid valves i
Region: IV | Columbia Generating Station | 16902 | 12/31/2008 02/11/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures during an Overhaul of Emergency Diesel Engine 1A1 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors identified a noncited violation (NCV) of Technical Specification 5.4.1.a (Procedures) for Energy Northwest's failure to follow site procedures during an overhaul of the Division 1 emergency diesel engine in 2003. Specifically, care w
Region: IV | Columbia Generating Station | 16903 | 12/31/2008 02/11/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis into Procedures for Residual Heat Removal Operating Modes |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion III (Design Control) for the failure to properly translate the design basis of the facility into procedures. Specifically, when the residual heat removal system, Tra
Region: IV | Columbia Generating Station | 16901 | 09/30/2008 11/07/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate procedures during maintenance of ECCS Pumps |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71111.12 | Green. The inspectors identified a noncited violation of Technical Specification 5.4.1.a for Energy Northwest's failure to provide adequate procedures during maintenance of emergency core cooling system pumps. Specifically, Energy Northwest failed to spec
Region: IV | Columbia Generating Station | 16895 | 09/30/2008 11/07/2008 | 2008004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Administrative Control of Keys to High Radiation Area with Dose Rates in Excess of 1 Rem per Hour |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspectors identified a noncited violation of Technical Specification 5.7.2.a.1 for failure to maintain administrative control of door and gate keys to high radiation areas with dose rates greater than 1 rem per hour. Specifically, on August 28
Region: IV | Columbia Generating Station | 16896 | 09/30/2008 11/07/2008 | 2008004-03 | Self - Revealed | FIN | Initiating Events | Green | DEH Leak Results in Reactor Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. The inspector reviewed a self-revealing finding for failure of Energy Northwest to provide an adequate procedure for the installation of a compression fitting in a digital electro-hydraulic system modification. Specifically, failure to provide the
Region: IV | Columbia Generating Station | 16894 | 09/30/2008 11/07/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | Failure to assure that Division 2 instrument sensing lines remained free of fire damage |  |  | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. The inspectors identified a noncited violation of License Condition 2.C.(14) for failure to protect one train of post fire safe shutdown equipment as required by 10 CFR Part 50, Appendix R, Section III.G. Specifically, the licensee failed to ensure
Region: IV | Columbia Generating Station | 6351 | 06/30/2008 07/29/2008 | 2008003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Access to an Area with Radiation Levels in excess of 1.0 Rem/hr |  | H.3(b) Work Activity Coordination | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.7.2 for failure to control a high radiation area with dose rates in excess of 1.0 rem per hour. Specifically, on January 30, 2008, a worker, within the 512' re
Region: IV | Columbia Generating Station | 6352 | 06/30/2008 07/29/2008 | 2008003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Barricade and Conspicuously Post a High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.7.1 for failure to barricade and conspicuously post a high radiation area. Specifically, a worker received a dose rate alarm of 216 millirem per hour while wor
Region: IV | Columbia Generating Station | 6353 | 06/30/2008 07/29/2008 | 2008003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiological Survey |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspectors reviewed a self-revealing noncited violation of 10 CFR 20.1501(a) for failure to perform a survey of a potentially contaminated barrel, resulting in the contamination of a worker. Specifically, on October 5, 2007, a worker alarmed a
Region: IV | Columbia Generating Station | 6347 | 03/31/2008 05/09/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Actions to Address Deficient Emergency Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | Green. An NRC identified noncited violation of Technical Specification 5.4.1.a was identified for an inadequate emergency support Procedure PPM 5.5.26, "Overriding RHR [Residual Heat Removal] Shutdown Cooling Return Valve Isolations," Revision 5. The defi
Region: IV | Columbia Generating Station | 6348 | 03/31/2008 05/09/2008 | 2008002-02 | NRC | NCV | Initiating Events | Green | Failure to Control Design of Residual Heat Removal Shutdown Cooling Suction Header Bypass Line |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. An NRC identified noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for Energy Northwest's failure to adequately review a design change to the facility in 1994. The design change installed a bypass li
Region: IV | Columbia Generating Station | 6349 | 03/31/2008 05/09/2008 | 2008002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Preclude a Recurrence and Further Degradation of Secondary Containment |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 71153 | -Green. A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to promptly correct a condition adverse to quality to preclude further degradation of a secondary containment sea
Region: IV | Columbia Generating Station | 6331 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Engineering Evaluation in Accordance with Scaffold Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000397 Columbia Generating Station |  | 71111.04Q | Green. An NRC identified noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for Energy Northwest's failure to follow Procedure PPM 10.2.53, "Seismic Requirements for Scaffolding, Ladders
Region: IV | Columbia Generating Station | 6341 | 12/31/2007 02/11/2008 | 2007005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedures for Shutdown of the High Pressure Core Spray Diesel Generator |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. A self-revealing Green noncited violation of Technical Specification 5.4.1.a (2 examples) was identified for failure to provide adequate procedures for shutdown of the high pressure core spray diesel generator resulting in inoperability of the dies
Region: IV | Columbia Generating Station | 6342 | 12/31/2007 02/11/2008 | 2007005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to survey airborne radioactivity |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspector reviewed a self-revealing, noncited violation of 10 CFR 20.1501(a) resulting from the licensee's failure to perform airborne radioactivity surveys during a work activity. The failure was discovered after five contract scaffold workers
Region: IV | Columbia Generating Station | 6343 | 12/31/2007 02/11/2008 | 2007005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to use the correct radiation work permit and obtain a briefing of dose rates |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 7112101 | Green. The inspector reviewed a self-revealing, noncited violation of Technical Specification 5.4.1 because a worker failed to use the correct radiation work permit and obtain a briefing of the dose rates in the work area. The worker had been working in t
Region: IV | Columbia Generating Station | 6344 | 12/31/2007 02/11/2008 | 2007005-06 | Self - Revealed | FIN | Occupational Radiation Safety | Green | ALARA Finding |  | H.3(a) Work Planning | TE?: N | 05000397 Columbia Generating Station |  | 7112102 | Green. The inspector reviewed a self-revealing ALARA finding because performance deficiencies resulted in the collective dose of a work activity exceeding five person-rem and the legitimate dose estimate by more than 50 percent. The licensee estimated Rad
Region: IV | Columbia Generating Station | 6330 | 09/28/2007 11/07/2007 | 2007004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Adhere to Operations Standards and Expectations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. A Green self-revealing finding was identified for the failure of operations staff to adhere to an operations instructions which provided operating expectations and standards for dealing with uncertain situations and time critical decisions. This re
Region: IV | Columbia Generating Station | 6357 | 09/06/2007 09/27/2007 | 2007008-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Provide Recurring Training to Hazmat Employees |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000397 Columbia Generating Station |  | 7112202 | Green. The team identified a noncited violation of 10 CFR 71.5 because the licensee failed to provide required recurring training to hazmat employees involved in the shipment of radioactive material. Specifically, the licensee did not provide recurring, f
Region: IV | Columbia Generating Station | 6322 | 06/29/2007 08/13/2007 | 2007003-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Adequate Oversight of Vendor Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000397 Columbia Generating Station |  | 71111.08G | Green. The inspectors identified a Green NCV of 10 CFR 50.55a(g)4 for the failure to meet the requirements of American Society of Mechanical Engineers (ASME) Code Section XI. Specifically, the licensee failed to provide adequate oversight of vendor activi
Region: IV | Columbia Generating Station | 6318 | 06/29/2007 08/13/2007 | 2007003-02 | Self - Revealed | FIN | Mitigating Systems | Green | Degraded Diesel Generator Output Breakers |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | Green. A self-revealing Green finding was identified for the failure to maintain the design of the station's division 1 and 2 diesel generator output breakers. This resulted in reduced reliability of the breakers to function as designed during surveillanc
Region: IV | Columbia Generating Station | 6320 | 06/29/2007 08/13/2007 | 2007003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Drawings to Support Emergent Work |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. A self-revealing noncited violation of Technical Specification 5.4.1.a associated with Energy Northwest's failure to establish adequate drawings to support emergent work was identified. As a result, Energy Northwest failed to identify during the wo
Region: IV | Columbia Generating Station | 6319 | 06/29/2007 08/13/2007 | 2007003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedural Configuration Control for Pressure Switch, RHR-PS-19A, During Planned Surveillance Activities |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71153 | Green. A self-revealing noncited violation Technical Specification 5.4.1.a was identified for a failure to provide adequate procedures for configuration control of pressure switch, RHR-PS-19A, during planned surveillance activities. This contributed to RH
Region: IV | Columbia Generating Station | 6321 | 06/29/2007 08/13/2007 | 2007003-05 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Actions Related to Out-of-Service Seismic Monitoring Instruments |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. An NRC identified noncited violation of 10 CFR 50.54(q) was identified for Energy Northwest's failure to effectively maintain a standard emergency action level scheme in place when adequate compensatory measures to address out-of-service seismic in
Region: IV | Columbia Generating Station | 6305 | 03/30/2007 05/14/2007 | 2007002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Clearance Order Results in Inoperable Diesel Generator |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | 71111.19 | Green. A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure to provide an adequate work instruction (clearance order) resulting in the failure of three diesel generator room ventilation fans to start when r
Region: IV | Columbia Generating Station | 6306 | 03/30/2007 05/14/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Battery Surveillance Test (Section 1R22) |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. An NRC identified noncited violation of TS 5.4.1.a for an inadequate battery surveillance test procedure was identified because of the use of a non-conservative specific gravity electrolyte level correction factor. This resulted in the inability of
Region: IV | Columbia Generating Station | 6307 | 03/30/2007 05/14/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Immediate Corrective Actions for Electrical Disconnect Deficiency (Section 4OA2.2) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. A self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for failure to take prompt corrective actions for conditions adverse to quality to assure the seismic qualification of safety-related e
Region: IV | Columbia Generating Station | 6317 | 03/30/2007 05/14/2007 | 2007002-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Reactor Protection Procedure and Subsequent Inadvertent Isolation of Shutdown Cooling |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for an inadequate procedure which resulted in an inadvertent isolation of shutdown cooling. A procedure step required opening an incorrect electrical power supply
Region: IV | Columbia Generating Station | 6299 | 12/31/2006 02/13/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Diesel Generator Test Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000397 Columbia Generating Station |  | 71111.22 | Green. A green self-revealing non-cited violation (NCV) of technical specification 5.4.1.a was identified for the failure to follow a diesel generator surveillance test procedure. This resulted in the unintentional inoperability of the backup transformer.
Region: IV | Columbia Generating Station | 6300 | 12/31/2006 02/13/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Degraded Conduit Jackets |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71152 | A green NRC identified NCV of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for failing to promptly identify conditions adverse to quality associated with loss of full environmental qualification of plant components due to degr
Region: IV | Columbia Generating Station | 6301 | 12/31/2006 02/13/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternate Boron Injection Emergency Procedure |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.04S | Green. A green NRC identified NCV of technical specification 5.4.1.a was identified for the failure to provide an adequate procedure for alternate boron injection. Specifically, procedure Emergency Support Procedure 5.5.8, "Alternate Boron Injection," Rev
Region: IV | Columbia Generating Station | 6291 | 09/30/2006 11/14/2006 | 2006004-03 | NRC | NCV | Mitigating Systems | Green | Failure to implement adequate design control measures for the station's safety-related batteries |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," when Energy Northwest failed to perform adequate design reviews to maintain appropriate control of the design and qualification of the station's safe
Region: IV | Columbia Generating Station | 6294 | 07/13/2006 08/18/2006 | 2006008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Redundant Safe Shutdown Systems Located In the Same Fire Area Are Free of Fire Damage |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.05T | The team identified a noncited violation (NCV) of License Condition 2.C.(14), Fire Protection Program (Generic Letter 86-10), for failure to ensure that redundant trains of safe shutdown systems in the same fire area were free of fire damage. The Columbia
Region: IV | Columbia Generating Station | 6295 | 07/13/2006 08/18/2006 | 2006008-02 | NRC | VIO | Mitigating Systems | Green | Lack of an Evaluation of the Effects of Fire on the Reactor protection System/Scram | EA Case: 2010137 |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.05T | The team identified an apparent violation (AV) of License Condition 2.C.(14) concerning failure to evaluate the potential effect of fire damage on the Reactor Protection System circuits relied upon for reactor scram capability in the approved fire protect
Region: IV | Columbia Generating Station | 6290 | 07/03/2006 07/03/2006 | 2006011-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify Degraded Shaft Couplings in Standby Service Water Pumps |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000397 Columbia Generating Station |  | 71152 | Green. A Green self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for failure to promptly identify conditions adverse to quality associated with the safety-related standby service water pum
Region: IV | Columbia Generating Station | 6297 | 06/30/2006 07/22/2006 | 2006003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Modification of LPCS |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000397 Columbia Generating Station |  | NONE | Green. An NRC identified noncited violation of 10CFR50, Appendix B, Criterion III, "Design Control," was identified when Energy Northwest failed to ensure the adequacy of a design modification, implemented in 1992, to a low pressure core spray instrument
Region: IV | Columbia Generating Station | 6288 | 01/20/2006 05/12/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Condition Adverse to Quality in Safety Related 4160 VAC Breakers |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for failure to promptly identify and evaluate conditions adverse to quality associated with the 4160 VAC safety related breakers. Although Energ
Region: IV | Columbia Generating Station | 6289 | 01/12/2006 05/12/2006 | 2006002-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Establish Adequate Compensatory Measure to Ensure Prompt Implementation of the Columbia Generating Station Emergency Plan |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50.54(q) for the failure to maintain the facility emergency plan commensurate with the standards provided in 10 CFR 50.47(b)(4). Specifically, Energy Northwest failed to establish adequate compensa
Region: IV | Columbia Generating Station | 124833 | 04/25/2019 |  |  | LIV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000397 Columbia Generating Station |  | 71152B
Region: IV | Comanche Peak | 126379 | 12/31/2019 02/07/2020 | 2019004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique Weaknesses During a Biennial Exercise |  | H.14 - Conservative Bias | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | ERO Performance | 71114.01 | The inspectors identified a Green, non-cited violation of 10 CFR 50.47(b)(14) for the licensee’s failure to identify and correct weaknesses in emergency response organization performance during a biennial emergency preparedness exercise conducted on Novem
Region: IV | Comanche Peak | 125286 | 06/30/2019 08/09/2019 | 2019002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate a Change to the Facilities AC Power System |  | NPP | TE?: N | 05000446 Comanche Peak 2 | Design Control | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” associated with the licensee’s failure to assure that a design change met regulatory requirements for sharing of systems among units. Spe
Region: IV | Comanche Peak | 125283 | 06/30/2019 08/09/2019 | 2019002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of Control Room Air Conditioning Unit X-01 |  | H.11 - Challenge the Unknown | TE?: N | 05000446 Comanche Peak 2 | Equipment Performance | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to follow the requirements of Station Procedure STI-422.01, “Operability Det
Region: IV | Comanche Peak | 125285 | 06/30/2019 08/09/2019 | 2019002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provice Adequate Procedure Results in a Reactor Trip |  | H.12 - Avoid Complacency | TE?: N | 05000446 Comanche Peak 2 | Human Performance | 71153 | The inspectors reviewed a Green, self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to establish an adequate procedural guidance for operators che
Region: IV | Comanche Peak | 124444 | 03/31/2019 05/10/2019 | 2019001-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions for Failure to Ensure Containment Hatch Closure Capability |  | H.6 - Design Margins | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | SSC and Barrier Performance | 71111.04Q | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Correct Actions," associated with the licensee's failure to take adequate corrective actions for an inadequate containment closure procedure. Specificall
Region: IV | Comanche Peak | 124451 | 03/31/2019 05/10/2019 | 2019001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor or Demonstrate Control of Performance Under the Maintenance Rule |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Equipment Performance | 71111.12 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(2), with three examples, for failure to demonstrate effective control of performance of a maintenance rule scoped system through appropriate preventive maintenance.
Region: IV | Comanche Peak | 124448 | 03/31/2019 05/10/2019 | 2019001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Control Hazard Barriers During Maintenance |  | H.14 - Conservative Bias | TE?: N | 05000445 Comanche Peak 1 | Configuration Control | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)4 for failure to implement risk mitigating actions during diesel generator maintenance.
Region: IV | Comanche Peak | 124762 | 03/31/2019 05/10/2019 | 2019001-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure When A Degraded Condition Was Identified |  | H.14 - Conservative Bias | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Protection Against External Factors | 71111.15 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion?V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to follow the requirements of Station Procedure STI-421.01, “Initiation of
Region: IV | Comanche Peak | 124352 | 03/31/2019 05/10/2019 | 2019001-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Safety Evaluations in Accordance with 10CFR50.59 |  | H.9 - Training | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.17T | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” (with four examples) in which the licensee failed to complete 50.59 evaluations as required by station procedures.
Region: IV | Comanche Peak | 124479 | 03/31/2019 05/10/2019 | 2019001-07 | Self - Revealed | NCV | Emergency Preparedness | Green | Inadequate Maintenance Instructions Result in Loss of Assessment Capability |  | H.8 - Procedure Adherence | TE?: N | 05000445 Comanche Peak 1 | Facilities and Equipment | 71152 | The inspectors reviewed a self-revealed Green, non-citied violation of 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," that occurred due to inadequate maintenance instructions for safety related radiation monitors which result
Region: IV | Comanche Peak | 124761 | 03/31/2019 05/10/2019 | 2019001-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedural Guidance for Flushing Lithium at Power |  | H.11 - Challenge the Unknown | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Equipment Performance | 71152 | The inspectors reviewed a Green, self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to establish an adequate procedure for flushing lithium from t
Region: IV | Comanche Peak | 25959 | 12/31/2018 02/11/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Programmatic Failures related to Procedures for the Control Transient Combustibles |  | H.2 - Field Presence | TE?: N | 05000446 Comanche Peak 2 | Protection Against External Factors | 71111.05Q | The inspectors identified a Green, non-cited violation of Operating License NPF-89, License Condition 2.G, "Fire Protection Program," for the failure to control transient combustibles in accordance with the station's Fire Protection Report. The licensee’s
Region: IV | Comanche Peak | 25960 | 12/31/2018 02/11/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Alignment of Priority Panels Normally Aligned to Class 1E Power |  | NPP | TE?: Y SL-IV-NCV | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Equipment Performance | 71111.15 | The inspectors identified a Green, Severity Level IV, non-cited violation of Technical Specification 5.4.1.a associated with the failure to establish, implement, and maintain procedures for operation and maintenance of electrical systems, which are recomm
Region: IV | Comanche Peak | 25961 | 12/31/2018 02/11/2019 | 2018004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality |  | H.5 - Work Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Equipment Performance | 71111.15 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to take corrective actions for condition adverse to quality. Specifically, a failure of a Class-1E power s
Region: IV | Comanche Peak | 10 | 12/31/2018 02/11/2019 | 2018004-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform Evaluations of State and Local Government Interface Based on Licensee Performance Indicators |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 | Offsite EP | 71114.05 | The inspector identified a Green, non-cited violation of 10 CFR 50.54(t) for failure to evaluate the adequacy of interfaces with State and local governments based on assessment against performance indicators. Specifically, the licensee failed to develop a
Region: IV | Comanche Peak | 24683 | 09/30/2018 10/31/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Ability to Withstand a Station Blackout |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50.63 for the licensee’s failure to maintain the ability to withstand and recover from a station blackout. Specifically, the licensee’s approved coping analysis for each unit required t
Region: IV | Comanche Peak | 24684 | 09/30/2018 10/31/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedural Guidance for Processing Technical Changes Performed by a Vendor on Installed Plant Equipment |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, NCV of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to establish an adequate procedure for controlling and processing vendor documents and vend
Region: IV | Comanche Peak | 24398 | 09/10/2018 10/04/2018 | 2018011-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow a Quality Procedure Associated with the Reactor Makeup and Chemical Control System | EA Case: EA-18-064 | H.12 - Avoid Complacency | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to follow a quality procedure associated with the reactor makeup and chemical control system which resulted in an unanticipat
Region: IV | Comanche Peak | 24375 | 08/20/2018 08/20/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Test Program to Verify Residual Heat Removal Suction Valve Capability |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.21M | Introduction: The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the failure to establish a test program to ensure that residual heat removal suction isolation valves would perform adeq
Region: IV | Comanche Peak | 24374 | 07/12/2018 08/20/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Procedural Guidance for the Failure of a Component Cooling Water Surge Tank Makeup Valve |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.21M | Introduction: The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the failure to provide procedural guidance for the failure of a CCW surge tank makeup valve.
Region: IV | Comanche Peak | 24084 | 06/30/2018 07/24/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality |  | H.11 - Challenge the Unknown | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” associated with the licensee’s failure to identify and correct a condition adverse to quality associated with unacceptable main steam isol
Region: IV | Comanche Peak | 24085 | 06/30/2018 07/24/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of Main Steam Isolation Valves |  | H.7 - Documentation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Controls,” for the licensee’s unacceptable preconditioning of the Unit 1 main steam isolations valves (MSIV) prior to performing as-found in-service
Region: IV | Comanche Peak | 24086 | 06/30/2018 07/24/2018 | 2018002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Information into System Test Procedures |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Controls,” for the licensee’s failure to ensure that the station’s in-service testing program for MSIVs incorporated the requirements and acceptance
Region: IV | Comanche Peak | 23981 | 03/31/2018 05/08/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Commercial Grade Dedication Process |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, associated with the licensee’s failure to accomplish activities affecting quality in accordance with documented proc
Region: IV | Comanche Peak | 23982 | 03/31/2018 05/08/2018 | 2018001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Information Into System Test Procedures |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the licensee’s failure to ensure that station test procedures incorporated all requirements contained in applicable design documents. Specif
Region: IV | Comanche Peak | 23983 | 03/31/2018 05/08/2018 | 2018001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Procedure |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1, "Procedures," associated with the licensee’s failure to provide procedures appropriate to the circumstances. Specifically, station procedure INC-2085, "Rework and Rep
Region: IV | Comanche Peak | 23984 | 03/31/2018 05/08/2018 | 2018001-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Maintenance Procedure for Feedwater Valves |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealed Green, non-cited violation of Technical Specification 5.4.1, "Procedures," associated with the licensee’s failure to prescribe adequate procedures for performing maintenance on the feedwater bypass control valves. S
Region: IV | Comanche Peak | 23985 | 03/31/2018 05/08/2018 | 2018001-05 | NRC | NCV | Initiating Events | Green | Failure to Correct a Significant Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee’s failure to take corrective action to preclude repetition of a significant condition adverse to quality. Spe
Region: IV | Comanche Peak | 23480 | 01/25/2018 02/22/2018 | 2017010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Measures for Corrective Actions |  | H.3 - Change Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the failure to accomplish activities affecting quality in accordance with approved procedures adequate to the cir
Region: IV | Comanche Peak | 23481 | 01/25/2018 02/22/2018 | 2017010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality |  | H.5 - Work Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to correct a condition adverse to quality effe
Region: IV | Comanche Peak | 22632 | 12/31/2017 02/09/2018 | 2017004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure for Containment Closure |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.04Q | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to prescribe adequate procedures for closing the containment equipment hatch for
Region: IV | Comanche Peak | 22655 | 12/31/2017 02/09/2018 | 2017004-02 | NRC | NCV | Initiating Events | Green | Failure to Perform Class 1 Piping Pressure Tests in Accordance with ASME Code |  | P.2 - Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.08P | Green. The inspectors identified a non-cited violation of 10CFR50.55a(g)(4) involving the licensee’s failure to perform pressure testing of all Class 1 pressure retaining components for Units 1 and 2, in accordance with the applicable edition of Section X
Region: IV | Comanche Peak | 22651 | 12/31/2017 02/09/2018 | 2017004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality |  | H.14 - Conservative Bias | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” associated with the licensee’s failure to take timely corrective actions for a condition adverse to quality. Specifically, since 2010 the
Region: IV | Comanche Peak | 22659 | 12/31/2017 02/09/2018 | 2017004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure When Breaching Control Room Envelope |  | P.3 - Resolution | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.13 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, associated with the licensee’s failure to accomplish activities affecting quality in accordance with documented proc
Region: IV | Comanche Peak | 22656 | 12/31/2017 02/09/2018 | 2017004-05 | NRC | NCV | Barrier Integrity | Green | Failure to Declare Equipment Inoperable |  | H.4 - Teamwork | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | Green. Inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” associated with the licensee’s failure to follow the requirements of station procedure STI-606.01, Work Control Process, Re
Region: IV | Comanche Peak | 22658 | 12/31/2017 02/09/2018 | 2017004-06 | NRC | NCV | Barrier Integrity | Green | Failure to Control Work Hours for Covered Personnel |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.2 | Green. The inspectors identified a non-cited violation of 10 CFR 26.205 associated with the licensee’s failure to calculate and control work hours of personnel subject to work hour controls. Specifically, the licensee failed to track work hours for person
Region: IV | Comanche Peak | 25902 | 12/14/2017 02/08/2018 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Station Procedures for Assigning Correct Shelf Life and Storage Requirements of Qualified Components |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.21N | The team identified a Green, non-cited violation with two examples of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” which states, in part, that “activities affecting quality shall be prescribed by documented instructio
Region: IV | Comanche Peak | 25903 | 12/14/2017 02/08/2018 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Specify a Schedule for the Replacement of Items |  | NPP | TE?: N | 05000446 Comanche Peak 2 |  | 71111.21N | The team identified a Green, non-cited violation of Technical Specification 5.4.1 which states, in part, “Written procedures shall be established, implemented, and maintained covering the applicable procedures recommended in Regulatory Guide 1.33, Revisio
Region: IV | Comanche Peak | 25901 | 12/06/2017 02/08/2018 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Normal Operating Room Temperatures |  | NPP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.21N | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” which states, in part, “Measures shall be established to assure that applicable regulatory requirements and the design basis for those structu
Region: IV | Comanche Peak | 21676 | 09/30/2017 10/26/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality |  | H.5 - Work Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, “Corrective Action,” associated with the licensee’s failure to take timely corrective actions for a condition adverse to quality. Specifically, the licensee failed to
Region: IV | Comanche Peak | 21677 | 09/30/2017 10/26/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Programmatic Failures to Control Transient Combustible Material in Accordance with a Fire Protection Procedure |  | H.8 - Procedure Adherence | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified 51 examples of a non-cited violation of Operating Licenses NPF-87 and NPF-89, License Condition 2.G, “Fire Protection Program,” for the failure to control transient combustibles in accordance with the station’s Fire Protection Re
Region: IV | Comanche Peak | 23495 | 06/30/2017 08/10/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Combustible Material in Accordance with a Fire Protection Procedure |  | P.3 - Resolution | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05Q | The inspectors identified a non-cited violation of Operating Licenses NPF-87 and NPF-89, License Condition 2.G, "Fire Protection Program," for the failure to control transient combustibles in accordance with the station's fire protection report. Specifica
Region: IV | Comanche Peak | 23494 | 06/30/2017 08/10/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Safety-Related Pipe Supports |  | P.3 - Resolution | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," that occurred when the licensee failed on two occasions to perform an adequate operability determination associated with
Region: IV | Comanche Peak | 31025 | 06/30/2017 08/10/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Relays Not Environmentally Qualified |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that design changes were subject to design control measures commensurate with those applied to
Region: IV | Comanche Peak | 31028 | 06/30/2017 08/10/2017 | 2017002-04 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Assess Risk and Implement Risk Management Actions for Proposed Maintenance |  | H.8 Procedure Adherence | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately assess risk and implement required risk management acti
Region: IV | Comanche Peak | 31029 | 06/30/2017 08/10/2017 | 2017002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Requirements Into the As Built Facility |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that applicable regulatory requirements and the design bases, as defined in 10 CFR 50.2 and as
Region: IV | Comanche Peak | 31033 | 06/29/2017 07/31/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain Adequate Inspection Procedures for Penetration Sealing Devices |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05T | Green. The team identified a non-cited violation of Operating License Condition 2.G related to the licensee's failure to maintain adequate procedures for the inspection of required penetration sealing devices as required by the licensee's Fire Protect
Region: IV | Comanche Peak | 31016 | 03/31/2017 05/09/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain B.5.b Equipment in a State of Readiness to Support Mitigation Strategies |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR 50.54(hh)(2), "Conditions of License," involving the licensee's failure to maintain available equipment needed to implement mitigating strategies to provide makeup to steam generators following los
Region: IV | Comanche Peak | 31017 | 03/31/2017 05/09/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Heat Loads on Control Room Air Conditioning System |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.04S | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to properly evaluate heat loads on the control room air conditioning system. Specifically, the licensee used a non-conser
Region: IV | Comanche Peak | 31018 | 03/31/2017 05/09/2017 | 2017001-03 | NRC | NCV | Mitigating Systems | Green | Use of Non-Design Fouling Factor for Component Cooling Water Heat Exchanger in Station Service Water Tornado Missile Calculation |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.07A | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the use of a non-design fouling factor for the component cooling water heat exchanger in a design basis calculation evaluating a tornado mi
Region: IV | Comanche Peak | 31022 | 03/31/2017 05/09/2017 | 2017001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality |  | H.1 Resources | TE?: N | 05000445 Comanche Peak 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to take timely corrective actions for a previously identified condition adverse to quality. Specifically,
Region: IV | Comanche Peak | 31009 | 12/31/2016 02/03/2017 | 2016004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Evaluate Inservice Testing Results of Power Operated Relief Valve |  | H.5 Work Management | TE?: N | 05000445 Comanche Peak 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to evaluate inservice testing results of a power operated relief valve (PORV). Specifically, the licensee restored a unit 1
Region: IV | Comanche Peak | 31010 | 12/31/2016 02/03/2017 | 2016004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope the Containment Ventilation System in the Maintenance Rule Program |  | H.12 Avoid Complacency | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(b)(2) associated with the licensee's failure to scope the containment ventilation system into the maintenance rule program. Specifically, the containment ventilation system, a non-safety rela
Region: IV | Comanche Peak | 31003 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor Feedwater System Check Valve Performance |  | H.10 Bases for Decisions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants." Specifically, the licensee failed to demonstrate that the performance of the Unit 2 auxiliary fe
Region: IV | Comanche Peak | 31004 | 09/30/2016 11/08/2016 | 2016003-02 | NRC | NCV | Initiating Events | Green | Failure to Manage Risk During Refueling Outages |  | H.10 Bases for Decisions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | Green. The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately manage the increase in risk associated with the
Region: IV | Comanche Peak | 30993 | 09/15/2016 10/28/2016 | 2016007-02 | NRC | NCV | Initiating Events | Green | Failure to Evaluate the Suitability of Teflon Gaskets in a Safety-Related Pressure Boundary |  | P.2 Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.17T | The inspectors identified a Green, non-cited violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," which requires, in part, that measures shall also be established for the selection and review for suitability of application of materials, par
Region: IV | Comanche Peak | 30990 | 06/30/2016 08/11/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality |  | P.2 Evaluation | TE?: N | 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to correct a condition adverse to quality in safety-related equipment. Specifically, following an in-servi
Region: IV | Comanche Peak | 30991 | 06/30/2016 08/11/2016 | 2016002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Determine Dose Rates Prior to Allowing Entry into a High Radiation Area |  | H.5 Work Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71124.01 | The inspectors reviewed a self-revealed non-cited violation of Technical Specification 5.7.1.e associated with the licensee allowing a worker access into the 2-077-B penetration valve room, a high radiation area, without an adequate knowledge of the radio
Region: IV | Comanche Peak | 29590 | 12/31/2015 02/04/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Incorrect Visual Resolution Requirements in Augmented Dissimilar Metal Weld Visual Examination Procedures |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion IX, "Control of Special Processes," because the licensee failed to assure that visual examination activities for the reactor vessel dissimilar metal nozzle welds and botto
Region: IV | Comanche Peak | 29574 | 12/31/2015 02/04/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Appropriate Maintenance Rule Corrective Actions for the 6.9 kV System |  | H.8 Procedure Adherence | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50.65(a)(1), for the failure to establish goals that provide reasonable assurance that the 6.9 kV electrical distribution system is capable of fulfilling its intended functions. Specifically,
Region: IV | Comanche Peak | 29575 | 12/31/2015 02/04/2016 | 2015004-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate Compensatory Measures for Seismic Monitoring System Maintenance |  | P.3 Resolution | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) for a failure to meet planning standard 10 CFR 50.47(b)(4) during periodic outages of the seismic monitoring system. Specifically, during planned maintenance on the seismic monitoring s
Region: IV | Comanche Peak | 29586 | 12/31/2015 02/04/2016 | 2015004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to Quality |  | P.2 Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified two examples of a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify conditions adverse to quality. Specifically, in two separate instances involving extent of
Region: IV | Comanche Peak | 29587 | 12/31/2015 02/04/2016 | 2015004-05 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedure When Disabling a Hazard Barrier |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71111.22 | The inspectors identified a finding associated with the licensee's failure to follow procedural requirements for disabling a hazard barrier. Specifically, Station Procedure STA 696, "Hazard Barrier Controls," Revision 2, requires that appropriate temporar
Region: IV | Comanche Peak | 29589 | 12/31/2015 02/04/2016 | 2015004-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Barricade High Radiation Areas |  | P.3 Resolution | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71124.01 | The inspector identified a non-cited violation (NCV) of Technical Specification 5.7.1.a, with two examples, associated with not barricading High Radiation Areas (HRAs) with dose rates not exceeding 1.0 rem/hour at 30 centimeters from the radiation source.
Region: IV | Comanche Peak | 29549 | 11/13/2015 11/13/2015 | 2015008-01 | NRC | NOV | Mitigating Systems | Green | Failure to Evaluate the Lack of Missile Protection on the Turbine Driven Auxiliary Feedwater Pumps' Steam Exhaust Piping | EA Case: 2015207 | H.14 Conservative Bias | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | Green. The team identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate the lack of missile protection on the turbine driven auxiliary feedwater pumps' steam exhaust piping. Speci
Region: IV | Comanche Peak | 29562 | 10/01/2015 11/13/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Assess and Document the Basis for Operability associated with the Turbine Driven Auxiliary Feedwater Pumps' Steam Exhaust Piping not being Evaluated for Tornado Generated Missil |  | H.14 Conservative Bias | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | Green. The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated the licensee's failure to perform adequate operability assessments when a degraded or nonconforming condition was
Region: IV | Comanche Peak | 29563 | 10/01/2015 11/13/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Surveillance on Safety-Related Service Water Systems |  | H.6 Design Margins | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | Green. The team identified a non-cited violation of Technical Specification (TS) 5.4.1, "Procedures," for an inadequate procedure for performing surveillances on the station service water (SSW) systems in units 1 and 2. Specifically, Procedures OPT-207 A
Region: IV | Comanche Peak | 29570 | 10/01/2015 11/13/2015 | 2015008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Controls for Design Calculations |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | Green. The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with two examples associated with the licensee's failure to ensure that design changes were subject to design control measures commensurate wi
Region: IV | Comanche Peak | 29571 | 10/01/2015 11/13/2015 | 2015008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Operability for a Degraded Condition |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The inspectors identified seven examples of a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to perform adequate operability assessments for a degraded or nonconf
Region: IV | Comanche Peak | 29540 | 09/30/2015 11/19/2015 | 2015003-01 | NRC | NCV | Initiating Events | Green | Failure to Take Appropriate Maintenance Rule Corrective Actions for the Instrument Air System |  | P.2 Evaluation | TE?: N | 05000445 Comanche Peak 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50.65(a)(1) for the failure to take appropriate corrective actions for a system that did not meet established goals. Specifically, the Unit 1 instrument air system had been in maintenance rule
Region: IV | Comanche Peak | 29547 | 09/30/2015 11/19/2015 | 2015003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Maintenance Procedure Results in Power Reduction |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | The inspectors reviewed a self-revealing finding associated with an inadequate procedure which resulted in a unit down power. Specifically, the procedure used for over speed testing of the main feedwater pumps did not provide adequate guidance for operati
Region: IV | Comanche Peak | 29524 | 08/03/2015 09/02/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Inverter Fault Interrupting Capability During Design Basis Loss of Offsite Power and Seismic Conditions |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, for those struct
Region: IV | Comanche Peak | 29531 | 08/03/2015 09/02/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Validate Inverter Ouput Demand Factor and to use the Correct Value of Inverter Efficiency when Determining Inverter Input D-C Power Requirements. |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, for those struct
Region: IV | Comanche Peak | 29532 | 08/03/2015 09/02/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Procedure forTornado Missile Impact of Diesel Vents |  | P.2 Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Comanche Peak | 29539 | 08/03/2015 09/02/2015 | 2015007-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate Changes to Ensure They Did Not Require Prior NRC Approval |  |  | TE?: Y SL-IV-NCVIV | 05000445 Comanche Peak 1 |  | 7111121 | The team identified a Severity Level IV, non-cited violation of 10 CFR 50.59, "Changes, Test, and Experiments," which states in part, "Section (c)(1), that a licensee may make changes in the facility as described in the Updated Safety Analysis Report with
Region: IV | Comanche Peak | 29484 | 06/30/2015 08/13/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess Risk and Implement Risk Management Actions for Proposed Maintenance |  | H.13 Consistent Process | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately assess risk and implement required risk management acti
Region: IV | Comanche Peak | 29498 | 06/30/2015 08/13/2015 | 2015002-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique Weaknesses in Radiation Protection Practices |  | P.1 Identification | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71114.07 | The NRC identified two examples of licensee failures to correct deficiencies occurring during the June 10, 2015, emergency preparedness exercise as required by 10 CFR 50.47(b)(14). Specifically, the licensee failed to identify that a lack of radiological
Region: IV | Comanche Peak | 29490 | 06/30/2015 08/13/2015 | 2015002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate and Appropriately Approve Design Changes |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that design changes were subject to design control measures commensurate with those applied to
Region: IV | Comanche Peak | 29507 | 03/31/2015 05/07/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability When Breeching Hazard Barriers |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to perform adequate operability assessments when disabling hazard barriers during
Region: IV | Comanche Peak | 29508 | 03/31/2015 05/07/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Have an Adequate Procedure for Vendor Information |  |  | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to have an adequate procedure for controlling and processing vendor documents and
Region: IV | Comanche Peak | 29509 | 03/31/2015 05/07/2015 | 2015001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Work Planning Procedure |  | H.5 Work Management | TE?: N | 05000445 Comanche Peak 1 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of Procedure STI-606.03, "Work Planning," when developi
Region: IV | Comanche Peak | 29510 | 03/31/2015 05/07/2015 | 2015001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Damages a Centrifugal Charging Pump |  | H.12 Avoid Complacency | TE?: N | 05000445 Comanche Peak 1 |  | 71111.22 | The inspectors identified a non-cited violation of 10 Part CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure during the performance of a surveillance test. Specifically, the licensee
Region: IV | Comanche Peak | 29511 | 03/31/2015 05/07/2015 | 2015001-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Provide an Accurate Shipping Manifest |  | H.12 Avoid Complacency | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 71.5, pursuant to 49 CFR 172.203(d)(3), and 10 CFR 20.2006(b) for the licensee's failure to ship radioactive waste with accurate manifests. Specifically, two radioactive waste shipments departed th
Region: IV | Comanche Peak | 29512 | 03/31/2015 05/07/2015 | 2015001-06 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure for Addressing Significant Conditions Adverse to Quality |  | H.13 Consistent Process | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for two examples of a failure to follow procedure for evaluating and correcting significant conditions adverse to quality
Region: IV | Comanche Peak | 29516 | 03/31/2015 05/07/2015 | 2015001-07 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Centrifugal Charging Pump Lubricating Oil Pump Installation Procedure |  | H.9 Training | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing finding of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings" for failure to provide documented instructions of a type appropriate to the circumstances when performing maintenance on t
Region: IV | Comanche Peak | 29482 | 12/31/2014 02/03/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Boundary Valve Leakage Testing |  | H.11 Challenge the Unknown | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow instructions for performing surveillance testing of the reactor coolant loop cold
Region: IV | Comanche Peak | 29483 | 12/31/2014 02/03/2015 | 2014005-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow the Troubleshooting Activities Procedure Results in a Manual Turbine Runback |  | H.7 Documentation | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow the troubleshooting activities procedure while working on the condensate system alarm and control circuit. The troubleshooting activities caused the condensate low press
Region: IV | Comanche Peak | 29477 | 09/26/2014 10/22/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Goals and Monitor the Performance of the Uninterruptible Power Supply Air Conditioning System |  | H.8 Procedure Adherence | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(1) for the failure to establish performance goals and perform monitoring to ensure the uninterruptible power supply air conditioning unit X-01 was capable of performing its intended functi
Region: IV | Comanche Peak | 29478 | 09/26/2014 10/22/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for Inservice Testing of Auxiliary Feedwater Discharge Check Valves |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure to incorporate adequate acceptance limits in a written procedure to demonstrate components will perform satisfactorily. The licens
Region: IV | Comanche Peak | 29479 | 09/26/2014 10/22/2014 | 2014004-03 | NRC | NCV | Emergency Preparedness | Green | Maintenance of a Standard Action Level Scheme for Main Steam Line Monitors |  | P.2 Evaluation | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) for the failure to follow and maintain the effectiveness of an emergency plan that meets the requirements of planning standard 50.47(b)(4), which requires that a standard emergency clas
Region: IV | Comanche Peak | 29480 | 09/26/2014 10/22/2014 | 2014004-04 | NRC | FIN | Initiating Events | Green | Failure to Install an Insulated Bushing on a Generator Current Transformer Circuit Results in an Automatic Reactor Trip |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow an electrical installation specification and install an insulated bushing on the end of a flexible conduit. As a result, a generator current transformer conductor shorte
Region: IV | Comanche Peak | 29458 | 06/26/2014 08/06/2014 | 2014003-01 | NRC | NCVIV | Barrier Integrity | Green | Failure to Follow 10 CFR 50.59 for a Change to the Spent Fuel Pool Configuration. |  |  | TE?: Y SL-IV-NCVIV | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," for failure to conduct an adequate safety evaluation and submit a license amendment for a change to the facility that required a technical specification am
Region: IV | Comanche Peak | 29463 | 06/26/2014 08/06/2014 | 2014003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Appropriate Instructions for Filling the Component Cooling Water System. |  | H.5 Work Management | TE?: N | 05000446 Comanche Peak 2 |  | 71111.2 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have documented instructions of a type appropriate to the circumstances when performing a
Region: IV | Comanche Peak | 29464 | 06/26/2014 08/06/2014 | 2014003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Adequately Brief Workers on Radiological Conditions Prior to Entry into High Radiation Areas. |  | H.4 Teamwork | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.7.1 resulting from the licensee's failure to control high radiation areas with radiation levels of 100 millirem per hour or greater on three separate occasions. In
Region: IV | Comanche Peak | 29465 | 06/26/2014 08/06/2014 | 2014003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Brazing Copper Tubing |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow procedure for brazing copper joints. Specifically, personnel failed to follow procedure and exe
Region: IV | Comanche Peak | 29469 | 06/26/2014 08/06/2014 | 2014003-06 | NRC | VIO | Mitigating Systems | Green | Failure to Correct Fire Protection Violations in a Timely Manner. | EA Case: 2014123 | H.5 Work Management | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a violation of License Condition 2.G for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the inspectors identified two examples where the licensee failed to im
Region: IV | Comanche Peak | 29470 | 06/26/2014 08/06/2014 | 2014003-07 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow the Site Design Modification Procedures. |  | H.2 Field Presence | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing finding for the failure to follow the design modification process. The licensee implemented a design modification using incorrect technical information. The personnel who conducted the design modification walkdowns
Region: IV | Comanche Peak | 29471 | 06/26/2014 08/06/2014 | 2014003-08 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure to Provide Adequate Work Instructions. |  | H.12 Avoid Complacency | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing finding for the failure to properly plan and review work activities to ensure equipment and personnel safety. Specifically, the licensee failed to ensure the work instructions met the requirements of Procedure STA-
Region: IV | Comanche Peak | 29457 | 03/27/2014 04/21/2014 | 2014002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure for Operation of the Containment Emergency Air Lock Doors |  | H.1 Resources | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow procedure for performing surveillance testing of the containment emergency air loc
Region: IV | Comanche Peak | 29456 | 03/19/2014 03/27/2014 | 2014008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Update Procedures for Cable Label Controls |  | H.1 Resources | TE?: N | 05000446 Comanche Peak 2 |  | NONE | The team reviewed a Green self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings," for the failure to ensure that quality related procedures provide adequate guidance for labeling and terminat
Region: IV | Comanche Peak | 29453 | 12/31/2013 02/04/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Instructions for Containment Sump Inspection Results in Debris Left in the Sump |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow instructions and maintain appropriate housekeeping and cleanliness controls when performing an
Region: IV | Comanche Peak | 29454 | 12/31/2013 02/04/2014 | 2013005-02 | Self - Revealed | FIN | Mitigating Systems | Green | Cutting Incorrect Cable Results in an Inoperable Offsite Power Source |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.18 | The inspectors reviewed a self-revealing finding for the failure of maintenance personnel to follow work instructions. Specifically, maintenance personnel failed to follow instructions and cut the wrong cable during a transformer modification. As a result
Region: IV | Comanche Peak | 29449 | 11/20/2013 12/24/2013 | 2013008-01 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Cause Evaluations for Maintenance Preventable Functional Failures |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The team identified a Green finding for a failure to follow procedures that required the licensee to perform cause evaluations for maintenance preventable functional failures (MPFFs). Two MPFFs were not evaluated for their causes because a condition repor
Region: IV | Comanche Peak | 29450 | 11/20/2013 12/24/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Acceptance Criteria |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | -The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to provide adequate acceptance criteria for bearing oil level in its residual heat removal pump mo
Region: IV | Comanche Peak | 29451 | 11/20/2013 12/24/2013 | 2013008-03 | NRC | NCV | Mitigating Systems | Green | Components of Indeterminate Quality Installed in Safety-Related Applications |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to control deviations from quality standards. After identifying that maintenance personnel had failed to ensure that subc
Region: IV | Comanche Peak | 29446 | 09/25/2013 11/06/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Remove Cable Material from Inside Containment |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow instructions and remove cables from containment as part of a modification. As a result, portion
Region: IV | Comanche Peak | 29447 | 09/25/2013 11/06/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Goals and Monitor the Performance of the Auxiliary Feedwater System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000445 Comanche Peak 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(1) for the licensee's failure to establish performance goals and perform monitoring to ensure the Unit 1 auxiliary feedwater system was capable of performing its intended function. The lic
Region: IV | Comanche Peak | 29441 | 09/25/2013 11/06/2013 | 2013004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Properly Install Auxiliary Condenser Tube Plugs Causes Steam Generator Chemistry Excursion and Unit Power Reduction |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000446 Comanche Peak 2 |  | 71111.18 | The inspectors reviewed a self-revealing finding for the licensee's failure to ensure the heat exchanger tube plugging procedure was adequate. As a result, auxiliary condenser plugs were improperly inserted and caused a tube to leak. This caused high sodi
Region: IV | Comanche Peak | 29448 | 09/25/2013 11/06/2013 | 2013004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Condition Report for a Degraded Under Frequency Relay |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000446 Comanche Peak 2 |  | 71111.19 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow procedures that require initiating a condition report for degradation to safety-related equipme
Region: IV | Comanche Peak | 29415 | 06/26/2013 07/30/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Testing Main Steam Safety Valves |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of the licensee to have documented instructions of a type appropriate to the circumstances for testing th
Region: IV | Comanche Peak | 28338 | 06/26/2013 07/30/2013 | 2013003-02 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure Results in Water Hammer |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000445 Comanche Peak 1 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the failure to follow an auxiliary feedwater system operating procedure. As a result, a water hammer occurred on the condensate storage tank makeup reject line. The lic
Region: IV | Comanche Peak | 29412 | 06/26/2013 07/30/2013 | 2013003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Properly Install an Air Regulator Causes Heater Drain Valve Closure and Reactor Trip |  | H.3(a) Work Planning | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors reviewed a self-revealing finding for the licensee's failure to appropriately plan and control work activities during the installation of an air regulator in the heater drain system. As a result, the fitting that connected the air regulator
Region: IV | Comanche Peak | 29416 | 06/20/2013 08/02/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations and Procedures for Offsite Power Availability |  | P.2(b) Implementing Operating Experience | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that states, in part, "applicable regulatory requirements and design basis are correctly translated into specifications, drawings, proce
Region: IV | Comanche Peak | 29417 | 06/20/2013 08/02/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Voltage Caculations for the 125 VDC and 120 VAC Buses |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that states, in part, "applicable regulatory requirements and design basis are correctly translated into specifications, drawings, proce
Region: IV | Comanche Peak | 29419 | 06/20/2013 08/02/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure To Establish 10 CFR 50.65(a)(1) Performance Goals for the APDG'S |  | H.2(d) Facilities & Equipment | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR 50.65(a)(1), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," that states, in part, that the licensee "shall monitor the performance or condition of st
Region: IV | Comanche Peak | 29420 | 06/20/2013 08/02/2013 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Effect of System Harmonics on Degraded Voltage Relays |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," that states, in part, "measures provide for verifying or checking the adequacy of design, such as by the performance of design reviews,
Region: IV | Comanche Peak | 29423 | 06/20/2013 08/02/2013 | 2013007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Operability Assessments |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation, with three examples, of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," that states, in part, "Activities affecting quality shall be prescribed by documented instru
Region: IV | Comanche Peak | 29432 | 06/20/2013 08/02/2013 | 2013007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Appropriate Acceptance Criteria and Testing Procedure Instructions |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," that states, in part, "A test program shall be established to assure that all testing required to demonstrate t
Region: IV | Comanche Peak | 29433 | 06/20/2013 08/02/2013 | 2013007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Appropriate Acceptance Criteria for the Safety Chill Water Pumps |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," that states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and
Region: IV | Comanche Peak | 29434 | 06/20/2013 08/02/2013 | 2013007-09 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Fouling on the Emergency Dieesel Generator Building Exhaust Ventilation Screens |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," that states, in part, " measures shall be established to assure that conditions adverse to quality are promptly identified and correc
Region: IV | Comanche Peak | 29439 | 06/20/2013 08/02/2013 | 2013007-10 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate the Refueling Water Storage Tank Vortexing Design Calculation Into the Emergency Operating Procedures for Containment Spray Pump Operation |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," states, in part, "measures shall be establish to assure that the design basis for systems, structures, and components are correctly tran
Region: IV | Comanche Peak | 29440 | 06/20/2013 08/02/2013 | 2013007-11 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Design Calculations to Incorporate Technical Specification Allowed Frequency Range for the Emergency Diesel Generator in a Timely Manner |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," states, in part, "measures shall be established to assure that conditions adverse to quality are promptly identified and corrected."
Region: IV | Comanche Peak | 29398 | 03/27/2013 05/02/2013 | 2013002-01 | Self - Revealed | FIN | Initiating Events | Green | Failed Condenser Support Causes Steam Generator Sodium Transient and Manual Reactor Trip |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.18 | The inspectors reviewed a self-revealing finding for the failure to evaluate the effects of vibration on pipe supports in accordance with the design control program when removing the supported pipes. As a result, a pipe support failed due to fatigue and t
Region: IV | Comanche Peak | 29399 | 03/27/2013 05/02/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Have Instructions When Performing Activities |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to accomplish an activity affecting quality as prescribed by documented instructions. Specifically, radiation protection personnel installed camera
Region: IV | Comanche Peak | 29400 | 03/27/2013 05/02/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Diesel Frequency Degradation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to preclude repetition of a significant condition adverse to quality. Specifically, the Unit 2 train B diesel generator failed to maintain 60 her
Region: IV | Comanche Peak | 29409 | 03/27/2013 05/02/2013 | 2013002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Inadequate Auxiliary Feedwater Valve Maintenance |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to identify and correct a condition adverse to quality. Specifically, the licensee failed to identify and correct an inadequate auxiliary feedwat
Region: IV | Comanche Peak | 29410 | 03/27/2013 05/02/2013 | 2013002-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Initiate a Condition Report for a Degraded Reactor Coolant Pump Motor Lower Oil Reservoir |  | P.1(b) Trend Performance CAP | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedures that require initiating a condition report for degradation of equipment. During a maintenance activity, the licen
Region: IV | Comanche Peak | 29411 | 03/27/2013 05/02/2013 | 2013002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Install Grout Under Pipe Support Base Plates |  |  | TE?: N | 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to install grout under pipe support base plates for a main steam line in accordance with drawings. As a result, the pipe support's ability to withs
Region: IV | Comanche Peak | 29390 | 12/31/2012 02/11/2013 | 2012005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Foreign Material in Diesel Generator Governor Causes Start Failure |  | H.3(b) Work Activity Coordination | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a for the failure of the licensee to follow procedure and properly replace diesel generator governor oil. As a result, foreign material was introduced into the g
Region: IV | Comanche Peak | 29389 | 09/26/2012 11/06/2012 | 2012004-03 | NRC | URI | Barrier Integrity | Green | Potential Failure to Follow 10 CFR 50.59 for a Change to the Spent Fuel Pool Configuration (Section 1R18) |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.18
Region: IV | Comanche Peak | 28396 | 09/25/2012 11/06/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Compensatory Measures for Inoperable Hose Stations |  | H.1(c) Communication of Decisions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.d for the failure of the licensee to place signs at inoperable fire hose stations and at the compensatory fire hoses identifying the purpose and location of the compensatory
Region: IV | Comanche Peak | 28397 | 09/25/2012 11/06/2012 | 2012004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Gasket Installation Causes Diesel Jacket Water Leak |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a for the failure of the licensee to adequately install a gasket in accordance with procedure. As a result, the diesel generator jacket water connection leaked a
Region: IV | Comanche Peak | 29388 | 09/25/2012 11/06/2012 | 2012004-04 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Correct a Nonconservative Technical Specification |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to promptly correct a nonconservative technical specification, a condition adverse to quality. Specifically, in December 2010, the licensee implement
Region: IV | Comanche Peak | 28381 | 06/26/2012 07/24/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Tornado Missile Strike on Turbine Driven Auxiliary Feedwater Exhaust Pipe |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure to translate tornado missile protection design requirements to a pipe stress analysis procedure. This resulted in the licensee's failure to analy
Region: IV | Comanche Peak | 28388 | 06/26/2012 07/24/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Revise Turbine Driven Auxiliary Feedwater Pump Acceptance Criteria |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, for the failure to incorporate acceptance limits from applicable design documents into test procedures. Specifically, the licensee revised the Unit 1 and Unit 2 r
Region: IV | Comanche Peak | 28389 | 06/26/2012 07/24/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate Fish Intrusion Operating Experience and Initiate Corrective Action |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure of the licensee to identify and correct a condition adverse to quality. Specifically, the licensee failed to adequately evaluate industry operati
Region: IV | Comanche Peak | 28390 | 06/26/2012 07/24/2012 | 2012003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Take Corrective Actions for Safety Chiller Trips |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to identify and correct a condition adverse to quality. Specifically, safety chiller 2-06 tripped twice, but the licensee failed to develop corre
Region: IV | Comanche Peak | 28369 | 03/27/2012 05/07/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Report for Emergency Core Cooling System Pump Leaks |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedure and initiate a condition report for degradation of safety-related equipment. Specifically, the licensee failed to initiate a co
Region: IV | Comanche Peak | 28379 | 03/27/2012 05/07/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Past Operability Determination for Degraded Pressurizer Power Operated Relief Block Valve |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedure and perform an adequate operability evaluation to determine if a condition would have made a system inoperable in the past. Spe
Region: IV | Comanche Peak | 28380 | 03/27/2012 05/07/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Past Operability Determination for the Diesel Generators |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedure and perform an adequate past operability evaluation to determine if a condition would have made a system inoperable in the past
Region: IV | Comanche Peak | 28361 | 12/31/2011 02/09/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Remove Materials and Debris from Containment |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000445 Comanche Peak 1 |  | 71111.2 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the failure to follow procedure and remove items from containment. As a result, maintenance personnel failed to remove materials that could be transported to the contai
Region: IV | Comanche Peak | 28362 | 12/31/2011 02/09/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Reassemble a Motor Operated Valve |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 |  | 71111.2 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the failure to follow procedure and correctly restore motor operated valves. As a result, the licensee inverted the Unit 1 power operated relief valve block valves' lim
Region: IV | Comanche Peak | 28363 | 12/31/2011 02/09/2012 | 2011005-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide Guidelines for Protective Action Recommendations Outside the Emergency Planning Zone |  | P.2(b) Implementing Operating Experience | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.47(b)(10) for failure of the licensee to have guidelines developed and in place for the choice of protective actions during an emergency. Specifically, Procedure EPP 304, "Protective Action Reco
Region: IV | Comanche Peak | 28364 | 12/31/2011 02/09/2012 | 2011005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Adequate Radiation Surveys |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 20.1501(a) because radiation protection staff failed to perform an adequate survey to evaluate and determine the radiological hazards in the floor drain tank room. The licensee entered
Region: IV | Comanche Peak | 28365 | 12/31/2011 02/09/2012 | 2011005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiological Work Permit Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a for the failure of a worker to follow radiological work permit requirements. Specifically, a chemistry technician received a dose rate alarm greater than 120 m
Region: IV | Comanche Peak | 28366 | 12/31/2011 02/09/2012 | 2011005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Inadequate Auxiliary Feedwater Pump Bearing Oil Levels |  | P.1(b) Trend Performance CAP | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to promptly identify and correct adverse auxiliary feedwater pump oil levels. As a result, the inspectors id
Region: IV | Comanche Peak | 28357 | 09/17/2011 10/27/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Operator Licensing Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure the integrity of annual operating exams. During the 2009 annual operating exam, 17 licensed operators rec
Region: IV | Comanche Peak | 28359 | 09/17/2011 10/27/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure All License Conditions Are Met for Licensed Operators |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.11Q | The inspectors identified a noncited violation of 10 CFR 55.53, "Conditions of License," for the failure of the licensee to ensure that licensed operators met all the conditions of their licenses in order to be considered an active watch stander. Specific
Region: IV | Comanche Peak | 28360 | 09/17/2011 10/27/2011 | 2011004-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Supervision Causes Inadvertent Engineered Safety Features Actuation |  | H.1(c) Communication of Decisions | TE?: N | 05000445 Comanche Peak 1 |  | 71111.2 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the failure of the unit supervisor to adequately maintain responsibility for the operation of Unit 1 and the supervision of operations personnel during prep
Region: IV | Comanche Peak | 28353 | 07/28/2011 09/12/2011 | 2011006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Diesel Generator Jacket Water Instructions |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to have documented instructions for an activity affecting quality. Specifically, the licensee did not have documented instructions
Region: IV | Comanche Peak | 28355 | 07/28/2011 09/12/2011 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Determination Process for a Degraded Condition Related to Emergency Diesel Generator |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a Green noncited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of the licensee to follow the operability determination Procedure ODA-309, "Operability Determ
Region: IV | Comanche Peak | 28356 | 07/28/2011 09/12/2011 | 2011006-04 | NRC | NCV | Mitigating Systems | Green | Repeated Diesel Generator Cam Cover Bolt Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a Green noncited violation of Title 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," in that the licensee did not correct a condition adverse to quality regarding the safety related emergency diesel generators. Spe
Region: IV | Comanche Peak | 28319 | 06/18/2011 07/29/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | Inadequate External Flooding Instructions |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.01 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the failure to have adequate external flooding instructions. The licensee's technical requirements manual included circulating water system s
Region: IV | Comanche Peak | 28320 | 06/18/2011 07/29/2011 | 2011003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Properly Install Insulation Results in Frozen Feedwater Flow Sensing Lines |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71111.01 | The inspectors reviewed a self-revealing finding for the failure of the licensee to provide adequate instructions to maintenance personnel when installing insulation on feedwater flow sensing lines. As a result, three sensing lines froze and caused a feed
Region: IV | Comanche Peak | 28326 | 06/18/2011 07/29/2011 | 2011003-03 | NRC | NCV | Initiating Events | Green | Failure to Follow the Requirements of the Boric Acid Program |  | H.3(b) Work Activity Coordination | TE?: N | 05000446 Comanche Peak 2 |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure STA-737, "Boric Acid Corrosion Detection and Evaluation," Revision 5. Speci
Region: IV | Comanche Peak | 28327 | 06/18/2011 07/29/2011 | 2011003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Degraded Emergency Diesel Generator Fuel Line |  | H.3(a) Work Planning | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI for the licensee's failure to promptly correct a fuel leak on a diesel generator. As a result, the leak became significantly worse during diesel opera
Region: IV | Comanche Peak | 28328 | 06/18/2011 07/29/2011 | 2011003-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correct a Degraded Charging System Valve |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71152 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to correct a deficiency with a charging header vent valve. As a result, the valve failed open after an operator attempted
Region: IV | Comanche Peak | 28329 | 06/18/2011 07/29/2011 | 2011003-06 | NRC | FIN | Emergency Preparedness | Green | Failure to Update Severe Accident Management Guidelines |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a finding for the licensee's failure to follow procedure guidance and update the severe accident management guidelines. As a result, as of May 16, 2011, the severe accident management guidelines did not incorporate the latest own
Region: IV | Comanche Peak | 28335 | 06/18/2011 07/29/2011 | 2011003-07 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Maintenance Instructions Causes Inadvertent Valve Closure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000446 Comanche Peak 2 |  | 71153 | The inspectors identified a finding for the failure of the licensee to provide adequate procedure instructions for refueling the alternate power generators. As a result, during a station blackout event, the alternate power generators could have ran out of
Region: IV | Comanche Peak | 28336 | 06/18/2011 07/29/2011 | 2011003-08 | NRC | NCV | Barrier Integrity | Green | Failure to Develop Adequate Guidance for Extreme Damage Mitigation Procedures |  | H.2(d) Facilities & Equipment | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation of 10 CFR 50.54(hh)(2) for the licensee's failure to develop adequate guidance to restore core and spent fuel cooling capabilities for a postulated loss of large areas of the plant. Specifically, the licensee
Region: IV | Comanche Peak | 28337 | 06/18/2011 07/29/2011 | 2011003-09 | NRC | FIN | Mitigating Systems | Green | Inadequate Alternate Power Generator Procedure |  | H.2(d) Facilities & Equipment | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a finding for the failure of the licensee to provide adequate procedure instructions for refueling the alternate power generators. As a result, during a station blackout event, the alternate power generators could have ran out of
Region: IV | Comanche Peak | 28342 | 05/03/2011 05/17/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Effective Corrective Actions for a Condition Adverse to Fire Protection |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05T | The team identified a noncited violation of License Condition 2.G for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified two examples where the licensee failed to imple
Region: IV | Comanche Peak | 28343 | 05/03/2011 05/17/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Mitigate or Correct Potential Single Spurious Fire Damage Scenario |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05T | The team identified a noncited violation of License Condition 2.G for failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to recognize that electrical cables for the pressur
Region: IV | Comanche Peak | 28351 | 05/03/2011 05/17/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Emergency Lights in Safe Shutdown Areas had an 8-Hour Capacity |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05T | The team identified a noncited violation of License Condition 2.G for failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to establish a maintenance and/or test program that
Region: IV | Comanche Peak | 28316 | 03/19/2011 05/03/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Emergency Boration Flow Path Isolated |  | H.4(a) Human Error Prevention | TE?: N | 05000446 Comanche Peak 2 |  | 71111.04Q | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the failure to implement a boric acid system procedure. As a result, an emergency boration flow path was isolated. The licensee entered the finding into the
Region: IV | Comanche Peak | 28317 | 03/19/2011 05/03/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Drill Evaluation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05A | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for the failure of the licensee to identify a critical item failure during an unannounced fire drill. As a result, the licensee evaluated the control room operators' perform
Region: IV | Comanche Peak | 28318 | 03/19/2011 05/03/2011 | 2011002-03 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct Safety Injection Reset Malfunction |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for the failure of the licensee to promptly identify and correct a safety injection reset malfunction caused by a design error. As a result, t
Region: IV | Comanche Peak | 28315 | 12/31/2010 01/24/2011 | 2010005-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Control of Test Equipment Causes Ground Interaction |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the failure to establish controls for grounded test equipment. As a result, the test equipment caused a ground interaction that degraded safety-related inst
Region: IV | Comanche Peak | 28307 | 11/04/2010 11/19/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Relevant Operating Experience Information into Station Procedures Regarding the Condensate Storage Tank and Diaphragm | EA Case: 2010044 | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 |  | 7111121 | The team identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion V, Instructions, Procedures, and Drawings, involving the failure of personnel to initiate a SmartForm to enter actual or potential adverse conditions into the corrective ac
Region: IV | Comanche Peak | 28308 | 11/04/2010 11/19/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control of the Diesel Generator Air Starting System |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, which states, in part, that all testing required to demonstrate that structures, systems, components will perform satisfactorily in service is identified a
Region: IV | Comanche Peak | 28309 | 11/04/2010 11/19/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Emergency Diesel Generator Frequency |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translate
Region: IV | Comanche Peak | 28310 | 11/04/2010 11/19/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Hydrogen Generation for Safety-Related and NonSafety-Related Batteries |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control which states, in part, that measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translated
Region: IV | Comanche Peak | 28314 | 11/04/2010 11/19/2010 | 2010006-06 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Design Features for Precluding or Minimizing Long- Term Accumulation of Water in Underground Conduits Contaning Medium Voltage Safety Related Cables |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control which states, in part, that measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translated
Region: IV | Comanche Peak | 28298 | 09/18/2010 11/01/2010 | 2010004-01 | NRC | NCV | Barrier Integrity | Green | "Failure to Consider Temperature Effects on Air Accumulator Overpressure Protection" |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion III, "Design Control" for the failure to consider the temperature effect on the pressurization of safety-related air accumulators for containment isolation valves in the mai
Region: IV | Comanche Peak | 28233 | 09/18/2010 11/01/2010 | 2010004-02 | NRC | FIN | Mitigating Systems | Green | "Failure to Correctly Evaluate Diesel Generator Past Operability" |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a finding for the failure of the licensee to adequately evaluate the past operability of the Unit 2 Train B diesel generator when its governor functioned in a droop mode during isochronous operations. As a result, the licensee's
Region: IV | Comanche Peak | 28302 | 09/18/2010 11/01/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | "Failure to Promptly Identify and Correct a Diesel Generator Frequency Degradation" |  | H.4(a) Human Error Prevention | TE?: N | 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for the failure of the licensee to promptly identify and correct a diesel generator operating in a droop condition instead of the isochronous
Region: IV | Comanche Peak | 28297 | 06/19/2010 07/29/2010 | 2010003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow the Radiation Work Permit Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 |  | NONE | Inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure of a rigger to follow radiation work permit requirements. Specifically, a rigger made an unauthorized entry into a high radiation area on a radiation work permit
Region: IV | Comanche Peak | 28296 | 06/19/2010 07/29/2010 | 2010003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Barricade and Post a High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000445 Comanche Peak 1 |  | NONE | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.7.1.a for the failure to maintain a high radiation area barricaded and conspicuously posted. A high radiation area in the Unit 1 containment was posted as a radiation
Region: IV | Comanche Peak | 28295 | 06/19/2010 07/29/2010 | 2010003-03 | NRC | NCV | Initiating Events | Green | Inadequate Procedure Causes Inadvertent Power Reduction |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000445 Comanche Peak 1 |  | 71151 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, for the failure to have an adequate procedure for placing a demineralizer resin bed in service. As a result, a reactivity management event occurred when the reactor coolant
Region: IV | Comanche Peak | 28304 | 03/20/2010 04/29/2010 | 2010002-01 | Self - Revealed | NCV | Initiating Events | Green | Mispositioned Instrument Card Setting Causes Pressurizer Power Operated Relief Valve |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000446 Comanche Peak 2 |  | 71111.19 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the failure of maintenance personnel to follow procedural requirements for reinstalling a pressurizer pressure control card. As a result, when operators rai
Region: IV | Comanche Peak | 28305 | 03/20/2010 04/29/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Condition Report for Degraded Undervoltage Relay |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedures that require initiating a condition report for degradation to safety-related equipment. During a surveillance activity, mainten
Region: IV | Comanche Peak | 28306 | 03/20/2010 04/29/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Test a Check Valve by Positive Means |  | H.2(d) Facilities & Equipment | TE?: N | 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR 50.55a(f)(4)(ii) for the failure to test a safety-related check valve in accordance with the requirements of the American Society of Mechanical Engineers (ASME) Code. Specifically, the licensee test
Region: IV | Comanche Peak | 28289 | 12/31/2009 02/09/2010 | 2009005-01 | NRC | NCV | Barrier Integrity | Green | Inadequate procedure for environmentally qualified actuator refurbishment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure of the licensee to translate environmental qualification requirements for motor operated valve and damper actuators into procedures. Specifically,
Region: IV | Comanche Peak | 28290 | 12/31/2009 02/09/2010 | 2009005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Close the Containment Airlock Outer Door |  | H.1(c) Communication of Decisions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.2 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of maintenance personnel to follow procedural requirements for closing the containment personnel airlock outer door. As a result, the containment personn
Region: IV | Comanche Peak | 28291 | 12/31/2009 02/09/2010 | 2009005-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Control Reactor Coolant System Pressure During Solid Plant Operations |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000446 Comanche Peak 2 |  | 71111.2 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operators to follow procedural requirements for maintaining reactor coolant system pressure. Specifically, a reactor operator adjusted charging flow d
Region: IV | Comanche Peak | 28292 | 12/31/2009 02/09/2010 | 2009005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to barricade and post a high radiation area |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | A self-revealing noncited violation of Technical Specification 5.7.1.a was identified for failure to maintain a high radiation area barricaded and conspicuously posted. The lower valve gallery on the 832-foot elevation of the auxiliary building had been d
Region: IV | Comanche Peak | 28250 | 09/19/2009 10/27/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Seal Electrical Enclosure |  |  | TE?: N | 05000446 Comanche Peak 2 |  | 71111.05Q | The inspectors identified a Green noncited violation of License Condition 2.G for the failure of the licensee to seal a penetration in the Unit 2 train B safety chiller electrical cabinet. As a result, the equipment was vulnerable to water damage from a f
Region: IV | Comanche Peak | 28251 | 09/19/2009 10/27/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Failure To Seal Electrical Penetrations |  |  | TE?: N | 05000446 Comanche Peak 2 |  | 71111.06 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure of the licensee to follow the design basis and seal electrical penetration conduits in the containment spray pump rooms. As a result, the wa
Region: IV | Comanche Peak | 28283 | 09/19/2009 10/27/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Equipment |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.18 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a for failure to comply with the work control procedure which requires that all transient equipment be tracked. Specifically, the licensee placed a floating dock in the
Region: IV | Comanche Peak | 28284 | 09/19/2009 10/27/2009 | 2009004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Postfire Safe Shutdown Procedure |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for the failure to maintain adequate written procedures covering fire protection program implementation. Specifically, Procedure ABN 803A, "Response to a Fire in the Control
Region: IV | Comanche Peak | 28285 | 09/19/2009 10/27/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Assure That One Train of Equipment is Free From Fire Damage |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation of Unit 1 License Condition 2.G and Unit 2 License Condition 2.G. Specifically, the licensee failed to ensure that one train of the equipment required to achieve and maintain safe hot shutdown conditions rema
Region: IV | Comanche Peak | 28286 | 09/19/2009 10/27/2009 | 2009004-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for the failure to maintain adequate written procedures covering fire protection program implementation. Specifically, during operator walkthroughs, the inspectors identifie
Region: IV | Comanche Peak | 28262 | 08/14/2009 09/25/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions For Bailey/Asea Brown Boveri Positioners |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure of to promptly correct a condition adverse to quality when they did not apply thread sealant to safety-related atmospheric relief
Region: IV | Comanche Peak | 28278 | 06/20/2009 07/28/2009 | 2009003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Initiate Smart Form for Damage to Steam Generator Tubes Due to Loose Parts |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedures that require initiating a Smart Form for damage to safety-related equipment. The licensee failed to initiate a Smart Form when
Region: IV | Comanche Peak | 28275 | 03/21/2009 04/24/2009 | 2009002-01 | NRC | FIN | Initiating Events | Green | Failure to Remove Debris from Rooftop Causes Potential Missle Hazard |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 |  | 71111.13 | The inspectors identified a finding for the failure to follow housekeeping guidance in Procedure STA 607, "Housekeeping Control," Revision 19. Specifically, the licensee failed to remove several pieces of thin scrap sheet steel approximately five feet lon
Region: IV | Comanche Peak | 28276 | 03/21/2009 04/24/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Smart Form for Damage to Safety-Related Breakers |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to follow procedures that require initiating a Smart Form for damage to safety-related equipment. The licensee discovered a bent shutter pin in the inte
Region: IV | Comanche Peak | 28277 | 03/21/2009 04/24/2009 | 2009002-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure Causes Unplanned Load Change |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operators to follow procedural requirements when reducing turbine load. As a result, operators transposed two digits and inadvertently reduced turbine
Region: IV | Comanche Peak | 28265 | 12/31/2008 02/12/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Non-Seismic Scaffolding Installed Over Service Water Equipment |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.04Q | The inspectors identified a noncited violation of Technical Specification 5.4.1.a (Procedures), for the licensee's failure to erect scaffolding over safety-related equipment with adequate seismic supports. As a result, the scaffolding would likely fail du
Region: IV | Comanche Peak | 28266 | 12/31/2008 02/12/2009 | 2008005-02 | NRC | NCV | Initiating Events | Green | Failure to Adequately Evaluate Material Condition Following a Boric Acid Leak |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000445 Comanche Peak 1 |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to follow procedures that required an evaluation and corrective actions in response to the effects of a borated water leak on primary coo
Region: IV | Comanche Peak | 28271 | 12/31/2008 02/12/2009 | 2008005-03 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk Associated with Maintenance Activities |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 |  | 71111.13 | The inspectors identified three examples of a noncited violation of 10 CFR 50.65(a)(4) (Maintenance Rule) for the failure to adequately assess and manage the risk of maintenance activities during the outage. In two instances the licensee performed mainten
Region: IV | Comanche Peak | 28272 | 12/31/2008 02/12/2009 | 2008005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Instructions Leads to Failure to Identify Fibrous Material in Containment |  | H.3(a) Work Planning | TE?: N | 05000445 Comanche Peak 1 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.4.1a (Procedures) for the failure to have adequate instructions in place for containment walkdowns looking for fibrous material. As a result, the licensee entered a mode where the
Region: IV | Comanche Peak | 28273 | 12/31/2008 02/12/2009 | 2008005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Corrective Actions for the Malfunction of a Reactor Trip Bypass Breaker |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedures to enter a malfunction of a reactor trip bypass breaker into the corrective action program. The breaker tripped slower than per
Region: IV | Comanche Peak | 28274 | 12/31/2008 02/12/2009 | 2008005-06 | NRC | NCV | Initiating Events | Green | Failure to Have an Adequate Procedure to Test Main Steam Safety Valves |  |  | TE?: N | 05000446 Comanche Peak 2 |  | 71111.22 | The inspectors documented a self-revealing noncited violation of Technical Specification 5.4.1a (Procedures) for an inadequate test procedure that resulted in inadvertently holding open a main steam safety valve at power. During testing, a test engineer s
Region: IV | Comanche Peak | 28260 | 09/21/2008 11/05/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | "Failure to Control Transient Combustibles" |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05Q | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for the licensee's failure to obtain an approved transient combustible permit before introducing transient combustibles into plant areas. As a result, the licensee placed un
Region: IV | Comanche Peak | 28261 | 09/21/2008 11/05/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | "Failure to Follow Diesel Generator Test Procedure" |  | H.2(d) Facilities & Equipment | TE?: N | 05000446 Comanche Peak 2 |  | 71111.15 | A self-revealing noncited violation of Technical Specification 5.4.1.a was reviewed for the failure of the licensee to follow the procedure for testing the emergency diesel generator. As a result, a cylinder indicator cock was left open and cylinder perfo
Region: IV | Comanche Peak | 28263 | 09/21/2008 11/05/2008 | 2008004-03 | NRC | NCV | Barrier Integrity | Green | "Unevaluated Temporary Modification of Containment Isolation Valve" |  | H.4(b) Procedural Compliance | TE?: N | 05000446 Comanche Peak 2 |  | 71111.18 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the licensee's failure to control a fire hose that was used to redirect the discharge of a vent chill water relief valve, which is also a containment isolation valve. As
Region: IV | Comanche Peak | 28264 | 09/21/2008 11/05/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | "Failure to Ensure Roll-up Fire Doors Complied With Fire Code" |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation of License Condition 2.G because the licensee failed to ensure that two fire-rated roll up doors complied with the mounting requirements in National Fire Protection Association (NFPA) 80 1977. Specifically, d
Region: IV | Comanche Peak | 28246 | 09/15/2008 10/21/2008 | 2008008-01 | NRC | NCV | Barrier Integrity | Green | B.5.b. Phase 2 and 3 Mitigating Strategy |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 2515/171 | This finding, affecting the Barrier Integrity Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-0
Region: IV | Comanche Peak | 28252 | 06/22/2008 08/04/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Protection Compensatory Actions During Refueling Outage. |  |  | TE?: N | 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation for failure to establish adequate compensatory measures for inoperable containment fire hose stations as required by the fire protection program as defined in Unit 2 License Condition 2.G. This resulted in a
Region: IV | Comanche Peak | 28253 | 06/22/2008 08/04/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Expeditiously Restore Fire Hose Stations in Containment to Service |  | H.3(b) Work Activity Coordination | TE?: N | 05000446 Comanche Peak 2 |  | NONE | The inspectors identified a noncited violation for failure to expeditiously return to service a manual isolation valve for fire protection water to containment as required by the fire protection program as defined in Unit 2 License Condition 2.G. This res
Region: IV | Comanche Peak | 28254 | 06/22/2008 08/04/2008 | 2008003-03 | NRC | FIN | Initiating Events | Green | Instrument Tubing Failure Causes Plant Trip |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000446 Comanche Peak 2 |  | NONE | The inspectors reviewed a self-revealing finding for the licensee's failure to follow a tubing installation specification when installing condenser vacuum instrument tubing. Specifically, the installation did not follow Tubing Specification CPSES-I-1018 f
Region: IV | Comanche Peak | 28258 | 06/22/2008 08/04/2008 | 2008003-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to barricade and conspicuously post a high radiation area |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspector identified a noncited violation of Technical Specification 5.7.1 because a high radiation area was not barricaded and conspicuously posted. The inspector identified dose rates as high as 109 millirems per hour at 30 centimeters in the compac
Region: IV | Comanche Peak | 28259 | 06/22/2008 08/04/2008 | 2008003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure a Flow Path for Containment Spray Pumps |  | H.4(b) Procedural Compliance | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for failure to implement Procedure OPT-435B. This resulted in the Unit 2 Train B containment spray pumps recirculation valves being closed when they were required to be ope
Region: IV | Comanche Peak | 28247 | 05/22/2008 07/03/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Suppression Systems |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71111.05T | A noncited violation of Unit 1, License Condition 2.G, "Fire Protection," was identified for the fire suppression systems in Fire Zones SE16 and SE18 (remote safety-related panels/Train B switchgear rooms) not being installed in accordance with the approv
Region: IV | Comanche Peak | 28249 | 05/22/2008 07/03/2008 | 2008006-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Post-Fire Safe Shutdown Procedures |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.05T | A noncited violation of Technical Specification 5.4.1.d was identified concerning the failure to maintain adequate written procedures covering fire protection program implementation. Specifically, procedures for operation of Valves 1-8000A and 1-8000B (po
Region: IV | Comanche Peak | 28242 | 02/28/2008 04/07/2008 | 2008007-02 | Self - Revealed | NCV | Public Radiation Safety | Green | "Failure to ship radioactive material corrrectly" |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112202 | The team reviewed a self-revealing, noncited violation of 10 CFR 71.5, which occurred when the licensee failed to ship radioactive material correctly. A radioactive shipment classified as an "excepted package-limited quantity" exceeded the external dose r
Region: IV | Comanche Peak | 28245 | 01/24/2008 02/29/2008 | 2007008-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Alarm Response Procedure for EDG Failure to Start |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 93812 | The inspectors identified a noncited violation of Unit 1 Technical Specification 5.4.1.a, "Procedures," for an inadequate alarm response procedure. The inspectors determined that Procedure ALM-1302A, "Diesel Generator 1-02 Panel," Revision 5, was inadequa
Region: IV | Comanche Peak | 28238 | 12/31/2007 02/08/2008 | 2007005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Use a Procedure Appropriate to the Circumstances Led to Inadvertent Actuations of the Turbine Drive Auxiliary Feedwater Pump |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000446 Comanche Peak 2 |  | 71152 | A Green self-revealing non-cited violation of Technical Specification 5.4.1.a was identified for the failure to use a procedure appropriate to the circumstances when performing maintenance on safety-related equipment. Specifically, on October 22, 2006, th
Region: IV | Comanche Peak | 28237 | 10/25/2007 02/08/2008 | 2007005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Evaluate Radiological Conditions |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspector reviewed a self-revealing non-cited violation of 10 CFR 20.1501(a) for failure to conduct a radiological survey. Specifically, on April 16, 2007, a worker's electronic dosimeter alarmed when the individual attempted to move a bag containing
Region: IV | Comanche Peak | 28236 | 09/25/2007 11/08/2007 | 2007007-01 | NRC | NCV | Initiating Events | Green | Failure to appropriately secure adjustment set screw resulted in RHR valve failure. |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to provide work instructions or procedures appropriate to the circumstances. Specifically, Work Order 3-05-333517-01 and Procedure INC-2085, "Rework and Repla
Region: IV | Comanche Peak | 28229 | 06/22/2007 08/05/2007 | 2007003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Evaluate Radiological Hazards |  | H.3(b) Work Activity Coordination | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of 10CFR20.1501(a) for the failure to adequately evaluate radiological conditions in a work area. While performing maintenance on proximity switch cable sleeves on an assembly from the spent fuel
Region: IV | Comanche Peak | 28230 | 06/22/2007 08/05/2007 | 2007003-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Provide a Detailed Work Plan |  | H.3(a) Work Planning | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure to develop an adequately detailed work plan for the maintenance of proximity switch sleeves which resulted in the internal contamination of one individual. S
Region: IV | Comanche Peak | 25843 | 06/22/2007 08/05/2007 | 2007003-04 | Self - Revealed | FIN | Initiating Events | Green | Inadequate restoration following valve maintenance |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71152 | The inspectors reviewed a self-revealing finding for the inadequate restoration from valve maintenance which resulted in a manual turbine runback. On November 30, 2006, while Unit 1 was at 100 percent power, the 2A Feedwater Heater Normal Level Control Va
Region: IV | Comanche Peak | 28228 | 03/23/2007 08/17/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform required inservice testing following pump replacement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000446 Comanche Peak 2 |  | 71111.22 | An NRC identified noncited violation of Technical Specification 5.4.1.e was identified for the failure to establish, implement and maintain written procedures for the inservice testing program. STA-711, "Inservice Testing Program for Pumps and Valves" req
Region: IV | Comanche Peak | 25846 | 12/31/2006 02/08/2007 | 2006005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to post a radiation area |  | H.4(a) Human Error Prevention | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of 10 CFR 20.1902 for a failure to post a radiation area. The posting deficiency was identified during an investigation of a dosimeter dose alarm in Auxiliary Building Room 208. A radiological sur
Region: IV | Comanche Peak | 25852 | 12/22/2006 02/05/2007 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | IMPROPER EVALUATION OF POSTMAINTENANCE TEST FOR INSERVICE TESTING CREDIT |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 7111121 | A noncited violation of Technical Specification 5.5.8 for inadequate inservice testing of safety related gate valves with stellite seats following maintenance. During maintenance a thin oxide coating forms on the internals of these valves, which acts as a
Region: IV | Comanche Peak | 25853 | 12/22/2006 02/05/2007 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | TWO CONTAINMENT SPRAY SYSTEM FUNCTIONS NOT DESCRIBED IN UFSAR OR DESIGN BASIS DOCUMENTS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000445 Comanche Peak 1 05000445 Comanche Peak 1 05000446 Comanche Peak 2 05000446 Comanche Peak 2 |  | 7111121 | A noncited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, with two examples, was identified for failure to correctly translate regulatory requirements and design bases associated with the containment spray system into specifications, d
Region: IV | Comanche Peak | 25851 | 12/20/2006 02/05/2007 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL TO EXCLUDE AIR FROM CONTAINMENT SPRAY PIPING |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7111121 | Two examples of 10 CFR 50, Appendix B, Criterion III violations were identified for failure to translate design basis into instructions, procedures, and drawings. The team found that surveillance testing drained water out of the containment sump suction l
Region: IV | Comanche Peak | 25845 | 10/18/2006 11/06/2006 | 2006004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Both Unit 1 Channels of Reactor Trip P4 Interlock Disabled in Mode 3 |  | H.4(b) Procedural Compliance | TE?: N | 05000445 Comanche Peak 1 |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for I&C technicians disabling both channels of P4 Reactor Trip Interlock in Unit 1, without procedural guidance, while performing main turbine stop/control valve leakage
Region: IV | Comanche Peak | 25841 | 06/23/2006 07/22/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Operators Unable to Meet Some Critical Action Times During Alternate Shutdown Walkthrough |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | NONE | The team identified a Green noncited violation of License Condition 2.G and Technical Specification 5.4.1.d for failure to complete simulated operator actions within analyzed times and for the inability to perform some of the required actions with five ex
Region: IV | Comanche Peak | 25842 | 05/19/2006 07/22/2006 | 2006003-01 | NRC | NCV | Occupational Radiation Safety | Green | Three Examples of a Failure to Conspicuously Post a Radiation Area |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112101 | The inspector identified three examples of a non-cited violation of 10 CFR 20.1902(a) because the licensee failed to conspicuously post a radiation area. Specifically, on May 18, 2006, two discrete radiation areas in the fuel building and one in the auxil
Region: IV | Comanche Peak | 25839 | 03/24/2006 05/04/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Receipt Inspection of Solenoid Valves |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | A self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," was identified for failing to assure that purchased equipment conform to the procurement documents. This failure r
Region: IV | Comanche Peak | 25840 | 03/24/2006 05/04/2006 | 2006002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to prevent foreign material from entering the station service water pump suction |  |  | TE?: N | 05000445 Comanche Peak 1 |  | 71153 | A self-revealing, noncited violation was identified for the failure to implement effective corrective actions to prevent recurrence of a significant condition adverse to quality as described in 10 CFR Part 50, Appendix B, Criterion XVI. During cleaning ac
Region: IV | Comanche Peak | 25847 | 03/17/2006 04/17/2006 | 2006008-01 | NRC | NCV | Public Radiation Safety | Green | Failure to train hazmat employees. |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112202 | The team identified a non-cited violation of 49 CFR 172.704(a) because the licensee failed to provide required training to hazmat employees involved in the shipment of radioactive material. The licensee did not provide general awareness training of the re
Region: IV | Comanche Peak | 25848 | 03/17/2006 04/17/2006 | 2006008-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to prevent radioactive material from being unconditionally released from a radiologically controlled area |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 7112203 | The team reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1, resulting from the licensee's failure to prevent radioactive material from being unconditionally released from a radiologically controlled area. On April 18, 2005, t
Region: IV | Comanche Peak | 124475 | 05/10/2019 |  | Licensee - Identified | LIV |  | Green | Inadequate Pressure Setpoint for PORV Accumulators |  |  | TE?: N | 05000445 Comanche Peak 1 05000446 Comanche Peak 2 |  | 71111.18
Region: IV | Cooper | 126287 | 12/31/2019 02/07/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Degraded Reactor Building Flood Seals |  | NPP | TE?: N | 05000298 Cooper | Protection Against External Factors | 71111.12 | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to assure that deficient reactor building penetration flood seals were promptly corr
Region: IV | Cooper | 126288 | 12/31/2019 02/07/2020 | 2019004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degraded Reactor Building Southeast Quad Fan Coil Unit Performance |  | H.14 - Conservative Bias | TE?: N | 05000298 Cooper | Equipment Performance | 71152 | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to assure that reactor building southeast quad fan coil unit FC-R-1E degraded perfor
Region: IV | Cooper | 125850 | 09/30/2019 10/30/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Protection Program Surveillance Requirements for a Fire Barrier Seal |  | P.1 - Identification | TE?: N | 05000298 Cooper | Protection Against External Factors | 71111.05Q | The inspectors identified a Green, non-cited violation of License Condition 2.C(4), “Fire Protection,” for the failure to implement in effect all provisions of the approved fire protection program. Specifically, prior to July 2, 2019, the licensee failed
Region: IV | Cooper | 125881 | 09/30/2019 10/30/2019 | 2019003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Take Required Actions of Technical Specification 3.5.2 for Reactor Pressure Vessel Water Inventory Control During Secondary Containment Work |  | H.5 - Work Management | TE?: N | 05000298 Cooper | Configuration Control | 71153 | The inspectors documented a self-revealed, Green, non-cited violation of Technical Specification 3.5.2, “Reactor Pressure Vessel Water Inventory Control,” for the licensee’s failure to take the technical specification required actions during a reactor pre
Region: IV | Cooper | 125141 | 06/30/2019 08/05/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operability in Accordance with Procedures for a High Pressure Coolant Injection System Degraded Condition |  | H.7 - Documentation | TE?: N | 05000298 Cooper | Equipment Performance | 71111.15 | The inspectors identified a finding of very low safety significance and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee’s failure to evaluate operability of the high pressure coolant injection system in accor
Region: IV | Cooper | 124783 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Configuration Control of a Fire Zone Boundary Barrier Resulting in a Fire |  | H.11 - Challenge the Unknown | TE?: N | 05000298 Cooper | Protection Against External Factors | 71152 | The inspectors reviewed a self-revealed, non-cited violation of License Condition 2.C(4), “Fire Protection,” for the failure to implement in effect all provisions of the approved fire protection program. Specifically, on September 19, 2018, the licensee f
Region: IV | Cooper | 25894 | 12/31/2018 01/28/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Nonconforming Safety-related Relays |  | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee’s failure to identify and correct a condition adverse to quality associated with safety-related low pressure coolant injection relays ins
Region: IV | Cooper | 25895 | 12/31/2018 01/28/2019 | 2018004-02 | NRC | NCV | Initiating Events | Green | Failure to Manage the Increase in Risk During Shutdown Cooling Maintenance |  | H.1 - Resources | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a Green, non-cited violation of 10 CFR 50.65(a)(4) for the licensee’s failure to manage the increase in risk that resulted from maintenance activities. Specifically, when the licensee removed shutdown cooling from service for pla
Region: IV | Cooper | 24405 | 09/30/2018 10/31/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Process Applicability Determination |  | H.5 - Work Management | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to follow Administrative Procedure 0.9, “Tagout,” Revision 88, for performing a monthly audit and Process Applicability Det
Region: IV | Cooper | 24406 | 09/30/2018 10/31/2018 | 2018003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Adequate Lubrication for Drywell Fan Coil Units |  | H.5 - Work Management | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a Green, self-revealed finding for the licensee’s failure to implement Work Order 5060136 during maintenance on the drywell fan coil units. Specifically, on October 26, 2016, during bearing replacement work on drywell fan coil, uni
Region: IV | Cooper | 24070 | 06/30/2018 07/25/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Alarm Procedure for Service Water Booster Pump Ventilation Manual Actions |  | H.3 - Change Management | TE?: N | 05000298 Cooper | Procedure Quality | 71111.18 | The inspectors identified a Green non-cited violation of Technical Specification 5.4, "Procedures," when the licensee failed to maintain Procedure 2.3_R-1 with the bounding time restrictions for required manual ventilation actions identified in Engineerin
Region: IV | Cooper | 24071 | 06/30/2018 09/26/2016 | 2018002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Adequate Work Instructions for Traversing In-Core Probe System Limit Switches |  | NPP | TE?: N | 05000298 Cooper |  | 71111.05XT | A self-revealed, Green, non-cited violation of Technical Specification 5.4, "Procedures," was identified when the licensee failed to maintain Procedure 14.2.14, "TIP Chamber Shield Maintenance," with adequate instructions for reinstalling the traversing i
Region: IV | Cooper | 24039 | 04/30/2018 06/13/2018 | 2018011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Extent of Condition of Surge Suppression Varistor Failures |  |  | TE?: N | 05000298 Cooper |  | 71111.21M | An NRC-identified, Green, Non-cited Violation of Title 10, Code of Federal Regulations Part 50, Appendix B, Criterion XVI, "Corrective Action," occurred when the licensee failed to correct conditions adverse to quality associated with the corrective actio
Region: IV | Cooper | 24040 | 04/30/2018 06/13/2018 | 2018011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Design control Measures are in Place Associated with RHR Service Water Booster Pump Room Cooling |  | H.6 - Design Margins | TE?: N | 05000298 Cooper |  | 71111.21M | An NRC-identified, Green, Non-cited Violation of Title 10, Code of Federal Regulations Part 50, Appendix B, Criterion III, "Design Control," occurred for failure to assure that applicable regulatory requirements and the design basis were correctly transla
Region: IV | Cooper | 24043 | 04/30/2018 06/13/2018 | 2018011-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Basis Calculation for the EDG Rooms Temperature Distribution |  | NPP | TE?: N | 05000298 Cooper |  | 71111.21M | An NRC-identified, Green, Non-cited Violation of Title 10, Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” occurred for the licensee’s failure to ensure design control measures provide for verifying or checking the adequa
Region: IV | Cooper | 24048 | 04/30/2018 06/13/2018 | 2018011-04 | NRC | NCV | Mitigating Systems | Green | Incorrect Classification of Potential Safety-Related Components |  | NPP | TE?: N | 05000298 Cooper |  | 71111.21M | An NRC-identified, Green, Non-cited Violation of Title 10, Code of Federal Regulations Part 50, Appendix B, Criterion III, “Design Control,” occurred for failure to assure that applicable regulatory requirements and the design basis were correctly transla
Region: IV | Cooper | 23529 | 04/16/2018 05/08/2018 | 2018010-01 | NRC | FIN | Emergency Preparedness | Green | Failure to Maintain Satellite Phones in Locations That Provide Reasonable Assurance They Will Remain Available Following All Beyond Design Basis External Events |  | H.3 - Change Management | TE?: N | 05000298 Cooper |  | 2515/191 | The NRC inspection team identified a Green finding related to the licensee’s failure to maintain the station satellite phones in locations that would provide reasonable assurance the phones would remain available following all beyond design basis external
Region: IV | Cooper | 22375 | 12/31/2017 02/12/2018 | 2017004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Procedure for Storage of Material in the Spent Fuel Pool |  | H.3 - Change Management | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee’s failure to maintain Maintenance Procedure 7.4.32, "Work Over, Near, or In Reactor Vessel, Dryer/Separator Storage Pool, or Spent Fuel Storage Pool," Rev
Region: IV | Cooper | 22376 | 12/31/2017 02/12/2018 | 2017004-02 | NRC | NCV | Initiating Events | Green | Failure to Correct Startup Transformer Bus Insulation Degradation in Accordance with the License Renewal Program |  | H.14 - Conservative Bias | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of License Condition 2.F for the licensee’s failure to implement a program in accordance with Cooper Nuclear Station License Renewal Commitment NLS2008071-14. Specifically, on September 27, 2017, the license
Region: IV | Cooper | 22377 | 12/31/2017 02/12/2018 | 2017004-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Tagout Process Resulting in a Hydrogen Leak |  | H.12 - Avoid Complacency | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed finding for the licensee’s failure to implement Administration Procedure 0.9, "Tagout," Revision 89, during planned maintenance on the main generator carbon dioxide purge line. Specifically, on November 14, 2017, wh
Region: IV | Cooper | 22642 | 12/18/2017 12/20/2017 | 2017012-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Inspection Activities for Emergency Transformer Bus | EA Case: 17-057 | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to implement Maintenance Procedure 7.3.41, "Examination and High Pot Testing of Non-Segregated Buses and Associated Equipment," Revi
Region: IV | Cooper | 22601 | 12/18/2017 12/20/2017 | 2017012-02 | NRC | NCV | Initiating Events | Green | Inadequate Testing Activities for Emergency Transformer Bus | EA Case: 17-057 | H.3 - Change Management | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to maintain Maintenance Procedure 7.3.41, "Examination and High Pot Testing of Non-Segregated Buses and Associated Equipment," Revision 10, to co
Region: IV | Cooper | 21643 | 11/13/2017 11/13/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure Suitability of Materials for the Reactor Building Northeast Fan Coil Unit |  | H.6 - Design Margins | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee’s failure to assure that appropriate measures were established for the selection and review for suitability of ap
Region: IV | Cooper | 21644 | 11/13/2017 11/13/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Instrument Uncertainty in Safety-Related Ventilation Surveillance Procedures |  | H.7 - Documentation | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for multiple examples of the licensee’s failure to assure that required testing was performed in accordance with written test procedures which inc
Region: IV | Cooper | 21645 | 09/30/2017 11/13/2017 | 2017003-03 | NRC | NCV | Barrier Integrity | Green | Loss of Control Room Ventilation Due to Inadequate Post-Maintenance Testing Activities |  | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee’s failure to assure that all testing required to demonstrate that the control room emergency filter system would perform satisfac
Region: IV | Cooper | 24753 | 08/03/2017 08/03/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess Operability of Technical Specification System Functions during Surveillance Testing |  | H.5 - Work Management | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to follow Station Procedure 0.26, "Surveillance Program," Revision 70, and to assess the operability of alternate shutdown reactor pressure inst
Region: IV | Cooper | 24761 | 08/03/2017 08/03/2017 | 2017002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Control Room Ventilation Due to Ineffective Preventive Maintenance Strategy |  | H.1 - Resources | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to maintain work order instructions for control room supply fan maintenance resulting in the loss of the control room emergency fil
Region: IV | Cooper | 24762 | 08/03/2017 08/03/2017 | 2017002-03 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Control Room Ventilation Due to Improper Switch Manipulation |  | H.11 - Challenge the Unknown | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to implement System Operating Procedure 2.2.38, "HVAC Control Building," Revision 43, during control building ventilation testing.
Region: IV | Cooper | 22614 | 06/29/2017 08/07/2017 | 2017010-01 | NRC | NCV |  | Green | Failure to adopt appropriate procedures in accordance with 10 CFR Part 21 |  |  | TE?: N | 05000298 Cooper |  | 71152B | The team identified a Green finding and associated Severity Level (SL) IV, non-cited violation of 10 CFR 21.21(a), for the licensee’s failure to adopt appropriate procedures to evaluate Part 21 deviations. Specifically, Procedure EN-LI-108, “10 CFR 21 Eva
Region: IV | Cooper | 24775 | 06/29/2017 08/07/2017 | 2017010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Accomplish Activities in Accordance with Documented Procedures for High Pressure Coolant Injection Failure |  | P.3 - Resolution | TE?: N | 05000298 Cooper |  | 71152B | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to accomplish activities affecting quality in accordance with Corrective Action Program Procedure
Region: IV | Cooper | 24783 | 06/29/2017 08/07/2017 | 2017010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor No. 2 Diesel Generator under 50.65(a)(1) due to Inadequate Maintenance Rule Evaluation |  | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71152B | The team identified a Green, non-cited violation of 10 CFR 50.65(a)(1)/(a)(2), for the licensee’s failure to perform an a(1) evaluation and establish a(1) goals when the No. 2 diesel generator (DG) a(2) preventive maintenance demonstration became invalid.
Region: IV | Cooper | 22603 | 05/17/2017 06/27/2017 | 2017009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Exceeding the Technical Specification Allowed Out of Service Time of the Division I RHR System |  | H.11 - Challenge the Unknown | TE?: N | 05000298 Cooper |  | 93812 | The team reviewed a self-revealed, non-cited violation of Technical Specification 3.5.1, "Emergency Core Cooling Systems – Operating," for the licensee’s failure to restore the Division I residual heat removal system (RHR) during clearance restoration, wh
Region: IV | Cooper | 22616 | 05/17/2017 06/27/2017 | 2017009-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement an Adequate Procedure for Equipment Control |  | H.1 - Resources | TE?: N | 05000298 Cooper |  | 93812 | The team reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee’s failure to maintain Station Procedure 2.0.2, "Conduct of Operations Procedure, Operator Logs and Reports," Revision 106, for conduc
Region: IV | Cooper | 24726 | 05/01/2017 05/01/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Alternate Shutdown Emergency Procedure |  | P.1 - Identification | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to maintain Emergency Procedure 5.1ASD, "Alternate Shutdown," Revision 17, for establishing reactor equipment cooling system flow to the high pre
Region: IV | Cooper | 24732 | 05/01/2017 05/01/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality Associated with the 250 Vdc Electrical System |  | P.2 - Evaluation | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to identify a condition adverse to quality associated with Station Procedure 2.2.2
Region: IV | Cooper | 24733 | 05/01/2017 05/01/2017 | 2017001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Condition Adverse to Quality |  | H.11 - Challenge the Unknown | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to identify a condition adverse to quality for Division 1 residual heat removal se
Region: IV | Cooper | 22374 | 05/01/2017 05/01/2017 | 2017001-04 | NRC | NCV | Mitigating Systems | Green | Failure to Address Nonconforming Pipe Thinning in Accordance with the ASME Code |  | H.6 - Design Margins | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4) for the licensee’s failure to use an approved method to disposition an American Society of Mechanical Engineers Code nonconforming condition in the residual heat removal service water
Region: IV | Cooper | 24738 | 05/01/2017 05/01/2017 | 2017001-05 | Self - Revealed | NCV | Initiating Events | Green | Loss of Shutdown Cooling due to Relay Maintenance |  | H.5 - Work Management | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to implement Maintenance Procedure 7.3.16, "Low Voltage Relay Removal and Installation," Revision 22, for relay replacement work. S
Region: IV | Cooper | 24748 | 05/01/2017 05/01/2017 | 2017001-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Install Correct Mechanical Stop and Verify Proper Operation |  | H.7 - Documentation | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 3.0.4 for the licensee's failure to install the correct reactor core isolation cooling pressure control valve, RCIC-AOV-PCV23, mechanical stop and verify proper operat
Region: IV | Cooper | 24618 | 12/31/2016 01/26/2017 | 2016004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Maintain Reactor Vessel Assembly Procedure to Ensure Adequate Moisture Separator Shielding |  | H.12 Avoid Complacency | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to ensure sufficient radiological work controls were in place when the reactor pressure vessel moisture separator was installed duri
Region: IV | Cooper | 24623 | 12/31/2016 01/26/2017 | 2016004-02 | NRC | NCV | Emergency Preparedness | Green | Failure of an Analysis to Demonstrate that Changes Did Not Reduce the Effectiveness of the Emergency Plan |  | H.3 Change Management | TE?: N | 05000298 Cooper |  | 71114.04 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(3) for the licensee's failure to perform an analysis demonstrating that proposed emergency plan implementing procedure changes did not reduce the effectiveness of the emergency plan. Speci
Region: IV | Cooper | 24624 | 12/31/2016 01/26/2017 | 2016004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Service Water Pump Maintenance Procedure |  | H.1 Resources | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 3.6.4.2, "Secondary Containment Isolation Valves," for the licensee's failure to maintain secondary containment isolation valve HV-AOV-265 operable as a result of erec
Region: IV | Cooper | 24628 | 12/31/2016 01/26/2017 | 2016004-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Main Steam System Operating Procedure |  |  | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to maintain Station Procedure 2.2.56, "Main Steam System," Revision 49, to prevent a main steam line high flow Group 1 primary conta
Region: IV | Cooper | 24597 | 09/30/2016 11/10/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for Reactor Equipment Cooling Pump B |  | P.2 Evaluation | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate the design basis into maintenance instructions for reactor equipment cooling pump B. Specific
Region: IV | Cooper | 24608 | 09/30/2016 11/10/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Low Pressure Injection/Spray Operable From Internal Flooding Hazards |  | H.7 Documentation | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 3.5.1, "Emergency Core Cooling Systems and Reactor Core Isolation Cooling System," for the licensee's failure to evaluate and implement adequate internal flooding protection compen
Region: IV | Cooper | 24609 | 09/30/2016 11/10/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Service Water Pump Maintenance Procedure |  |  | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to maintain a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, the licensee failed
Region: IV | Cooper | 24592 | 06/30/2016 07/29/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Meet Technical Specification Requirements for Traversing In-Core Probe B Ball Valve |  | H.14 Conservative Bias | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 3.6.1.3, "Primary Containment Isolation Valves," for the licensee's failure to maintain traversing in-core probe B ball valve, a primary containment isolation valve, operable for i
Region: IV | Cooper | 24593 | 06/30/2016 07/29/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Work Instructions for Post-Maintenance Testing of Safety-Related Ventilation Systems |  | H.5 Work Management | TE?: N | 05000298 Cooper |  | 71111.19 | The inspectors identified two examples of a non-cited violation of Technical Specification 5.4.1.a, associated with the licensee's failure to perform required post-maintenance testing for safety-related ventilation systems in accordance with documented in
Region: IV | Cooper | 24596 | 06/30/2016 07/29/2016 | 2016002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for High Pressure Coolant Injection System Electrical Circuit |  |  | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of design of the high pressure coolant injection auxiliary lube oil pump 125 Vdc
Region: IV | Cooper | 24584 | 03/31/2016 04/28/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow ASME Code Requirements when taking Corrective Actions for a Pump in the Required Action Range |  | P.2 Evaluation | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR 50.55a, "Codes and Standards," for the licensee's failure to follow the ASME Code for Operation and Maintenance of Nuclear Power Plants when addressing the performance of reactor equipment cooling
Region: IV | Cooper | 24585 | 03/31/2016 04/28/2016 | 2016001-02 | NRC | NCV | Barrier Integrity | Green | Failure to Assess Operability of Technical Specification System Functions during Surveillance Testing |  | H.5 Work Management | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to follow Station Procedure 0.26, "Surveillance Program," and assess the operability of high pressure coolant injection steam line isolation ins
Region: IV | Cooper | 24565 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Diesel Fuel Oil Cloud Point Acceptance Criteria not in accordance with ASTM D975, Revision 1989a |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper 05000298 Cooper |  | 71111.01 | The inspectors identified a non-cited violation of Technical Specification 5.5.9, "Diesel Fuel Oil Testing Program," for the licensee's failure to establish an emergency diesel generator fuel oil cloud point acceptance criterion in accordance with ASTM D9
Region: IV | Cooper | 24572 | 12/31/2015 02/11/2016 | 2015004-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform a Complete Evaluation of the Licensee Interface With Offsite Organizations |  | P.2 Evaluation | TE?: N | 05000298 Cooper 05000298 Cooper |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.54(t)(2), for the licensee's failure to include an evaluation of the adequacy of the interfaces with state and local governments in a review of emergency preparedness program elements in Audit 2
Region: IV | Cooper | 24547 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Turbine Building Design Calculation was Correct and Justified |  | H.14 Conservative Bias | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, as defined in º
Region: IV | Cooper | 24548 | 09/30/2015 11/12/2015 | 2015003-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Ensure Measurement Conditions were Consistent With Instrument Calibration |  | P.1 Identification | TE?: N | 05000298 Cooper |  | 71124.05 | The inspectors identified a non-cited violation of 10 CFR 20.1501(c) for the failure to ensure measurement conditions were consistent with instrument calibration parameters for the elevated release point monitor, compromising the ability to accurately d
Region: IV | Cooper | 24555 | 09/30/2015 11/12/2015 | 2015003-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Control Licensed Material |  | H.5 Work Management | TE?: N | 05000298 Cooper |  | 71124.08 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 20.1802 for the failure to control licensed material not in storage when the licensee sent 14 bags of radioactively contaminated dirt and debris to an off-site landfill for disposal.
Region: IV | Cooper | 24557 | 09/30/2015 11/12/2015 | 2015003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Primary Containment Atmosphere Sampling Procedure |  | H.12 Avoid Complacency | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to appropriately implement a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, on
Region: IV | Cooper | 24564 | 09/30/2015 11/12/2015 | 2015003-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Preclude Repetition for a Significant Condition Adverse to Quality |  |  | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," associated with the inadequate extent of condition and extent of cause evaluations to preclude repetition for a significant
Region: IV | Cooper | 24542 | 06/30/2015 08/11/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Failure to Prevent Reactor Thermal Power from Exceeding 2419 MWt for Preplanned Activity |  | H.14 Conservative Bias | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, associated with the licensee's failure to appropriately implement General Operating Procedure 2.1.10, "Station Power Changes," Revision 107. Specifically, the procedure
Region: IV | Cooper | 24535 | 06/26/2015 07/20/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate a Valve Degraded Condition before Returning the Valve to Service |  | H.4 Teamwork | TE?: N | 05000298 Cooper |  | 71152B | The team identified a non-cited violation of Technical Specification 5.4.1.a regarding implementation of maintenance procedures for work on safety-related motor-operated valves (MOVs). Specifically, a degraded component within the actuator was not evaluat
Region: IV | Cooper | 24536 | 06/26/2015 07/20/2015 | 2015008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Torque Fasteners on Emergency Diesel Generator Number 2 |  | P.3 Resolution | TE?: N | 05000298 Cooper |  | 71152B | The team reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which occurred when the licensee failed to include specific instructions in work orders with respect to the use of
Region: IV | Cooper | 24541 | 06/26/2015 07/20/2015 | 2015008-03 | NRC | NCV | Mitigating Systems | Green | Main Steam Isolation Valve Scram Closure Condition Prohibited By Technical Specifications |  | H.8 Procedure Adherence | TE?: N | 05000298 Cooper |  | 71152B | The team identified two examples of a non-cited violation of Technical Specification 3.3.1.1, "Reactor Protection System Instrumentation," required Action A, for the licensee's failure to place inoperable main steam isolation valve closure scram channels
Region: IV | Cooper | 24534 | 06/20/2015 06/22/2015 | 2015007-04 | NRC | VIO | Mitigating Systems | Green | Failure to Evaluate the Lack of Missile Protection on the Emergency Diesel Generator 1 and 2 Fuel Oil Storage Tank Vents |  | H.14 Conservative Bias | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green, cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Design control measures shall provide for verifying or checking the adequacy of design, such as by the performance of desi
Region: IV | Cooper | 24527 | 05/08/2015 06/22/2015 | 2015007-01 | NRC | NCV | Initiating Events | Green | Failure to Perform an Operability Review of a Condition Report |  | H.4 Teamwork | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented procedures of a type appropriate
Region: IV | Cooper | 24532 | 05/08/2015 06/22/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Maintain Design Modifications to Prevent Fire Protection System Water Hammer |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as by the performanc
Region: IV | Cooper | 24526 | 03/31/2015 05/01/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operations Procedure |  | H.12 Avoid Complacency | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, associated with the inadequate Operation's Procedure 2.2.7, "Condensate Storage and Transfer System," Revision 56. Specifically, the procedure did not require that the aff
Region: IV | Cooper | 24525 | 12/31/2014 02/11/2015 | 2014005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure for Post Maintenance Testing |  | H.2 Field Presence | TE?: N | 05000298 Cooper |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Special Procedure GEH-TP-116, "Procedure for the Operation
Region: IV | Cooper | 24521 | 09/30/2014 11/10/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.12 Avoid Complacency | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," associated with the licensee's failure to assess and document the basis for operability when a degraded or nonconforming cond
Region: IV | Cooper | 24523 | 09/30/2014 11/10/2014 | 2014004-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Follow a Requirement of the Emergency Plan |  | H.3 Change Management | TE?: N | 05000298 Cooper |  | 71114.05 | The inspectors identified a non-cited violation for the licensee's failure to follow the site emergency plan between March 6, 2008, and June 23, 2014, as required by 10 CFR 50.54(q)(2). Specifically, the licensee failed to store respiratory protection equ
Region: IV | Cooper | 24524 | 09/30/2014 11/10/2014 | 2014004-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct an Inaccurate Classification During a Drill |  | P.1 Identification | TE?: N | 05000298 Cooper |  | 71151 | The inspectors identified a non-cited violation for the licensee's failure to correct a deficiency occurring in a drill conducted on December 18, 2013, as required by 10 CFR 50.47(b)(14). Specifically, licensee evaluators failed to identify that the shift
Region: IV | Cooper | 24505 | 06/30/2014 08/12/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Requirements into Installed Plant Configurations |  |  | TE?: N | 05000298 Cooper |  | 71111.04Q | Inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis for applicable structures, systems, and components were correct
Region: IV | Cooper | 24519 | 06/30/2014 08/12/2014 | 2014003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Seismic Housekeeping Requirements for Scaffolding |  | H.9 Training | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of Station Procedure 0.41, "Seismic Housekeeping," Revi
Region: IV | Cooper | 24485 | 03/31/2014 05/15/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions for Maintenance Activities |  | H.8 Procedure Adherence | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to implement required risk management actions for maintenance activit
Region: IV | Cooper | 24486 | 03/31/2014 05/15/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.14 Conservative Bias | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to perform an adequate operability determination in accordance wit
Region: IV | Cooper | 24494 | 03/31/2014 05/15/2014 | 2014002-03 | NRC | NCVIV | MISC | Green | Failure to Evaluate Changes to Ensure They Did Not Require Prior Approval |  |  | TE?: Y SL-IV-NCVIV | 05000298 Cooper |  | 71152 | Inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Test, and Experiments," and associated Green finding, associated with the licensee's failure to adequately evaluate changes to determine if prior NRC approval is requ
Region: IV | Cooper | 24495 | 03/31/2014 05/15/2014 | 2014002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Tagout Procedure |  | H.12 Avoid Complacency | TE?: N | 05000298 Cooper |  | 71153 | Inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, associated with the licensee's failure to follow station procedures which resulted in secondary containment inoperability. Specifically, on January 6, 2014, a st
Region: IV | Cooper | 24478 | 12/31/2013 02/13/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," associated with the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, from July 2010 to pre
Region: IV | Cooper | 24481 | 12/31/2013 02/13/2014 | 2013005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions for Proposed Maintenance Activities |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness for Maintenance at Nuclear Power Plants," for the licensee's failure to implement required risk management actions during maintenance act
Region: IV | Cooper | 24482 | 12/31/2013 02/13/2014 | 2013005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," associated with the licensee's failure to perform an adequate operability determination in accordance with Station Procedure
Region: IV | Cooper | 24483 | 12/31/2013 02/13/2014 | 2013005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Implement a Radiation Protection Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71152 | Inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, associated with a radiation protection technician who failed to follow the requirements of Radiation Work Permit 2013-001, "Radiation Protection Activities," Revi
Region: IV | Cooper | 24471 | 09/21/2013 11/12/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Control Room Emergency Filter System Safety-related Air Operated Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure the correct materials were installed in the control room emergency filtration system air opera
Region: IV | Cooper | 24472 | 09/21/2013 11/12/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Goals and Monitor for the Roof Drain System |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," associated with the licensee's failure to establish goals per paragraph (a)(1), and monitor the perfor
Region: IV | Cooper | 24476 | 09/21/2013 11/12/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," associated with the licensee's failure to follow Station Procedure 0.5OPS, "Operations Review of Condition Reports/Operabilit
Region: IV | Cooper | 24477 | 09/21/2013 11/12/2013 | 2013004-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Provide a Staging Area for Augmented Emergency Response Personnel When the Site Is Not Accessible |  | H.2(d) Facilities & Equipment | TE?: N | 05000298 Cooper |  | 71114.05 | The inspector identified a non-cited violation of 10 CFR Part 50, Appendix E, IV.E(8)(d), for failure to implement by June 20, 2012, a facility that would be accessible even if the site is under threat of or experiencing hostile action to function as a st
Region: IV | Cooper | 24467 | 08/30/2013 09/30/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action for a Condition Adverse to Fire Protection |  |  | TE?: N | 05000298 Cooper |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C.(4), "Fire Protection," for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified that the license
Region: IV | Cooper | 24456 | 06/22/2013 08/06/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess Risk and Implement Risk Management Actions for Proposed Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified two examples of a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness for Maintenance at Nuclear Power Plants," for the licensee's failure to adequately assess risk and implement risk mana
Region: IV | Cooper | 24466 | 06/22/2013 08/06/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Station Procedure 0.5OPS, "Operations Review of Condition Reports/Ope
Region: IV | Cooper | 24446 | 03/29/2013 05/09/2013 | 2013009-01 | NRC | VIO | Mitigating Systems | Green | Failure to Maintain Seismic Qualification of Standby Liquid Control System | EA Case: 2013075 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152B | The team identified a Green violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that design basis requirements associated with the standby liquid control (SLC) system test tank were correctly tran
Region: IV | Cooper | 24436 | 03/23/2013 05/02/2013 | 2013002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the High Pressure Coolant Injection System |  |  | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors reviewed a self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to maintain design control of high pressure coolant injection relief valve HPCI-RV-12
Region: IV | Cooper | 24437 | 03/23/2013 05/02/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Internal Flooding Analysis |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis requirements, associated with the station's internal fl
Region: IV | Cooper | 24438 | 03/23/2013 05/02/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Station Procedure 0.5OPS, "Operations Review of Condition Reports/
Region: IV | Cooper | 24439 | 03/23/2013 05/02/2013 | 2013002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Work Instructions |  | H.3(a) Work Planning | TE?: N | 05000298 Cooper |  | 71111.17T | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for work instructions associated with the emergency diesel generator 1 voltage regulator cabinet that did not include a step to record the final thickness o
Region: IV | Cooper | 24440 | 03/23/2013 05/02/2013 | 2013002-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Implement a Radiation Protection Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1, associated with an operator who entered a high radiation/high-noise area contrary to an ALARA pre-job briefing and without high-noise dosimetry as required by
Region: IV | Cooper | 24445 | 03/21/2013 04/10/2013 | 2012301-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Maintain Initial Licensing Examination and Licensed Operator Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: Y SL-IV-NCVIV | 05000298 Cooper |  | NONE | The examiners identified a non-cited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure the integrity of initial licensing exams and licensed operator annual operating tests from 1997 to 2012.
Region: IV | Cooper | 24317 | 12/31/2012 02/14/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure for the Service Water Pump Room |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.01 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, associated with the inadequate Maintenance Procedures 7.2.15, "Service Water Pump Column Maintenance and Bowl Assembly Replacement," Revision 35, Maintenance Procedure 7.2
Region: IV | Cooper | 24318 | 12/31/2012 02/14/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of Roof Drains |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2), "Requirements for monitoring the effectiveness of maintenance at nuclear power plants." Specifically, the licensee failed to appropriately consider the availability of the reactor buil
Region: IV | Cooper | 24319 | 12/31/2012 02/14/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedural Requirements During Roof Inspection |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of Station Procedure 0.27.1, "Periodic Structural Inspe
Region: IV | Cooper | 24320 | 12/31/2012 02/14/2013 | 2012005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Consider All Relevant Information and Appropriately Assess Operability when a Degraded Nonconforming Condition was Identified |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-citied violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of Station Procedure 0.5OPS, "Operations Review of Con
Region: IV | Cooper | 24326 | 12/31/2012 02/14/2013 | 2012005-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Service Water Booster Pumps |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to correctly translate certain parts of the design bases into installed plant equipment.
Region: IV | Cooper | 24327 | 12/31/2012 02/14/2013 | 2012005-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiation Surveys Before Allowing Work to Commence |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a), "Standards for Protection against Radiation," Subpart F, "Surveys and Monitoring," associated with the licensee's failure to perform an adequate radiation survey to determ
Region: IV | Cooper | 24328 | 12/31/2012 02/14/2013 | 2012005-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, which resulted from a worker failing to follow radiation protection procedures. In response, the licensee investigated the occurrence, coached the individual
Region: IV | Cooper | 24290 | 12/31/2012 02/14/2013 | 2012005-08 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform an Adequate Radiological Survey |  | H.3(a) Work Planning | TE?: N | 05000298 Cooper |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a) for the licensee's failure to perform an adequate radiological survey. In response, the licensee immediately restricted access to the torus area, performed a follow-up surv
Region: IV | Cooper | 24435 | 12/31/2012 02/14/2013 | 2012005-09 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure and Initiate Condition Reports When Degraded Nonconforming Conditions Were Identified |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000298 Cooper |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," associated with the licensee's failure to follow the requirements of Station Procedure 0.5CR, "Condition Report Initiation
Region: IV | Cooper | 24295 | 09/26/2012 11/09/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Emergency Diesel Generators Voltage Regulator Cabinets |  |  | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis requirements associated with the emergency diesel generators'
Region: IV | Cooper | 24296 | 09/26/2012 11/09/2012 | 2012004-02 | NRC | VIO | Mitigating Systems | Green | Failure to Demonstrate that Emergency Diesel Generators can Perform Mutiple Air Starts from a Single Air Receiver |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.11Q | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the applicable design basis for applicable structures, systems, and components were correctly translated
Region: IV | Cooper | 24300 | 09/26/2012 11/09/2012 | 2012004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Reactor Equipment Cooling System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to correctly translate certain parts of the design bases into documents used to order an
Region: IV | Cooper | 24301 | 09/26/2012 11/09/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Control Vendor Changes to a Service Water Booster Pump |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the failure of the licensee to appropriately implement their configuration control process which resulted
Region: IV | Cooper | 24308 | 09/26/2012 11/09/2012 | 2012004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess and Manage Risk for Maintenance Activities That Affected the A Zurn Strainer |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately assess and manage the increase in risk associated with
Region: IV | Cooper | 24313 | 09/26/2012 11/09/2012 | 2012004-07 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Procedure Appropriate to the Circumstance of Assembling the Zurn Strainer |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" associated with the licensee's failure to provide complete, accurate, and up-to-date procedures for proper
Region: IV | Cooper | 24314 | 09/26/2012 11/09/2012 | 2012004-08 | NRC | NCV | Mitigating Systems | Green | Failure to Consider All Relevant Information and Appropriately Assess Operability When A Degraded Nonconforming Condition Was Identified |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of Station Procedure 0.5OPS, "Operations Review of Cond
Region: IV | Cooper | 24315 | 09/26/2012 11/09/2012 | 2012004-09 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct Exercise Performance Deficiencies |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71114.01 | The inspectors identified the licensee's failure to correct weaknesses occurring during the biennial emergency preparedness exercise conducted July 31, 2012. The licensee's failure to identify problems in implementing radiation protection measures for eme
Region: IV | Cooper | 24316 | 09/26/2012 11/09/2012 | 2012004-10 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Surveillance Procedures for Reactor Equipment Cooling |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the failure of the licensee to ensure compliance with the requirements of the station's S
Region: IV | Cooper | 24242 | 06/26/2012 08/02/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Postmaintenance Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors documented a self revealing, non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to develop and specify adequate postmaintenance testing requiremen
Region: IV | Cooper | 24243 | 06/26/2012 08/02/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Compliance with the Requirements of Station Troubleshooting Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors documented a self-revealing, non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the failure of the licensee to ensure compliance with the requirements of the station's t
Region: IV | Cooper | 24244 | 06/26/2012 08/02/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize the Need for An Evaluation and to Properly Document the Bases for Operability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified two examples of a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the failure of the licensee to recognize the need for an evaluation and to properly docum
Region: IV | Cooper | 24245 | 06/26/2012 08/02/2012 | 2012003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Standby Liquid Control System and Sumps Credited in the Internal Flooding Analysis |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to: (1) assure that the applicable seismic design basis requirements associated with the
Region: IV | Cooper | 24246 | 06/26/2012 08/02/2012 | 2012003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Furnish Evidence of an Activity Affecting Quality |  |  | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," associated with the licensee's failure to furnish evidence of an activity affecting quality associated with the emergency diesel ge
Region: IV | Cooper | 24247 | 06/26/2012 08/02/2012 | 2012003-06 | NRC | NCV | Mitigating Systems | Green | Design Changes Not Appropriately Approved by the Licensee |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that design changes were subject to design control measures commensurate with those applied to
Region: IV | Cooper | 24248 | 06/26/2012 08/02/2012 | 2012003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Changes for Adverse Impacts |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.18 | The inspectors identified four examples of a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow the requirements of station procedure 0.8, "10CFR50.59
Region: IV | Cooper | 24249 | 06/26/2012 08/02/2012 | 2012003-08 | NRC | NCV | Mitigating Systems | Green | Non-conservative Service Water Booster Pump A and D Differential Pressure Operability Limits During In-Service Surveillance Testing |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Controls," for the licensee's non-conservative service water booster pump A and D differential pressure operability limits. The licensee entered this defici
Region: IV | Cooper | 24250 | 06/26/2012 08/02/2012 | 2012003-09 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non cited violation of Technical Specification 5.4.1, associated with station personnel's failure to follow radiation work permit requirements. Specifically, inspectors observed workers breaching a contaminated system during pl
Region: IV | Cooper | 24281 | 06/26/2012 08/02/2012 | 2012003-10 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform a Radiation and Contamination Survey |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000298 Cooper |  | 71124.02 | The inspectors reviewed a self revealing, non cited violation of 10 CFR 20.1501(a) for the failure to perform adequate radiation and contamination surveys. Specifically, a survey was not performed prior to power washing the reactor vessel studs during rea
Region: IV | Cooper | 24282 | 06/26/2012 08/02/2012 | 2012003-11 | NRC | FIN | Occupational Radiation Safety | Green | ALARA Program Failed to Prevent Unintended Doses for Refueling Floor Activities |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 71124.02 | Inspectors identified a finding of very low safety significance for the failure to follow ALARA planning and control procedures to maintain doses ALARA for refueling floor activities covered under Radiological Work Package 2011 05. Specifically, the licen
Region: IV | Cooper | 24283 | 06/26/2012 08/02/2012 | 2012003-12 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Essential Ventilation System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that the control buildings essential ventilation system would maintain battery room tempera
Region: IV | Cooper | 24288 | 06/26/2012 08/02/2012 | 2012003-13 | NRC | NCV | Mitigating Systems | Green | Fail to Correct a Condition Adverse to Quality for Determining the Number of Multiple Starts for a Single Diesel Generator Starting Air Accumulator |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to prepare an adequate design calculation demonstrating that a single diesel generator starting air accumulator
Region: IV | Cooper | 24289 | 06/26/2012 08/02/2012 | 2012003-14 | NRC | NCV | Mitigating Systems | Green | Failure to Use Design-Basis Parameter Values in Design-Related Calculations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that design bases parameters documented in the Updated Safety Analysis Report were used for station
Region: IV | Cooper | 24253 | 06/15/2012 07/20/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Analyze Seismic Requirements for Service Water Instrument Rack |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly trans
Region: IV | Cooper | 24254 | 06/15/2012 07/20/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Resistance Values for the Preventative Maintenance of the Non-Segregated Phase Bus Duct |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A program shall be established to assure that all testing required to demonstrate that structures, systems, and components
Region: IV | Cooper | 24265 | 06/15/2012 07/20/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Address the Design Bases of the Battery Chargers Following Identification of an Undersized Fused Disconnect Switch Connecting the Swing Battery Chargers to the Direct Current (DC) Buses |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficienc
Region: IV | Cooper | 24266 | 06/15/2012 07/20/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Preventative Maintenance Program for Molded Case Curcuit Breakers |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly trans
Region: IV | Cooper | 24273 | 06/15/2012 07/20/2012 | 2012007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Have an Adequate Procedure for Erecting Flood Barriers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of Technical Specification 5.4.1.a, which states, in part, "Written procedures shall be established, implemented, and maintained, covering the procedures recommended in Regulatory Guide 1.33, Revision 2, Appe
Region: IV | Cooper | 24274 | 06/15/2012 07/20/2012 | 2012007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate all Design and Technical Data Available into the Operability Determinations for the Standby Liquid Control Tank and Test Tank |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation, with two examples, of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, p
Region: IV | Cooper | 24226 | 03/27/2012 05/10/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for Internal Flooding |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis requirements associated with the station's internal flooding
Region: IV | Cooper | 24227 | 03/27/2012 05/10/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Required Components in the Station's Maintenance Rule Monitoring Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified two examples of a non-cited violation of 10 CFR 50.65(b)(2)(i) associated with the licensee's failure to monitor nonsafety-related structures, systems or components that are relied upon to mitigate accidents or transients. Specif
Region: IV | Cooper | 24228 | 03/27/2012 05/10/2012 | 2012002-03 | NRC | NCV | Initiating Events | Green | Failure to Appropriately Manage Risk for Maintenance in the Station's Switchyard |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to manage risk associated with switchyard maintenance. Sp
Region: IV | Cooper | 24229 | 03/27/2012 05/10/2012 | 2012002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of Standby Liquid Control System |  |  | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis requirements associated with the standby liquid control syste
Region: IV | Cooper | 24230 | 03/27/2012 05/10/2012 | 2012002-05 | NRC | NCV | Mitigating Systems | Green | Unevaluated Pre-conditioning for Core Spray Motor-operated Valves prior to Conducting As Found In-service Surveillance Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Controls," for the licensee's unevaluated preconditioning of core spray motor operated valves prior to performing as-found inservice stroke time testing. Th
Region: IV | Cooper | 24235 | 03/27/2012 05/10/2012 | 2012002-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.22 | The inspectors identified two examples of a non-cited violation of Technical Specification 5.4.1, associated with station personnel's failure to follow radiation work permit requirements. Specifically, on two separate occasions inspectors observed differe
Region: IV | Cooper | 24236 | 03/27/2012 05/10/2012 | 2012002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Furnish Evidence of an Activity Affecting Quality |  |  | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50 Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," associated with the licensee's failure to furnish evidence of an activity affecting quality associated with the station's analys
Region: IV | Cooper | 24237 | 03/27/2012 05/10/2012 | 2012002-08 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Station Procedure Results in Inadequate Work Instructions |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71153 | The inspectors documented a self-revealing finding associated with the licensee's failure to ensure the requirements of Station Procedure 0-CNS-52, "Control of Switchyard and Transformer Yard Activities at CNS," Revision 22, were implemented. Specifically
Region: IV | Cooper | 24214 | 12/31/2011 02/10/2012 | 2011005-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post a High Radiation Area |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | NONE | The inspector identified a non-cited violation of Technical Specification 5.7.1, resulting from the licensee's failure to conspicuously post a high radiation area during Refueling Outage 26. As corrective action, the licensee immediately stopped work and
Region: IV | Cooper | 24215 | 12/31/2011 02/10/2012 | 2011005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Control and Continuous Coverage of a Locked High Radiation Area |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | NONE | The inspector identified a non-cited violation of Technical Specification 5.7.2, resulting from the licensee's failure to maintain controls by not providing continuous coverage in a posted locked high radiation area with dose rates greater than 1000 mrem
Region: IV | Cooper | 24216 | 12/31/2011 02/10/2012 | 2011005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedures for Dose Rate Alarms Received by Two Individuals |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | NONE | The inspector reviewed a self revealing, non-cited violation of Technical Specification 5.4.1, resulting from workers who failed to follow procedures to exit the area when two dose rate alarms were received while performing decontamination work in the rea
Region: IV | Cooper | 24217 | 12/31/2011 02/10/2012 | 2011005-05 | NRC | NCV | Emergency Preparedness | Green | Failure to Identify Deficient Performance During a Single-Facility Drill |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71151 | The inspector identified a non-cited violation of 10 CFR 50.47(b)(14) for failure to correct a deficiency in drill or exercise performance. Specifically, the licensee failed to identify an inaccurate protective action recommendation during the critique of
Region: IV | Cooper | 24224 | 12/31/2011 02/10/2012 | 2011005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Requirements into Installed Plant Configuration |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the design basis requirements associated with a turbine building high energy line break w
Region: IV | Cooper | 24197 | 09/23/2011 11/07/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Place the Essential Servicer Water System Strainers in (a)(1) |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65 (a)(2), requirements for monitoring the effectiveness of maintenance at nuclear power plants. Specifically the licensee failed to demonstrate that the performance of the essential service wate
Region: IV | Cooper | 24198 | 09/23/2011 11/07/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Reactor Building Drain Components and Steam Exclusion Doors that Affect Safety-related Systems in the Maintenance Rule Monitoring Program |  |  | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified two examples of a noncited violation of 10 CFR 50.65 (b)(2) for the licensee's failure to monitor nonsafety-related components whose failure could prevent safety-related systems from fulfilling their safety-related function. Spec
Region: IV | Cooper | 24208 | 09/23/2011 11/07/2011 | 2011004-03 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Maintenance Near Electrical Towers That Could Impact Initiating Events |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure of the licensee to adequately assess and manage the increase in risk associated
Region: IV | Cooper | 24207 | 09/23/2011 11/07/2011 | 2011004-04 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Maintenance Near an Operating Reactor Feed Pump That Could Impact Initiating Events |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65 (a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure of the licensee to adequately assess and manage the increase in risk associated
Region: IV | Cooper | 24209 | 09/23/2011 11/07/2011 | 2011004-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure Results in Personnel Contaminations |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71152 | The inspectors reviewed a self revealing, noncited violation of Technical Specification 5.4.1, resulting from a plant individual who failed to follow radiation work permit requirements and was contaminated as a result. The condition was detected when the
Region: IV | Cooper | 24211 | 09/23/2011 11/07/2011 | 2011004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Identify, Correct, and Prevent Recurrence of a Significant Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to implement adequate corrective actions to preclude recurrence of a significant condition adverse to quality. Spe
Region: IV | Cooper | 24212 | 09/23/2011 11/07/2011 | 2011004-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Inoperable Essential Pump |  |  | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion VII, Control of Purchased Material, Equipment, and Services, associated with the licensee's failure to have adequate receipt inspection procedures to establish measure
Region: IV | Cooper | 24188 | 06/24/2011 08/08/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Conditions Adverse to Quality |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with four examples of the licensee's failure to promptly identify and correct conditions adverse to quality. Specifically, the lic
Region: IV | Cooper | 24193 | 06/24/2011 08/08/2011 | 2011006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Take Action for an Ineffective Corrective Action |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct a condition adverse to quality. Specifically, the licensee determined that an interim corrective action to prevent
Region: IV | Cooper | 24194 | 06/24/2011 08/08/2011 | 2011006-05 | NRC | VIO | Mitigating Systems | Green | Failure to Correctly Translate Design Requirements into Installed Plant Configuration | EA Case: 2011176 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71152B | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure that the applicable design basis for applicable structures, systems, and components were correctly translated
Region: IV | Cooper | 23936 | 06/23/2011 08/05/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess Potential Adverse Effects On Internal Flooding Analysis |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the failure of the licensee to ensure compliance with the requirements of station Procedur
Region: IV | Cooper | 23941 | 06/23/2011 08/05/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Determinations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified multiple examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of EN-OP-104, "Operability Determinations
Region: IV | Cooper | 23942 | 06/23/2011 08/05/2011 | 2011003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure Results in Personnel Contaminations |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1, resulting from workers who entered a posted contamination area without required protective clothing and were contaminated as a result. The condition was detecte
Region: IV | Cooper | 24160 | 06/23/2011 08/05/2011 | 2011003-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71124.01 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1, resulting from workers who failed to follow radiation work permit requirements and entered a high radiation area, after climbing from one scaffold to another. A
Region: IV | Cooper | 24161 | 06/23/2011 08/05/2011 | 2011003-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correctly Translate Design Requirements into Installed Plant Configuration |  |  | TE?: N | 05000298 Cooper |  | 71152 | The inspectors documented a self revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that the applicable design basis for structures, systems, and components were c
Region: IV | Cooper | 24162 | 06/23/2011 08/05/2011 | 2011003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess and Manage Risk When Disabling A Hazard Barrier |  |  | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to perform an adequate risk assessment for a planned maint
Region: IV | Cooper | 24166 | 06/23/2011 08/05/2011 | 2011003-08 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Degraded Emergency Diesel Generator |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow written work instructions. Specifically, the inspectors identified that mainten
Region: IV | Cooper | 24181 | 06/23/2011 08/05/2011 | 2011003-09 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Reports for Nonconformances Identified During System Walk Downs |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of licensee personnel to follow the requirements of Procedure 0.5, "Conduct of the Condition Report Proces
Region: IV | Cooper | 24182 | 06/23/2011 08/05/2011 | 2011003-10 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct an Adverse Condition Related to Emergency Core Cooling System Venting |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000298 Cooper |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure of licensee personnel to take actions to promptly correct a condition adverse to quality. Specifically, the licensee did not take any interim acti
Region: IV | Cooper | 24167 | 05/03/2011 07/01/2011 | 2011008-01 | NRC | NCV | Occupational Radiation Safety | Green | Unclear Work Instruction |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1, for a failure to implement procedures described in Regulatory Guide 1.33, Appendix A. Specifically, the licensee failed to implement procedures that provide guidance on creat
Region: IV | Cooper | 24168 | 05/03/2011 07/01/2011 | 2011008-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Recognize Work Order Risk |  | H.3(a) Work Planning | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1, for failure to implement procedures described in Regulatory Guide 1.33, Appendix A. Specifically, the licensee failed to implement procedures that provide guidance on recogni
Region: IV | Cooper | 24176 | 05/03/2011 07/01/2011 | 2011008-03 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Implement Human Performance Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a finding for a failure to implement human performance procedures. Specifically, the licensee failed to implement procedures that provided guidance on conducting pre-job briefs, preparing work in the field, and informing technici
Region: IV | Cooper | 24177 | 05/03/2011 07/01/2011 | 2011008-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Revise An Unclear Work Instruction |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1, for a failure to comply with procedures described in Regulatory Guide 1.33, Appendix A. Specifically, the licensee failed to implement procedures and a work order instruction
Region: IV | Cooper | 24178 | 05/03/2011 07/01/2011 | 2011008-05 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate High Radiation Area Briefing |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.7.2, for the failure to adequately brief radiation workers entering a locked high radiation area. Specifically, the radiation protection pre-job briefing failed to make workers kn
Region: IV | Cooper | 24180 | 05/03/2011 07/01/2011 | 2011008-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Job Coverage Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of Technical Specification 5.4.1(a), for the failure to follow Radiation Procedure 9.EN-RP-141, "Job Coverage," Revision 8. Specifically, the radiation protection personnel were monitoring workers pulling the
Region: IV | Cooper | 23912 | 03/24/2011 05/03/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Evaluate All Senior Operator License Holders during Annual Operating Test |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR Part 55.59 (a)(2)(ii), "Requalification," for the failure of the licensee to ensure that three senior operator license holders were evaluated during the annual operating test to the appropriate leve
Region: IV | Cooper | 23913 | 03/24/2011 05/03/2011 | 2011002-02 | NRC | VIO | Initiating Events | Green | Failure to Assess and Manage Risk for Maintenance That Could Impact Initiating Events | EA Case: 2011090 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure of work control and operations personnel to adequately assess and manage the increas
Region: IV | Cooper | 23922 | 03/24/2011 05/03/2011 | 2011002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement Foreign Material Exclusion Controls |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement Procedure 0.45, "Foreign Material Exclusion Program," Revis
Region: IV | Cooper | 23923 | 03/24/2011 05/03/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Repeat Failure to Follow Procedure for Initiating Condition Reports |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," regarding the licensee's failure to follow the requirements of Administrative Procedure 0.5.CR, "Condition Report Initiation, Rev
Region: IV | Cooper | 23905 | 03/14/2011 03/17/2011 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Performance of the Emergency Lights Against the Maintenance Rule Criteria |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.05T | A noncited violation of 10 CFR 50.65(a)(2) was identified for the failure to monitor the performance of the emergency lighting system against the established performance criteria. The licensee included the emergency lighting system in the Maintenance Rule
Region: IV | Cooper | 23895 | 12/31/2010 02/10/2011 | 2010005-01 | NRC | FIN | Initiating Events | Green | Failure to Implement Fire Protection Plan Requirements Related to Hot Work Activities |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.05Q | The inspectors identified two examples of a finding for the failure of contract personnel to properly implement the requirements of the station procedure for control of hot work activities, where one instance resulted in a fire. Specifically, between Nove
Region: IV | Cooper | 23900 | 12/31/2010 02/10/2011 | 2010005-02 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Electrical Switchyard Impacting Maintenance |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the failure of operations and work control personnel to adequately assess and manage risk ass
Region: IV | Cooper | 23901 | 12/31/2010 02/10/2011 | 2010005-03 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess and Manage Risk During Maintenance Activities |  | P.2(b) Implementing Operating Experience | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors documented a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to perform an adequate risk assessment for the planned mai
Region: IV | Cooper | 23902 | 12/31/2010 02/10/2011 | 2010005-04 | NRC | VIO | Emergency Preparedness | Green | Failure to Have Guidelines for the Choice of Protective Actions During an Emergency Consistent with Federal Guidance | EA Case: 2010151 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71114.01 | A cited violation of 10 CFR 50.47(b)(10) was identified for failure to develop and have in place guidelines for the choice of protective actions during an emergency that were consistent with federal guidance. Federal guidance for the choice of protective
Region: IV | Cooper | 23903 | 12/31/2010 02/10/2011 | 2010005-05 | NRC | URI | MISC | Green | Diesel Generator Overspeed Governor Loose Bolting Issue |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | NONE | The inspectors identified an unresolved item associated with the loose bolting issue on the over speed governor of diesel generator two. Specifically, the issue concerns past operability of the diesel, adequacy of previous evaluations and corrective actio
Region: IV | Cooper | 23876 | 10/20/2010 12/03/2010 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design and Operating Requirements into Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 7111121 | The team identified four examples of a Green noncited violation of Technical Specification 5.4.1.a, which states in part that, "Written procedures shall be established, implemented, and maintained, covering the procedures recommended in Regulatory Guide 1
Region: IV | Cooper | 23877 | 10/20/2010 12/03/2010 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Failure to promptly Correct Conditions Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 7111121 | The team identified three examples of a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to ensure conditions adverse to quality were promptly corrected. Specifically, as of August 12, 2010, the l
Region: IV | Cooper | 23878 | 10/20/2010 12/03/2010 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Control |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 7111121 | The team identified three examples of a Green noncited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for failure to ensure that design information was correctly translated into station test procedures. Specifically, as of August 12, 20
Region: IV | Cooper | 23886 | 10/20/2010 12/03/2010 | 2010007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control |  | P.2(b) Implementing Operating Experience | TE?: N | 05000298 Cooper |  | 7111121 | The team identified seven examples of a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to establish measures to ensure that applicable regulatory requirements and the design bases were correctly transl
Region: IV | Cooper | 23887 | 10/20/2010 12/03/2010 | 2010007-05 | NRC | NCV | Mitigating Systems | Green | Ice Deflector Pontoon Barge Storage in Service Water Discharge Canal |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of design for the service water system. Specifically, prior to August 10, 2010, the licensee did not have
Region: IV | Cooper | 23893 | 10/20/2010 12/03/2010 | 2010007-07 | NRC | NCV | Mitigating Systems | Green | URI 05000298/2007011-07, Fuel Oil Storage Tank Required Submergence To Prevent Vortexing And Available Volume Are Marginal Without Accounting For Instrument Uncertainties |  |  | TE?: N | 05000298 Cooper |  | NONE | The team identified a Green noncited violation of CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to verify the adequacy of design for the diesel fuel oil transfer system. Specifically, the licensee failed to demo
Region: IV | Cooper | 23894 | 10/20/2010 12/03/2010 | 2010007-08 | NRC | NCV | Mitigating Systems | Green | URI 05000298/2007011-08, High Pressure Coolant Pump Swap-Over from Emergency Condensate Storage Tank to Torus Vortex Calculation |  |  | TE?: N | 05000298 Cooper |  | NONE | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to verify the adequacy of design for the high pressure coolant injection system. Specifically, prior to December
Region: IV | Cooper | 23873 | 10/08/2010 11/05/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Failure to Adequately Monitor the Performance of the Screen Wash System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified that the licensee failed to correctly determine that a plant power reduction caused by a clogged screen wash system for the circulating water system was a maintenance preventable functional failure that exceeded the plant level p
Region: IV | Cooper | 23874 | 10/08/2010 11/05/2010 | 2010004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure Results in Repeat Equipment Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing finding was identified for the licensee's failure to follow the guidance of Administrative Procedure 0.5.EVAL, "Preparation of Condition Reports," Revision 21. Specifically, corrective actions to fix the Reactor Recirculation Motor Genera
Region: IV | Cooper | 23863 | 06/23/2010 08/04/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Document Design of Service Water Discharge Piping in Plant Drawings |  |  | TE?: N | 05000298 Cooper |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR 50 App B Criterion III, "Design Control," in which the licensee failed to maintain accurate design drawings of the service water system discharge piping. Specifically, Drawing BR 2120, "Yard Circ. &
Region: IV | Cooper | 23864 | 06/23/2010 08/04/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Place the Essential 4160 Volt Alternating Current System Agastat Relays in (a)(1). |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2), requirements for monitoring the effectiveness of maintenance at nuclear power plants, for failure to demonstrate that the performance of the essential 4160 volt alternating current powe
Region: IV | Cooper | 23872 | 06/23/2010 08/04/2010 | 2010003-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Perform Required Maintenance Causes Unplanned Down Power |  |  | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing finding was identified for the licensee's failure to implement the preventive maintenance requirements of the vendor manual for the plant traveling water screens. Specifically, Vendor Manual 140, "Traveling Water Screen," Revision 35, con
Region: IV | Cooper | 23871 | 04/28/2010 08/04/2010 | 2010003-03 | Self - Revealed | NCV | Initiating Events | Green | Work Preparation Activities Cause Unplanned Increase in Reactor Power |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71153 | A self revealing noncited violation of 10 CFR 50.54.j was identified when the licensee failed to ensure that mechanisms which may affect reactivity are manipulated only with the knowledge and consent of a licensed operator at the controls. Specifically, a
Region: IV | Cooper | 23859 | 03/24/2010 05/05/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Repeat Failure to Follow Procedure for Initiating Condition Reports |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," regarding the licensee's failure to follow the requirements of Administrative Procedure 0.5, "Conduct of the Condition Reporting
Region: IV | Cooper | 23861 | 03/24/2010 05/05/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Service Water Pump Room Loss of Heat Calculation |  |  | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a noncited violation of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," for the licensee's use of an incorrect post-accident service water flow rate in the design basis calculation of record. Calculation NEDC 91-232
Region: IV | Cooper | 23844 | 12/31/2009 02/11/2010 | 2009005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Surveillance Procedure Causes Near Toxic Gas Release |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.05Q | A self-revealing noncited violation of Technical Specification 5.4.1.d, "Fire Protection Program Implementation" was identified for the licensee's failure to follow the requirements of Surveillance Procedure 6.FP.306, "Fire Detection Systems Semi-Annual E
Region: IV | Cooper | 23845 | 12/31/2009 02/11/2010 | 2009005-02 | NRC | FIN | Initiating Events | Green | Multiple Examples of a Failure to Follow Procedure For Extension Cord Configuration Control |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.05Q | The inspectors identified multiple examples of a finding for the licensee's failure to initiate condition reports as required by Administrative Procedure 0.36.7, "Electrical Cord Control/GFCI Program," to resolve extension cords which had been in place lo
Region: IV | Cooper | 23846 | 12/31/2009 02/11/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Set Goals and Monitoring for the Diesel Generator Lubricating Oil System |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(1) for the failure to monitor the performance of the diesel generator lubricating oil system against licensee-established goals in a manner sufficient to provide reasonable assurance that t
Region: IV | Cooper | 23847 | 12/31/2009 02/11/2010 | 2009005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Prescribed Risk Mitigating Action |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65.a (4) for the licensee's failure to manage the increase in risk that may result from proposed maintenance activities. Specifically, inspectors discovered that after the licensee had designated
Region: IV | Cooper | 23848 | 12/31/2009 02/11/2010 | 2009005-05 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Foreign Material in the Reactor Core |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify a condition adverse to quality. Specifically, the licensee failed to identify of foreign material in the rea
Region: IV | Cooper | 23849 | 12/31/2009 02/11/2010 | 2009005-06 | NRC | FIN | Initiating Events | Green | Maintenance Error Results in Recirculation Pump Trip |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.2 | The inspectors identified a finding for the licensee's failure to follow the requirements of Administrative Procedure 0.40, "Work Control Program," Revision 68. Specifically, a maintenance technician violated the procedure by attempting corrective mainten
Region: IV | Cooper | 23850 | 12/31/2009 02/11/2010 | 2009005-07 | Self - Revealed | NCV | Barrier Integrity | Green | Procedure Violation Results in Loss of Fuel Pool Cooling |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.2 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified regarding the licensee's failure to follow the requirements of System Operating Procedure 2.2.18, "4160V Auxiliary Power Distribution System." Specifically, operators pr
Region: IV | Cooper | 23852 | 12/31/2009 02/11/2010 | 2009005-08 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Establish an Adequate Procedure to Ensure Constant Communications in a Locked High Radiation Area |  | H.2(d) Facilities & Equipment | TE?: N | 05000298 Cooper |  | 7112101 | The inspectors identified a noncited violation of Technical Specifications 5.4.1 for a failure to establish a procedure with adequate provisions to control work inside a locked high radiation area. Specifically, although the licensee's procedure required
Region: IV | Cooper | 23853 | 12/31/2009 02/11/2010 | 2009005-09 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements in Two Instances |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 7112102 | The inspectors reviewed a self-revealing, noncited violation of Technical Specifications 5.4.1 involving two examples of a failure to follow Radiation Work Permit requirements. In the first example, workers were not monitored with telemetry and constant c
Region: IV | Cooper | 23854 | 12/31/2009 02/11/2010 | 2009005-10 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Diesel Generator 2 Oil Leakage |  | P.1(b) Trend Performance CAP | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," occurred for the licensee's failure to assure that a condition adverse to quality was corrected. Specifically, the licensee identified oil leakage on Diesel G
Region: IV | Cooper | 23855 | 12/31/2009 02/11/2010 | 2009005-11 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Preclude Repetition of Loss of Shutdown Cooling |  |  | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to preclude repetition of a significant condition adverse to quality, namely the loss of shutdown cooling caused by
Region: IV | Cooper | 23856 | 12/31/2009 02/11/2010 | 2009005-12 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure For Control of Material |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing finding was identified for the licensee's failure to follow Administrative Procedure 0.47, "Control of In-Process Material," Specifically, a maintenance technician violated the procedure by obtaining a spare o-ring from an uncontrolled to
Region: IV | Cooper | 23857 | 12/31/2009 02/11/2010 | 2009005-13 | Self - Revealed | NCV | Initiating Events | Green | Procedure Noncompliance Causes Fire in Heater Bay |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.d, "Fire Protection Program Implementation," was identified for the licensee's failure to follow Administrative Procedure 0.39, "Hot Work." Specifically, contractors under the licensee's
Region: IV | Cooper | 23837 | 09/23/2009 10/29/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Scaffold Procedure Threatens Fire Protection Equipment |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 71111.05Q | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a regarding regarding the licensee's failure to follow the requirements of Maintenance Procedure 7.0.7, "Scaffolding Construction and Control." Specifically, licensee pe
Region: IV | Cooper | 23838 | 09/23/2009 10/29/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Incorrect Assumptions and Loss of Configuration Control in Internal Flooding Analysis |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," regarding the licensee's failure to ensure that the design basis of certain structures, systems and components were translated into specif
Region: IV | Cooper | 23828 | 06/23/2009 08/03/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of the Diesel Generator Fuel Oil Transfer System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.12 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(2) for the failure by the licensee to demonstrate that the Train A diesel generator fuel oil transfer system performance was being effectively controlled through preventive maintenanc
Region: IV | Cooper | 23835 | 06/23/2009 08/03/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Freeze Protection Procedure Results in Loss of Condensate Storage Tank Vent Path |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.15 | A self-revealing noncited violation of very low safety significance (Green) of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was reviewed involving the licensee's failure to develop an adequate procedure for freeze pro
Region: IV | Cooper | 23836 | 06/23/2009 08/03/2009 | 2009003-03 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Tagout Results in Draining of Turbine Equipment Cooling System |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.01 | A self-revealing noncited violation of Technical Specification 5.4.1.a was reviewed when the licensee failed to follow the requirements of Administrative Procedure 0.9, "Tagout." This procedure violation resulted in an inadequate tagout for the station sa
Region: IV | Cooper | 23817 | 05/12/2009 06/09/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate corrective actions to repair a lubricating oil pipe |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for inadequate corrective actions to prevent recurrence of a significant condition adverse to quality. The licensee inappropriately changed the roo
Region: IV | Cooper | 23818 | 05/12/2009 06/09/2009 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Failure to perform effective common mode failure evaluation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," regarding failure to follow the requirements of Procedure ENN OP 104, "Operability Determinations," Revision 2. Specifically, the te
Region: IV | Cooper | 23819 | 05/12/2009 06/09/2009 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Failure to identify a condition adverse to quality |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," for the failure of maintenance personnel to initiate a condition report, as required by Procedure 0.5, "Conduct of The Condition Rep
Region: IV | Cooper | 23820 | 05/12/2009 06/09/2009 | 2009008-04 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate work instructions to perform maintenance |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 93812 | The team identified two examples of a noncited violation of Technical Specification 5.4.1.a for the failure of the licensee to provide work instructions appropriate to the circumstances. In the first example, the work orders generated to monitor vibration
Region: IV | Cooper | 23826 | 05/12/2009 06/09/2009 | 2009008-05 | NRC | NCV | Mitigating Systems | Green | Failures to identify nonconforming design characteristics |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000298 Cooper |  | 93812 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," for the failure of engineering personnel to review and accept a nonconforming pipe configuration. Specifically, wh
Region: IV | Cooper | 23827 | 05/12/2009 06/09/2009 | 2009008-06 | NRC | NCV | Mitigating Systems | Green | Failure to identify root cause of a significant condition adverse to quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify the root cause of a significant condition adverse to quality as required by Procedure 0.5.Root Cause, "Root Cause Analy
Region: IV | Cooper | 23816 | 04/10/2009 05/22/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Determinations of Degraded Agastat Timer Relays |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | NONE | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow the requirements of Procedure ENN OP 104, "Operability Determinations." Specifically, betwe
Region: IV | Cooper | 23810 | 03/24/2009 04/30/2009 | 2009002-01 | NRC | NCV | Initiating Events | Green | Procedure Violation Results in Exceeding Allowed Injection Pressure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when maintenance personnel exceeded the specified leak injection pressure by 900 psig. Specifically, on March 7, 2009, con
Region: IV | Cooper | 23811 | 03/24/2009 04/30/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Repeat Failure to Assess and Manage the Risk of Heavy Equipment Operations. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65.a(4) for the licensee's failure to assess and manage the risk of planned maintenance activities. Specifically, the licensee failed to include planned heavy equipment operations in the vicinity
Region: IV | Cooper | 23812 | 03/24/2009 04/30/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Incompatible Materials Installed in Diesel Fuel Oil System |  |  | TE?: N | 05000298 Cooper |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," regarding the licensee's failure to assure that appropriate quality standards are specified and included in design documents and that deviations
Region: IV | Cooper | 23813 | 03/24/2009 04/30/2009 | 2009002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Procedural Requirements for Tracking Control Room Deficiencies |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000298 Cooper |  | 71152 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow procedural requirements for tracking operator work arounds, operator burdens, or contr
Region: IV | Cooper | 23814 | 03/24/2009 04/30/2009 | 2009002-05 | NRC | NCV | Barrier Integrity | Green | Control Room Envelope Door Left Open Results in Loss of Safety Function |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred regarding the licensee's failure to follow the requirements of Administrative Procedure 0.16, "Control of Doors," when Door
Region: IV | Cooper | 23798 | 12/31/2008 02/09/2009 | 2008005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Misaligned Lubricating Oil Piping Causes Diesel Generator 2 Failure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.12 | A Green self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to establish measures to assure that long standing diesel generator 2 lube oil discharge piping misalign
Region: IV | Cooper | 23799 | 12/31/2008 02/09/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage the Risk of Heavy Equipment Operations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65.a(4) for the licensee's failure to assess and manage the risk of planned maintenance activities. Specifically, the licensee failed to include planned heavy equipment operations in the vi
Region: IV | Cooper | 23800 | 12/31/2008 02/09/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Determinations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 71111.15 | The inspectors identified four examples of a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure ENN OP 104, "Operability D
Region: IV | Cooper | 23801 | 12/31/2008 02/09/2009 | 2008005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Initiating Condition Reports |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified three examples of a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Administrative Procedure 0.5, "Cond
Region: IV | Cooper | 23804 | 12/31/2008 02/09/2009 | 2008005-05 | Self - Revealed | FIN | Public Radiation Safety | Green | Procedure Violation Causes Augmented Off-gas System Isolation |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing finding was identified regarding the licensee's failure to follow procedural requirements during system maintenance. Specifically, licensee personnel failed to heed a cautionary note in a maintenance procedure, resulting in an inadvertent
Region: IV | Cooper | 23805 | 12/31/2008 02/09/2009 | 2008005-06 | NRC | FIN | Mitigating Systems | Green | Improper Storage of Hazardous Chemicals |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a finding regarding the licensee's failure to comply with the requirements of the Material Safety Data Sheets for two hazardous chemicals stored in the protected area. Specifically, licensee personnel stored a 55 gallon barrel of
Region: IV | Cooper | 23806 | 09/21/2008 10/28/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess Potential Adverse Effects on Internal Flooding Analysis |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified two examples of a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to comply with the requirements of Engineering Procedure 3.3 SAFE, "Safety Assessm
Region: IV | Cooper | 23807 | 09/21/2008 10/28/2008 | 2008004-02 | NRC | NCV | Initiating Events | Green | Operator Error Results in Uncontrolled Reactivity Addition |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.2 | A self-revealing Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified regarding the licensee's failure to follow the requirements of Administrative Procedure 0-CNS-61, "CNS Reactivity Management Pr
Region: IV | Cooper | 23782 | 09/21/2008 10/28/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Restore Standby Gas System to Standby Lineup |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing Green NCV of TS 5.4.1.a was identified regarding the licensee's failure to follow the requirements of General Operating Procedure 2.1.22, "Recovering from a Group Isolation." Specifically, control room operators failed to restore Train B
Region: IV | Cooper | 23792 | 06/21/2008 08/04/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Manage Elevated Risk |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4) with three examples regarding the licensee's failure to manage the increase in risk that resulted from maintenance activities. Specifically, the licensee did not post protected equ
Region: IV | Cooper | 23793 | 06/21/2008 08/04/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Construct Drywell Shielding According to Design Documents |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to build a permanent drywell shielding system in accordance with the approved design doc
Region: IV | Cooper | 23794 | 06/21/2008 08/04/2008 | 2008003-05 | NRC | FIN | Initiating Events | Green | Failure to Follow Work Control Program Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.18 | A self-revealing Green finding was identified associated with the licensee's failure to follow Administrative Procedure 0.40, "Work Control Program," requirements that would have ensured the 4160 V bus breaker fuse maintenance would not trip reactor recir
Region: IV | Cooper | 23781 | 03/22/2008 05/06/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Scaffold Inspection Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.18 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a regarding the licensee's failure to follow the requirements of Maintenance Procedure 7.0.7, "Scaffolding Construction and Control." Specifically, licensee personnel fa
Region: IV | Cooper | 23756 | 12/31/2007 02/06/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Inaccurate Assumptions in Control Room Flooding Calculation |  |  | TE?: N | 05000298 Cooper |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to verify the adequacy of input assumptions to a design basis calculation. Specifically, a design basis control room flood
Region: IV | Cooper | 23757 | 12/31/2007 02/06/2008 | 2007005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate PMT Results in Inoperable Emergency Diesel Generator |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.19 | A self-revealing noncited violation of Technical Specification 5.4.1. a, "Written Procedures," was identified because the licensee failed to establish an adequate postmaintenance test procedure to verify component performance following maintenance. Specif
Region: IV | Cooper | 23758 | 12/31/2007 02/06/2008 | 2007005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Procedure Noncompliance Causes Reactor Equipment Cooling System Leakage |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1. a, "Written Procedures," was identified for the failure of maintenance personnel to follow procedures. Specifically, maintenance personnel failed to follow site administrative procedure
Region: IV | Cooper | 23766 | 12/31/2007 02/06/2008 | 2007005-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Tagout Procedure Results in Inadvertent Stroke of Motor Operated Valve |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Written Procedures," was identified involving an inadequate procedure for controlling work on energized circuits. Specifically, inadequate procedural guidance in Administrative Proce
Region: IV | Cooper | 23767 | 11/28/2007 12/06/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct battery surveillance requirements |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI for failure to correct a nonconservative technical specification. The licensee determined on March 14, 2007 that Technical Specification Surveillance Requirements 3.8.4.
Region: IV | Cooper | 23769 | 11/02/2007 01/25/2008 | 2007011-01 | NRC | NCV | Mitigating Systems | Green | Failure to consider vortexing and available net positive suction head impact on the emergency diesel fuel oil system |  | P.2(b) Implementing Operating Experience | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to verify the adequacy of design for the emergency diesel generator fuel oil system. Specifically,
Region: IV | Cooper | 23772 | 11/02/2007 01/25/2008 | 2007011-02 | NRC | NCV | Mitigating Systems | Green | Installation of essential electrical cable with inadequate fault current ratings and not in accordance with original design basis requirements |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for a design change, associated with the emergency diesel generator, that failed to be subjected to control measur
Region: IV | Cooper | 23773 | 11/02/2007 01/25/2008 | 2007011-03 | NRC | NCV | Mitigating Systems | Green | Failure to ensure design basis information remains consistent within affected design documents |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance, for the failure to correctly translate the emergency core cooling system design basis into instructions, procedur
Region: IV | Cooper | 23774 | 11/02/2007 01/25/2008 | 2007011-04 | NRC | NCV | Mitigating Systems | Green | Failure to comply with design control program requirements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to correctly translate the design basis into specifications, drawings, procedures, and instruction
Region: IV | Cooper | 23779 | 11/02/2007 01/25/2008 | 2007011-05 | NRC | NCV | Mitigating Systems | Green | Inadequate corrective actions associated with multiple workmanship issues on safety related valves |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," having very low safety significance for the failure to adequately evaluate the extent of equipment failures resulting from workmanship issues, and
Region: IV | Cooper | 23780 | 11/02/2007 01/25/2008 | 2007011-06 | NRC | NCV | Mitigating Systems | Green | Failure to comply with the requirements of 10CFR50.71.e and to assure the updated safety analysis report has the latest information developed |  |  | TE?: N | 05000298 Cooper |  | 7111121 | The team identified a noncited Severity Level IV violation for the failure to comply with the requirements of 10 CFR 50.71(e). The correct value for the automatic depressurization system accumulator minimum pressure was not used to revise the Updated Safe
Region: IV | Cooper | 23446 | 09/22/2007 10/25/2007 | 2007004-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Survey Radioactive Ellluents |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.22 | The inspector identified a noncited violation of 10 CFR 20.1302(a) because the licensee's surveys of effluents containing radioactive particulates originating in the multi-purpose facility were not adequate to ensure compliance with the dose limits for in
Region: IV | Cooper | 23447 | 09/22/2007 10/25/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Flow Erosion in Service Water Piping |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," regarding the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, a degraded condition that was disc
Region: IV | Cooper | 23448 | 09/22/2007 10/25/2007 | 2007004-03 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Requirements of Industrial Safety Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a Green finding regarding the licensee's failure to follow the requirements of industrial safety procedures. Specifically, licensee personnel violated the requirements of Administrative Procedure 0.36, "Industrial Safety Procedur
Region: IV | Cooper | 23755 | 09/22/2007 10/25/2007 | 2007004-04 | NRC | NCV | Emergency Preparedness | Green | Inadequate Procedural Guidance to Implement the Emergency Plan |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71153 | The inspectors identified a noncited violation of 10 CFR 50.47 (b)(4) regarding the licensee's failure to establish adequate procedural guidance to implement the emergency plan. Specifically, Emergency Plan Implementing Procedure 5.7.1, "Emergency Classif
Region: IV | Cooper | 23433 | 06/23/2007 07/26/2007 | 2007003-01 | NRC | NCV | Barrier Integrity | Green | Control Rod Mispositioned During Reactor Startup |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71111.2 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the inadequate isolation instructions contained in System Operating Procedure 2.2.8, "Control Rod Drive Hydraulic System." The use of these inadequate isolation inst
Region: IV | Cooper | 23431 | 06/23/2007 07/26/2007 | 2007003-02 | NRC | FIN | Occupational Radiation Safety | Green | ALARA Finding with three examples |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 7112102 | The inspector reviewed a self-revealing ALARA finding with three examples. The collective dose of three work activities exceeded five person-rem and the planned doses by more than 50 percent. Valve work accrued 34.829 person-rem and exceeded the dose esti
Region: IV | Cooper | 23440 | 06/23/2007 07/26/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | Entry Into the Stability Exclusion Region of the Power to Flow Map |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified involving an inadequate procedure for transitioning to single recirculation loop operation during power operations. This procedural inadequacy resulted in operators ente
Region: IV | Cooper | 23441 | 06/23/2007 07/26/2007 | 2007003-04 | NRC | NCV | Mitigating Systems | Green | Operator Error Leads to Draining RHR Loop |  | H.4(a) Human Error Prevention | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified involving the failure to follow the procedural requirements of System Operating Procedure 2.2.69.3, "RHR Suppression Pool Cooling and Containment Spray." This procedural
Region: IV | Cooper | 23445 | 06/23/2007 07/26/2007 | 2007003-05 | NRC | NCV | Initiating Events | Green | Inadequate Equipment Isolation Instructions Results in Unisolable Leak and Reactor Scram |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the inadequate isolation instructions contained in System Operating Procedure 2.2.8, "Control Rod Drive Hydraulic System." The use of these inadequate isolation inst
Region: IV | Cooper | 23432 | 04/24/2007 05/22/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Conducting Maintenance on Emergency Diesel Generator 2 |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 93812 | The team identified three examples of a noncited violation of Technical Specification 5.4.1.a involving the licensee's failure to establish adequate maintenance procedures for maintenance activities on Emergency Diesel Generator 2. Specifically, these pro
Region: IV | Cooper | 23439 | 03/24/2007 05/01/2007 | 2007002-01 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Results in a Loss of Shutdown Cooling |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.12 | A self revealing noncited violation of Technical Specification 5.4.1(a) was identified regarding the licensee's failure to establish an adequate maintenance procedure for Reactor Protection System Motor Generator Set B. On November 19, 2006, the voltage r
Region: IV | Cooper | 23427 | 03/24/2007 05/01/2007 | 2007002-02 | NRC | NCV | Initiating Events | Green | Inadequate Operating Procedures for Draining Main Steam Lines |  |  | TE?: N | 05000298 Cooper |  | 71152 | A self revealing noncited violation of Technical Specification 5.4.1(a) was identified for licensee's failure to establish adequate operating procedures for filling, venting, draining, and startup of the main steam system. This procedural inadequacy led t
Region: IV | Cooper | 23430 | 03/24/2007 05/01/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Condition Adverse to Quality on Safety-Related 4160 V Switchgear |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71152 | An NRC identified noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI was identified regarding the licensee's failure to correct a degraded condition on the safety-related switchgear. Misalignment between the breakers and the switchgear cubicl
Region: IV | Cooper | 23414 | 12/31/2006 02/02/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Medical Certification and Monitoring of Personnel Requiring Operator Licenses for Nuclear Power Plants |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000298 Cooper |  | 71111.11B | The inspector identified a non-cited violation of 10 CFR 55.21, "Medical Examination," and 10 CFR 55.23, "Certification." The inspector identified that the licensee failed to conduct all the medical testing required by American Nuclear Standards Institute
Region: IV | Cooper | 23419 | 12/31/2006 02/02/2007 | 2006005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Work Instructions |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71111.19 | A self-revealing non-cited violation of Technical Specification 5.4.1.a was identified regarding the licensee's failure to follow procedures for maintenance affecting the performance of safety-related equipment. Work Order 4514076 provided instructions to
Region: IV | Cooper | 23423 | 12/31/2006 02/02/2007 | 2006005-03 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify and Correct an Unanalyzed Condition in the Torus |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71111.2 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, involving the licensee's failure to promptly identify and correct a condition adverse to quality regarding an unanalyzed condition in the torus. Specifically, the inspec
Region: IV | Cooper | 23426 | 12/31/2006 02/02/2007 | 2006005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure Results in Safety-Related Valve Failure |  |  | TE?: N | 05000298 Cooper |  | 71111.22 | A self-revealing non-cited violation of Technical Specification 5.4.1a was identified for licensee's failure to establish adequate maintenance procedures for safety-related, motor-operated valves. Between 1993 and 2006, maintenance procedures for Limitorq
Region: IV | Cooper | 23425 | 12/31/2006 02/02/2007 | 2006005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Technical Specification 5.4.1.a Violation for Inadequate Procedure For Reactor Pressure Vessel Refueling Preparation |  | H.3(b) Work Activity Coordination | TE?: N | 05000298 Cooper |  | 7112101 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a involving the licensee's procedure for reactor pressure vessel refueling preparation was not adequate. The licensee's refueling procedure allowed the control r
Region: IV | Cooper | 23420 | 12/31/2006 02/02/2007 | 2006005-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Nonconforming Conditions in Safety-Related Motor-Operated Valves |  |  | TE?: N | 05000298 Cooper |  | 71152 | A self-revelaing,noncited violation of 10 CFR, Part 50, Appendix B, Criterion XVI, was identified regarding the licensee's failure to correct a nonconforming condition in safety-related, motor-operated valves. In 1994, Limitorque and the NRC notified the
Region: IV | Cooper | 23421 | 12/31/2006 02/02/2007 | 2006005-07 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degraded Condition on Service Water Strainer |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 71152 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI was identified regarding the licensee's failure to identify and correct age-related degradation in the motor coupling for Service Water Discharge Strainer A. Corrective maintenan
Region: IV | Cooper | 23424 | 12/31/2006 02/02/2007 | 2006005-08 | NRC | NCV | Barrier Integrity | Green | Operation of Reactor Above Total Core Flow Limit |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 71152 | The NRC identified a non-cited violation of Technical Specification 5.4.1.a regarding the licensee's failure to follow procedures for power operation and process monitoring. Specifically, the licensee operated the reactor above the total core flow limit,
Region: IV | Cooper | 23422 | 12/31/2006 02/02/2007 | 2006005-09 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Implement Vendor Recommendations Results in a Fire |  |  | TE?: N | 05000298 Cooper |  | 71153 | A self-revealing finding was identified regarding the failure to install heat trace on the standby liquid control system in accordance with the vendor manual. The heat trace was installed in 1994 without the required ground-fault circuit protection. This
Region: IV | Cooper | 23407 | 09/23/2006 11/07/2006 | 2006004-01 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment for Safety-Related Undervoltage Relay Testing |  | H.3(a) Work Planning | TE?: N | 05000298 Cooper |  | 71111.13 | The NRC identified a noncited violation of 10 CFR 50.65(a)(4) regarding the online risk evaluation for a surveillance test on safety-related undervoltage relays. On August 21, 2006, the licensee performed routine testing of the under-voltage relays for sa
Region: IV | Cooper | 23411 | 09/23/2006 11/07/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Requirements for Scaffolding Construction |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.15 | The NRC identified a noncited violation of Technical Specification 5.4.1.a regarding the licensee's failure to follow procedures for maintenance affecting the performance of safety-related equipment. Specifically, the inspectors discovered three examples
Region: IV | Cooper | 23412 | 09/23/2006 11/07/2006 | 2006004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Tracking Failed Control Room Annunciators |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71152 | The NRC identified a noncited violation of Technical Specification 5.4.1.a regarding the licensee's inadequate procedure for tracking abnormal, off-normal or alarm conditions. On August 11, 2006, during a review of operator work arounds, the inspectors id
Region: IV | Cooper | 23413 | 09/23/2006 11/07/2006 | 2006004-04 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify Reactor Operation in Excess of Licensed Thermal Power Limits |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000298 Cooper |  | 71152 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, regarding the failure to promptly identify a significant condition adverse to quality regarding operation of the reactor above the licensed thermal power limits for 3 da
Region: IV | Cooper | 23406 | 06/29/2006 07/17/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Respond to Control Room Alarms in Accordance with Plant Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000298 Cooper |  | 7111114 | The NRC identified two examples of a noncited violation of Technical Specification 5.4.1.a. In the first example, on June 20, 2006, operators failed to sound the fire alarm, announce the fire, and dispatch the fire brigade, as required by plant procedures
Region: IV | Cooper | 23404 | 06/24/2006 07/17/2006 | 2006003-01 | NRC | NCV | Initiating Events | Green | Failures to Properly Control Combustibles in the Plant |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000298 Cooper |  | 71111.05Q | The NRC identified a noncited violation of Technical Specification 5.4.1.d regarding the licensee's failure to implement fire protection program procedures. On April 11 and June 8, 2006, the inspectors identified a total of four examples of transient comb
Region: IV | Cooper | 23405 | 05/17/2006 07/17/2006 | 2006003-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Fire Fighting Standards |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000298 Cooper |  | 7111114 | The NRC identified a finding regarding the failure to implement fire fighting standards when responding to a possible fire in the radwaste building. On May 17, 2006, operators entered their emergency procedure for fires and dispatched the fire brigade in
Region: IV | Cooper | 23399 | 03/24/2006 05/05/2006 | 2006002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of Service Water Discharge Strainers |  |  | TE?: N | 05000298 Cooper |  | 71152 | The NRC identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," regarding the use of unqualified parts in the service water discharge strainers. Specifically, between 1994 and 2004, the mechanical components used in
Region: IV | Cooper | 23390 | 03/14/2006 04/25/2006 | 2005015-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Service Water Plugging Events |  |  | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure of the licensee to take adequate and timely corrective action to prevent recurrence of a significant condition adverse to quality. Specifically, the l
Region: IV | Cooper | 23401 | 03/14/2006 04/25/2006 | 2005015-03 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Commitment in Response to Generic Letter 89-13 |  |  | TE?: N | 05000298 Cooper |  | 93812 | The inspectors identified a Green finding for failure of the licensee to implement a commitment made to the NRC. Specifically, the licensee did not carry out the programmatic service water intake bay inspections described in their response to NRC Generic
Region: IV | Cooper | 23398 | 01/23/2006 05/05/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Renders Emergency Diesel Generator and One Offsite Power Source Inoperable |  |  | TE?: N | 05000298 Cooper |  | 71111.22 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified regarding the failure of operations personnel to follow procedures for testing safety-related undervoltage relays. Specifically, on January 23, 2006, two licensed operat
Region: IV | Cooper | 125686 | 09/05/2019 |  | Licensee - Identified | LIV |  | Green | (OUO-SRI) the licensee allowed a vehicle to be operated inside of the protected area without being properly escorted by an armed security officer. |  |  | TE?: N | 05000298 Cooper |  | 71130.02
Region: IV | Diablo Canyon | 126326 | 12/31/2019 01/23/2020 | 2019004-01 | NRC | NCV | Barrier Integrity | Green | Unevaluated Preconditioning of the Quick Opening Transfer Tube Closure |  | NPP | TE?: N | 05000323 Diablo Canyon 2 | SSC and Barrier Performance | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” because the licensee established unevaluated preconditioning, with a reasonable doubt of whether the preconditioning was acceptable, prior to perf
Region: IV | Diablo Canyon | 126039 | 12/31/2019 01/23/2020 | 2019004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to the Fire Protection Program |  | H.1 - Resources | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 | Protection Against External Factors | 71152 | The inspectors identified a Green, non-cited violation of Operating License DPR-82, License Condition 2.C.(4), "Fire Protection," Operating License DPR-80, License Condition 2.C.(5), "Fire Protection," and the requirements of National Fire Protection Asso
Region: IV | Diablo Canyon | 126477 | 12/31/2019 01/23/2020 | 2019004-04 | Self - Revealed | FIN | Barrier Integrity | Green | Human Performance Event Leads to Isolation of Seal Cooling to Reactor Coolant Pump 2-3 |  | H.12 - Avoid Complacency | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors reviewed a Green, self-revealed finding in that PG&E personnel failed to follow multiple station standards and procedures including OM15.ID8, “Human Performance Error Prevention Tools,” and AD2.ID1, “Procedure and Work Plan Use and Adherenc
Region: IV | Diablo Canyon | 125886 | 09/30/2019 10/30/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Structural Fire Barrier in an Approved Design Configuration |  | H.7 - Documentation | TE?: N | 05000323 Diablo Canyon 2 | Protection Against External Factors | 71111.05Q | The inspectors identified a Green, non-cited violation of Operating License DPR-82, License Condition 2. C. (4), “Fire Protection,” for the failure to control structural gap seal fire barrier configuration in accordance with the station’s NRC approved fir
Region: IV | Diablo Canyon | 125279 | 06/30/2019 08/01/2019 | 2019002-01 | Self - Revealed | NCV | Initiating Events | Green | Human Performance Event Leads to Inadvertent Unit 2 Bus F Vital Bus Transfer |  | H.12 - Avoid Complacency | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 | Equipment Performance | 71111.15 | The inspectors reviewed a Green, self-revealed non-cited violation of Technical Specification (TS) 5.4.1.a, “Procedures,” because PG&E personnel failed to follow the requirements of procedure STP M-75F, “4kV Vital Bus F Undervoltage Relay Calibration,” Re
Region: IV | Diablo Canyon | 125368 | 06/27/2019 08/01/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Improper Sequencing of Maintenance of 4160 Vac Sulfur Hexaflouride Circuit Breakers Prior to As-Found Tests |  | NPP | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.21M | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control.” Specifically, the licensee’s preventive maintenance procedures for safety-related 4160 Vac sulfur hexaflouride (SF6) breakers failed to inc
Region: IV | Diablo Canyon | 125386 | 06/27/2019 08/01/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedural Steps that Ensure 480 Volt Switchgear Room Ventilation Remained Functional |  | H.11 - Challenge the Unknown | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 | Equipment Performance | 71111.21M | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1.a for failure to establish, implement, and maintain maintenance procedures as recommended in NRC Regulatory Guide 1.33, Appendix A, Section 9, "Procedures for Performi
Region: IV | Diablo Canyon | 124692 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Promptly Correct an Adverse Condition Related to Reactor Coolant Pump Seal Damage |  | NPP | TE?: N | 05000275 Diablo Canyon 1 | Equipment Performance | 71152 | The inspectors reviewed a Green, self-revealed non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct a condition adverse to quality. Specifically, prior to Februa
Region: IV | Diablo Canyon | 124690 | 03/31/2019 05/10/2019 | 2019001-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Corrective Actions Leads to Increased Time at Yellow Risk and Lowered Inventory |  | P.3 - Resolution | TE?: N | 05000275 Diablo Canyon 1 | Configuration Control | 71152 | The inspectors reviewed a Green, self-revealed finding in that PG&E personnel failed to promptly correct a condition in accordance with OM7.ID1, “Problem Identification and Resolution.” Specifically, personnel did not promptly correct a condition associat
Region: IV | Diablo Canyon | 124689 | 03/31/2019 05/10/2019 | 2019001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Human Performance Event Leads to Sodium Hydroxide Leak and Loss of Level Indication for Containment Spray System Spray Additive Tank |  | H.12 - Avoid Complacency | TE?: N | 05000323 Diablo Canyon 2 | Equipment Performance | 71153 | The inspectors reviewed a Green, self-revealed non-cited violation of Technical Specification 5.4.1.a “Procedures,” because personnel failed to follow the requirements of MP I-12-L931, “Spray Additive Tank Level Channel 931 Calibration,” Revision 2. Speci
Region: IV | Diablo Canyon | 24413 | 09/30/2018 10/31/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Multiple Examples of Scaffolding in Place Greater Than 90 Days Without Required Evaluation |  | P.2 - Evaluation | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Procedures,” because PG&E personnel failed to follow the requirements of AD7.ID5, “Scaffold Material Structure.” Specifically, 20 instances of scaffold structur
Region: IV | Diablo Canyon | 24414 | 09/30/2018 10/31/2018 | 2018003-02 | NRC | NCV | Mitigating Systems | Green | 4 kV Vital Switchgear Room Ventilation Degraded or Non-Conforming Condition and Associated Compensatory Measure Not Corrected in a Timely Manner |  | H.1 - Resources | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B,Criterion XVI, “Corrective Action,” because PG&E personnel failed to promptly correct a degraded or non-conforming condition associated with an open operability condition. Spe
Region: IV | Diablo Canyon | 24380 | 07/25/2018 08/22/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Failure to install conduit to environmentally qualified solenoid valves in a manner to prevent moisture intrusion and accumulation within the solenoid enclosure |  | NPP | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.21N | The inspectors identified a Green finding and associated NCV of 10 CFR Part 50.49, “Environmental Qualification of Electric Equipment Important to Safety for Nuclear Power Plants,” for failure to install conduit to environmentally qualified solenoid valve
Region: IV | Diablo Canyon | 24044 | 05/03/2018 06/08/2018 | 2018008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Diesel Generator Air Inlet Boot Seal Critical Characteristics |  | NPP | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | A self-revealed, Green, non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criteria VII and XV, occurred when the licensee failed to ensure materials intended for installation in safety-related applications conformed to procurement requirements or,
Region: IV | Diablo Canyon | 24045 | 05/03/2018 06/08/2018 | 2018008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Emergency Diesel Generator 1-1 Cardox System Inoperability |  | H.14 - Conservative Bias | TE?: N | 05000275 Diablo Canyon 1 |  | 71152B | An NRC-identified, Green, Non-cited Violation of the licensee’s fire protection license condition occurred when licensee personnel failed to identify a trouble light lit on the DG 1-1 cardox fire protection system panel. The light, which had been lit for
Region: IV | Diablo Canyon | 23943 | 03/31/2018 04/24/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Troubleshooting Results in Reactor Trip Signal and Loss of Source Range Nuclear Instrument Power |  | H.5 - Work Management | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.2 | The inspectors reviewed a Green, self-revealed non-cited violation of Technical Specification 5.4.1.a “Procedures,” because PG&E personnel failed to follow the requirements of MA1.DC54, “Conduct of Maintenance,” Revision 15. Specifically, on March 20, 201
Region: IV | Diablo Canyon | 23508 | 03/31/2018 04/24/2018 | 2018001-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Operating Experience Procedures Results in Inadequate Screen of Operating Experience Report |  | NPP | TE?: N | 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a finding of very low safety significance (Green) because PG&E personnel failed to follow the requirements of OM4.ID3, “Operating Experience Program,” Revision 20. Specifically, PG&E personnel failed to screen relevant operating
Region: IV | Diablo Canyon | 22629 | 12/31/2017 02/06/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedural Guidance in Order to Prevent Relief Valve Seat Damage |  | NPP | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors identified a self-revealing, non-cited violation of Technical Specification (TS) 5.4.1, “Procedures,” for the licensee’s failure to provide adequate guidance in operating procedure OP K-11:I, “Operating the Nitrogen Supply System,” Revision
Region: IV | Diablo Canyon | 21631 | 09/30/2017 10/26/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions resulted in a Failure to Comply with Technical Specification 3.4.11 and an Emergency Declaration |  | H.13 - Consistent Process | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the failure of the licensee to identify and correct a condition adverse to quality. Specifically, the licensee failed to implement promp
Region: IV | Diablo Canyon | 23468 | 06/30/2017 08/10/2017 | 2017002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Expansion Scope of Risk-Informed Welds |  | H.3 - Change Management | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.08P | The inspectors identified a non-cited violation of the licensee's risk-informed inservice inspection program (which is their alternative to portions of the ASME Code, Section XI inservice inspection program approved in accordance with 10 CFR 50.55a(z)) fo
Region: IV | Diablo Canyon | 7921 | 06/30/2017 08/10/2017 | 2017002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Results in Partial Loss of Cooling Flow to Shutdown Cooling |  | H.14 Conservative Bias | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.2 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because PG&E personnel failed to follow the requirements of AD7.ID14, "Assessment of Integrated Risk," Revision
Region: IV | Diablo Canyon | 7914 | 12/31/2016 02/08/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Maintenance Procedure Resulted in Improper Configuration of Safety Related Equipment |  | H.7 Documentation | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a,"Procedures," for the failure to follow Procedure AD7.ID16, "Tool Pouch and MinorMaintenance Program," Revision 2. Specifically, the licensee failed to screen work on the s
Region: IV | Diablo Canyon | 7910 | 07/14/2016 08/26/2016 | 2016009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure affected the Performance of Safety-Related Emergency Diesel Generator |  | H.5 Work Management | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The inspectors assessed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee's failure to implement properly preplanned maintenance procedures that affected the performance of safety-related equipment. Sp
Region: IV | Diablo Canyon | 7904 | 06/30/2016 08/02/2016 | 2016002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Misplaced Spent Fuel Assembly in the Spent Fuel Pool |  | H.12 Avoid Complacency | TE?: N | 05000323 Diablo Canyon 2 |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification (TS) 5.4.1.a, "Procedures," for the licensee's failure to place a spent fuel assembly in its correct location in the spent fuel pool (SFP) in accordance with Procedure
Region: IV | Diablo Canyon | 7903 | 05/11/2016 06/07/2016 | 2016301-01 | NRC | NCV | Barrier Integrity | Green | Insufficient procedural direction contained within EOP E-2, Faulted Steam Generator Isolation |  | H.1 Resources | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The examiners identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, Procedure EOP E-2, "Faulted Steam Generator Isolation," does not contain sufficient procedural direction for
Region: IV | Diablo Canyon | 7870 | 03/31/2016 04/26/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequate Design Airflow for 480 volt AC Switchgear and 125 volt DC Inverter Rooms |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the design adequacy of the safety-related ventilation system for the 480-volt AC switchgear and 125-volt DC inverter
Region: IV | Diablo Canyon | 7876 | 03/10/2016 04/21/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate 480 Vac Motor Starters with Circuit Breaker Trip Settings Higher than Manufacturers' Specifications |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the use of alte
Region: IV | Diablo Canyon | 7877 | 03/10/2016 04/21/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct the Lack of Design Verification of 460 Vac Motors at Maximum Allowable Frequency |  | P.2 Evaluation | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficie
Region: IV | Diablo Canyon | 7886 | 03/10/2016 04/21/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Safety-Related Alternating Current and Direct Current Equipment Functionality at Maximum Allowable Voltages |  | H.6 Design Margins | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the use of alte
Region: IV | Diablo Canyon | 7887 | 03/10/2016 04/21/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Extent of Condition for a Degraded Condition on a Nonsafety-Related 4160 Vac Breaker |  | H.14 Conservative Bias | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Diablo Canyon | 7895 | 03/10/2016 04/21/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Voltage Effects of Limiting Design Basis Events on the 230 kV Offsite Power Circuit |  | H.6 Design Margins | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the performance
Region: IV | Diablo Canyon | 7896 | 03/10/2016 04/21/2016 | 2016007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Appropriate Load Tap Changer Timing Acceptance Criteria into Periodic Tests |  | H.6 Design Margins | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Instructions, procedures, or drawings shall include appropriate quantitative or qualitative acce
Region: IV | Diablo Canyon | 7865 | 12/31/2015 02/04/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Failure to Properly Evaluate for Aggregate Impact of Fire Impairments |  | H.4 Teamwork | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.d, "Procedures," for the failure to follow approved fire protection program procedures to review the fire impairments list to assess the aggregate impact on the fire protecti
Region: IV | Diablo Canyon | 7866 | 12/31/2015 02/04/2016 | 2015004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify a Cause and Implement Actions to Prevent Recurrence of a Significant Condition Adverse to Quality |  | H.14 Conservative Bias | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.08P | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI "Corrective Action," for the failure to identify the cause and take corrective action to prevent recurrence of a significant condition adverse to qua
Region: IV | Diablo Canyon | 7869 | 12/31/2015 02/04/2016 | 2015004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Design the Emergency Diesel Generators to operate under Worst Case Environmental Conditions |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III "Design Control," for the failure to implement design control measures to verify the adequacy of the Unit 1 emergency diesel generators (EDGs) cooling system desi
Region: IV | Diablo Canyon | 7862 | 09/30/2015 11/13/2015 | 2015003-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Document an Adequate Evaluation for a Change in Seismic Load Combination Methodology |  | H.6 Design Margins | TE?: Y SL-IV-NCVIV | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors identified a Severity Level IV, Green, non cited violation of 10 CFR 50.59(d)(1) which requires, in part, that the licensee shall maintain records of changes in the facility, of changes in procedures, and of tests and experiments made pursu
Region: IV | Diablo Canyon | 7864 | 09/30/2015 11/13/2015 | 2015003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Secure a Locked High Radiation Area |  | H.12 Avoid Complacency | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The inspectors reviewed a self-revealing non-cited violation (NCV) of Technical Specification 5.4.1(a), "Procedures," for failure to secure a locked high radiation area. Specifically, the padlock on the Letdown Filter 1-1 locking bar was found unlocked. U
Region: IV | Diablo Canyon | 7847 | 06/30/2015 08/07/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Pre-plan and Perform Maintenance on Hydrogen Guard Piping |  | H.6 Design Margins | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.05Q | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1 involving the failure to appropriately pre-plan and implement written procedures associated with configuration control of the hazard barrier hydrogen guard piping in t
Region: IV | Diablo Canyon | 7848 | 06/30/2015 08/07/2015 | 2015002-02 | Self - Revealed | NCVIV | Mitigating Systems | Green | Failure to Maintain Operator Licensing Examination Integrity | EA Case: 2015040 | H.1 Resources | TE?: Y SL-IV-NCVIV | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.11B | The inspectors reviewed a self-revealing, Severity Level IV non-cited violation of 10 CFR 55.49, "Integrity of Examinations and Tests," and an associated Green finding for the licensee's failure to provide adequate examination security measures during adm
Region: IV | Diablo Canyon | 7849 | 06/30/2015 08/07/2015 | 2015002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for High-Energy Line Break Vent Flow Path |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to ensure credited design features, such as flow vent paths, protect safety-related systems, from tempe
Region: IV | Diablo Canyon | 7853 | 06/30/2015 08/07/2015 | 2015002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Technical Specification 3.3.4 Not Met Due to Inoperable Remote Shutdown System Function |  | H.5 Work Management | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors reviewed a self-revealing Green, non-cited violation of Technical Specification 3.3.4 "Remote Shutdown System," for the licensee's failure to maintain adequate configuration control of fuses associated with an emergency diesel generator (ED
Region: IV | Diablo Canyon | 7854 | 06/30/2015 08/07/2015 | 2015002-05 | NRC | NCV | Initiating Events | Green | Failure to Appropriately Scope 230 KV Switchyard into the Maintenance Rule Monitoring Program |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71153 | The inspectors identified a Green, non-cited violation of 10 CFR 50.65(b)(2) for the licensee's failure to appropriately scope the 230 kV switchyard in the Maintenance Rule monitoring program. Specifically, from the inception of the facilities' monitoring
Region: IV | Diablo Canyon | 7861 | 06/30/2015 08/07/2015 | 2015002-06 | Self - Revealed | FIN | Initiating Events | Green | High Voltage Insulator Flashover Resulted in Loss of 230 kV Offsite Power and Start of Emergency Diesel Generators |  | H.5 Work Management | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71153 | The inspectors reviewed a self-revealing, Green finding for the licensee's failure to adequately implement procedure OM7.ID1, Problem Identification and Resolution, to prevent a high voltage insulator flashover event in the 230 kV switchyard that occurred
Region: IV | Diablo Canyon | 7844 | 03/31/2015 05/05/2015 | 2015001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Design Review of Emergency Diesel Generator 2-3 |  |  | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors documented a self-revealing violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that design control measures shall provide for verifying or checking the adequacy of design by the pe
Region: IV | Diablo Canyon | 7841 | 12/31/2014 01/29/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Protection Program |  | H.5 Work Management | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a non-cited violation of the licensee's approved fire protection program as defined in Diablo Canyon Unit 2 Facility Operating License Condition 2.C(4) for failure to effectively implement the fire protection program. Specificall
Region: IV | Diablo Canyon | 7842 | 12/31/2014 01/29/2015 | 2014005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Control Access to a High Radiation Area With Dose Rates Greater Than 1 Rem/Hour |  | H.12 Avoid Complacency | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.7.2 because the licensee failed to control access to a high radiation area with dose rates greater than 1 rem/hour. A radiation protection technician assumed respons
Region: IV | Diablo Canyon | 7843 | 12/31/2014 01/29/2015 | 2014005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Effectively Implement Risk Management Actions Associated with Safety-Related Emergency Diesel Generators |  | H.11 Challenge the Unknown | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50.65(a)(4) for failing to manage risk when a protected train emergency diesel generator was unexpectedly rendered inoperable while another train was being returned to service. Specifi
Region: IV | Diablo Canyon | 7831 | 09/19/2014 10/27/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Document Degraded Conditions in the Corrective Action Process |  | H.11 Challenge the Unknown | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and drawings," in that the licensee did not enter degraded conditions into the corrective action process. The inspectors identifie
Region: IV | Diablo Canyon | 7832 | 09/19/2014 10/27/2014 | 2014004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure Resulted in Improper Configuration of Safety Related Equipment |  | H.7 Documentation | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors reviewed a Green self-revealing, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for failure to implement properly preplanned maintenance procedures affecting the performance of safety-related equipment. Specifically,
Region: IV | Diablo Canyon | 7833 | 09/19/2014 10/27/2014 | 2014004-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Provide Adequate Procedural Guidance Resulting in a Loss of Unit 1 230kV Off-site Power |  | H.5 Work Management | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors reviewed a Green self-revealing finding for the licensee's failure to provide appropriate acceptance criteria to ensure work activities were satisfactorily accomplished. Specifically, the licensee failed to provide acceptance criteria for t
Region: IV | Diablo Canyon | 7838 | 09/19/2014 10/27/2014 | 2014004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Unnecessary Main Steam Safety Valve Lift |  | H.12 Avoid Complacency | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee failure to prescribe a procedure appropriate to the circumstances with respect to safety-related a
Region: IV | Diablo Canyon | 7823 | 09/12/2014 10/22/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Document Degraded Emergency Diesel Generator Fuel Injector Nozzles in the Corrective Action Program |  | P.1 Identification | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," in that the licensee did not enter degraded conditions into the corrective action process. The first example of this violation occurred in ten ide
Region: IV | Diablo Canyon | 7824 | 09/12/2014 10/22/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Technical Specification Surveillance Requirement for Emergency Diesel Generators |  | P.3 Resolution | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a Green non-cited violation of 10 CFR 50.36 for the licensee's failure to establish an appropriate surveillance test to demonstrate operability of its emergency diesel generators. After revising its emergency diesel generator loading a
Region: IV | Diablo Canyon | 7825 | 09/12/2014 10/22/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Longstanding Uncompensated Nonconforming Condition |  | H.14 Conservative Bias | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50 Appendix B Criterion XVI for the licensee's failure to take timely corrective actions. In 2011, the licensee identified a potential path for gas intrusion into the containment spray system,
Region: IV | Diablo Canyon | 7813 | 06/30/2014 08/08/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Associated with Seismic Induced Structural Interactions |  | P.1 Identification | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.04Q | The inspectors identified a Green non-cited violation of 10 CFR, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to properly identify and evaluate system interactions as required by the licensee's Seismically-In
Region: IV | Diablo Canyon | 7814 | 06/30/2014 08/08/2014 | 2014003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control with Respect to Seismic Induced System Interaction of Safety Related Components |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.04Q | The inspectors identified a Green non-cited violation of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to verify the adequacy of their design with respect to seismic induced system interaction of safety rel
Region: IV | Diablo Canyon | 7807 | 03/21/2014 04/23/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Assessment |  | P.2 Evaluation | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow the operability assessment procedure in considering the tornado atmospheric e
Region: IV | Diablo Canyon | 7812 | 03/21/2014 04/23/2014 | 2014002-02 | NRC | NCV | Initiating Events | Green | Inappropriate Fatigue Rule Waivers |  | H.1 Resources | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.2 | The inspectors identified a Green non-cited violation of 10 CFR 26.207(a) for Pacific Gas and Electric's (PG&E) inappropriate granting of waivers necessary to mitigate or prevent conditions adverse to safety, and to the extent practicable, rely on the gra
Region: IV | Diablo Canyon | 7806 | 12/31/2013 02/11/2014 | 2013005-04 | Self - Revealed | NCV | Barrier Integrity | Green | Loss of Control Room Ventilation System due to Inadequate Design Control |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71153 | The inspectors reviewed a Green self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after the licensee performed a design change to the control room ventilation system (CRVS) that resulted in none of the four
Region: IV | Diablo Canyon | 7805 | 10/14/2013 02/11/2014 | 2013005-03 | Self - Revealed | FIN | Initiating Events | Green | Auxiliary Feedwater Actuation Due to a Main Feedwater Pump Trip |  | H.3(a) Work Planning | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors reviewed a Green self-revealing finding due to an inadequate procedure for calibrating non-vital bus relays. This caused an initiating event due to a main feed pump trip and unplanned downpower transient to 50 percent power on Unit 1. Th
Region: IV | Diablo Canyon | 7800 | 09/20/2013 11/01/2013 | 2013004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Use Procedures to Perform Corrective Maintenance on an Emergency Diesel Generator. |  | H.4(a) Human Error Prevention | TE?: N | 05000275 Diablo Canyon 1 |  | 71152 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after the licensee performed corrective maintenance on a diesel fuel oil system leak without appropriate docu
Region: IV | Diablo Canyon | 7801 | 09/20/2013 11/01/2013 | 2013004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Valid EDG 2-1 Start Signal Caused by a Loss of 4 kV Class 1E Bus G |  | H.4(a) Human Error Prevention | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with troubleshooting of the Unit 2, 4kV bus G that resulted in an unplanned de-energization. This ca
Region: IV | Diablo Canyon | 7783 | 07/11/2013 08/22/2013 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Effects on the Emergency Diesel Generator Load Capability for Maximum Combustion Air Temperature Conditions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tran
Region: IV | Diablo Canyon | 7788 | 07/11/2013 08/22/2013 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Auxiliary Feedwater Pump Motor Capability for the Effects of Pump Maximum Breakhorsepower Conditions |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tran
Region: IV | Diablo Canyon | 7789 | 07/11/2013 08/22/2013 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Establishing Temporary Ventilation |  | H.2(d) Facilities & Equipment | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111121 | The team identified a Green non-cited violation associated with Technical Specification 5.4.1(a), "Procedures," which requires that written procedures be established, implemented, and maintained covering the applicable procedures in Regulatory Guide 1.33,
Region: IV | Diablo Canyon | 7804 | 07/10/2013 02/11/2014 | 2013005-02 | Self - Revealed | NCV | Initiating Events | Green | Reactor Trip due to a Lightning Arrester Flashover |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | The inspectors reviewed a Green self revealing non cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for failure to implement adequate oversight controls and risk assessment whil
Region: IV | Diablo Canyon | 7782 | 06/30/2013 08/12/2013 | 2013003-01 | NRC | NCV | Initiating Events | Green | Failure to Implement the Fire Protection Program Requirements for the Control of Transient Combustible Material | EA Case: 2012075 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | Green. The inspectors identified a Green non-cited violation of the licensee's approved fire protection program as defined in Diablo Canyon Facility Operating License Conditions 2.C(5) for Unit 1 and 2.C(4) for Unit 2 involving the failure to effectively
Region: IV | Diablo Canyon | 7779 | 03/23/2013 05/02/2013 | 2013002-01 | NRC | NCV | Initiating Events | Green | Failure To Provide Adequate Guidance To Address General Welding Standard Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.08P | On February 14, 2013, the inspectors observed field welders add a partial circumferential weld on one side of the pipe in efforts to repair the pipe misalignment prior to the completion of the final visual inspection. This action represents a violation of
Region: IV | Diablo Canyon | 7780 | 03/23/2013 05/02/2013 | 2013002-02 | NRC | NCV | Initiating Events | Green | Failure To Identify Existing Indications During Prior Ultrasonic Examinations Of Pressurizer Structural Weld Overlays |  |  | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR 50.55a(a)(3)(i), which requires that proposed alternatives to industry codes and standards provide an acceptable level of quality and safety. The NRC staff approved relief request REP 1 U2 da
Region: IV | Diablo Canyon | 7781 | 03/23/2013 05/02/2013 | 2013002-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Effectively Evaluate Design Change for High Voltage Bushing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors reviewed a self-revealing finding for failure to effectively and accurately evaluate all available resources to procure appropriate equipment for plant modifications. Specifically, design engineering staff was not effective in using applica
Region: IV | Diablo Canyon | 7767 | 12/31/2012 02/12/2013 | 2012005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Operability Evaluation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after personnel failed to adequately assess the impact of an unanalyzed condition on control room envelope operability.
Region: IV | Diablo Canyon | 7770 | 12/31/2012 02/12/2013 | 2012005-02 | NRC | NCV | Barrier Integrity | Green | Non-conservative Decision Making Resulted in a Violation of Technical Specification |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 3.7.10, "Control Room Ventilation System (CRVS)," after the control room envelope boundary for both units was inoperable for a greater duration than permitted by the out-of-service
Region: IV | Diablo Canyon | 7771 | 12/31/2012 02/12/2013 | 2012005-03 | NRC | NCV | Initiating Events | Green | Failure to Update Emergency Operating Procedures |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors identified a self-revealing non-cited violation of Technical Specification 5.4.1(b) for failure to maintain emergency operating procedures after personnel reviewing a temporary modification failed to identify and change affected emergency o
Region: IV | Diablo Canyon | 7772 | 12/20/2012 02/07/2013 | 2012008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Required Firewater System Configuration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111105P | The team reviewed a self-revealing non-cited violation of License Conditions 2.C(4) for Unit 1 and 2.C(5) for Unit 2, "Fire Protection Program," due to the licensee inadvertently isolating the firewater yard loop for approximately three days, reducing the
Region: IV | Diablo Canyon | 7778 | 12/20/2012 02/07/2013 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Compensatory Measures for Fire Protection Program Deficiencies |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111105P | The team identified a non-cited violation of License Conditions 2.C(4) for Unit 1 and 2.C(5) for Unit 2, "Fire Protection Program," due to the licensee's failure to establish or adequately implement compensatory measures for non-compliances with the licen
Region: IV | Diablo Canyon | 7766 | 09/30/2012 11/13/2012 | 2012004-01 | NRC | VIO | Mitigating Systems | Green | Inadequate Corrective Actions to Update the Final Safety Analysis Report Update (FSARU) with Required Information | EA Case: 2012238 | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-V-VIO | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors identified a cited violation of 10 CFR Part 50.71(e), "Maintenance of Records, Making of Reports," for failing to update the Final Safety Analysis Report. Specifically, the licensee failed to update the Final Safety Analysis Report to inclu
Region: IV | Diablo Canyon | 7755 | 06/22/2012 08/03/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Preferrd Offsite Power System Design Control |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.01 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after plant engineers failed to adequately translate regulatory requirements and the design bases into the offsite power interface calculation
Region: IV | Diablo Canyon | 7756 | 06/22/2012 08/03/2012 | 2012003-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform a 50.59 Evaluation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-IV-NCVIV | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.01 | The inspectors identified a non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," because the licensee failed to document an evaluation providing a basis that changes made to the facility and associated changes to Procedure OP J-2:VIII,
Region: IV | Diablo Canyon | 7757 | 06/22/2012 08/03/2012 | 2012003-03 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure for the Control of Tools for Use on Stainless Steel |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.08P | Inspectors identified a non-cited violation of Technical Specification 5.4.1.e, for the failure to follow procedures that ensured hand files and wire brushes designated for stainless steel weld preparation were stored and maintained separately from hand f
Region: IV | Diablo Canyon | 7760 | 06/22/2012 08/03/2012 | 2012003-04 | NRC | FIN | Initiating Events | Green | Feedwater System Weld Flaw |  | H.4(a) Human Error Prevention | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.08P | The inspectors identified a finding for failure to follow applicable ASME Code requirements prior to returning the feedwater system to service after code repairs for flow accelerated corrosion. The licensee failed to recognize a rejectable indication in f
Region: IV | Diablo Canyon | 7762 | 06/22/2012 08/03/2012 | 2012003-06 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedure Resulted in the Loss of Low Temperature Overpressure Protection System Safety Function |  | H.4(a) Human Error Prevention | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.2 | The inspectors identified a non-cited self-revealing violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," following the unplanned loss of the Unit 1 low temperature overpressure protection system during Mode 5 op
Region: IV | Diablo Canyon | 7763 | 06/22/2012 08/03/2012 | 2012003-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entering a High Raditation Area with Dose Rates Greater than 1.0 Rem/Hour withough knowing the Dose Rates in the Area |  | H.2(d) Facilities & Equipment | TE?: N | 05000275 Diablo Canyon 1 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.7.2, which was the result of a worker entering a high radiation area with dose rates greater than 1 rem/hour without knowing of the dose rates in the area. In respon
Region: IV | Diablo Canyon | 7751 | 03/23/2012 05/04/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate OperabilityDetermination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR, Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after operations personnel declared diesel generator 2-3 operable after failing to meet all surveillance test acceptance
Region: IV | Diablo Canyon | 7752 | 03/23/2012 05/04/2012 | 2012002-02 | NRC | VIO | Barrier Integrity | Green | Incomplete and Inaccurate Information Provided to the NRC in Response to Generic Letter 2003-01, "Control Room Habitability" | EA Case: 2012075 |  | TE?: Y SL-III-VIO | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.04Q | The inspectors identified a Green finding and Severity Level III violation of 10 CFR 50.9, "Completeness and Accuracy of Information," after Pacific Gas and Electric failed to submitted complete and accurate information in response to Generic Letter 2003-
Region: IV | Diablo Canyon | 7741 | 12/31/2011 02/14/2012 | 2011005-01 | NRC | NCV | Barrier Integrity | Green | Less than Adequate Evaluation of a Nonconforming Control Room Habitability Train |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after operations personnel failed to adequately evaluate the operability and extent of condition of a nonconforming control
Region: IV | Diablo Canyon | 7742 | 12/31/2011 02/14/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination for New Seismic Information |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric failed to evaluate the affect of new seismic information on the operability of plant structu
Region: IV | Diablo Canyon | 7733 | 09/25/2011 11/18/2011 | 2011004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain the Control Room Habitability System in the Design Configuration |  | H.3(a) Work Planning | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.04Q | The inspectors identified a Green noncited violation of Technical Specification 5.5.19, "Control Room Envelope Habitability Program," after the licensee failed to maintain the Unit 1 control room ventilation train in the design configuration. The inspecto
Region: IV | Diablo Canyon | 7735 | 09/25/2011 11/18/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain a Fire Barrier |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Facility Operating License Condition 2.C (4), "Fire Protection," after the licensee failed to maintain the integrity of a fire barrier. On July 21, 2011, the inspectors identified that Fire D
Region: IV | Diablo Canyon | 7736 | 09/25/2011 11/18/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Surveillances on Fire Barriers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Facility Operating License Condition 2.C (4), "Fire Protection," after the licensee failed to identify and correct the failure to perform required surveillance testing on fire-rated assemblie
Region: IV | Diablo Canyon | 7737 | 09/25/2011 11/18/2011 | 2011004-05 | NRC | NCV | Emergency Preparedness | Green | Failure to Ensure Emergency Response Organization Qualifications |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71114.05 | A noncited violation of 10 CFR 50.47(b)(10) was identified for the licensee's failure to ensure a range of protective actions is available for emergency workers during emergencies. Specifically, an operator filled an on-shift emergency response organizati
Region: IV | Diablo Canyon | 7738 | 09/25/2011 11/18/2011 | 2011004-06 | NRC | NCV | Barrier Integrity | Green | Failure to Follow a Procedural Requirement for Reactivity Manipulation |  | H.4(b) Procedural Compliance | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," after operations personnel conducted a reactivity manipulation during shift turnover. Procedure OP1.ID3, "Reactivity Management Program," required pla
Region: IV | Diablo Canyon | 7716 | 06/26/2011 08/10/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Hazard Evaluations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Facility Operating License Condition 2.C (5), "Fire Protection," after Pacific Gas and Electric failed to implement the required compensatory actions described in Equipment Control Guideline
Region: IV | Diablo Canyon | 7722 | 06/26/2011 08/10/2011 | 2011003-02 | Self - Revealed | FIN | Mitigating Systems | Green | Unplanned Loss of Preferred Offsite Power Due to Less than Adequate Work Planning |  | H.3(a) Work Planning | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.18 | The inspectors identified a self-revealing finding following the unplanned loss of 230 kV preferred offsite power to Unit 1 due to inadequate work planning. On May 17, 2011, Unit 1 lost preferred offsite power after a technician began cutting a hole in a
Region: IV | Diablo Canyon | 7723 | 06/26/2011 08/10/2011 | 2011003-03 | Self - Revealed | FIN | Mitigating Systems | Green | Unplanned Loss of Preferred Offsite Power Due to the Failure to Follow Work Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.18 | The inspectors identified a self-revealing finding following two unplanned losses of 230 kV preferred offsite power to Unit 1 due to personnel errors. On May 26, 2011, Unit 1 lost preferred offsite power after a technician incorrectly installed test equip
Region: IV | Diablo Canyon | 7724 | 06/26/2011 08/10/2011 | 2011003-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedures for Testing HEPA Ventilation Units |  | H.4(b) Procedural Compliance | TE?: N | 05000323 Diablo Canyon 2 |  | 71124.01 | The inspectors identified a noncited violation of Technical Specification 5.4.1(a) for the failure to follow procedures for testing and using the high-efficiency particulate air ventilation units used to prevent personal contamination. Licensee immediate
Region: IV | Diablo Canyon | 7725 | 06/26/2011 08/10/2011 | 2011003-05 | NRC | FIN | Barrier Integrity | Green | Inadequate Review of Severe Accident Management Guidelines |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a finding after Pacific Gas and Electric failed to periodically review and update the severe accident management guidelines. Procedure OM10.ID5, "Severe Accident Management," required the licensee to review and update the severe
Region: IV | Diablo Canyon | 7726 | 06/26/2011 08/10/2011 | 2011003-06 | NRC | NCV | Mitigating Systems | Green | Less Than Adequate Evaluation of New Security Modifications |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric failed to adequately evaluate the impact of protected area boundary modifications. These mo
Region: IV | Diablo Canyon | 7727 | 03/27/2011 05/11/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for the Preferred Offsite Power System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.01 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after Pacific Gas and Electric failed to ensure that the preferred offsite power system design basis was correctly translated into electri
Region: IV | Diablo Canyon | 7731 | 03/27/2011 05/11/2011 | 2011002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Document Design Basis of Containment Fan Cooler Unit Cooling Coil Casings |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.07A | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that measures shall be established to assure that applicable regulatory requirements and the design basis are correctly t
Region: IV | Diablo Canyon | 7732 | 03/27/2011 05/11/2011 | 2011002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Design Control for the Auxiliary Building Ventilation System Control Panel Modification |  | H.4(a) Human Error Prevention | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after Pacific Gas and Electric failed to ensure that the design basis requirements for single failure criteria were correctly trans
Region: IV | Diablo Canyon | 7690 | 12/31/2010 02/07/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain a Fire Barrier |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Facility Operating License Condition 2.C (5), "Fire Protection," after Pacific Gas and Electric failed to maintain the integrity of Door 155 in the rated condition. On December 9, 2010, the i
Region: IV | Diablo Canyon | 7691 | 12/31/2010 02/07/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Transient Combustibles Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Unit 2 Facility Operating License Condition 2.C.(5), "Fire Protection," after Pacific Gas and Electric failed to ensure procedures for controlling flammable and combustible materials adequate
Region: IV | Diablo Canyon | 7697 | 12/31/2010 02/07/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determinations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric failed to adequately evaluate two nonconforming conditions for operability as required by Pr
Region: IV | Diablo Canyon | 7698 | 12/31/2010 02/07/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Less than Adequate Containment Recirculation Sump Design Control |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after Pacific Gas and Electric failed to ensure Calculation STA-255, "Minimum Required Refueling Water Storage Tank Level for GE Sumps," Revisio
Region: IV | Diablo Canyon | 7702 | 12/31/2010 02/07/2011 | 2010005-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Diesel Generator Surveillance Testing |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," after Pacific Gas and Electric failed to develop and implement an adequate testing program for the emergency diesel generators that met design requ
Region: IV | Diablo Canyon | 7703 | 12/31/2010 02/07/2011 | 2010005-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Quality Verification Audits |  | P.3(c) Communicates & Acts on Assessment Results | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 92723 | The inspectors identified a noncited violation of 10CFR Appendix B, Criterion XVIII, "Audits", which required that a comprehensive system of planned and periodic audits be carried out to verify compliance with all aspects of the quality assurance program
Region: IV | Diablo Canyon | 7672 | 09/25/2010 11/01/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify a Degraded Fire Barrier |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of the Diablo Canyon Facility Operating License Condition (5), "Fire Protection," after Pacific Gas and Electric failed to maintain the integrity of a fire door in the rated configuration. On August 19, 2010,
Region: IV | Diablo Canyon | 7673 | 09/25/2010 11/01/2010 | 2010004-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Risk Management During a Planned Auxiliary Saltwater Pump Outage |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.13 | The inspectors identified a finding after Pacific Gas and Electric failed to adequately manage risk during planned maintenance activity as required by Procedure AD7.DC6, "On-line Maintenance Risk Management." On April 5, 2010, work control personnel reque
Region: IV | Diablo Canyon | 7674 | 09/25/2010 11/01/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment during Planned Maintenance Activities |  | H.4(b) Procedural Compliance | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65 after Pacific Gas and Electric failed to perform a risk assessment after plant conditions had changed. On July 13, 2010, Pacific Gas and Electric identified that station personnel failed to co
Region: IV | Diablo Canyon | 7675 | 09/25/2010 11/01/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric failed to promptly evaluate two nonconforming conditions for operability as required by Procedure
Region: IV | Diablo Canyon | 7676 | 09/25/2010 11/01/2010 | 2010004-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for the AuxiliarySaltwater System |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to maintain adequate design control measures associated with the auxiliary saltwater system. The inspectors identifi
Region: IV | Diablo Canyon | 7677 | 07/27/2010 09/09/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for the Emergency Diesel Generator |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to maintain adequate design control measures associated with the emergency diesel generating air system. Specifically, failure o
Region: IV | Diablo Canyon | 7683 | 07/27/2010 09/09/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Proficiency of Operators to Meet the Time Critical Operator Actions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to ensure that operators are able to implement specified actions in response to operational events and accidents. Specifically,
Region: IV | Diablo Canyon | 7685 | 07/27/2010 09/09/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Untimely and Inadequate Corrective Actions for the Emergency Diesel Generators |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," with two examples for the failure of the licensee to promptly identify and correct nonconforming conditions related to the emergency diesel generat
Region: IV | Diablo Canyon | 7689 | 07/27/2010 09/09/2010 | 2010006-05 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Evaluate Failed Residual Heat Removal Surveillance Test |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 71152B | The team identified a noncited violation of Technical Specification 5.4.1.a for failure to appropriately evaluate and correct a condition adverse to quality, as instructed by Surveillance Test Procedure P-RHR-A22," Comprehensive Testing of Residual Heat R
Region: IV | Diablo Canyon | 7632 | 06/26/2010 08/28/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Following Identification of a Non-conservative Technical Specification |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, "Corrective Action," after Pacific Gas and Electric failed to implement prompt corrective actions after identifying a nonconservative technical specification. In D
Region: IV | Diablo Canyon | 7633 | 06/26/2010 08/28/2010 | 2010003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Unit 1 Containment Concrete Inspections |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 71152 | The inspectors identified a noncited violation of Technical Specification 5.5.16.a.1, "Containment Leakage Rate Testing Program," after Pacific Gas and Electric failed to perform containment concrete inspections in accordance with the requirements of and
Region: IV | Diablo Canyon | 7649 | 06/10/2010 07/23/2010 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Non-Conservative Decision Making resulted in a Violation of Technical Specification |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 7111121 | On March 10, 2010, the inspectors identified a noncited violation of Technical Specification 3.7.7, "Vital Component Cooling Water System," after both Unit 2 component cooling water loops were inoperable longer than permitted during power operations. On M
Region: IV | Diablo Canyon | 7653 | 06/10/2010 07/23/2010 | 2010007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination Associated With the Offsite Degraded Voltage Protection Scheme |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 7111121 | On February 27, 2010, the inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric failed to complete an adequate operability evaluation, as required by Proce
Region: IV | Diablo Canyon | 7654 | 06/10/2010 07/23/2010 | 2010007-06 | NRC | NCV | Mitigating Systems | Green | Second Level Undervoltage Relay Time Delay to Initiate Load Shed and Sequencing Upon the Diesel Generator is Adequate to Assure Plant Safety |  |  | TE?: N | 05000323 Diablo Canyon 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to ensure that plant conditions were consistent with design calculation inputs and assumptions. The licensee failed to assure and verify t
Region: IV | Diablo Canyon | 7659 | 06/10/2010 07/23/2010 | 2010007-07 | NRC | NCV | Mitigating Systems | Green | Nonconservative Inputs into Motor Operated Valve Calculation |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" involving multiple mechanical and electrical errors in documentation associated with torque, thrust, and operation of certain safety related motor oper
Region: IV | Diablo Canyon | 7660 | 06/10/2010 07/23/2010 | 2010007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Drawings and Procedures to Align Emergency Makeup Water Supply from Diablo Canyon Creek to Support the Auxiliary Feedwater System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 7111121 | The team identified a noncited violation of Diablo Canyon Technical Specification 5.4.1. "Procedures," for failure to have a procedure. The Diablo Canyon Final Safety Analysis Report Update, Revision 18, Section 6.5.2.1.1 documents the design of the auxil
Region: IV | Diablo Canyon | 7613 | 03/27/2010 04/29/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Effectively Implement the Seismically-induced Systems Interaction Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric personnel failed to effectively implement the Seismically Induced System Interaction Progra
Region: IV | Diablo Canyon | 7622 | 03/27/2010 04/29/2010 | 2010002-04 | NRC | NCV | Mitigating Systems | Green | Less Than Adequate Evaluation Following the Failure of Both Motor-Driven Auxiliary Feedwater Trains |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71153 | The inspectors identified a noncited violation of 10 CFR, Part 50, Appendix B, Criteria XVI, "Corrective Actions," after Pacific Gas and Electric failed to implement adequate corrective actions following a protection system failure. On June 29, 2009, a pr
Region: IV | Diablo Canyon | 7624 | 01/25/2010 03/09/2010 | 2009009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Design and Configuration Control Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000323 Diablo Canyon 2 |  | 93812 | The inspection team identified a noncited violation of 10 CFR 50, Appendix B, Criterion III, Design Control, which requires licensees to implement measures to assure that applicable regulatory requirements and the design basis are correctly translated int
Region: IV | Diablo Canyon | 7628 | 01/25/2010 03/09/2010 | 2009009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct an Adequate Post-Modification Test |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000323 Diablo Canyon 2 |  | 93812 | The inspection team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XI, Test Control, which requires that a test program be established to assure that all testing required to demonstrate that structures, systems, and components will pe
Region: IV | Diablo Canyon | 7593 | 12/31/2009 02/03/2010 | 2009005-01 | NRC | NCV | Barrier Integrity | Green | Less Than Adequate Work Planning Resulted in the Release of Two Gas Decay Tanks |  | H.3(b) Work Activity Coordination | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.2 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," after Pacific Gas and Electric inadvertently released the contents of two gas decay tanks into the auxiliary building. Gas Decay Tank 2-2 was in
Region: IV | Diablo Canyon | 7594 | 12/31/2009 02/03/2010 | 2009005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Properly Plan a Maintenance Activity |  | H.3(a) Work Planning | TE?: N | 05000323 Diablo Canyon 2 |  | 7112102 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1(a) for failure to properly plan numerous outage maintenance activities including the disassembly of the Unit 2 reactor head. Specifically, Work Orders 68004363 (
Region: IV | Diablo Canyon | 7600 | 12/31/2009 02/03/2010 | 2009005-04 | NRC | NCV | Initiating Events | Green | Less Than Adequate Replacement Reactor Head Modification Design Control |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000323 Diablo Canyon 2 |  | 71007 | The inspectors identified a noncited violation of Title 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," after the design contractor failed to perform adequately calculations demonstrating that the replacement reactor head met ASME Code accep
Region: IV | Diablo Canyon | 7583 | 09/25/2009 10/27/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Degraded Fire Barrier |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of Diablo Canyon Facility Operating License Condition (5), "Fire Protection," after Pacific Gas and Electric failed to maintain Fire Door 155 in the rated condition. On September 1, 2009, the inspectors ident
Region: IV | Diablo Canyon | 7588 | 09/25/2009 10/27/2009 | 2009004-02 | NRC | FIN | Initiating Events | Green | Failure to Perform Corrective Actions Resulted in an Unplanned Trip |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.12 | A self-revealing finding was identified after Pacific Gas and Electric failed to implement planned corrective actions resulting in the loss of cooling to a main transformer, a rapid shutdown and a manual reactor trip of Unit 2. On June 30, 2009, cooling t
Region: IV | Diablo Canyon | 7589 | 09/25/2009 10/27/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Emergency Operating Procedures Following a Reactor Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specification 5.4.1.b, "Emergency Operating Procedures," after plant operators failed to enter Emergency Operating Procedures E-0, "Reactor Trip or Safety Injection," and E-0.1, "Reactor Trip Res
Region: IV | Diablo Canyon | 7582 | 07/24/2009 09/10/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Safe Shutdown Procedure Not Consistent with Safe Shutdown Analysis |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.05T | An NRC identified noncited violation of License Condition 2.C.(4), "Fire Protection," was identified in that post-fire safe shutdown Procedure CP M-10, "Fire Protection of Safe Shutdown Equipment," Revision 20, was not consistent with the calculation M-92
Region: IV | Diablo Canyon | 7569 | 06/30/2009 08/05/2009 | 2009003-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Promptly Declare an Unusual Event |  | H.4(b) Procedural Compliance | TE?: N | 05000275 Diablo Canyon 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR 50.54(q), after a Pacific Gas and Electric shift manager failed to promptly declare an Unusual Event in accordance with the emergency plan. Station procedures required that the emergency plan be act
Region: IV | Diablo Canyon | 7570 | 06/30/2009 08/05/2009 | 2009003-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Following the Loss of Design Control for the 500 kV Offsite Power Source |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, "Corrective Action," after Pacific Gas and Electric failed to adequately correct a nonconforming condition related to the adequacy of design documentation to demon
Region: IV | Diablo Canyon | 7561 | 03/31/2009 05/05/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Power Ascension Procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specification 5.4.1, "Procedures," after plant operators failed to stabilize reactor power and perform a comparison between the calorimetric heat balance calculation and the power range output pr
Region: IV | Diablo Canyon | 7560 | 03/12/2009 05/05/2009 | 2009002-02 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Procedure |  | H.3(a) Work Planning | TE?: N | 05000275 Diablo Canyon 1 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1 for failure to develop a procedure for removing the reactor head from the reactor pressure vessel and the subsequent filling of the reactor coolant system in a ma
Region: IV | Diablo Canyon | 7555 | 12/31/2008 02/06/2009 | 2008005-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Effective Actions to Correct an Adverse Trend |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a finding after Pacific Gas and Electric was ineffective in addressing an adverse trend in missed quality control inspection hold points. Licensee Procedure OM7, "Corrective Action Program," required that the licensee evaluate pr
Region: IV | Diablo Canyon | 7554 | 12/31/2008 02/06/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Operation of 230 kV Offsite Power System Outside the Design Basis |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria III, Design Control, after Pacific Gas and Electric failed to adequately translate the design basis for the 230 kV preferred offsite power system into specifications an
Region: IV | Diablo Canyon | 7556 | 12/31/2008 02/06/2009 | 2008005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for the Emergency Diesel Generator |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after Pacific Gas and Electric failed to provide adequate design control measures for verifying the emergency diesel generators meet the design
Region: IV | Diablo Canyon | 7551 | 11/20/2008 12/30/2008 | 2008008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Violations of the Seismically-Induced Systems Interaction Program |  | H.4(b) Procedural Compliance | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to properly implement housekeeping procedures to prevent seismically-induced system interactions. Specifically,
Region: IV | Diablo Canyon | 7552 | 11/20/2008 12/30/2008 | 2008008-02 | NRC | FIN | Public Radiation Safety | Green | Failure to Take Appropriate Actions to Correct an Identified Adverse Trend |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152B | The team identified a finding for failure to take adequate corrective actions to correct adverse trends in control of radioactive and potentially contaminated material as required by the corrective action program. Specifically, between May 2005 and June 2
Region: IV | Diablo Canyon | 7542 | 09/30/2008 11/03/2008 | 2008004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Resulting in Inoperable Auxiliary Building Ventilation System |  | H.4(a) Human Error Prevention | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.04Q | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," after Pacific Gas and Electric personnel failed to provide adequate work instructions for removal of equipment from service, resulting in the inope
Region: IV | Diablo Canyon | 7543 | 09/30/2008 11/03/2008 | 2008004-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a Safety Assessment for Following Discovery of Explosive Gas in the Auxiliary and Containment Buildings |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.05Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Pacific Gas and Electric personnel failed to perform a safety assessment prior to implementing a temporary procedure
Region: IV | Diablo Canyon | 7549 | 09/30/2008 11/03/2008 | 2008004-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Operability Evaluation of Reactor Coolant Leakage Detection System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 3.4.15, "RCS Leakage Detection Instrumentation," after the Unit 1 containment atmosphere gaseous radioactivity monitor reactor coolant leak detection system was inoperable for great
Region: IV | Diablo Canyon | 7533 | 06/30/2008 08/05/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope a Radiation Monitoring System into the Maintenance Rule Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(b) after Pacific Gas and Electric Company failed to include a radiation monitoring system in the maintenance rule scope for monitoring of maintenance effectiveness. The licensee relied on the
Region: IV | Diablo Canyon | 7534 | 06/30/2008 08/05/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," after the licensee failed to adhere to several requirements in Administrative Procedure OM7.ID12, "Operability Determinati
Region: IV | Diablo Canyon | 7541 | 06/30/2008 08/05/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Diesel Generator Snubber Valve Receipt Inspection |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000275 Diablo Canyon 1 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," after Pacific Gas and Electric failed to perform an adequate receipt inspection to identify defective emergency di
Region: IV | Diablo Canyon | 7527 | 03/31/2008 05/01/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate that the Unit 2 Containment Atmosphere Particulate Radioactivity Monitor Performance was Being Effectively Controlled per 10 CFR 50.65(a)(2) |  | H.4(b) Procedural Compliance | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2), after Pacific Gas and Electric Company failed to effectively control performance monitoring of the Unit 2 containment atmosphere particulate radiation monitor through appropriate preven
Region: IV | Diablo Canyon | 7526 | 02/17/2008 05/01/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Integrity of an Auxiliary Building Fire Door |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | On February 17, 2008, the inspectors identified a noncited violation of Technical Specification 5.4.1.d, "Fire Protection Program," after Pacific Gas and Electric failed to maintain the integrity of an auxiliary building fire door. The inspectors identifi
Region: IV | Diablo Canyon | 7532 | 02/13/2008 05/01/2008 | 2008002-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conduct an Adequate Evaluation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7112101 | Part 20.1501(a) of Title 10 of the Code of Federal Regulations requires that each licensee make or cause to be made surveys that may be necessary for the licensee to comply with the regulations in 10 CFR Part 20 and that are reasonable under the circumsta
Region: IV | Diablo Canyon | 7519 | 12/31/2007 02/05/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Plant Operators Failed to Identify a Degraded Emergency Diesel Generator |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000275 Diablo Canyon 1 |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, "Corrective Action," after Pacific Gas and Electric failed to identify a degraded emergency diesel generator. On October 15, 2007, the inspectors identified a buildup of black soot o
Region: IV | Diablo Canyon | 7518 | 08/09/2007 10/26/2007 | 2007004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate main turbine repair procedure resulted in an unplanned power reduction and forced outage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.12 | A self-revealing finding after an inadequate main turbine maintenance procedure resulted in an unplanned load reduction and a reactor shutdown. On August 9, 2007, Unit 1 generator output decreased by 60MW due to failed main turbine stop valve. Pacific Gas
Region: IV | Diablo Canyon | 7517 | 06/30/2007 08/01/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Scope Reactor Cavity and Containment Structure Sump Level Indication Systems Into the Maintenance Rule Program |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.12 | GREEN. The inspectors identified a Green, noncited violation of 10 CFR 50.65(b) was identified for the failure of engineering personnel to include the reactor cavity and containment structure sump level indication systems into the scope of its program for
Region: IV | Diablo Canyon | 7510 | 02/16/2007 05/08/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Update 480 V Switchgear Heat Dissipation Calculaiton |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.04Q | An NRC-identified, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was determined for the failure of engineering personnel to appropriately update the heat dissipation calculation for vital 480 V switchgear rooms. Since
Region: IV | Diablo Canyon | 7511 | 01/30/2007 05/08/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | Inappropriate Temporary Modification to Control Room Condenser |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000323 Diablo Canyon 2 |  | 7111123 | An NRC-identified, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was determined for the failure of maintenance personnel to make modifications to the Control Room Condenser CR-38 filter mount consistent with the compon
Region: IV | Diablo Canyon | 7512 | 01/11/2007 02/23/2007 | 2006011-01 | NRC | NCV | Mitigating Systems | Green | Failure to Use Correct Design Inputs in Determination of a Potential for Choking Flow/Cavitation Across the Auxiliary Service Water Throttled Butterfly Valves |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111121 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to translate design basis information into specifications and procedures. The team identified that a nonconservative flow rate wa
Region: IV | Diablo Canyon | 7513 | 01/11/2007 02/23/2007 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Consider Instrument Uncertainty in Surveillance Requirements for Technical Specifications LCO 3.7.9 |  |  | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7111121 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to demonstrate that the acceptance criteria for surveillance tests had conservatively accounted for uncertainties in determinatio
Region: IV | Diablo Canyon | 7495 | 12/31/2006 02/13/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Change to Auxiliary Saltwater Pump Routine Surveillance Test Acceptance Criteria |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71152 | GREEN. An NRC-identified, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was determined for the failure of engineering personnel to apply adequate design control measures. Specifically, on February 9, 2006, engineering
Region: IV | Diablo Canyon | 7498 | 10/15/2006 02/13/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Temporary Modification to a Vital Battery |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.15 | An NRC-identified, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure to promptly correct a condition adverse to quality. Specifically, on October 15, 2006, Pacific Gas and Electric Compa
Region: IV | Diablo Canyon | 7496 | 09/29/2006 02/13/2007 | 2006005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Evaluate Operability of Auxiliary Building Ventilation Control Panels |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.13 | An NRC-identified, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was determined for the failure of engineering and operations personnel to promptly identify and correct a condition adverse to quality. On two occas
Region: IV | Diablo Canyon | 7488 | 09/25/2006 10/31/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Include Floor Drains Credited in the Flood Analysis Into the Maintenance Rule Program |  | P.2(b) Implementing Operating Experience | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.06 | An NRC-identified, noncited violation of 10 CFR 50.65(b) was determined for the failure of engineering staff to include the auxiliary feedwater pump room floor drains within the scope of Pacific Gas and Electric Company's program for monitoring the effect
Region: IV | Diablo Canyon | 7490 | 08/31/2006 02/13/2007 | 2006005-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Preserve Corrective Action for Thimble Tube Wear |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000323 Diablo Canyon 2 |  | 71153 | A self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to apply adequate design control measures regarding the installation of thimble tubes with chrome-plated bands. Specificall
Region: IV | Diablo Canyon | 7500 | 08/29/2006 01/18/2007 | 2006013-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Survey Material Unconditionally Released |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 7112203 | The team reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a) that resulted in an unconditional release of radioactive material from the radiologically controlled area. Specifically, the contents of a vehicle cab were not removed and survey
Region: IV | Diablo Canyon | 7487 | 08/23/2006 10/31/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify that the Correct Equipment Necessary for Implementing EOP for Inadequate Core Cooling Was Not Pre-staged |  | H.2(d) Facilities & Equipment | TE?: N | 05000275 Diablo Canyon 1 05000323 Diablo Canyon 2 |  | 71111.05Q | An NRC-identified, noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify a condition adverse to quality. Specifically, Pacific Gas and Electric Company failed to promptly identify that i
Region: IV | Diablo Canyon | 7483 | 06/12/2006 08/14/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | Failure to prevent recurrence of limitorque model SMB-000 failures |  | P.1(b) Trend Performance CAP | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.15 | An NRC-identified, non-cited violation of 10 CFR Part 50, Criterion XVI, "Corrective Actions" was determined for the failure to prevent recurrence of a similar failures of Limitorque SMB-000 actuators in the auxiliary feedwater system. Pacific Gas and Ele
Region: IV | Diablo Canyon | 7480 | 05/24/2006 08/14/2006 | 2006003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to promptly identify voiding in accumulator discharge line |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000275 Diablo Canyon 1 |  | 71111.15 | A self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI was determined for the failure of operations personnel to promptly identify a condition adverse to quality. Specifically, on November 27, 2005, operators failed to document
Region: IV | Diablo Canyon | 7479 | 05/03/2006 08/14/2006 | 2006003-01 | NRC | NCV | Barrier Integrity | Green | Failure to follow welding procedures |  |  | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.08P | An NRC-identified, non-cited violation of Technical Specification 5.4.1 was identified because Pacific Gas and Electric Company (PG&E) failed to follow the procedure for ensuring that welding preheat temperatures were verified prior to welding. Specifical
Region: IV | Diablo Canyon | 7481 | 04/20/2006 08/14/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate refueling procedure for draining and depressurizing the reactor coolant system |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000323 Diablo Canyon 2 |  | 71111.2 | An NRC-identified, non-cited violation of Technical Specification 5.4.1.a was determined for an inadequate procedure, Procedure OP A-2:II, "Reactor Vessel - Draining the RCS to the Vessel Flange - With Fuel in Vessel," Revision 33A. Specifically, on April
Region: IV | Diablo Canyon | 7482 | 04/18/2006 08/14/2006 | 2006003-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to survey to identify the magnitude and extent of radiation levels to identify radiological hazards |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000323 Diablo Canyon 2 |  | 7112101 | The inspectors identified a non-cited violation of 10 CFR 20.1501(a) because Pacific Gas and Electric Company (PG&E) failed to survey to determine the extent and magnitude of radiation levels and evaluate the radiological hazards. Specifically, on April 1
Region: IV | Diablo Canyon | 7477 | 02/09/2006 05/15/2006 | 2006002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Special Work Permit Instructions |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 7112101 | The inspectors reviewed a self-revealing, NCV of Technical Specification 5.4.1, resulting from failure to follow special work permit instructions by a radiation protection technician. On October 26, 2005, a radiation protection technician working on Speci
Region: IV | Diablo Canyon | 7478 | 01/27/2006 05/15/2006 | 2006002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Maintain Abormal Operating Procedure for Reactor Coolant Pump Malfunctions |  |  | TE?: N | 05000275 Diablo Canyon 1 |  | 71152 | A self-revealing, non-cited violation of Technical Specification 5.4.1.a was identified for the failure to adequately maintain abnormal operating Procedure OP AP-28, "Reactor Coolant Pump Malfunction," Revision 1. On January 27, 2006 operators vented the
Region: IV | Fort Calhoun | 13302 | 12/31/2016 01/18/2017 | 2016004-01 | Self - Revealed | NCV | Emergency Preparedness | Green | Failure to Provide Training on Changes to Protective Action Recommendation Procedures |  | H.3 Change Management | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The inspector reviewed a self-revealed non-cited violation associated with Fort Calhoun Station's failure to provide radiological emergency response training to those who may be called upon to assist in an emergency, as required by 10 CFR 50.47(b)(15). Sp
Region: IV | Fort Calhoun | 13298 | 08/12/2016 09/22/2016 | 2016008-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain Prior NRC Approval for a Change When Required |  |  | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 71111.17T | The inspectors identified a Severity Level IV, Green, non cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," Section (c)(1), which states, in part, that a licensee may make changes in the facility as described in the final safety analysis
Region: IV | Fort Calhoun | 13285 | 06/30/2016 08/03/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Evaluation of Service Life for Component Cooling Water Pump Motors |  |  | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, design control, associated with the licensee's failure to perform an adequate evaluation of the service life of component cooling water pump motors. Specifical
Region: IV | Fort Calhoun | 13291 | 06/30/2016 08/03/2016 | 2016002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Develop Adequate Procedures for Post Modification Testing |  | H.4 Teamwork | TE?: N | 05000285 Fort Calhoun |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.8.1., for failure to establish, implement, and maintain a procedure recommended in Regulatory Guide 1.33, Revision 2, Appendix A. Specifically, the licensee failed
Region: IV | Fort Calhoun | 13280 | 03/31/2016 04/20/2016 | 2016001-01 | NRC | NCVIV | Mitigating Systems | Green | Implementing a Procedure Change for Alternative Shutdown Cooling that would have Required NRC Approval |  |  | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 71153 | The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," for the failure to recognize that a change to the facility as described in the Updated Safety Analysis Report would require prior NRC rev
Region: IV | Fort Calhoun | 13268 | 12/11/2015 01/21/2016 | 2015009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Adequate Corrective Action to Preclude Repetition of a Significant Condition Adverse to Quality Associated with Emergency Diesel Generator Room Water Intrusions |  | P.3 Resolution | TE?: N | 05000285 Fort Calhoun |  | 71152B | Green. The team identified an NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to take corrective actions to prevent repetition of a significant condition adverse to quality. Specifically, since February 2
Region: IV | Fort Calhoun | 13269 | 12/11/2015 01/21/2016 | 2015009-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Revise Procedures and Perform Additional Training |  | P.5 Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71152B | Green. The team evaluated a self-revealing NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions", which states, in part, that "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, def
Region: IV | Fort Calhoun | 13270 | 11/06/2015 12/17/2015 | 2015012-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement and Maintain Required NFPA 805 Implementation Items |  | H.3 Change Management | TE?: N | 05000285 Fort Calhoun |  | 71111.05XT | -Green. The inspectors identified two examples of a non-cited violation of License Condition 3.D, "Fire Protection Program," for the failure to adequately implement required National Fire Protection Association Standard 805 implementation items in accorda
Region: IV | Fort Calhoun | 13278 | 11/06/2015 12/17/2015 | 2015012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Isolation for Pressurizer Heaters |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.05XT | -Green. The inspectors identified a non-cited violation of License Condition 3.D, "Fire Protection Program," for the failure to ensure one success path necessary to achieve and maintain the nuclear safety performance criteria was maintained free of fire d
Region: IV | Fort Calhoun | 13279 | 11/06/2015 12/17/2015 | 2015012-03 | NRC | NCV | Mitigating Systems | Green | Failure to Set Action Levels to Ensure that the Assumptions in the Engineering Analysis Remain Valid |  | H.3 Change Management | TE?: N | 05000285 Fort Calhoun |  | 71111.05XT | -Green. The inspectors identified a non-cited violation of License Condition 3.D, "Fire Protection Program," for the failure to establish an appropriate monitoring program in accordance with National Fire Protection Association Standard 805, Section 2.6.
Region: IV | Fort Calhoun | 13264 | 09/30/2015 11/10/2015 | 2015003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Safety Injection Tank Boron Concentration within Technical Specification Limits |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | NONE | A Green, self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI "Corrective Action" was identified because the licensee failed to identify and evaluate an adverse trend related to boron concentration in Safety Injection Tank (SIT
Region: IV | Fort Calhoun | 13265 | 09/30/2015 11/10/2015 | 2015003-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Maintain Fire Watch and Fire Watch Logs |  | H.1 Resources | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | NONE | Inspectors identified a Green, Severity Level IV, non-cited violation of 10 CFR 50.9(a), "Completeness and Accuracy of Information," for the licensees failure to maintain the required fire watch logs complete and accurate in all material respects. The lic
Region: IV | Fort Calhoun | 13256 | 08/14/2015 09/24/2015 | 2015011-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure the Suitability of Replacement Materials during the Design Review Process |  | P.5 Operating Experience | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors reviewed a Green, self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate the suitability of materials utilized during the design review process. Specifica
Region: IV | Fort Calhoun | 13257 | 08/14/2015 09/24/2015 | 2015011-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Technical Basis for Operability of the Auxiliary Feedwater System |  | H.13 Consistent Process | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow the operability determination procedure. Specifically, the licensee failed
Region: IV | Fort Calhoun | 13263 | 08/14/2015 09/24/2015 | 2015011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Non-Conforming Condition Associated with Auxiliary Feedwater Valves |  | H.10 Bases for Decisions | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to correct a condition adverse to quality. Specifically, the licensee failed to take corrective actions
Region: IV | Fort Calhoun | 13240 | 06/30/2015 07/30/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Failure to Include a Class 1 Component in the Reactor Vessel Pressure Boundary Integrity Test |  | H.14 Conservative Bias | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4), involving the failure to adequately perform periodic reactor coolant system (RCS) integrity inspections as required by ASME Code Section XI. Specifically, Procedure OP ST RC 3007, "Pe
Region: IV | Fort Calhoun | 13241 | 06/30/2015 07/30/2015 | 2015002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform a Valid 40-Month Inservice Test |  | H.14 Conservative Bias | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4) for the failure to perform a valid 40-month inservice test of the spent fuel pool cooling system. Specifically, the licensee failed to identify an existing through-wall leak on dischar
Region: IV | Fort Calhoun | 13243 | 06/30/2015 07/30/2015 | 2015002-03 | NRC | NCV | Initiating Events | Green | Failure to Establish Adequate Work Instructions to Clean and Inspect the Reactor Vessel Head |  | H.4 Teamwork | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to establish adequate work instructions to clean and inspect the reactor vessel head. Specifically, the w
Region: IV | Fort Calhoun | 13244 | 06/30/2015 07/30/2015 | 2015002-04 | NRC | NCV | Initiating Events | Green | Failure to Incorporate Vendor Manual Recommendations for Conducting Preventative Maintenance on the Reactor Vessel Head Vent Valve |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of Technical Specification 5.8.1.a associated with the failure to establish a preventative maintenance schedule for the reactor vessel head vent manual isolation valve, RC-100. Specifically, engineering pers
Region: IV | Fort Calhoun | 13245 | 06/30/2015 07/30/2015 | 2015002-05 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Involving a Spent Fuel Pool Cooling Vent Valve Leak |  | H.2 Field Presence | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to take corrective actio
Region: IV | Fort Calhoun | 13249 | 06/30/2015 07/30/2015 | 2015002-06 | NRC | NCV | Initiating Events | Green | Failure to Identify and Correct Loose Incore Instrument Nozzle Connection |  | H.10 Bases for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify and correct a condition adverse to quality. Specifically, maintenance personnel failed to document a loose conne
Region: IV | Fort Calhoun | 13250 | 06/30/2015 07/30/2015 | 2015002-07 | NRC | FIN | Barrier Integrity | Green | Failure to Perform Functionality Assessments for the Spent Fuel Pool Cooling System |  | H.9 Training | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a finding associated with the failure of operations personnel to follow procedures used to perform functionality assessments. Specifically, operations personnel failed to provide sufficient technical justification for the reasona
Region: IV | Fort Calhoun | 13251 | 06/30/2015 07/30/2015 | 2015002-09 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Instructions and Procedures Related to Snubber Activities |  | H.5 Work Management | TE?: N | 05000285 Fort Calhoun |  | 71153 | The inspectors identified a non-cited violation of very low safety significance of 10 CFR 50, Appendix B, Criterion V "Instructions, Procedures, and Drawings," because activities affecting quality were not accomplished in accordance with instructions and
Region: IV | Fort Calhoun | 13218 | 03/31/2015 05/08/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Risk Management Actions for Planned Maintenance Activities |  | H.3 Change Management | TE?: N | 05000285 Fort Calhoun |  | 71111.13 | Green. The inspectors identified an NCV of very low safety significance of 10 CFR 50.65 paragraph (a)(4) "Requirements for Monitoring the Effectiveness of Maintenance of Nuclear Power Plants," because the licensee did not effectively manage the increase i
Region: IV | Fort Calhoun | 13222 | 03/13/2015 04/16/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Battery Sizing and Load Profile Calculation |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis\x85are cor
Region: IV | Fort Calhoun | 13223 | 03/13/2015 04/16/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Correct Acceptance Criteria Values for Battery Intercell Resistance Measurements |  | H.7 Documentation | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis\x85are cor
Region: IV | Fort Calhoun | 13224 | 03/13/2015 04/16/2015 | 2015007-03 | NRC | FIN | Mitigating Systems | Green | Failure to Account for Elevated Battery Room Temperature Effects on Battery Service Life |  | P.5 Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green finding for the licensee's failure to verify or check the adequacy of design of the 125 Vdc batteries from environmental effects. Specifically, the licensee failed to account for the effects of elevated battery room temp
Region: IV | Fort Calhoun | 13225 | 03/13/2015 04/16/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Justification for Power Supplies Installed Beyond Vendor Recommended Life |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Fort Calhoun | 13226 | 03/13/2015 04/16/2015 | 2015007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Evaluation for the Auxiliary Building Crane |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Fort Calhoun | 13229 | 03/13/2015 04/16/2015 | 2015007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Auxiliary Feedwater Pump Runout Design Calculation |  | H.14 Conservative Bias | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Fort Calhoun | 13230 | 03/13/2015 04/16/2015 | 2015007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Evaluation for the Intake Crane Trolley and Bridge Rail |  | H.7 Documentation | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Fort Calhoun | 13234 | 03/13/2015 04/16/2015 | 2015007-08 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain Prior NRC Approval for a Change in Seismic Analysis Damping |  | H.6 Design Margins | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 7111121 | Severity Level IV/Green. The team identified two examples of a Severity Level IV, Green, non-cited violation, of 10 CFR 50.59, "Changes, Tests and Experiments," for the licensee's failure to obtain a license amendment prior to implementing a change if the
Region: IV | Fort Calhoun | 13236 | 03/13/2015 04/16/2015 | 2015007-10 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Account for Raw Water Pump Discharge Check Valve Back Leakage |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as by the per
Region: IV | Fort Calhoun | 13239 | 03/13/2015 04/16/2015 | 2015007-12 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Procedures for Verifying Operator Time Critical Actions |  | H.13 Consistent Process | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented procedures of a type appro
Region: IV | Fort Calhoun | 13216 | 03/05/2015 05/08/2015 | 2015001-01 | NRC | FIN | Mitigating Systems | Green | Failure to Conduct and Evaluate Simulator Testing In Accordance with ANSI/ANS-3.5-2009 |  | H.3 Change Management | TE?: N | 05000285 Fort Calhoun |  | 71111.11B | The inspectors identified a Green finding with four examples for failing to conduct and evaluate simulator performance testing in accordance with the standards of ANSI/ANS-3.5-2009. Specifically, the licensee failed to do the following: -Set initial r
Region: IV | Fort Calhoun | 13213 | 03/05/2015 03/30/2015 | 2015010-01 | NRC | VIO | MISC | Green | Failure to Provide Complete and Accurate Information on Licensed Operator Applications | EA Case: 2015020 |  | TE?: Y SL-V-VIO | 05000285 Fort Calhoun |  | NONE | On April 3, 2014, during performance of a self-assessment, the licensee identified a Severity Level IV violation of 10 CFR 50.9, "Completeness and Accuracy of Information," for the Fort Calhoun Station's failure to perform combustion order testing as requ
Region: IV | Fort Calhoun | 13203 | 01/30/2015 03/12/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure during an Operability Determination |  | H.11 Challenge the Unknown | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, for the failure to perform an operability determination in accordance with documented procedures. Specifically, the licensee failed to complete an operability determina
Region: IV | Fort Calhoun | 13211 | 01/30/2015 03/12/2015 | 2015008-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.8 Procedure Adherence | TE?: N | 05000285 Fort Calhoun |  | 71152 | The team reviewed a self-revealing Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify a condition adverse to quality. On October 27, 2014, a condition report was written
Region: IV | Fort Calhoun | 13196 | 12/31/2014 02/12/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Appropriate Preventive Maintenance and Failure to Identify Raw Water SSC Maintenance Rule Performance Criteria Exceeded and thereby establish Monitoring Requirements for the SSC |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | 71111.12 | The inspectors identified an NCV of very low safety significance of 10 CFR 50.65 paragraph (a)(2) "Requirements for Monitoring the Effectiveness of Maintenance of Nuclear Power Plants," because the licensee did not demonstrate that performance of an SSC w
Region: IV | Fort Calhoun | 13202 | 12/31/2014 02/12/2015 | 2014005-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Determine the Availability of Local Population Data for Use in Estimating Changes in the EPZ Population |  | H.5 Work Management | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The NRC identified a Green non-cited violation for the licensee's failure to determine the availability of 2013 state and local population data for use in estimating annual changes in the plume exposure emergency planning zone population. This finding is
Region: IV | Fort Calhoun | 13132 | 10/16/2014 11/25/2014 | 2013018-02 | NRC | NCV | Mitigating Systems | Green | Use of Non-conservative Values in Design Analyses | EA Case: 2014187 | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with non-conservative errors identified in station calculations. Specifically, the licensee failed to use the yield streng
Region: IV | Fort Calhoun | 13133 | 10/16/2014 11/25/2014 | 2013018-03 | NRC | NCV | Mitigating Systems | Green | Failure to Furnish Evidence of Activities Affecting Quality | EA Case: 2014187 |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified three examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," associated with the licensee's failure to furnish evidence of an activity affecting quality. Specifically, the licensee
Region: IV | Fort Calhoun | 13140 | 10/16/2014 11/25/2014 | 2013018-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Inadequate Internal Flooding Analysis | EA Case: 2014187 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," associated with the licensee's failure to adequately evaluate and take prompt corrective actions to address an identified condition adverse to qu
Region: IV | Fort Calhoun | 13141 | 10/16/2014 11/25/2014 | 2013018-05 | NRC | NCV | Mitigating Systems | Green | Use of Non-Conservative Inputs in Thermal Lag Analyses | EA Case: 2014187 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to use conservative inputs. Specifically, the licensee failed to verify that all inputs used in the thermal lag analysis for th
Region: IV | Fort Calhoun | 13144 | 10/16/2014 11/25/2014 | 2013018-06 | NRC | NCV | Mitigating Systems | Green | Failure to Recognize Adverse Design Changes | EA Case: 2014187 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to maintain design control of the auxiliary feedwater system. Specifically, the licensee implemented a modific
Region: IV | Fort Calhoun | 13145 | 10/16/2014 11/25/2014 | 2013018-07 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Auxiliary Feedwater System | EA Case: 2014187 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to maintain design control of the auxiliary feedwater system. Specifically, the licensee implemented a modific
Region: IV | Fort Calhoun | 13117 | 09/30/2014 11/13/2014 | 2014004-01 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Procedural and Alarm Setpoint Changes in Support of an Operability Evaluation |  | H.12 Avoid Complacency | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a Green finding for the licensee's failure to implement procedural changes and water level alarm setpoint changes relied upon by operators to initiate compensatory actions to maintain the operability of raw water pump AC-10C. The
Region: IV | Fort Calhoun | 13118 | 09/30/2014 11/13/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain a Testing Program for the CS System (Section 1R15) |  | P.4 Trending | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee failed to ensure that a surveillance test program was sufficient to demonstrate that the containment spray (CS) system
Region: IV | Fort Calhoun | 13122 | 09/30/2014 11/13/2014 | 2014004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design of the FO-10 to FO-1 Fuel Oil Transfer System |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.18 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." because the licensee did not implement design-control measures commensurate with those applied to the original design when they implement
Region: IV | Fort Calhoun | 13152 | 09/12/2014 09/18/2014 | 2014009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Reports for Gaps Identified in Resolving NRC Non-Cited Violations |  | H.13 Consistent Process | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," was identified involving the failure to follow procedures to initiate condition reports to enter conditions adverse to quality into the corrective a
Region: IV | Fort Calhoun | 13153 | 09/12/2014 09/18/2014 | 2014009-02 | NRC | NCV | Mitigating Systems | Green | Multiple Examples of Failure to Evaluate Operability of Degraded or Non-Conforming Conditions |  | H.14 Conservative Bias | TE?: N | 05000285 Fort Calhoun |  | NONE | Multiple examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified involving the failure to follow Procedure OP-FC-108-115, "Operability Determinations," Revision 0a. In each exa
Region: IV | Fort Calhoun | 13154 | 09/12/2014 09/18/2014 | 2014009-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Adequately Perform an Operability and 50.59 Evaluation |  | P.2 Evaluation | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified involving the failure to evaluate and impleme
Region: IV | Fort Calhoun | 13157 | 09/12/2014 09/18/2014 | 2014009-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Perform an Evaluation for a New Operator Manual Action to Refill Component Cooling Water System During Post-Accident Conditions |  |  | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR 50.59, "Changes, Test, and Experiments," was identified involving the failure to evaluate if a change to the facility as described in the Updated Safety Analysis Report would require prior NRC review and approval. Specifica
Region: IV | Fort Calhoun | 13158 | 09/12/2014 09/18/2014 | 2014009-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Inputs into Safety Injection Piping Stress Calculation |  | H.6 Design Margins | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to implement appropriate design control measures associated with a safety-related pipe stress calculation. Specifically, several unv
Region: IV | Fort Calhoun | 13159 | 09/12/2014 09/18/2014 | 2014009-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of Raw Water Strainer Control Panel |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to maintain design control of the raw water strainer AC-12B control panel AI-348. Specifically, the licensee failed t
Region: IV | Fort Calhoun | 13160 | 09/12/2014 09/18/2014 | 2014009-07 | NRC | NCV | Mitigating Systems | Green | Failure to Accurately Model Flow Path for External Flood Mitigation |  | P.5 Operating Experience | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to accurately model cell level control of river water during external flooding events. Specifically, the licensee failed to account
Region: IV | Fort Calhoun | 13162 | 09/12/2014 09/18/2014 | 2014009-09 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Requirements for Switchgear Room Cooling |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to translate applicable design requirements into the specifications for plant systems. Specifically, inadequate design control input
Region: IV | Fort Calhoun | 13167 | 09/12/2014 09/18/2014 | 2014009-10 | NRC | VIO | Mitigating Systems | Green | Deficient Evaluation of NRC Bulletin 88-04, Strong Pump Weak Pump Due to Failure to Consider the Effect of AFW Pumps Discharge Check Valves Leakage | EA Case: 2014151 | H.14 Conservative Bias | TE?: N | 05000285 Fort Calhoun |  | NONE | (Initial Entry) A cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to assure that applicable regulatory requirements and design bases were correctly translated into specifications, drawi
Region: IV | Fort Calhoun | 13168 | 09/12/2014 09/18/2014 | 2014009-11 | NRC | VIO | Mitigating Systems | Green | Failure to Ensure Safe Operations at Design Basis Low River Level | EA Case: 2014151 | H.1 Resources | TE?: N | 05000285 Fort Calhoun |  | NONE | A cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to ensure that the safety-related raw water pumps are available for safe plant operations down to the design basis low river level. Spec
Region: IV | Fort Calhoun | 13176 | 09/12/2014 09/18/2014 | 2014009-12 | NRC | VIO | Emergency Preparedness | Green | Failure to Maintain Effectiveness of an Emergency Plan | EA Case: 2014151 | H.1 Resources | TE?: N | 05000285 Fort Calhoun |  | NONE | A cited violation of 10 CFR 50.54(q)(2), "Conditions of License," was identified involving the failure to maintain the effectiveness of the site's emergency plan. Specifically, the licensee established an "Alert" low river level emergency classification c
Region: IV | Fort Calhoun | 13177 | 09/12/2014 09/18/2014 | 2014009-13 | NRC | VIO | MISC | Green | Failure to Perform Evaluation for Design Change | EA Case: 2014151 |  | TE?: Y SL-V-VIO | 05000285 Fort Calhoun |  | NONE | A cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," was identified involving the failure to evaluate if a change to the facility as described in the Updated Safety Analysis Report would require prior NRC review and approval. Specifically
Region: IV | Fort Calhoun | 13178 | 09/12/2014 09/18/2014 | 2014009-14 | NRC | VIO | Mitigating Systems | Green | Failure to Account for Worst Case Diesel Frequency in Fuel Oil Consumption Calculations | EA Case: 2014151 | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | NONE | A cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to account for design basis conditions in station calculations. Specifically, the licensee failed to account for worst-case electrical f
Region: IV | Fort Calhoun | 13182 | 09/12/2014 09/18/2014 | 2014009-15 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.6 Design Margins | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take corrective actions for a condition adverse to quality. Specifically, the licensee failed to take corrective actions to ad
Region: IV | Fort Calhoun | 13183 | 09/12/2014 09/18/2014 | 2014009-16 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Longstanding Software Classification Issues |  | H.9 Training | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take timely corrective actions to ensure the proper control and use of software products used in safety related applications.
Region: IV | Fort Calhoun | 13184 | 09/12/2014 09/18/2014 | 2014009-17 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Properly Implement Applicable ASME OM Code Requirements |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to correct a condition adverse to quality associated with classification of check valves in the auxiliary feedwater system. Specifical
Region: IV | Fort Calhoun | 13185 | 09/12/2014 09/18/2014 | 2014009-18 | NRC | NCV | MISC | Green | Failure to Complete Corrective Actions in a Timely Manner |  | H.5 Work Management | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take timely corrective actions to address deficiencies in station calculations. Specifically, the licensee failed to update st
Region: IV | Fort Calhoun | 13186 | 09/12/2014 09/18/2014 | 2014009-19 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain B.5.b Equipment in a State of Readiness to Support Mitigation Strategies |  | H.1 Resources | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR 50.54(hh)(2), "Conditions of License," was identified involving the failure to maintain available equipment needed to implement mitigating strategies to maintain or restore core, containment, and spent fuel pool cooling cap
Region: IV | Fort Calhoun | 13187 | 09/12/2014 09/18/2014 | 2014009-20 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality in the Diesel Generator Starting Air System |  | H.12 Avoid Complacency | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take timely corrective actions to address service life related degradation of the emergency diesel generator st
Region: IV | Fort Calhoun | 13195 | 09/12/2014 09/18/2014 | 2014009-21 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions for an Unsealed Raw Water System Control Panel |  | P.5 Operating Experience | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take corrective actions to address a design deficiency affecting the control panel for raw water strainer AC-12
Region: IV | Fort Calhoun | 13116 | 06/30/2014 07/29/2014 | 2014003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control an Entry to a High Radiation Area Resulting in a Dose Rate Alarm |  | H.4 Teamwork | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.11.1.b, which resulted from an individual entering a high radiation area without being aware of the radiological conditions. Specifically, on July 19, 2013, an oper
Region: IV | Fort Calhoun | 13098 | 03/31/2014 05/14/2014 | 2014007-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures for Classifying Component Failures |  | H.9 Training | TE?: N | 05000285 Fort Calhoun |  | 71111.12 | The inspectors identified a Green finding for the licensee's failure to follow a procedure for classifying component failures. Specifically, the licensee's failure to follow Procedure FCSG-69-5, "Failure Identification and Reporting," is a performance def
Region: IV | Fort Calhoun | 13101 | 03/31/2014 05/14/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow an Immediate Operability Determination Procedure |  | H.7 Documentation | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow an operability determination procedure. Upon identifying that that a relief va
Region: IV | Fort Calhoun | 13103 | 03/31/2014 05/14/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement an Adequate PMT Procedure |  | P.2 Evaluation | TE?: N | 05000285 Fort Calhoun |  | 71111.19 | The inspectors identified a green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to establish and implement an adequate procedure for Post Maintenance Testing (PMT). Specifically,
Region: IV | Fort Calhoun | 13104 | 03/31/2014 05/14/2014 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Immediate Operability Determination |  | H.9 Training | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a green non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an operability determination as required by NOD-QP-31, "Operability Determinations
Region: IV | Fort Calhoun | 13099 | 03/31/2014 05/14/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality in the Containment Internal Structure and Auxiliary Building |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors identified multiple examples of a green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct conditions adverse to quality. Specifically, the lic
Region: IV | Fort Calhoun | 13100 | 03/31/2014 05/14/2014 | 2014007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Check the Adequacy of the Design for the Reactor Vessel Head Structural Elements |  | H.6 Design Margins | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors identified a green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure the design of the Containment Internal Structure (CIS) for the reactor vessel head stand met Curren
Region: IV | Fort Calhoun | 13106 | 03/14/2014 04/25/2014 | 2013017-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," involving the failure to promptly identify and correct a condition adverse to quality. Specifically, from August 2005 to July 15, 2013 the licens
Region: IV | Fort Calhoun | 13107 | 03/14/2014 04/25/2014 | 2013017-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Station Procedure NOD-QP-31, "Operability Determination
Region: IV | Fort Calhoun | 13114 | 03/14/2014 04/25/2014 | 2013017-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Temporary Modification to Protect Against Tornado Generated Missiles |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to provide adequate instructions or procedures for the construction of temporary barrier
Region: IV | Fort Calhoun | 13115 | 03/14/2014 04/25/2014 | 2013017-05 | NRC | NCVIV | MISC | Green | Failure to Obtain Prior NRC Approval for a Change in Method of Evaluation |  |  | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 92702 | The team identified three examples of a non-cited violation of 10 CFR 50.59, "Changes, Test, and Experiments," associated with the licensee's failure to adequately evaluate changes to determine if prior NRC approval is required. Specifically, from April 1
Region: IV | Fort Calhoun | 13015 | 02/15/2014 03/19/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate HPSI Pump Design Requirements to Design Documents (Section 4OA3.2). | EA Case: 2014037 |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | A non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to translate the High Pressure Safety Injection (HPSI) pump design and runout characteristics to design documents such as the Updated Saf
Region: IV | Fort Calhoun | 13016 | 02/15/2014 03/19/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of HPSI Injection Valve (Section 4OA3.4) | EA Case: 2014037 |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | Two examples of a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," were identified. The first example involved the failure to establish procedures or Technical Specifications to accomplish required HPSI injection flow balanci
Region: IV | Fort Calhoun | 13020 | 02/15/2014 03/19/2014 | 2014002-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Request a License Amendment for Required Change to Technical Specifications (Section 4OA3.4) | EA Case: 2014037 | H.9 Training | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 71153 | A Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," and an associated Green finding was identified involving the failure to request a license amendment for a facility change that required a change to the Technical S
Region: IV | Fort Calhoun | 13036 | 02/15/2014 03/19/2014 | 2014002-06 | NRC | VIO | Barrier Integrity | Green | Failure to Restore Compliance for Containment Spray Runout Conditions | EA Case: 2014037 | H.12 Avoid Complacency | TE?: N | 05000285 Fort Calhoun |  | NONE | (Initial Entry) A cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to take timely corrective action for a condition adverse to quality. Specifically, the licensee failed to restore complia
Region: IV | Fort Calhoun | 13037 | 02/15/2014 03/19/2014 | 2014002-07 | NRC | NCV | Mitigating Systems | Green | Inadequate 10 CFR 50.59 Screening for Containment Spray Design Change (Section 4OA3.8 | EA Case: 2014037 |  | TE?: N | 05000285 Fort Calhoun |  | NONE | A non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" was identified involving the licensee's failure to complete a 10 CFR 50.59 screening that met the requirements of Procedure NOD-QP-3, "10 CFR 50.59 and 1
Region: IV | Fort Calhoun | 13038 | 02/15/2014 03/19/2014 | 2014002-08 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Design Anchorage for Containment Spray and Raw Water System Pipe Supports | EA Case: 2014037 |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | Several examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," were identified involving the failure to ensure the adequacy of the anchorage for several raw water system and containment spray system pipe supports
Region: IV | Fort Calhoun | 13041 | 02/15/2014 03/19/2014 | 2014002-09 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Design Requirements for Containment Air Cooler Pipe Supports | EA Case: 2014037 |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | A non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified involving the failure to ensure the adequacy of the U-bolts for containment air cooler pipe supports VAS-1 and VAS-2. Specifically the U-bolt design was n
Region: IV | Fort Calhoun | 13009 | 12/31/2013 02/10/2014 | 2013019-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct Deficiencies in Operations Support Center Functions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71114.01 | A Green noncited violation was identified for the failure of the licensee to correct deficiencies identified as a result of four exercises conducted between March 27, 2012, and May 7, 2013, as required by 10 CFR 50.47(b)(14). Specifically, the licensee fa
Region: IV | Fort Calhoun | 13042 | 07/19/2013 04/03/2014 | 2013013-01 | NRC | NCV | Mitigating Systems | Green | Failure to Complete all Testing for a Condition Averse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to fully implement
Region: IV | Fort Calhoun | 13043 | 07/19/2013 04/03/2014 | 2013013-02 | NRC | NCV | Mitigating Systems | Green | Failure to Furnish Evidence of an Activity Affecting Quality |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVII, "Quality Assurance Records," associated with the licensee's failure to furnish evidence of an activity affecting quality associated with the 480 V breakers. Specifica
Region: IV | Fort Calhoun | 13048 | 07/19/2013 04/03/2014 | 2013013-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Prevent Repetition of a Significant Condition Adverse to Quality, a White MSPI SSFF Degrading Tend |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's approval of Root Cause Analysis 2013-03424, Revision 0 and Revision 1, "MSPI Safety System Functional Failures Degrading Trend," which did not assur
Region: IV | Fort Calhoun | 13053 | 07/19/2013 04/03/2014 | 2013013-06 | NRC | NCV | Mitigating Systems | Green | Failure to Control Deviations From the Design Basis Requirements for Structural Calculations Related to the Reactor Coolant System |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified multiple examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to control deviations from design standards. Specifically, the licensee failed to control deviations
Region: IV | Fort Calhoun | 13054 | 07/19/2013 04/03/2014 | 2013013-07 | NRC | NCV | Mitigating Systems | Green | Programmatic Failure to Evaluate Safety Impact of Degraded Conditions During Use of Interim Operability Criteria |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified multiple examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, the licensee's failure to follow station procedures for corrective actions, operability, and
Region: IV | Fort Calhoun | 13055 | 07/19/2013 04/03/2014 | 2013013-08 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Overstressed Components |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified multiple examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, the licensee's failure to follow station procedures for corrective actions, operability, and
Region: IV | Fort Calhoun | 13057 | 07/19/2013 04/03/2014 | 2013013-09 | NRC | NCV | Mitigating Systems | Green | Non-conservative Criteria in Operability Procedure |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to develop an adequate procedure for assessing operability of degraded piping and pipe support
Region: IV | Fort Calhoun | 13058 | 07/19/2013 04/03/2014 | 2013013-10 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Station Procedure NOD-QP-31, "Operability Determination Process." Specifically
Region: IV | Fort Calhoun | 13059 | 07/19/2013 04/03/2014 | 2013013-11 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Effects of Modifying the Turbine Driven Auxiliary Feedwater Pump |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to conduct an adequate evaluation of the impacts of modifying the turbine driven auxiliary feedwater pump (FW
Region: IV | Fort Calhoun | 13060 | 07/19/2013 04/03/2014 | 2013013-12 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Operating Experience Reviews |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's programmatic failure to conduct adequate operating experience reviews for root cause evaluations in accordan
Region: IV | Fort Calhoun | 13061 | 07/19/2013 04/03/2014 | 2013013-13 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Requirements for Switchgear Room Cooling |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to fully incorporate applicable design requirements into the plant design. Specifically, from initial construc
Region: IV | Fort Calhoun | 13062 | 07/19/2013 04/03/2014 | 2013013-14 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Action for Non-Seismic Category 1 Piping |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions regarding non-Category I (seismic) piping in the intake structure raw water vault.
Region: IV | Fort Calhoun | 13063 | 07/19/2013 04/03/2014 | 2013013-15 | NRC | NCV | Mitigating Systems | Green | Lack of an Adequate Operability Evaluation for Class 1 Raw Water Piping in Non-Class 1 Service Building |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to follow Station Procedure NOD-QP-31, "Operability Determination Process," to adequatel
Region: IV | Fort Calhoun | 13064 | 07/19/2013 04/03/2014 | 2013013-16 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination Due to Failure to Consider an Unavailable Raw Water Pump |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," involving the licensee's failure to follow procedures when evaluating the impact of the removal of the motor for raw water Pump
Region: IV | Fort Calhoun | 13065 | 07/19/2013 04/03/2014 | 2013013-17 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Sluice Gate Leakage Into Operating Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to correctly translate the acceptance limit of intake sluice gate leakage values into procedures. Specifically
Region: IV | Fort Calhoun | 13066 | 07/19/2013 04/03/2014 | 2013013-18 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Intake Cell Level Control During a Flooding Event |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to maintain an adequate procedure for site flooding. Specifically, since June 2013, the licensee fai
Region: IV | Fort Calhoun | 13067 | 07/19/2013 04/03/2014 | 2013013-19 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Appendix R License Exemptions into the Plant's Fire Protection Program Design |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of License Condition 3.D, "Fire Protection Program," for the failure to translate Appendix R license exemptions into the fire protection program design. Specifically, the licensee failed to translate the exemption
Region: IV | Fort Calhoun | 13085 | 07/19/2013 04/03/2014 | 2013013-21 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Extent of Condition Reviews |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to document the extent of condition review for a number of Root Cause Analyses in accordance with correct
Region: IV | Fort Calhoun | 12995 | 06/30/2013 08/09/2013 | 2013005-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Post A High Radiation Area Resulting In A Dose Rate Alarm |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.11.1, which was the result of a radiation protection technician failing to monitor changing radiological conditions and post a high radiation area. As a result, an o
Region: IV | Fort Calhoun | 12998 | 06/30/2013 08/09/2013 | 2013005-02 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Adequately Plan and Control Work Activities to Maintain Doses ALARA |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 71124.02 | The inspectors reviewed a self-revealing finding of very low safety significance involving the licensee's failure to adequately plan and control work activities relating to the Chemical Volume Control System piping to maintain doses ALARA. Specifically, t
Region: IV | Fort Calhoun | 12999 | 06/30/2013 08/09/2013 | 2013005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure To Survey Resulting In Unintended Occupational Dose |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 71124.03 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 20.1501(a), which was the result of an inadequate survey to evaluate potential hazards from airborne radiation. As a result, a radiation worker received an uptake of 10 millirem i
Region: IV | Fort Calhoun | 12955 | 06/10/2013 07/16/2013 | 2013008-02 | NRC | FIN | Mitigating Systems | Green | Frazil Ice Monitor Not Operational |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a finding for the licensee's failure to maintain their frazil ice detector operational. The detector was sampling a non-representative water temperature which would not have warned operators of the presence of conditions favorable for
Region: IV | Fort Calhoun | 12956 | 06/10/2013 07/16/2013 | 2013008-03 | NRC | NCV | Mitigating Systems | Green | Lack of Safety-Related Equipment for Design Basis Low River Level |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to have safety-related equipment to ensure safe operations down to the design basis low river level. Specifica
Region: IV | Fort Calhoun | 12981 | 06/10/2013 07/16/2013 | 2013008-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Combating Loss of Raw Water |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of Technical Specification 5.8.1, Procedures, for the licensee's failure to maintain an adequate procedure for the loss of raw water cooling. Specifically, since April 2011, the licensee failed to maintain Procedu
Region: IV | Fort Calhoun | 12962 | 06/10/2013 07/16/2013 | 2013008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Worst Case Conditions in Fuel Oil Inventory Calculation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to account for design basis conditions in their fuel oil consumption calculation. Specifically, since June 201
Region: IV | Fort Calhoun | 12963 | 06/10/2013 07/16/2013 | 2013008-08 | NRC | NCV | Mitigating Systems | Green | Sluice Gate Leakage Not Periodically Verified |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that a critical parameter in the design calculation for intake cell level control (sluice gate leaka
Region: IV | Fort Calhoun | 12964 | 06/10/2013 07/16/2013 | 2013008-10 | NRC | NCV | Mitigating Systems | Green | Failure to Accurately Model Raw Water Flow into the Intake Structure |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to accurately model the traveling screens and trash racks in the flow calculation for cell level control. Spec
Region: IV | Fort Calhoun | 12968 | 06/10/2013 07/16/2013 | 2013008-11 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Usable Fuel Oil Tank Level in Inventory |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to translate the usable volume of fuel oil in tank FO-1 into the applicable design documentation. Specifically
Region: IV | Fort Calhoun | 12969 | 06/10/2013 07/16/2013 | 2013008-12 | NRC | NCV | Mitigating Systems | Green | Inadequate Root Cause for a Significant Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to promptly identify, correct, and prevent recurrence of a significant condition adverse to quality. Specif
Region: IV | Fort Calhoun | 12970 | 06/10/2013 07/16/2013 | 2013008-13 | NRC | NCV | Mitigating Systems | Green | Failure to Establish and Document Basis for Test Acceptance Criteria |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to assure that applicable design basis information, as defined in 10 CFR 50.2, for breaker testing was correct
Region: IV | Fort Calhoun | 12971 | 06/10/2013 07/16/2013 | 2013008-15 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality Involving Frequency Compatibility Issues in the 120 Vac System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun 05000285 Fort Calhoun |  | 92702 | The team reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to address frequency compatibility issues in the 120 Vac electrical distribution system. Specifically, be
Region: IV | Fort Calhoun | 12972 | 06/10/2013 07/16/2013 | 2013008-16 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Additional Diesel Loading from Non-Safety Loads |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criteria III, "Design Control," for the licensee's failure to update calculations to account for non safety-related loads supplied by the emergency diesel generator through non-quali
Region: IV | Fort Calhoun | 12977 | 06/10/2013 07/16/2013 | 2013008-17 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Maintenance Rule |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to adequately monitor the performance of structures, systems, and com
Region: IV | Fort Calhoun | 12992 | 06/10/2013 07/16/2013 | 2013008-18 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Instructions for Restoring Temporary Modifications |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to establish adequate instructions for restoring temporary modifications. Specifically,
Region: IV | Fort Calhoun | 12978 | 06/10/2013 07/16/2013 | 2013008-19 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Condition Reports in Accordance with the Corrective Action Program Procedures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to initiate condition reports when problems or conditions adverse to quality were identified in acco
Region: IV | Fort Calhoun | 12979 | 06/10/2013 07/16/2013 | 2013008-20 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Conditions Adverse to Quality |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct conditions adverse to quality. Specifically, between July 2012 and March 2013, the tea
Region: IV | Fort Calhoun | 12980 | 06/10/2013 07/16/2013 | 2013008-24 | NRC | NCV | Mitigating Systems | Green | Failure to Effectively Monitor the Performance of Penetration Seals |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50.65(a)(2), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," associated with the licensee's failure to effectively monitor the performance of penetration seals in
Region: IV | Fort Calhoun | 12982 | 06/10/2013 07/16/2013 | 2013008-25 | NRC | NCV | Mitigating Systems | Green | Deficient Evaluation for Known Degraded Conditions: Safety-Related Air Operated Valve Elastomers not Qualified for HELB/LOCA Temperatures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to properly evaluate a known degraded condition regarding safety-related air operated valve elastomers that
Region: IV | Fort Calhoun | 12986 | 06/10/2013 07/16/2013 | 2013008-31 | NRC | NCV | Mitigating Systems | Green | Multiple Examples of Operability Determinations that Lacked Adequate Technical Justification |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," involving multiple examples of the licensee's failure to perform an adequate operability determination as required by Procedure
Region: IV | Fort Calhoun | 12987 | 06/10/2013 07/16/2013 | 2013008-32 | NRC | NCV | Mitigating Systems | Green | Multiple Examples of Inadequate Risk-Based Operability Determinations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," involving multiple examples of the licensee's use of probability or probabilistic risk assessment when performing operability de
Region: IV | Fort Calhoun | 12950 | 05/29/2013 07/11/2013 | 2013010-01 | NRC | NCV | Initiating Events | Green | HPSI Pump Flow Imbalance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 92702 | The NRC identified a non-cited violation of Technical Specification 5.8.1.a for failure to establish, implement, and maintain a procedure recommended in Regulatory Guide 1.33, Revision 2, Appendix A. Specifically, the licensee failed to establish a proced
Region: IV | Fort Calhoun | 12951 | 05/29/2013 07/11/2013 | 2013010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Multiple Alarm Response Procedures Related to SIT Operation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The NRC identified a non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, for failure to correct a condition adverse to quality. Specifically, the licensee failed to identify and correct 18 alarm response procedures (ARPs) associ
Region: IV | Fort Calhoun | 12952 | 05/29/2013 07/11/2013 | 2013010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Emergency Operating Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The NRC identified a non-cited violation of Technical Specification 5.8.1.a. for failure to maintain written procedures identified in Regulatory Guide 1.33, Revision 2, Appendix A. Specifically, the licensee failed to maintain Emergency Operating Procedur
Region: IV | Fort Calhoun | 12953 | 05/29/2013 07/11/2013 | 2013010-04 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Extent of Condition Evaluation |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors identified a finding for the licensee's failure to follow their corrective action program procedures and perform an extent of condition evaluation. Specifically, the licensee failed to perform an extent of condition evaluation on emergency
Region: IV | Fort Calhoun | 12954 | 05/29/2013 07/11/2013 | 2013010-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Work Control Procedures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.8.1.a, which resulted from workers failing to follow maintenance work control procedures. On April 1, 2012, the facility experienced a raw water pump trip and subse
Region: IV | Fort Calhoun | 13003 | 05/18/2013 06/13/2013 | 2013004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform Siren Maintenance as Required by the Alert and Notification System Design Report |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71114.02 | The inspectors identified a noncited violation of 10 CFR 50.54(q)(2) for failure to follow an emergency plan meeting the planning standards of 10 CFR 50.47(b). Specifically, the licensee did not meet 50.47(b)(5) because they failed to fully implement prev
Region: IV | Fort Calhoun | 12910 | 05/01/2013 05/24/2013 | 2013012-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to translate raw water pump anchor bolt specifications into calculations and drawings |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team reviewed a self-revealing finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the failure to translate the design basis into instruction
Region: IV | Fort Calhoun | 12348 | 05/01/2013 05/24/2013 | 2013012-02 | NRC | FIN | Mitigating Systems | Green | Inadequate functionality evaluation of the raw water pump anchor bolts |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified a finding of very low safety significance involving the licensee's failure to meet the requirements of the American Concrete Institute (ACI) 349-01. Specifically, the licensee's past functionality calculation failed to ensur
Region: IV | Fort Calhoun | 12811 | 05/01/2013 05/24/2013 | 2013012-03 | NRC | NCV | Mitigating Systems | Green | Failure to correct thermal stress acceptance limits in raw water piping and piping support calculations |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified a finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct a condition adverse to quality involving r
Region: IV | Fort Calhoun | 12311 | 05/01/2013 05/24/2013 | 2013012-04 | NRC | NCV | Mitigating Systems | Green | Failure to adequately design containment air coolers structural bracing |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified a finding of very low safety significance (Green) and an associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the for the failure to ensure the adequacy of the design for the cont
Region: IV | Fort Calhoun | 12846 | 05/01/2013 05/24/2013 | 2013012-05 | NRC | NCV | Mitigating Systems | Green | Failure to adequately implement design requirements for U-bolt support |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified a finding of very low safety significance (Green) and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the adequacy of the design for Raw Water Pipe Sup
Region: IV | Fort Calhoun | 12847 | 05/01/2013 05/24/2013 | 2013012-06 | NRC | NCV | Mitigating Systems | Green | Failure to translate design requirements for embedded unistrut supports into calculations |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified several examples of very low safety significance (Green) non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the design basis for pipe supports SIH-17, SIH-94 and SIH
Region: IV | Fort Calhoun | 12801 | 05/01/2013 05/24/2013 | 2013012-07 | NRC | NCV | Mitigating Systems | Green | Failure to translate electrical switchgear cabinet anchor bolt design specifications into drawings |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspection team identified several examples of a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to ensure the design basis for all the 480V and 4160V buss switchgear cabinets were correctly tr
Region: IV | Fort Calhoun | 12938 | 04/15/2013 07/16/2013 | 2013008-04 | NRC | NCV | Emergency Preparedness | Green | Non-Conservative Value for Declaring an Alert on Low River Level |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50.54(q)(2) for the licensee's failure to maintain the effectiveness of an emergency plan. Specifically, since May 14, 2009, the licensee failed to maintain a proper value for low river level associated
Region: IV | Fort Calhoun | 12937 | 04/15/2013 07/16/2013 | 2013008-21 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure that Design Requirements Associated with the Containment Electrical Penetration Assemblies Were Correctly Translated Into Installed Plant Equipment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to translate applicable regulatory requirements and the design basis into specifications, drawings, procedures
Region: IV | Fort Calhoun | 12917 | 04/15/2013 07/16/2013 | 2013008-26 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Inspect, Maintain, and Test Emergency Feedwater Tank Equipment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure proper inspection, maintenance, and testing of equipment associated with emergency feedwater tank FW
Region: IV | Fort Calhoun | 12921 | 04/15/2013 07/16/2013 | 2013008-33 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination due to Failure to Establish Component Cooling Water System Leakage Criteria |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," involving the licensee's failure to follow procedures when evaluating the impact of component cooling water system leakage on th
Region: IV | Fort Calhoun | 12922 | 04/15/2013 07/16/2013 | 2013008-34 | NRC | NCV | Mitigating Systems | Green | Failure to Follow ASME Code Requirements when Establishing New Pump Reference Values as Corrective Actions (#35) |  |  | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50.55a, "Codes and Standards," for the failure of the licensee to follow the ASME Code when establishing new reference curves as corrective action to address the performance of component cooling water pu
Region: IV | Fort Calhoun | 12923 | 04/15/2013 07/16/2013 | 2013008-35 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Condition Adverse to Quality Associated with Corrective Action Program Procedures and the Operability Process |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to implement corrective actions to address significant flaws identified in procedures involving the degraded/nonconforming condit
Region: IV | Fort Calhoun | 12924 | 04/15/2013 07/16/2013 | 2013008-36 | NRC | NCV | Mitigating Systems | Green | Deficient Evaluation of NRC Bulletin 88-04, Strong Pump Weak Pump Due to Failure to Consider The Effect of AFW Pumps Discharge Check Valves Leakage |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to properly evaluate NRC Bulletin 88-04, "Potential Safety-Related Pump Loss," regarding the auxiliary feedwat
Region: IV | Fort Calhoun | 12925 | 04/15/2013 07/16/2013 | 2013008-37 | NRC | NCV | Mitigating Systems | Green | Improper Storage of the Raw Water to Auxiliary Feedwater Emergency Tank Fill Hose |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to properly store the raw water to emergency feedwater storage tank fill hose. Specifica
Region: IV | Fort Calhoun | 12929 | 04/15/2013 07/16/2013 | 2013008-38 | NRC | NCV | Mitigating Systems | Green | Deficient Evaluation for Known Degraded Conditions - AFW Pumps Discharge Check Valve Leakage and Potential Overpressure of AFW Pump Suction Piping |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to properly evaluate a known degraded condition regarding the auxiliary feedwater pump discharge check valv
Region: IV | Fort Calhoun | 12930 | 04/15/2013 07/16/2013 | 2013008-39 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Applicable ASME OM Code Requirements |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified two examples of a non-cited violation of 10 CFR 50.55a.(f)(4)(ii), "Codes and Standards," associated with the licensee's failure to properly implement applicable code requirements for in-service testing of safety-related pumps and chec
Region: IV | Fort Calhoun | 12939 | 04/15/2013 07/16/2013 | 2013008-40 | NRC | NCVIV | MISC | Green | Failure to Obtain Prior NRC Approval for a Facility Change |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR 50.59, "Changes, Test, and Experiments," associated with the licensee's failure to adequately evaluate changes in order to ensure that they did not require prior NRC approval. Specifically, from March 4,
Region: IV | Fort Calhoun | 12936 | 04/15/2013 07/16/2013 | 2013008-41 | NRC | NCV | Mitigating Systems | Green | Inappropriate Modification of Turbine Driven Auxiliary Feedwater Pump Back Pressure Protection Trip |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with an inappropriate modification of the auxiliary feedwater system. Specifically, from April 2011 through February 2013, measures establ
Region: IV | Fort Calhoun | 12895 | 03/01/2013 03/11/2013 | 2013011-02 | NRC | NCVIV | Mitigating Systems | Green | Two Examples of Failure to Obtain Prior NRC Approval for Flooding Mitigation Strategies |  | P.1(c) Evaluation of Identified Problems | TE?: Y SL-IV-NCVIV | 05000285 Fort Calhoun |  | 92702 | The inspectors identified two examples of a Severity Level IV violation of 10 CFR 50.59, Changes, Tests and Experiments," and associated Green findings for the licensee's failure to appropriately perform written evaluations for two changes for flooding mi
Region: IV | Fort Calhoun | 12882 | 12/31/2012 02/14/2013 | 2012012-01 | NRC | NCV | Initiating Events | Green | Hot Work Procedures Allowed a Roving Fire Watch |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a Green non-cited violation of Technical Specification 5.8.1.c for the failure to maintain written procedures covering fire protection program implementation. Specifically, the licensee changed the hot work procedure to allow a r
Region: IV | Fort Calhoun | 12890 | 12/31/2012 02/14/2013 | 2012012-03 | NRC | FIN | Mitigating Systems | Green | Failure to Manage Functionality of the River Sluice Gates |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a finding for the failure to manage the functionality of the river sluice gates. Specifically, the licensee's preventive maintenance program requirements were not appropriately implemented for a period of 12 months and as a result, the
Region: IV | Fort Calhoun | 12891 | 12/31/2012 02/14/2013 | 2012012-04 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Maintenance Rule Program |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The team identified a Green noncited violation of 10 CFR 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants" which states, in part, that "the licensee shall monitor the performance or condition of structures, syst
Region: IV | Fort Calhoun | 12875 | 11/17/2012 12/31/2012 | 2012011-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Operability Determination for Containment Internal Structures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The NRC identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Procedures," for the failure to perform an adequate operability determination as required by FCS Procedure NOD-QP-31, "Operability Determination Process." Specific
Region: IV | Fort Calhoun | 12876 | 11/17/2012 12/31/2012 | 2012011-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71124.01 | Inspectors reviewed a self-revealing Green noncited violation of Technical Specification 5.8.1.a for the failure to follow procedure requirements related to radiation work permit requirements. Specifically, workers unexpectedly created a high radiation ar
Region: IV | Fort Calhoun | 12877 | 11/17/2012 12/31/2012 | 2012011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Adequate Equipment was Available to Measure River Level Locally to be Able to Comply with an Abnormal Operating Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 92702 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to ensure that adequate equipment was available to measure river level locally to comply with an abnormal operating proce
Region: IV | Fort Calhoun | 12878 | 11/17/2012 12/31/2012 | 2012011-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Basis Documentation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 92702 | The NRC identified a non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Procedures," for failing to follow a quality procedure. Specifically; PED-QP-13 "Design Basis Document Control," requires FCS to update and maintain their Design Bases Documen
Region: IV | Fort Calhoun | 12881 | 11/17/2012 12/31/2012 | 2012011-05 | NRC | FIN | Mitigating Systems | Green | Failure to Properly Scope All the Pertinent External Flood Protection Features into the Walkdown List in Accordance with Industry Guidance NEI 12-07 |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a finding of very low safety significance (Green) for the licensee's failure to generate a complete inspection list, with all the external flood protection features credited in the current licensing basis documents for flooding e
Region: IV | Fort Calhoun | 12871 | 09/30/2012 11/13/2012 | 2012005-02 | NRC | NCV | Initiating Events | Green | Untimely Corrective Actions for 480 VAC Breaker Issues |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 92702 | The NRC identified a noncited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to take timely corrective actions with respect to nonconforming conditions in several circuit breakers. These conditions were
Region: IV | Fort Calhoun | 12868 | 08/18/2012 10/02/2012 | 2012004-02 | NRC | NCV | Barrier Integrity | Green | Fuel Move with SFP Ventilation Inoperable a Condition Prohibited by Technical Specification 2.8.3(4) |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71124.06 | The inspectors identified a non-cited violation of very low safety significance of Technical Specification 2.8.3(4), the limiting condition for refueling operations in the spent fuel pool. In December 2009, the licensee performed refueling operations with
Region: IV | Fort Calhoun | 12869 | 08/18/2012 10/02/2012 | 2012004-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Establish and Implement Adequate Procedures for Meteorological Monitoring and the Off-Site Dose Calculation Manual |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71124.07 | Inspectors identified two examples of a non-cited violation of very low safety significance of Technical Specification 5.8.1 for the failure to adequately establish, implement, and maintain procedures for: (1) the onsite meteorological monitoring systems;
Region: IV | Fort Calhoun | 12860 | 06/30/2012 08/13/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Personnel Meet Minimum Educational Requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a noncited violation of Technical Specification 5.3.1, "Facility Staff Qualifications," for failure to ensure electrical group supervisors met the minimum qualification requirements specified in American National Standards Instit
Region: IV | Fort Calhoun | 12839 | 06/07/2012 07/05/2012 | 2012301-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE PROCEDURES WITH SEVEN EXAMPLES FOR MITIGATING SYSTEMS CORNERSTONE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with seven examples. - Example 1: There is no procedure guidance p
Region: IV | Fort Calhoun | 12845 | 06/07/2012 07/05/2012 | 2012301-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO COMPLY WITH TECHNICAL SPECIFICATIONS 2.3(1)(i) FOR SAFETY INJECTION TANK OPERABILITY |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a non-cited violation for failing to comply with Technical Specification 2.3(1)(i) in that multiple Safety Injection Tanks were connected together simultaneously for filling operations on at least two occasions, once while sluicing on
Region: IV | Fort Calhoun | 12852 | 06/07/2012 07/05/2012 | 2012301-04 | NRC | NCV | Initiating Events | Green | INADEQUATE PROCEDURES WITH FIVE EXAMPLES FOR THE INITIATING EVENTS CORNERSTONE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with five examples. - Example 1: Alarm Response Procedure ARP-CB-1
Region: IV | Fort Calhoun | 12853 | 06/07/2012 07/05/2012 | 2012301-05 | NRC | NCV | Barrier Integrity | Green | FAILURE TO CORRECTLY TRANSLATE THE DESIGN BASIS FOR THE CONTAINMENT SPRAY SYSTEM |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, design control measures did not assure that the design basis for safety related sy
Region: IV | Fort Calhoun | 12859 | 06/07/2012 07/05/2012 | 2012301-06 | NRC | NCV | Barrier Integrity | Green | INADEQUATE PROCEDURES WITH FOUR EXAMPLES FOR THE BARRIER INTEGRITY CORNERSTONE |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a finding of very low safety significance involving a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with four examples. - Example 1. The normal operating instruction
Region: IV | Fort Calhoun | 12830 | 05/17/2012 06/13/2012 | 2012007-03 | NRC | NCV | Mitigating Systems | Green | ALTERNATE SHUTDOWN PROCEDURE DOES NOT ACCOUNT FOR SINGLE WORST CAST SPURIOUS ACTUATIONS |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The inspectors identified a non-cited violation with two examples related to the failure to establish an alternate shutdown capability that met the requirements of License Condition 3.D and the performance criteria in 10 CFR Part 50, Appendix R, Section I
Region: IV | Fort Calhoun | 12831 | 05/17/2012 06/13/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE ADEQUATE ALTERNATE SHUTDOWN CAPABILITY |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The inspectors identified a non-cited violation of Technical Specification 5.8.1.c for an inadequate fire protection procedure. Specifically, the post fire safe shutdown procedure had several deficiencies that would have prevented implementation of the al
Region: IV | Fort Calhoun | 12838 | 05/17/2012 06/13/2012 | 2012007-05 | NRC | NCV | Mitigating Systems | Green | UNTIMELY CORRECTIVE ACTIONS RELATED TO REVISING A POST-FIRE SAFE SHUTDOWN PROCEDURE |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a non-cited violation of License Condition 3.D and the Quality Assurance Plan for failure to take timely corrective action. Specifically, the licensee revised procedure steps to open the breakers for the reactor coolant gas vent
Region: IV | Fort Calhoun | 12817 | 03/31/2012 05/11/2012 | 2012002-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Promptly Recognize and Communicate Siren System Failures |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The inspector identified a non-cited violation of 10 CFR 50.54(q)(2) for failure to follow the licensee's emergency plan. Specifically, the licensee did not follow the Radiological Emergency Response Plan, Section E, "Notification Methods and Procedures,"
Region: IV | Fort Calhoun | 12818 | 03/31/2012 05/11/2012 | 2012002-05 | NRC | NCV | Emergency Preparedness | Green | Failure To Comply With An Emergency Plan Requirement To Notify Offsite Authorities Within 15 Minutes Of An Emergency |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 71151 | The inspectors identified a non-cited violation of 10 CFR 50.54(q) for failure to follow an emergency plan requirement during a declared alert. Specifically, the licensee did not notify the states of Nebraska and Iowa of the emergency within 15 minutes of
Region: IV | Fort Calhoun | 12808 | 02/02/2012 03/16/2012 | 2011006-01 | NRC | NCV | MISC | Green | Failure to Correct Identified Corrective Action Program Deficiencies |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71152B | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions." After identifying deficiencies that constituted a significant condition adverse to quality in the implementation of the corrective action progra
Region: IV | Fort Calhoun | 12809 | 02/02/2012 03/16/2012 | 2011006-02 | NRC | VIO | Initiating Events | Green | Inadequate Corrective Actions to Ensure Reliability of Raw Water Pump Power Cables | EA Case: 2012035 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take effective corrective action following the initial discovery of water intrusion in cable vault manholes MH-5 and MH-31 in 1998, 2005
Region: IV | Fort Calhoun | 12810 | 02/02/2012 03/16/2012 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Degraded Electrical Insulation on the Component Cooling Water System Motors Cables |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct conditions adverse to quality. Specifically, the licensee failed to correct degraded conditions asso
Region: IV | Fort Calhoun | 12812 | 02/02/2012 03/16/2012 | 2011006-04 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Extent of Condition Evaluation |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a finding for failure of the licensee to follow directions of an apparent cause evaluation to perform an extent of condition evaluation. Specifically, following the identification of an inadequate temporary design modification that rend
Region: IV | Fort Calhoun | 12813 | 02/02/2012 03/16/2012 | 2011006-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Measures to Maintain Vendor Manual Design Control Information |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to establish adequate measures for the selection and review for suitability of application of parts equipment, and processes that are
Region: IV | Fort Calhoun | 12814 | 02/02/2012 03/16/2012 | 2011006-06 | NRC | NCV | Mitigating Systems | Green | Failure to Implement an Adequate Trending Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for inadequate procedures that are used to implement the licensee trending program. Specifically, on December 1, 2011, the
Region: IV | Fort Calhoun | 12815 | 02/02/2012 03/16/2012 | 2011006-07 | NRC | NCV | Initiating Events | Green | Failure to Follow Housekeeping Program Requirements |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71152B | The NRC identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to properly implement procedural requirements to control transient equipment and materials. Specifically,
Region: IV | Fort Calhoun | 12804 | 12/31/2011 02/14/2012 | 2011005-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure Results in a Loss of Reactor Coolant |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71111.04Q | A self-revealing noncited violation of Fort Calhoun Station Technical Specification 5.8.1 occurred due to the licensee's failure to follow a procedure for placing the reactor coolant system level monitors into service. This failure resulted in the inadver
Region: IV | Fort Calhoun | 12799 | 12/31/2011 02/14/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Performance Monitoring Test For Component Cooling Water Heat Exchangers |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71111.07T | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which requires, in part, that a test program shall be established to assure that all testing required to demonstrate that structures, systems, and
Region: IV | Fort Calhoun | 12798 | 12/31/2011 02/14/2012 | 2011005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 71124.04 | Inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.8.1 for failure to follow procedures requiring workers to comply with radiological work permit instructions. Specifically, two workers changed the work scope for valve F
Region: IV | Fort Calhoun | 12800 | 12/31/2011 02/14/2012 | 2011005-04 | NRC | NCV | Emergency Preparedness | Green | Inadequate Licensee Procedure for Making Protective Action Recommendations |  |  | TE?: N | 05000285 Fort Calhoun |  | 71151 | The inspectors identified a noncited violation of 10 CFR 50.47(b)(10) for failure to develop and put into place guidelines for the choice of protective actions during an emergency that implemented federal guidance. Specifically, licensee guidance did not
Region: IV | Fort Calhoun | 12354 | 09/30/2011 11/14/2011 | 2011004-01 | NRC | NCV | Initiating Events | Green | Failure to Incorporate Design Information Into Procedures |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for failure to incorporate design information into procedures for operation of the component cooling water system for temporary off-normal system
Region: IV | Fort Calhoun | 12355 | 09/30/2011 11/14/2011 | 2011004-02 | NRC | NCV | Initiating Events | Green | Failure to Provide Adequate Procedures to Ensure Leak Before Break Commitment |  |  | TE?: N | 05000285 Fort Calhoun |  | 71151 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V for failure to have adequate instructions, procedures, or drawings including appropriate quantitative or qualitative acceptance criteria to ensure they can de
Region: IV | Fort Calhoun | 12356 | 09/30/2011 11/14/2011 | 2011004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Identify and Correct the Lack of Calibration for the HE-2 Crane Load Weighing System |  |  | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B Criterion XVI for the failure to identify and correct a condition adverse to quality. Specifically, with regard to the calibration of the load weighing system for the HE-2 crane prior
Region: IV | Fort Calhoun | 12346 | 06/30/2011 08/11/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Design a Reactant Coolant Pump Lube Oil Collection System |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.05Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix R, Section III.O for the failure to ensure an adequate seismic design of the reactor coolant pumps oil collection system. The licensee used 2-inch copper pipe with brazed joints in
Region: IV | Fort Calhoun | 12347 | 06/30/2011 08/11/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Scaffolding Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.8.1.a for failure to follow scaffold specification and construction Procedures SO-M-35 and PED-CSS-12. This led to the licensee declaring a number of emergency core cooling compon
Region: IV | Fort Calhoun | 12350 | 06/30/2011 08/11/2011 | 2011003-03 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Radiation Work Permit Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71124.02 | Inspectors identified a noncited violation of Technical Specification 5.8.1a for the failure to follow procedural requirements to plan and carry out decontamination work in the spent fuel pool transfer canal. On January 24, 2011, decontamination work was
Region: IV | Fort Calhoun | 12349 | 06/30/2011 08/11/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Procedural Guidance to Replace Or Evaluate Age Degraded Components |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71152 | A self-revealing noncited violation of Fort Calhoun Technical Specification 5.8.1, "Procedures," occurred due to the failure of the licensee to ensure that adequate procedures were available for maintenance which was conducted on the reactor protective sy
Region: IV | Fort Calhoun | 12337 | 03/31/2011 05/10/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operating Instruction Results in a Loss of Auxiliary Feedwater." |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.2 | A self-revealing Green noncited violation of Fort Calhoun Station Technical Specification 5.8.1 occurred for an inadequate procedure for securing auxiliary feedwater flow when feeding the steam generators through the auxiliary feedwater ring. This inadequ
Region: IV | Fort Calhoun | 12338 | 03/31/2011 05/10/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Determine the Cause of the Out Of Tolerance Condition Regarding Reactor Protection System Channel A Trip Unit 6 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.22 | The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B Criterion XVI, "Corrective Actions," which states in part, that measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, defici
Region: IV | Fort Calhoun | 12340 | 03/31/2011 05/10/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Design Adequacy of Refueling Water Tank Vortex Eliminator |  |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that "design control measures shall provide for verifying or checking the adequacy of design, such as, by the perform
Region: IV | Fort Calhoun | 12326 | 11/17/2010 02/11/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.11B | The inspectors identified a Green noncited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure that the integrity of an operating test administered to licensed operators was maintained. Two lice
Region: IV | Fort Calhoun | 12333 | 10/04/2010 02/11/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Apply an Approved ASME Code Case |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR 50.55a(b)(5)(i) because the licensee failed to adequately apply ASME Section XI Code Case N-513-2 when they evaluated a degraded section of raw water piping for operability. The licensee has e
Region: IV | Fort Calhoun | 12302 | 09/30/2010 11/08/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Documentation of the Adequacy of Design for the Pumps that Transfer Fuel Oil from Storage Tank FO-10 to FO-01 |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criteria III due to the failure of the licensee to perform suitable testing to determine the adequacy of the design of equipment related to transferring diesel fuel from o
Region: IV | Fort Calhoun | 12305 | 09/30/2010 11/08/2010 | 2010004-04 | NRC | NCV | Barrier Integrity | Green | Failure to Translate Calculation into Calibration Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 71111.17T | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, as defined in 10 C
Region: IV | Fort Calhoun | 12309 | 09/30/2010 11/08/2010 | 2010004-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71124.01 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.8.1, for failure to follow radiation work permit requirements. On November 13, 2009, two individuals became contaminated while cleaning the gasket seating surface on
Region: IV | Fort Calhoun | 12310 | 09/30/2010 11/08/2010 | 2010004-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Properly Plan a Maintenance Activity |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000285 Fort Calhoun |  | 71124.02 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.8.1, for failure to appropriately control radiation exposures due to improperly planned maintenance activities associated with Work Package 09-AP-20. The maintenance
Region: IV | Fort Calhoun | 12312 | 09/30/2010 11/08/2010 | 2010004-08 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Maintenance Procedure Results in Water in East Switchgear Room and Room 19 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors reviewed a self-revealing Green noncited violation of Fort Calhoun Station Technical Specification 5.8.1, for the licensee's failure to provide an adequate maintenance procedure for fire protection system flushing. Specifically, while perfo
Region: IV | Fort Calhoun | 12313 | 09/30/2010 11/08/2010 | 2010004-09 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Vendor and Industry Recommended Testing on Safety-Related and Risk Significant 4160 V and 480 V Circuit Breakers |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a Green noncited violation of Technical Specification 5.8.1(a) for inadequate procedures associated with 4160 V and 480 V safety-related breaker maintenance procedures. The inspectors determined that maintenance procedures used t
Region: IV | Fort Calhoun | 12314 | 09/30/2010 11/08/2010 | 2010004-10 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedure Results in a Plant Shutdown |  |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | A self-revealing Green noncited violation of Fort Calhoun Station Technical Specification 5.8.1 occurred for an inadequate procedure for verifying the connection between cable lugs and cables. This inadequacy resulted in the loss of Motor Control Center M
Region: IV | Fort Calhoun | 12332 | 09/22/2010 02/11/2011 | 2010005-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a Risk Assessment When Required by 10 CFR 50.65(a)(4) for Maintenance in the Vicinity of Safety-Related Equipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for failing to perform a risk assessment prior to performing activities involving a man bas
Region: IV | Fort Calhoun | 12290 | 06/30/2010 07/26/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROVIDE ADEQUATE LIMITING CONDITION FOR OPERATIONS FOR HIGH RIVER LEVEL |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.01 | The inspectors identified a noncited violation of 10 CFR 50.36(c)(2)(ii)(B) for the failure to include an adequate limiting condition for operation in the technical specification. Specifically, the reactor cannot be placed in a cold shutdown condition usi
Region: IV | Fort Calhoun | 12282 | 06/30/2010 07/26/2010 | 2010003-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Conduct an Adequate Audit of Emergency Preparedness Interfaces with Offsite Authorities |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The inspectors identified a noncited violation of 10 CFR 50.54(t)(2) for the failure to conduct an evaluation of the adequacy of interfaces between the licensee and state and local governments during a periodic review of the site emergency preparedness pr
Region: IV | Fort Calhoun | 12288 | 06/30/2010 07/26/2010 | 2010003-03 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO CONDUCT DRILLS TO MAINTAIN ENVIRONMENTAL MONITORING SKILLS |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The inspectors identified a noncited violation of 10 CFR 50.47(b)(14) for the failure to conduct drills that were adequate to maintain key skills. Specifically, environmental monitoring teams were not required to collect environmental samples during the 2
Region: IV | Fort Calhoun | 12289 | 06/30/2010 07/26/2010 | 2010003-04 | NRC | NCV | Emergency Preparedness | Green | PROTECTIVE ACTION RECOMMENDATION PROCESSES ALLOW FOR THE UNNECESSARY EVACUATION OF THE PUBLIC |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71114.05 | The inspectors identified a noncited violation of 10 CFR 50.47(b)(10) and 50.54(q) for the failure to develop and put into place guidelines for the choice of protective actions during an emergency that were consistent with federal guidance. Specifically,
Region: IV | Fort Calhoun | 12296 | 06/30/2010 08/12/2010 | 2010006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Repeated Tripping of the Turbine Driven Auxiliary Feedwater Pump FW-10 |  | P.1(b) Trend Performance CAP | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Action," occurred for the licensee's failure to assure that a condition adverse to quality was corrected. Specifically, five instances were identified where the licens
Region: IV | Fort Calhoun | 12297 | 06/30/2010 08/12/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify that the Turbine Driven Auxiliary Feedwater Pump Exhaust Backpressure Trip Lever was Fully Latched |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | NONE | The team identified a noncited violation of Technical Specification 5.8.1.a regarding the licensee's failure to implement written procedures as recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Paragraph 3.l of Appendix A requir
Region: IV | Fort Calhoun | 12298 | 06/30/2010 08/12/2010 | 2010006-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Vent Control Oil Following Maintenance Results in Failure of Turbine Driven Auxiliary Feedwater Pump to Start. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing noncited violation of Technical Specification 5.8.1.a was identified regarding the licensee's failure to implement and maintain the applicable procedures recommended in Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Paragra
Region: IV | Fort Calhoun | 12300 | 06/30/2010 08/12/2010 | 2010006-04 | Self - Revealed | NCV | Mitigating Systems | Green | Turbine Driven Auxiliary Feedwater Pump Trip Due to Inadequate Design Margin |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | NONE | A self revealing noncited violation of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," occurred when the licensee failed to ensure that the design basis of certain structures, systems and components were translated into specifications, drawi
Region: IV | Fort Calhoun | 12278 | 12/31/2009 02/05/2010 | 2009005-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Provide Adequate Instruction to Pregnant Workers |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 7112102 | The inspectors identified a noncited violation of 10 CFR 19.12 for failure to provide adequate instruction to declared pregnant workers. Specifically, the licensee did not provide adequate information concerning the potential health protection problems an
Region: IV | Fort Calhoun | 12260 | 12/31/2009 12/30/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Seismic Qualification of Raw Water Pumps |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, from February 1992 to September 8, 2009, the licensee failed to adequately evaluate the seismic qualification of the raw w
Region: IV | Fort Calhoun | 12268 | 12/31/2009 12/30/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Flood Protection for the Intake Structure |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, from August 9, 1973, to September 8, 2009, the licensee failed to prescribe instructions into procedures th
Region: IV | Fort Calhoun | 12270 | 12/31/2009 12/30/2009 | 2009006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Ensure the Reliability of the Raw Water Pump Power Cables |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 7111121 | Green. The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action" for failure to take adequate corrective action following the discovery of water intrusion in manholes MH-5 and MH-31 in 1998, 2005, an
Region: IV | Fort Calhoun | 12251 | 07/17/2009 11/13/2009 | 2009004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Valve Motor Maintenance Work Instruction |  |  | TE?: N | 05000285 Fort Calhoun |  | 71152 | A self-revealing, Green noncited violation of Technical Specification 5.8.1.a (Procedures) was identified for failure to provide an adequate maintenance work instruction. While performing maintenance on the motor, the HPSI Header - Charging Header Crossti
Region: IV | Fort Calhoun | 12258 | 07/17/2009 11/13/2009 | 2009004-03 | NRC | FIN | Barrier Integrity | Green | Failure to Perform Checks at the Beginning of Each Work Shift on the Main Hoist Limit Switches |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a finding of having very low safety significance (Green) for failure to perform checks at the beginning of each shift on the main hoist limit switches of the refueling area crane (HE - 2) in the spent fuel pool area as specified
Region: IV | Fort Calhoun | 12259 | 07/17/2009 11/13/2009 | 2009004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Auxiliary Building Crane Operating Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71152 | A self-revealing Green noncited violation (NCV) of 10 CFR 50, Appendix B, Criterion V, was identified for the failure of personnel to follow an auxiliary building crane operating procedure. This resulted in the crane contacting the fuel handling bridge an
Region: IV | Fort Calhoun | 12244 | 06/30/2009 08/03/2009 | 2009003-01 | NRC | VIO | Mitigating Systems | Green | Failure to Properly Translate Raw Water System Design Basis Requirements | EA Case: 2009174 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure to correctly translate the Fort Calhoun Station raw water strainer component's design basis into specifications, procedures, and instructions. The ra
Region: IV | Fort Calhoun | 12245 | 06/24/2009 07/14/2009 | 2009007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination after Identifying a Degraded Condition |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71152B | The team identified a Green non-cited violation for the licensee's failure to meet 10 CFR Part 50, Appendix B, Criterion V in that the licensee failed to perform an operability determination for a degraded condition. The licensee determined that certain r
Region: IV | Fort Calhoun | 12243 | 03/31/2009 04/30/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement adequate corrective action for floor cracks |  |  | TE?: N | 05000285 Fort Calhoun |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to take prompt corrective measures after identifying that water could penetrate cracks in the turbine building
Region: IV | Fort Calhoun | 12241 | 11/18/2008 02/12/2009 | 2008005-03 | NRC | FIN | Initiating Events | Green | Inadequate Corrective Actions for Repetitive Failures of a Risk-Significant Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 71152 | DRAFT - The inspectors identified a Green finding for inadequate corrective actions, which resulted in a plant transient. Specifically, prior corrective actions were ineffective at preventing repeated failures of condensate makeup control Valve, LCV 1190,
Region: IV | Fort Calhoun | 12240 | 09/30/2008 11/03/2008 | 2008004-01 | NRC | NCV | Initiating Events | Green | Reactor Coolant System Leak During Plant Heat-up Due to Inadequate Valve Packing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71153 | A Green self-revealing noncited violation of Technical Specification 5.8.1.a (Procedures) was identified for an inadequate maintenance procedure. Specifically, the licensee's maintenance procedures did not provide adequate instructions for the craft to re
Region: IV | Fort Calhoun | 12235 | 08/15/2008 09/24/2008 | 2008009-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Degraded Fire Protection Water Supply System |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The team identified a noncited violation of License Condition 2.D and the Quality Assurance Plan for failure to implement timely corrective actions to address a degraded fire water supply system. Despite determining that the system was degraded and taking
Region: IV | Fort Calhoun | 12239 | 08/15/2008 09/24/2008 | 2008009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Related to Revising a Post-fire Safe Shutdown Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The team identified a noncited violation of License Condition 2.D and the Quality Assurance Plan for failure to take adequate corrective action for a condition adverse to fire protection. Specifically, the licensee had included steps to open the breakers
Region: IV | Fort Calhoun | 12220 | 06/30/2008 08/12/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Boric Acid Corrosion Control Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," having very low safety significance for the licensee's failure to maintain an adequate Boric Acid Corrosion Control Proced
Region: IV | Fort Calhoun | 12221 | 06/30/2008 08/12/2008 | 2008003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post a Radiation Area |  |  | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspectors identified a noncited violation of 10 CFR 20.1902(a) because the licensee failed to post radiation areas in the radwaste building with a conspicuous sign or signs bearing the radiation symbol and the words "Caution, Radiation Area." The lic
Region: IV | Fort Calhoun | 12222 | 06/30/2008 08/12/2008 | 2008003-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 7112102 | The inspectors identified a noncited violation of Technical Specification 5.8.1.a which resulted from a worker failing to follow procedural requirements. Specifically, on March 18, 2008, the radiation protection count room technician failed to properly do
Region: IV | Fort Calhoun | 12227 | 06/30/2008 08/12/2008 | 2008003-04 | NRC | NCV | Initiating Events | Green | Failure to Write an Adequate Suhtdown Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71153 | A self-revealing noncited violation of Technical Specification 5.8.1.a was identified for the failure to have an adequate procedure for plant cooldown. Specifically, on June 10, 2008, the plant cooldown procedure allowed the control room staff to unexpect
Region: IV | Fort Calhoun | 12228 | 06/30/2008 08/12/2008 | 2008003-05 | NRC | NCV | Barrier Integrity | Green | Inadequate Corrective Actions for a Containment Spray Design Deficiency |  |  | TE?: N | 05000285 Fort Calhoun |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly implement corrective actions for a condition adverse to quality. Specifically, in 1990 the licensee identified t
Region: IV | Fort Calhoun | 12229 | 06/20/2008 08/01/2008 | 2008008-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to accurately calibrate area radiation monitors |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 7112103 | The team identified a noncited violation of 10 CFR 20.1501(b) for failure to ensure that area radiation monitors used for quantitative measurements were calibrated. Specifically, the licensee's area radiation monitors calibration procedure established an
Region: IV | Fort Calhoun | 12233 | 06/20/2008 08/01/2008 | 2008008-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to provide an accurate shipping manifest |  |  | TE?: N | 05000285 Fort Calhoun |  | 7112202 | The team reviewed a self-revealing, noncited violation of 10 CFR 20.2006(b) resulting from the licensee's failure to provide an accurate shipping manifest. On June 29, 2006, the licensee shipped used filters to a waste processor. The shipment included a t
Region: IV | Fort Calhoun | 12234 | 06/20/2008 08/01/2008 | 2008008-03 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to ship radioactive materials correctly |  |  | TE?: N | 05000285 Fort Calhoun |  | 7112202 | The team reviewed a self-revealing, noncited violation of 10 CFR 71.5 and 49 CFR 173.421(a)(2), which occurred when the licensee failed to ship radioactive material correctly. On December 8, 2006, the licensee was notified about a problem with a radioacti
Region: IV | Fort Calhoun | 12236 | 05/18/2008 02/12/2009 | 2008005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Properly Pre-Plan a Maintenance Activity |  | H.3(a) Work Planning | TE?: N | 05000285 Fort Calhoun |  | 7112102 | DRAFT - The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.8.1 for failure to properly pre-plan the replacement of reactor coolant pump motor A. This failure resulted in the collective dose of a work activity exceedi
Region: IV | Fort Calhoun | 12208 | 03/31/2008 05/16/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Inadequate Internal Flooding Procedure |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.06 | The inspectors identified a noncited violation of Technical Specification 5.8.1.a (Procedures) for an inadequate internal flooding procedure. Specifically, the licensee's abnormal operating procedures did not provide adequate instructions for operators to
Region: IV | Fort Calhoun | 12209 | 03/31/2008 05/16/2008 | 2008002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Identify Internal Flooding Deficiencies |  | P.2(b) Implementing Operating Experience | TE?: N | 05000285 Fort Calhoun |  | 71111.06 | The inspectors identified a finding for the licensee's failure to identify various deficiencies that would increase the severity of postulated internal flooding events in the auxiliary building. Specifically, the licensee did not recognize in-plant condit
Region: IV | Fort Calhoun | 12210 | 03/31/2008 05/16/2008 | 2008002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent Raw Water Pump Packing Leakage |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Actions," for the failure to implement adequate corrective actions to prevent recurrence of a significant condition adverse to quality. Specifically, i
Region: IV | Fort Calhoun | 12211 | 03/31/2008 05/16/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Supply Suitable Materials for Diesel Generator Control Cabinets |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.19 | The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in response to a leak of diesel fuel oil into an enclosure containing electrical equipment. Specifically, the licensee failed to
Region: IV | Fort Calhoun | 12217 | 03/31/2008 05/16/2008 | 2008002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Multiple Conditions Adverse to Quality |  | H.4(b) Procedural Compliance | TE?: N | 05000285 Fort Calhoun |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to ensure that conditions adverse to quality are promptly identified and corrected. Specifically, multiple boric acid leaks were identified in the
Region: IV | Fort Calhoun | 12242 | 03/15/2008 02/12/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Redundant Trains of Auxiliary Feedwater Inoperable Concurrently |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | DRAFT - The inspectors identified a Green non-cited violation for failure to comply with Technical Specification 2.0.1.(2), which required that a system, subsystem, or train must be considered inoperable if its associated emergency power source is inopera
Region: IV | Fort Calhoun | 12193 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Cold Weather Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.01 | Green. A noncited violation of Technical Specification 5.8.1.c was identified for failure to have an adequate procedure to implement cold weather protective actions. Specifically, Procedure OI-EW-1, "Extreme Weather," Revision 13, did not provide adequate
Region: IV | Fort Calhoun | 12204 | 12/31/2007 02/11/2008 | 2007005-02 | NRC | URI | Mitigating Systems | Green | Inadequate Internal Flooding Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.06 | The inspectors identified an unresolved item associated with a potentially inadequate procedure for internal flooding events. Specifically, the licensee's Abnormal Operating Procedures did not provide adequate instructions for operators to mitigate the ef
Region: IV | Fort Calhoun | 12205 | 12/31/2007 02/11/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Take Appropriate Corrective Actions When Raw Water Performance Goals Were Not Met |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000285 Fort Calhoun |  | 7111112B | Green. A noncited violation (NCV) of 10 CFR 50.65(a)(1) was identified for failure to implement corrective action to correct the condition causing unreliability of the raw water pumps and strainers. Specifically, the cause evaluation concluded that debris
Region: IV | Fort Calhoun | 12206 | 12/31/2007 02/11/2008 | 2007005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of Component Cooling Water Bypass Valve |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | Green. A noncited violation of Criterion III, "Design Control," was identified for not translating calculation results on controlling the position of HCV-497, Component Cooling Heat Exchangers AC-1A-D CCW Bypass Line Isolation Valve, into procedures to ma
Region: IV | Fort Calhoun | 12207 | 12/31/2007 02/11/2008 | 2007005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Correct Setpoints Into Design Calculations |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 7111117A | Green. A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" was identified when the licensee failed to use the correct set points in design calculations. This error, when translated into plant equipment, affec
Region: IV | Fort Calhoun | 12198 | 09/30/2007 10/12/2007 | 2007004-01 | NRC | FIN | Initiating Events | Green | Ineffective Corrective Actions for Hydrazine Spills |  |  | TE?: N | 05000285 Fort Calhoun |  | 71152 | A Green self-revealing finding was identified for inadequate corrective actions, which resulted in a hydrazine spill. Specifically, corrective actions taken previously were ineffective at preventing hydrazine spills, a condition that had the potential to
Region: IV | Fort Calhoun | 12196 | 09/14/2007 10/26/2007 | 2007010-01 | NRC | NCV | Initiating Events | Green | Failure to Follow a Procedure That Would Identify Potential Missile Hazards (Section 4OA2.e(2)(a)) |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 71152B | A noncited violation was identified for failure of operators to follow a procedure as required by Technical Specification 5.8.1.a. This failure resulted in the station not identifying that loose material had the potential to become airborne during high wi
Region: IV | Fort Calhoun | 12197 | 09/14/2007 10/26/2007 | 2007010-02 | NRC | NCV | Initiating Events | Green | Inadequate Definition of a Missile Hazard Results in Loss of 161 KV Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71152B | A self-revealing noncited violation of Technical Specification 5.8.1.a occurred for an inadequate procedure that narrowly defined the definition of a missile. This inadequacy resulted in the loss of 161 kilovolt power to the safety-related busses on Augus
Region: IV | Fort Calhoun | 11656 | 08/31/2007 10/10/2007 | 2007011-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Emergency Diesel Generator Postmaintenance Test |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | NONE | A self-revealing Green non-cited violation of TS 5.8.1.a (Procedures) was identified for an inadequate postmaintenance testing procedure. Craftsmen had replaced the field flash relay auxiliary contacts (following a previous field flash failure on February
Region: IV | Fort Calhoun | 12186 | 07/25/2007 09/07/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Abnormal Operating Procedure for loss of Component Cooling Water |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 7111121 | The team identified a noncited violation of Fort Calhoun Technical Specification 5.8, "Procedures," for an inadequate Technical Specification required procedure. Specifically, Abnormal Operating Procedure 11, "Loss of Component Cooling Water," could not b
Region: IV | Fort Calhoun | 12190 | 07/25/2007 09/07/2007 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Impact of Heat Loading in Safety Injection Pump Room from the Start of a Third High Head Safety Injection Pump |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure to perform a complete and adequate analysis of safety injection pump room temperatures to support operation of two high pressure safety injection pumps
Region: IV | Fort Calhoun | 12191 | 07/25/2007 09/07/2007 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Regulatory Requirements and Design Basis to Equipment Required to Support the Raw Water System - Unresolved Item 05000285/2005009-01 |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | The team identified a non-cited violation of 10CFR Part 50, Appendix B, Criterion III, for the failure to translate the Fort Calhoun Station raw water strainer component's design basis into specifications, procedures, and instructions. The licensee had cl
Region: IV | Fort Calhoun | 12192 | 07/25/2007 09/07/2007 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for the Turbine Driven Auxilary Feedwater Keep Warm Line Bypass Throttle Valves MS-366 and -368 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 7111121 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Action, for failure to promptly identify and correct conditions adverse to quality. Specifically, between November 11, 2005, to April 28, 2006, during quarterly s
Region: IV | Fort Calhoun | 12194 | 07/25/2007 09/07/2007 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Single Failure Criteria Configuration for Component Isolation Valves |  |  | TE?: N | 05000285 Fort Calhoun |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to meet the single valve failure requirements for the component cooling water surge tank. The component cooling water surge tank water
Region: IV | Fort Calhoun | 11655 | 06/30/2007 08/14/2007 | 2007003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Stop Work and Notify RP Upon Receiving a Dose Rate Alarm |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 7112101 | A self-revealing noncited violation of Technical Specification 5.8.1(a) was identified because a worker failed to stop work and notify radiation protection upon receiving a dose rate alarm per procedural requirements. On March 24, 2007, a chemist received
Region: IV | Fort Calhoun | 11652 | 03/31/2007 05/15/2007 | 2007002-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Obtain a High Radiation Area Access Authorizations and Associated Radiological Briefing |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspectors reviewed two examples of a self-revealing, noncited violation of Technical Specification 5.11.1 in which workers failed to obtain high radiation area radiological briefing before entering the area. The first example occurred on October 25,
Region: IV | Fort Calhoun | 11653 | 03/31/2007 05/15/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct an Inoperable component Cooling Water flow Element |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000285 Fort Calhoun |  | 71152 | A Green self-revealing noncited violation was identified for the licensee's failure to promptly identify and correct a repetitively inoperable component cooling flow element. The initial failure occurred in 1999 and had failed three times within the past
Region: IV | Fort Calhoun | 11654 | 03/31/2007 05/15/2007 | 2007002-03 | Self - Revealed | NCV | Initiating Events | Green | Loss of Shut Down Cooling Due to Inadequate Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71153 | A Green self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, occurred when operating procedure OP-3A, "Plant Shutdown," Revision 66, did not contain appropriate guidance to licensed operators to prevent the loss of shutdown coolin
Region: IV | Fort Calhoun | 11638 | 12/31/2006 02/10/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Degraded Component Cooling Water Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a Green NCV for the licensee's failure to promptly identify and correct a degraded component cooling water pump. The failure to recognize and fix this condition led to the pump being more likely to fail upon a valid demand to sta
Region: IV | Fort Calhoun | 11643 | 12/31/2006 02/10/2007 | 2006005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Determine Operability of Component Cooling Water Valves to Containment Cooling Units |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 2.4. The violation was identified as a result of the licensee's failure to identify corrective actions two years ago that caused the Licensee to incorrectly determine the operabilit
Region: IV | Fort Calhoun | 11644 | 12/31/2006 02/10/2007 | 2006005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Pump Down of Intake Bay Resulting in Less Than Required Raw Water Pumps |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 71111.2 | A Green finding was identified for failure of operators to follow a standing operational procedure as required by Technical Specification 5.8.1.a. This failure resulted in less than the minimum number of raw water pumps required for decay heat removal fro
Region: IV | Fort Calhoun | 11650 | 12/31/2006 02/10/2007 | 2006005-07 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Over-Pressurization of Piping During Testing |  |  | TE?: N | 05000285 Fort Calhoun |  | 71153 | A Green finding was identified for failure to follow procedures during testing. This condition resulted in the damage to safety-related equipment and potential over-pressurization of chemical and volume control system (CVCS) and high pressure safety injec
Region: IV | Fort Calhoun | 11645 | 11/17/2006 02/10/2007 | 2006005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Obtain High Radiation Area Briefing |  | H.3(b) Work Activity Coordination | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspector identified a self-revealing, noncited violation of Technical Specification 5.11.1, in which a worker failed to obtain a high radiation area access authorization and associated radiological briefing prior to entering the posted area. Specific
Region: IV | Fort Calhoun | 11646 | 11/17/2006 02/10/2007 | 2006005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Wear Appropriate Alarming Dosimetry |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspector identified a self-revealing, noncited violation of Technical Specification 5.11.1.b, in which a contractor's ALARA Coordinator failed to wear an alarming device that could be heard while working in a High Radiation Area. Specifically, on Oct
Region: IV | Fort Calhoun | 11649 | 11/17/2006 02/10/2007 | 2006005-06 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Provide Adequate Instructions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspector identified a self-revealing, noncited violation of Technical Specification 5.8.1.a, in which instructions for the use of a high-efficiency particulate air (HEPA) filtration units were not adequately incorporated into RWP instructions resulti
Region: IV | Fort Calhoun | 11630 | 09/30/2006 11/14/2006 | 2006004-01 | NRC | NCV | Initiating Events | Green | Failure to Translate Replacement Pressurizer Weight Into Design Calculations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 7111117B | The inspectors identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to use the correct total dead weight of the replacement pressurizer in two design calculations. The failure to correctly
Region: IV | Fort Calhoun | 11631 | 09/30/2006 11/14/2006 | 2006004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Shutdown Cooling Train Operable as Required by Technical Specification 2.1.1(3) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.2 | A noncited violation was identified for failure to comply with Technical Specification 2.1.1.(3), which required two operable decay heat removal loops. This failure resulted in a condition where only one shutdown cooling train was operable. This condition
Region: IV | Fort Calhoun | 11637 | 09/30/2006 11/14/2006 | 2006004-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Optain High Radiation Area Access Authorization and an Associated Radiological Briefing |  | H.4(a) Human Error Prevention | TE?: N | 05000285 Fort Calhoun |  | 7112101 | The inspectors reviewed two examples of a self-revealing, noncited violation of Technical Specification 5.11.1 in which workers failed to obtain high radiation area access authorization and associated radiological briefing before entering the area. The fi
Region: IV | Fort Calhoun | 11635 | 09/30/2006 11/14/2006 | 2006004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement readonable and Feasible Manual Actions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The inspectors identified a noncited violation of Technical Specification 5.8.1.c for failure to have an adequate procedure to implement postfire safe shutdown actions. Specifically, Procedure SO-G-28, "Station Fire Plan," Revision 61, Attachment 14, fail
Region: IV | Fort Calhoun | 11636 | 09/30/2006 11/14/2006 | 2006004-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternate Shurdown Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000285 Fort Calhoun |  | 71111.05T | The inspectors identified a noncited violation of Technical Specification 5.8.1.c for failure to have an adequate procedure to implement postfire safe shutdown actions. Specifically, simulated operator actions during a walkthrough of Procedure AOP-06, "Fi
Region: IV | Fort Calhoun | 11620 | 06/30/2006 08/04/2006 | 2006003-01 | NRC | NCV | Initiating Events | Green | Failure to Identify Potential Missiles During adverse Weather Conditions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 71111.01 | A noncited violation was identified for failure of operators to follow an abnormal operating procedure as required by Technical Specification 5.8.1.a. This failure resulted in the station not identifying that loose material had the potential to become air
Region: IV | Fort Calhoun | 11628 | 06/30/2006 08/04/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Nonfunctional Fire Barrier Separating Corridor 23 (Fire Area 20.1) and Room 61 (Fire Area 20.4) |  |  | TE?: N | 05000285 Fort Calhoun |  | 71111.05Q | A noncited violation of Technical Specification 5.8.1.c, Fire Protection Program Implementation, was identified for the failure to ensure that all fire barriers protecting safety-related areas were functional. Specifically, Fire Door 1007-10 between Fire
Region: IV | Fort Calhoun | 11629 | 06/30/2006 08/04/2006 | 2006003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Identify a Condition Adverse to Quality Associated with an Inoperable Personnel Access Lock |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000285 Fort Calhoun |  | 7111114 | A noncited self-revealing violation of 10 CFR Part 50, Appendix B, Criterion XVI, was identified for the failure to ensure that conditions adverse to quality are promptly identified and corrected. Specifically, a licensed operator and radiation protection
Region: IV | Fort Calhoun | 11621 | 06/30/2006 08/04/2006 | 2006003-04 | Self - Revealed | FIN | Initiating Events | Green | Reactor Trip Caused by Inadequate Operator Control During Low Power Operations |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000285 Fort Calhoun |  | 71153 | A self-revealing finding was identified for inadequate operator control of plant parameters, which resulted in an unplanned reactor trip during testing. The cause of the finding is related to the crosscutting element of human performance in that the opera
Region: IV | Fort Calhoun | 11618 | 05/12/2006 06/20/2006 | 2006014-01 | NRC | NCV | Public Radiation Safety | Green | Failure to train hazardous material employees |  |  | TE?: N | 05000285 Fort Calhoun |  | 7112202 | The team identified a non-cited violation (NCV) of 49 CFR 172.704(a) because the licensee failed to provide required training to hazardous material employees involved in the shipment of radioactive material. Specifically, the licensee did not provide func
Region: IV | Fort Calhoun | 11619 | 05/12/2006 06/20/2006 | 2006014-02 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to survey and control radioactive material. |  |  | TE?: N | 05000285 Fort Calhoun |  | 7112203 | The team reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a) that resulted from the licensee's failure to properly survey items contaminated with radioactive material. On March 8, 2005, the licensee failed to adequately evaluate the radiol
Region: IV | Grand Gulf | 126459 | 12/31/2019 02/13/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Degradation of the Division 1 Diesel Generator Jacket Water Heat Exchanger |  | H.4 - Teamwork | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71111.13 | An NRC-identified, Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified when the licensee failed to follow station procedures. Specifically, the licensee fail
Region: IV | Grand Gulf | 125956 | 12/31/2019 02/13/2020 | 2019004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Worker Entered Overhead High Radiation Area without Radiation Protection Brief |  | H.8 - Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 | Program & Process | 71124.01 | The inspectors reviewed a self-revealed, Green non-cited violation of Technical Specification 5.7.1 for an individual entering a high radiation area without the dose rates in the area being known and the worker being briefed to ensure awareness of the dos
Region: IV | Grand Gulf | 126086 | 12/31/2019 02/13/2020 | 2019004-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Technical Specification 5.4.1 Procedures for Process Radiation Monitor Calibrations |  | H.11 - Challenge the Unknown | TE?: N | 05000416 Grand Gulf 1 | Plant Facilities/Equipment and Instrumentation | 71124.03 | An NRC-identified Green finding and associated non-cited violation of Technical Specification 5.4.1(a) was identified when the licensee failed to properly calibrate containment and drywell ventilation exhaust, fuel handling area pool sweep, and fuel handl
Region: IV | Grand Gulf | 126404 | 12/31/2019 02/13/2020 | 2019004-04 | NRC | NCV | Barrier Integrity | Green | Failure to Correct a Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000416 Grand Gulf 1 | Configuration Control | 71152 | An NRC-identified, Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” was identified when the licensee failed to ensure that conditions adverse to quality were promptly identified and correc
Region: IV | Grand Gulf | 126358 | 12/31/2019 02/13/2020 | 2019004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Degraded Standby Gas Treatment Charcoal |  | H.1 - Resources | TE?: N | 05000416 Grand Gulf 1 | Procedure Quality | 71153 | An NRC-identified Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Actions,” was identified when the licensee failed to promptly identify and correct a condition adverse to quality. The results of
Region: IV | Grand Gulf | 125531 | 11/04/2019 11/22/2019 | 2019013-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Test to Demonstrate that the Standby Service Water System Siphon Line Will Perform Acceptably in Service | EA Case: EA-19-099 | NPP | TE?: N | 05000416 Grand Gulf 1 | Design Control | 71152 | The inspectors identified a Green non-cited Violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XI, “Test Control,” for the licensee’s failure to establish a testing program to assure that all testing required to demonstrate that structures, systems,
Region: IV | Grand Gulf | 126115 | 10/17/2019 11/26/2019 | 2019040-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify and Correct Animal Intrusion Vulnerabilities in a Timely Manner |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71153 | The inspection team reviewed a self-revealed, Green finding for the licensee’s failure to identify and correct animal intrusion into electrical component vulnerabilities in a timely manner. Specifically, the licensee experienced an unplanned downpower in
Region: IV | Grand Gulf | 126116 | 10/17/2019 11/26/2019 | 2019040-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Identify and Correct Turbine Control System Issues in a Timely Manner |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71153 | The inspection team reviewed a self-revealed, Green finding for the licensee’s failure to identify and correct turbine control system issues in a timely manner. Specifically, the licensee experienced both a scram and unplanned downpower in 2016 due to def
Region: IV | Grand Gulf | 125713 | 09/30/2019 11/05/2019 | 2019003-01 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustibles |  | H.2 - Field Presence | TE?: N | 05000416 Grand Gulf 1 | Protection Against External Factors | 71111.05Q | An NRC-identified, Green finding and associated non-cited violation of License Condition 2.c.(41) of Facility Operating License No. NPF-29 for the Grand Gulf Nuclear Station, Unit 1, was identified when inspectors identified uncontrolled transient combust
Region: IV | Grand Gulf | 125825 | 09/26/2019 11/05/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Include Beta Radiation Effects on Total Integrated Dose to Conax Connectors |  | H.3 - Change Management | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21N | The inspectors identified a Green finding and associated non-cited violation (NCV) of Title 10 of the Code of Federal Regulations 10 CFR Part 50.49 (e)(4), "Radiation." for the licensee's failure to include beta radiation effects in the environmental qual
Region: IV | Grand Gulf | 125828 | 09/26/2019 11/05/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Use Calibrated Maintenance and Test Equipment to Monitor Warehouse Temperature and Humidity for Safety-Related Components |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71111.21N | The inspectors identified a Green finding and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations 10 CFR Part 50, Appendix B, Criterion XII, "Control of Measuring and Test Equipment," for the licensee's failure to use calib
Region: IV | Grand Gulf | 125835 | 09/26/2019 11/05/2019 | 2019010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Warehouse Temperature and Humidity Exceeding Limitations |  | H.8 - Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21N | The inspectors identified a Green finding and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to identify and correct exceeding
Region: IV | Grand Gulf | 125217 | 06/30/2019 08/14/2019 | 2019002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Design Control Procedure |  | H.6 - Design Margins | TE?: N | 05000416 Grand Gulf 1 | Design Control | 71152 | A self-revealed, Green finding was identified when an actuation of the generator protection negative phase sequence trip caused a generator lockout and a reactor scram. The licensee failed to ensure that a recent change in the applicable trip setpoint was
Region: IV | Grand Gulf | 124752 | 03/31/2019 05/10/2019 | 2019001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Scope Standby Service Water Piping into the Inspection Program |  | H.1 - Resources | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71111.19 | A self-revealed, Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” was identified when a pinhole leak developed in a portion of the standby service water piping. The lice
Region: IV | Grand Gulf | 124682 | 02/28/2019 03/29/2019 | 2018050-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish RCIC Injection Flow to the Reactor Vessel During Manual Operation |  | H.9 - Training | TE?: N | 05000416 Grand Gulf 1 | Human Performance | 93812 | A self-revealed, Green finding with an associated non-cited violation of 10 CFR 55.46(c), “Plant-referenced simulators,” was identified for the licensee’s failure to ensure that the simulator demonstrated expected plant response to operator input and cond
Region: IV | Grand Gulf | 124683 | 02/28/2019 03/29/2019 | 2018050-02 | NRC | FIN | Mitigating Systems | Green | Failure to Correct a Condition Associated with Post-Scram Control Rod Drive Pump Trips |  | P.5 - Operating Experience | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 93812 | The inspectors identified a Green finding for the licensee’s failure to address the cause and correct a condition associated with post-scram control rod drive system pump trips as required for an adverse condition by station procedure EN-LI-102, “Correcti
Region: IV | Grand Gulf | 25905 | 12/31/2018 02/07/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Lubrication Oil Program for Quality Systems |  | H.2 - Field Presence | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” for the licensee’s failure to implement procedures for the lubrication program for safety-related and quality components. Specifically, licensee Proce
Region: IV | Grand Gulf | 25906 | 12/31/2018 02/07/2019 | 2018004-03 | NRC | NCV | Mitigating Systems | Green | Design Control for Reactor Core Isolation Cooling and Emergency Diesel Generators |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 | Design Control | 71111.12 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to correctly translate the design basis of the reactor core isolation cooling system and the emergency diesel
Region: IV | Grand Gulf | 25923 | 12/31/2018 02/07/2019 | 2018004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Lubricate Motor-Operated Valve Stem Nut |  | NPP | TE?: N | 05000416 Grand Gulf 1 | Equipment Performance | 71111.13 | A self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a, “Procedures,” was identified when the licensee failed to have adequate instructions to perform preventive maintenance. Specifically, the licensee failed to properly lubricate
Region: IV | Grand Gulf | 25924 | 12/31/2018 02/07/2019 | 2018004-05 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform Complete Evaluations of the Licensee Interface with Offsite Organizations |  | H.8 - Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 | Offsite EP | 71114.05 | The inspector identified a Green, non-cited violation of 10 CFR 50.54(t)(2) for the licensee’s failure to include an evaluation of the adequacy of the interfaces with State and local governments in a review of emergency preparedness program elements in Au
Region: IV | Grand Gulf | 25925 | 12/31/2018 02/07/2019 | 2018004-06 | NRC | NCV | Emergency Preparedness | Green | Failure to Conduct Drills in Accordance with the Site Emergency Plan |  | H.9 - Training | TE?: N | 05000416 Grand Gulf 1 | ERO Performance | 71114.05 | The inspector identified a Green, non-cited violation of 10 CFR 50.54(q)(2) associated with the licensee’s failure to follow their emergency plan. Specifically, the licensee failed to follow Grand Gulf Nuclear Station Emergency Plan, Revisions 66 to 77, S
Region: IV | Grand Gulf | 25887 | 12/17/2018 12/17/2018 | 2018010-01 | NRC | NCV | Mitigating Systems | Green | Conditions Adverse to Quality Not Promptly Corrected Using Work Management System |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee’s failure to promptly identify and correct conditions adverse to quality when corrective actions were moved from the CAP to the work manag
Region: IV | Grand Gulf | 25888 | 12/17/2018 12/17/2018 | 2018010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Adverse Conditions Related to Barrier Doors |  | P.2 - Evaluation | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct adverse conditions related to degraded barrier doors as required by regula
Region: IV | Grand Gulf | 25889 | 12/17/2018 12/17/2018 | 2018010-03 | NRC | FIN | Mitigating Systems | Green | Immediate Operability Determinations Not Documented in Accordance with Procedures |  | P.3 - Resolution | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified a Green NRC identified finding for the licensee’s failure to consistently complete immediate operability determinations in accordance with station procedures. The failure to assess operability immediately following discover
Region: IV | Grand Gulf | 24666 | 09/30/2018 11/13/2018 | 2018003-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Develop Adequate Work Instructions |  | H.9 - Training | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | A self-revealed, Green finding was identified when feedwater heater drain tank oscillations caused a feedwater perturbation which required a manual reactor scram. Specifically, the licensee failed to develop appropriate work instructions for filling and
Region: IV | Grand Gulf | 24108 | 06/30/2018 08/02/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Institute Effective Corrective Action to Preclude Repetition |  | P.2 - Evaluation | TE?: N | 05000416 Grand Gulf 1 |  | 71111.01 | An NRC-identified, Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified when the licensee failed to institute effective corrective actions to preclude repetition of a significant condition adverse to
Region: IV | Grand Gulf | 24109 | 06/30/2018 08/02/2018 | 2018002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow ASME Requirements for Maintaining Inservice Inspection (ISI) Cycles and Perform ASME Required Inservice Inspections within the Scheduled ISI Cycle |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 |  | 71111.08G | The inspector identified 15 examples of a Green non-cited violation (NCV) of 10 CFR 50.55(a)(g)(4)(ii), which requires that inservice examination of components classified as American Society of Mechanical Engineers (ASME), Section XI, Code Class 1, Class
Region: IV | Grand Gulf | 24110 | 06/30/2018 08/02/2018 | 2018002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Test NUS Temperature Switch |  | NPP | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | A self-revealed, Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified when the reactor core isolation cooling (RCIC) system automatically isolated due to an inadvertent high temperature input from the le
Region: IV | Grand Gulf | 24020 | 06/30/2018 08/02/2018 | 2018002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | High Radiation Area Boundary Violation |  | H.8 - Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 71124.01 | A self-revealed, Green non-cited violation of Technical Specification 5.7.1 was identified when an individual received a dose rate alarm when the individual failed to comply with established radiological barriers and protective measures and entered a high
Region: IV | Grand Gulf | 24021 | 06/30/2018 08/02/2018 | 2018002-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedural Requirements Resulting in Unplanned Dose |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71124.02 | A self-revealed, Green non-cited violation of Technical Specification 5.4.1 was identified when an individual alarmed a personnel contamination monitor upon exit from the radiologically controlled area. Specifically, the licensee failed to follow procedur
Region: IV | Grand Gulf | 24114 | 06/30/2018 08/02/2018 | 2018002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Evaluation and Resolution of Intermediate Range Monitor Noise Leads to Manual Reactor Shutdown |  | P.2 - Evaluation | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | A self-revealed, Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure of the licensee to identify and correct a condition adverse to quality. Specifically, the licensee failed to imple
Region: IV | Grand Gulf | 24115 | 06/30/2018 08/02/2018 | 2018002-07 | Self - Revealed | NCV | Initiating Events | Green | Loss of Shutdown Cooling |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | A self-revealed, Green non-cited violation of Technical Specification 5.4, "Procedures," for the licensee’s failure to follow written procedures was identified when the residual heat removal (RHR) system automatically isolated due to an inadvertent emerg
Region: IV | Grand Gulf | 24116 | 06/30/2018 08/02/2018 | 2018002-08 | NRC | NCV | Barrier Integrity | Green | Performance of Surveillance Testing Following Maintenance on Containment Airlock |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee’s failure to perform surveillance testing of containment airlock seals under appropriate conditions. The licensee failed to
Region: IV | Grand Gulf | 23973 | 03/31/2018 05/14/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Correct Lube Oil Leak on Division 2 Diesel Generator |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action", associated with the licensee’s failure to promptly correct an identified condition adverse to quality. Specifically, the licens
Region: IV | Grand Gulf | 23974 | 03/31/2018 05/14/2018 | 2018001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure when Returning Containment Airlock to Operable Status |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures", for the licensee’s failure to follow written procedures for returning a technical specification component to service. Specifically, the licensee
Region: IV | Grand Gulf | 23975 | 03/31/2018 05/14/2018 | 2018001-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance Which Resulted in Control Room Air Conditioning Inoperability |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures", for the licensee’s failure to have adequate procedural guidance while performing a standby service water surveillance procedure. Specifically, t
Region: IV | Grand Gulf | 23976 | 03/31/2018 05/14/2018 | 2018001-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedural Guidance which Resulted in Undemanded Control Valve Movements and Manual Scram |  | H.1 - Resources | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, "Procedures," associated with the licensee’s failure to provide appropriate procedural guidance while performing calibration of a steam line compensator. Spec
Region: IV | Grand Gulf | 23197 | 01/18/2018 02/12/2018 | 2017011-01 | NRC | FIN | Mitigating Systems | Green | Failure to Categorize Condition Reports for Significant Conditions Adverse to Quality as Required by Procedures |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified five examples of a finding for the licensee’s failure to categorize and evaluate conditions in accordance with procedural requirements. Specifically, the licensee did not categorize adverse conditions that represented the loss of
Region: IV | Grand Gulf | 23198 | 01/18/2018 02/12/2018 | 2017011-02 | NRC | FIN | Mitigating Systems | Green | Failure to Disposition Adverse Conditions as Required by Procedures |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified a finding for the licensee’s failure to disposition conditions as required by Procedure EN-LI-102, “Corrective Action Program,” Revisions 24 through 30. Specifically, the licensee did not identify 72 conditions as either Adverse
Region: IV | Grand Gulf | 23199 | 01/18/2018 02/12/2018 | 2017011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Common Cause Failure Evaluation in Response to Inoperable Emergency Diesel Generator |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified three instances of a non-cited violation of Technical Specification 3.8.1, “AC Sources – Operating,” for the licensee’s failure to take required actions for an inoperable emergency diesel generator. Specifically, after classifyin
Region: IV | Grand Gulf | 23200 | 01/18/2018 02/12/2018 | 2017011-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Install the Residual Heat Removal Pump A Mechanical Seal in Accordance with Procedures |  | H.12 - Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4, “Procedures,” for the licensee’s failure to perform maintenance on the residual heat removal pump A mechanical seal in accordance with written procedures. Specifi
Region: IV | Grand Gulf | 23201 | 01/18/2018 02/12/2018 | 2017011-05 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Correct Control Room Boundary Door Resulted in Loss of Safety Function |  | P.3 - Resolution | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Criterion XVI, “Corrective Action,” for the licensee’s failure to appropriately correct a condition adverse to quality. Specifically, the control room envelope door had been d
Region: IV | Grand Gulf | 23202 | 01/18/2018 02/12/2018 | 2017011-06 | NRC | FIN | Public Radiation Safety | Green | Failure to Perform Functionality Assessments as Required by Procedures |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The inspectors identified a finding for the licensee’s failure to follow Procedure EN-OP-104, “Operability Determination Process,” Revisions 10 through 12. Specifically, the licensee did not perform functionality assessments for adverse conditions on the
Region: IV | Grand Gulf | 22607 | 11/13/2017 12/06/2017 | 2017013-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Turbine Stop Valve Testing | EA Case: 17-184 |  | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | The inspectors documented a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's use of an inappropriate procedure to test turbine stop and control valves.
Region: IV | Grand Gulf | 22608 | 11/13/2017 12/06/2017 | 2017013-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Corrective Action Leads to Reactor Scram | EA Case: 17-184 | H.14 - Conservative Bias | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | The inspectors documented a self-revealed finding for the licensee's failure to follow plant Procedure EN-Ll-102, "Corrective Action Program," Revision 28, that ensures adverse conditions were identified and corrected. Specifically, licensee staff failed
Region: IV | Grand Gulf | 22316 | 10/18/2017 12/01/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Engineering Seismic Evaluation for the Construction of Long Term Scaffolding in the Div I and Div II Diesel Rooms |  | H.6 - Design Margins | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Grand Gulf | 22317 | 10/18/2017 12/01/2017 | 2017007-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Standby Diesel Generator Trip |  | H.8 - Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21M | The team identified a Green, self-revealed, non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions," which states, in part, "Conditions adverse to quality are promptly identified and corrected." On June 22, 2016, the station ident
Region: IV | Grand Gulf | 22318 | 10/18/2017 12/01/2017 | 2017007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Preventive Maintenance Procedure for Safety-Related Equipment |  | H.5 - Work Management | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21M | The team identified a Green, non-cited violation of Technical Specification (TS) 5.4.1, which states, in part, "Written procedures shall be established, implemented, and maintained covering the following activities," referenced in Regulatory Guide (RG) 1.
Region: IV | Grand Gulf | 22320 | 10/18/2017 12/01/2017 | 2017007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Update a Calculation and Procedure to Address Standby Service Water Passive Failure |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tra
Region: IV | Grand Gulf | 22321 | 10/18/2017 12/01/2017 | 2017007-06 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure Adequate Design Control Measures Are in Place Associated with Leakage Control Systems |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis…for those structu
Region: IV | Grand Gulf | 21646 | 09/30/2017 11/05/2017 | 2017003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Isolation of Reactor Core Isolation Cooling System during Surveillance Testing |  | H.2 - Field Presence | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee’s failure to accomplish quality related activities in accordance with Surveillance Procedur
Region: IV | Grand Gulf | 32048 | 08/22/2017 08/22/2017 | 2017012-01 | NRC | VIO | Public Radiation Safety | Green | Failure to Correct Instrument Calibration Process in a Timely Manner |  | P.3 - Resolution | TE?: N | 05000416 Grand Gulf 1 |  | 71124.05 | The inspectors identified a violation of 10 CFR 20.1501(c) for the failure to properly calibrate installed radiation monitors using industry accepted calibration methods and tolerances. Specifically, since January 2012, the licensee failed to properly cal
Region: IV | Grand Gulf | 32053 | 07/14/2017 08/22/2017 | 2017012-02 | NRC | FIN | Public Radiation Safety | Green | Failure to Operate the Gaseous Radwaste System Within Design Specifications |  | P.3 - Resolution | TE?: N | 05000416 Grand Gulf 1 |  | 71124.06 | The inspectors identified a finding associated with the licensee's failure to operate the gaseous radwaste system within design specifications. These deficiencies in design specifications were associated with the off gas charcoal adsorber and vault refrig
Region: IV | Grand Gulf | 32047 | 06/30/2017 08/03/2017 | 2017002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish an Appropriate Preventative Maintenance Procedure for the HPCS Jockey Pump |  | H.13 - Consistent Process | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to establish appropriate procedural instructions for performing preventative maintenance on the high pressure core spray jockey pum
Region: IV | Grand Gulf | 22604 | 05/31/2017 10/27/2017 | 2016008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have Alternate Decay Heat Removal Capability | EA Case: 16-277 | H.2 - Field Presence | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team reviewed a self-revealed, non-cited violation of Technical Specification 3.4.10, "Residual Heat Removal Shutdown Cooling System – Cold Shutdown," for the licensee’s failure to verify an alternate method of decay heat removal was available when re
Region: IV | Grand Gulf | 22605 | 05/31/2017 10/27/2017 | 2016008-02 | NRC | NCV | Initiating Events | Green | Failure to Have Adequate Procedures | EA Case: 16-277 | NPP | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee’s failure to have adequate procedures for activities affecting quality. Specifically, Grand Gu
Region: IV | Grand Gulf | 22606 | 05/31/2017 10/27/2017 | 2016008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operations Procedures | EA Case: 16-277 | H.11 - Challenge the Unknown | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the licensee’s failure to implement procedures required by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, contrary to procedures,
Region: IV | Grand Gulf | 32037 | 04/21/2017 06/02/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action |  | H.14 - Conservative Bias | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(41) for failure to correct a condition adverse to fire protection in a timely manner. Specifically, the licensee failed to complete evaluations of multiple spurious operations (MSO) conce
Region: IV | Grand Gulf | 32040 | 04/21/2017 06/02/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure Timing |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | The team identified a Green non-cited violation of Technical Specification 5.4.1.a for the failure to implement and maintain adequate written procedures covering a fire in the control room. Specifically, the licensee failed to maintain an alternative shut
Region: IV | Grand Gulf | 32041 | 04/21/2017 06/02/2017 | 2017008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Isolate Control Circuits for Safe Shutdown Equipment From the Effects of a Control Room Fire |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C.(41) for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to adequately isolate control circu
Region: IV | Grand Gulf | 32042 | 04/21/2017 06/02/2017 | 2017008-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure Steps |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | The team identified a Green non-cited violation of Technical Specification 5.4.1.a for the failure to maintain adequate written procedures covering a fire in the control room. Specifically, the licensee failed to ensure that all steps in Procedure 05-1-02
Region: IV | Grand Gulf | 32023 | 03/31/2017 05/15/2017 | 2017001-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Conduct a Drill Required by the Site Emergency Plan in 2014 |  | H.9 - Training | TE?: N | 05000416 Grand Gulf 1 |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) associated with the licensee's failure to conduct a drill required by the site emergency plan in 2014. The licensee was required to conduct a drill involving both the site first-aid tea
Region: IV | Grand Gulf | 32016 | 12/31/2016 02/08/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Requirements for Switchgear Room Cooling |  | H.7 Documentation | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspector identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to implement appropriate design control measures associated with a safety-related service water flow calculation. Specific
Region: IV | Grand Gulf | 32022 | 12/31/2016 02/08/2017 | 2016004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Use Procedures and Engineering Controls to Maintain Occupational Doses ALARA |  | P.5 Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71124.02 | The inspectors identified a non-cited violation of 10 CFR 20.1101(b) for the licensee's failure to implement radiation exposure reduction procedures and engineering controls to minimize unplanned and unintended radiation dose to workers and to maintain oc
Region: IV | Grand Gulf | 31998 | 11/04/2016 12/09/2016 | 2016007-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Technical Specification Surveillance Requirements for Reactor Protection System |  | H.3 Change Management | TE?: N | 05000416 Grand Gulf 1 |  | 71111.17T | The team identified a Green non-cited violation of 10 CFR 50.36, "Technical Specifications," which requires that "surveillance requirements are requirements relating to test, calibration, or inspection to assure that the necessary quality of systems and c
Region: IV | Grand Gulf | 31999 | 11/04/2016 12/09/2016 | 2016007-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain NRC Approval For Changes to the Reactor Protection System |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 71111.17T | The team identified a Severity Level IV non-cited violation of 10 CFR 50.59(c)(2), "Changes, Tests, and Experiments," for the licensee's failure to obtain a license amendment prior to implementing a proposed change, test, or experiment that would result i
Region: IV | Grand Gulf | 32006 | 11/04/2016 12/09/2016 | 2016007-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain NRC Approval For Changes to Diesel Generator Trips and Flood Mitigation Strategy |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 71111.17T | The team identified two examples of a Severity Level IV non-cited violation of 10 CFR 50.59(c)(2), "Changes, Tests, and Experiments," for the licensee's failure to conclude that modifications to the Division 3 diesel generator trip logic circuits and floo
Region: IV | Grand Gulf | 32007 | 11/04/2016 12/09/2016 | 2016007-04 | NRC | NCVIV | Mitigating Systems | Green | Failure to Evaluate Delaying Inspection of Diesel Fuel Oil Storage Tank |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 71111.17T | The team identified a Severity Level IV non-cited violation of 10 CFR 50.59(d)(1), "Changes, Tests, and Experiments," for the licensee's failure to provide a written evaluation describing the basis for determining that a change to how often the Division 3
Region: IV | Grand Gulf | 32015 | 11/04/2016 12/09/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Building Sandbag Barriers |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71111.17T | The team identified a Green, non-cited violation of Technical Specification 5.4.1(a), "Procedures," for failure to establish adequate procedures for severe weather operations. Specifically, the licensee failed to establish adequate severe weather procedur
Region: IV | Grand Gulf | 31980 | 09/30/2016 11/10/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify Conditions Adverse to Quality in the RCIC System |  | H.11 Challenge the Unknown | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify a condition adverse to quality. Specifically, operations personnel failed to identify oscillations in the r
Region: IV | Grand Gulf | 31989 | 09/30/2016 11/10/2016 | 2016003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Procedures and Work Order Instructions used for Safety-Related Heat Exchanger Testing |  | H.7 Documentation | TE?: N | 05000416 Grand Gulf 1 |  | 71111.07T | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "conditions adverse to quality are promptly identified and corrected." Specifically, prior to April 2012, the license
Region: IV | Grand Gulf | 31990 | 09/30/2016 11/10/2016 | 2016003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have an Offnormal Event Procedure for Malfunctions of the Pressure Control System |  | P.1 Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the failure to establish a procedure for combating malfunctions of the reactor pressure control system. Specifically, on June 17, 2016, operators combate
Region: IV | Grand Gulf | 31993 | 09/30/2016 11/10/2016 | 2016003-04 | NRC | FIN | Initiating Events | Green | Failure to Use the Operational Decision-Making Issue Process to Communicate Trigger Points for Power and Pressure Oscillations |  | H.3 Change Management | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a finding for the licensee's failure to aggressively and fully communicate an operational decision-making instruction implementation action plan, particularly the trigger points and those actions if trigger points are exceeded, t
Region: IV | Grand Gulf | 31966 | 06/30/2016 08/03/2016 | 2016002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain Secondary Containment Operable during Roof Inspections |  | H.7 Documentation | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green, non-cited violation of Technical Specification Surveillance Requirement 3.0.1, for the failure to meet Surveillance Requirement 3.6.4.1.1 and declare Limiting Condition for Operation 3.6.4.1 not met. Specifically, the li
Region: IV | Grand Gulf | 31971 | 06/30/2016 08/03/2016 | 2016002-02 | NRC | FIN | Initiating Events | Green | Failure to Provide Detailed Work Instructions Resulted In A Reactor Scram |  | H.2 Field Presence | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a Green, self-revealed finding of Procedure EN-WM-105, "Planning," Revision 16, for the failure to ensure Work Order 397549 provided detailed instructions for performing troubleshooting on the 'B' phase of the main transformer. Spe
Region: IV | Grand Gulf | 31979 | 01/31/2016 01/28/2016 | 2015301-01 | NRC | NCV | Mitigating Systems | Green | ER 05000416/2015301; 10/26/2015 - 01/19/2016; Grand Gulf Nuclear Station; Initial Operator Licensing Examination Report |  | H.8 Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," states, in part, "Instructions, procedures, or drawings shall include appropriate quantitative or qualitative acceptance criteria for determining that important activ
Region: IV | Grand Gulf | 31954 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Have Appropriate Instructions for Preventative Maintenance on the Division I Diesel Generator Simulated Run |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000416 Grand Gulf 1 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, for the failure to establish adequate instructions to perform a simulated surveillance on the division I diesel generator. Specifically, the simulated surveil
Region: IV | Grand Gulf | 31955 | 12/31/2015 02/11/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Timely Enter Technical Specification Surveillance Requirement 3.0.1 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors identified a non-cited violation of Technical Specification Surveillance Requirement 3.0.1, for the failure to follow requirements when a surveillance was not performed within the specified frequency and declare the Limiting Condition for O
Region: IV | Grand Gulf | 31960 | 12/31/2015 02/11/2016 | 2015004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Maintenance Instructions to Perform Work Activities on the Division III Diesel Generator Overspeed Trip Limit Switch |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a, for the failure to establish adequate maintenance instructions to perform work activities on the division III diesel generator overspeed trip limit switch. Sp
Region: IV | Grand Gulf | 31950 | 10/09/2015 11/20/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Enter a Condition Adverse to Quality into the Corrective Action Program |  | P.1 Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify and correct a condition adverse to quality by entering it into the corrective action program for resolution. Specifically,
Region: IV | Grand Gulf | 30976 | 10/09/2015 11/20/2015 | 2015008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Initiate Condition Reports |  | H.9 Training | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The team identified five examples of a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct conditions adverse to quality. Specifically, on October 8, 2015, the team identified
Region: IV | Grand Gulf | 30977 | 10/09/2015 11/20/2015 | 2015008-03 | NRC | NCV | Barrier Integrity | Green | Failure to Declare Secondary Containment Inoperable Based on Failed Surveillance Testing |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | The team identified a non-cited violation of Technical Specification 3.6.4.1 Condition A, for the failure to declare secondary containment inoperable. Specifically, on August 1, 2015, the licensee failed to declare secondary containment inoperable after i
Region: IV | Grand Gulf | 30979 | 10/01/2015 11/13/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Safety-Related Alternating Current and Direct Current Equipment Operability and Functionality at Maximum Allowable Voltage Levels |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified two examples of a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as
Region: IV | Grand Gulf | 31927 | 10/01/2015 11/13/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Electrical Interrupting Devices are Rated for Available Fault Current Levels |  | H.6 Design Margins | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Grand Gulf | 31929 | 10/01/2015 11/13/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Address Impacts of Revised Calculation Output Data |  | H.8 Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures,
Region: IV | Grand Gulf | 31932 | 10/01/2015 11/13/2015 | 2015007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Surveillance Requirement 3.8.1.9 |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green, non-cited violation of Technical Specification 3.8.1, AC Sources-Operating, LCO 3.8.1, which requires that three diesel generators be operable. Specifically, since July 1985, the licensee failed to perform Surveillance
Region: IV | Grand Gulf | 31939 | 10/01/2015 11/13/2015 | 2015007-09 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain a License Amendment for Use of Probabilistic Methods to Evaluate Tornado Missile Hazards |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 7111121 | Severity Level IV/Green. The team identified a Green, Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," paragraph c(2), (1995 version) which requires that a licensee who desires to make a change in the facility desc
Region: IV | Grand Gulf | 31940 | 10/01/2015 11/13/2015 | 2015007-10 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Equipment Operability and Functionality of Allowable Alternating Current Frequency Range |  | P.6 Self Assessment | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Grand Gulf | 31944 | 10/01/2015 11/13/2015 | 2015007-11 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Equipment Control Procedures for Loose Items in Containment |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green, non-cited violation of Technical Specification 5.4, "Procedures," 5.4.1, which states, "Written procedures shall be established, implemented, and maintained covering the following activities: (a) The applicable procedur
Region: IV | Grand Gulf | 30975 | 09/30/2015 11/12/2015 | 2015003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have Appropriate Instructions for Preventative Maintenance on the Division II Diesel Generator Fuel Rack Control Lever |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, for the failure to establish appropriate maintenance instructions to perform maintenance activities on the fuel rack control lever of the division II diesel
Region: IV | Grand Gulf | 30965 | 06/30/2015 08/11/2015 | 2015002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Have Appropriate Instructions Resulted in the Unplanned Unavailability of the Reactor Core Isolation Cooling System |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, for failure to establish appropriate work instructions to properly preplan and perform maintenance that affected the performance of the reactor core isolat
Region: IV | Grand Gulf | 30967 | 06/30/2015 08/11/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify High Vibration on the Division 3 EDG Soak Back Oil Pump |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the failure to have appropriate maintenance instructions to review and analyze vibration data on the division 3 emergency diesel generator soak back oil pump. Specif
Region: IV | Grand Gulf | 30969 | 06/30/2015 08/11/2015 | 2015002-04 | NRC | NCV | Mitigating Systems | Green | Possible Loss of Communications Systems During Control Room Fire Scenarios |  |  | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The team identified a non-cited violation of License Condition 2.C.9, "Fire Protection," for the failure to provide reliable communications systems for use by operators during control room fire scenarios. The licensee included this deficiency in their c
Region: IV | Grand Gulf | 30955 | 03/31/2015 05/12/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions Associated with Division 1 and 2 Standby Service Water Pump House Ventilation System Due to Degraded Relays |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take timely corrective actions to correct a condition adverse to quality associated with the division 1 and 2
Region: IV | Grand Gulf | 30960 | 03/31/2015 05/12/2015 | 2015001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow a Procedure Resulting in the Unplanned Inoperability of the Reactor Core Isolation Cooling System |  | H.12 Avoid Complacency | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, for failure to follow a procedure which resulted in the unplanned inoperability of the reactor core isolation cooling system. This occurred when licensee tec
Region: IV | Grand Gulf | 30961 | 03/31/2015 05/12/2015 | 2015001-03 | NRC | NCV | Emergency Preparedness | Green | Emergency Action Level Scheme for Nonfunctional Seismic Monitor |  | P.2 Evaluation | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) for the licensee's failure to follow and maintain the effectiveness of an emergency plan that meets the requirements of the planning standard 50.47(b)(4), which requires that a standard
Region: IV | Grand Gulf | 30964 | 03/31/2015 05/12/2015 | 2015001-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Properly Calibrate Main Steam Line Radiation Monitors and Containment/Drywell High Range Radiation Monitors |  | H.1 Resources | TE?: N | 05000416 Grand Gulf 1 |  | 71124.05 | The inspectors identified a non-cited violation of 10 CFR 20.1501(c) for the licensee's failure to properly calibrate the main steam line radiation monitors and the containment/drywell high range radiation monitors. The violation was of very low safety si
Region: IV | Grand Gulf | 30963 | 03/31/2015 05/12/2015 | 2015001-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Establish, Implement, and Maintain Appropriate Changes to the Offsite Dose Calculation Manual For REMP Airborne Sampling |  | H.8 Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 71124.07 | The inspectors identified a non-cited violation of Technical Specification 5.5.1, "Offsite Dose Calculation Manual (ODCM)." Specifically, when changes were made to the Offsite Dose Calculation Manual in 1997, the licensee failed to establish an airborne s
Region: IV | Grand Gulf | 30962 | 03/31/2015 05/12/2015 | 2015001-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Establish Commercial-Grade Items as Basic Components |  |  | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the suitability of replacement parts that were procured from commercial suppliers. Specifically, the inspe
Region: IV | Grand Gulf | 30933 | 12/31/2014 02/07/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assure Quality Installation on RCIC Steam Line |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to assure quality installation of the steam line tubing of the reactor core isolation cooling (RCIC) system. Specifica
Region: IV | Grand Gulf | 30925 | 09/30/2014 10/28/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control Transient Combustible Material in Accordance with a Fire Protection Procedure |  | H.14 Conservative Bias | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | The inspectors identified a non-cited violation of License Condition 2.C(41), "Fire Protection Program," for the failure to control transient combustibles in accordance with a fire protection program procedure. On August 13, 2014, the inspectors identifie
Region: IV | Grand Gulf | 30931 | 09/30/2014 10/28/2014 | 2014004-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Corrective Actions Leads to Automatic Plant Scram |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow procedure EN-LI-102, "Corrective Action Process", Revision 12, which requires the licensee to appropriately complete assigned corrective actions within the prescribed ti
Region: IV | Grand Gulf | 30921 | 06/30/2014 08/14/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Reinstate an Essential-Critical Preventative Maintenance Task for a High-Critical Component |  | H.14 Conservative Bias | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly reinstate an essential-critical preventative maintenance task after they identified that it had bee
Region: IV | Grand Gulf | 30923 | 06/20/2014 08/26/2014 | 2014009-01 | NRC | FIN | Initiating Events | Green | Failure to Correct Degraded Viewing Ports in a Timely Manner |  | P.5 Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a Green finding resulting from the licensee's failure to follow Procedure EN-LI-102, "Corrective Action Process," Revision 23, and Procedure EN-OP-104,"Operability Determination Process," Revision 7, for an adverse condition. The
Region: IV | Grand Gulf | 30924 | 06/20/2014 08/26/2014 | 2014009-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Correct A Significant Condition Adverse to Quality and Preclude Repetition |  | P.2 Evaluation | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "corrective Action," resulting from the licnesee's failure to prevent the repetition of a break of the first stage turbine sensing line, whi
Region: IV | Grand Gulf | 30922 | 05/02/2014 06/30/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Emergency Lighting |  | H.1 Resources | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C.(41), "Fire Protection Program," for the failure to provide adequate 8-hour emergency lights. Specifically, the licensee failed to provide adequate lighting at all locations operator
Region: IV | Grand Gulf | 30912 | 03/31/2014 05/14/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Scaffold Activity Would not Interfere with Fire Brigade Response |  | H.4 Teamwork | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | The inspectors identified a non-cited violation of License Condition 2.C(41), "Fire Protection Program," for the failure to adhere to procedural requirements to ensure that scaffold installed in the plant would not prevent or restrict the fire brigade fro
Region: IV | Grand Gulf | 30913 | 03/31/2014 05/14/2014 | 2014002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control a Locked High Radiation Area Due to Unsecured Highly Radioactive Materials Stored in the Pool |  | H.8 Procedure Adherence | TE?: N | 05000416 Grand Gulf 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.7.3, resulting from the licensee's failure to control a high radiation area with radiation levels greater than 1000 millirem per hour. As immediate corrective actio
Region: IV | Grand Gulf | 30894 | 12/31/2013 02/12/2014 | 2013005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Comply with Technical Specification 3.4.11 |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | The inspectors identified a non-cited violation of Technical Specification 3.4.11 for the failure to comply with the Reactor Coolant System (RCS) Pressure and Temperature Limits Report (PTLR) during plant cold startups. Specifically, the PTLR had a lower
Region: IV | Grand Gulf | 30895 | 12/31/2013 02/12/2014 | 2013005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Provide Adequate Procedures Results in Loss of Safety Function |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to provide an adequate procedure for a safety related activity. On December 17, 2013, while
Region: IV | Grand Gulf | 30899 | 12/31/2013 02/12/2014 | 2013005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Entry Into A High Radiation Area Without A Required Radiation Monitoring Device |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.7.1, resulting from an individual entering a high radiation area without the required radiation monitoring device. This issue was entered into the licensee's correc
Region: IV | Grand Gulf | 30900 | 12/31/2013 02/12/2014 | 2013005-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Survey Resulting in Personnel Entry To A High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a) for failure to survey, which resulted in a worker entering an unposted high radiation area. This issue was entered into the licensee's corrective action program as Conditio
Region: IV | Grand Gulf | 30874 | 09/30/2013 11/27/2013 | 2013004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Determination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure EN-OP-104, "Operability Determinations." S
Region: IV | Grand Gulf | 30880 | 09/30/2013 11/27/2013 | 2013004-02 | NRC | NCVIV | Barrier Integrity | Green | Failure to Obtain NRC Approval for a Change in Method of Evaluation for Determining Reactor Vessel Fluence |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 71111.17T | SL-IV. The team identified a Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," involving the licensee's failure to obtain a license amendment pursuant to 10 CFR 50.90 prior to implementing a new method of evaluation
Region: IV | Grand Gulf | 30881 | 09/30/2013 11/27/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Review Temporary Modifications by Operations Personnel During Turnover |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71111.18 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure 02-S-01-4, "Shift Relief and Turnover," Re
Region: IV | Grand Gulf | 30883 | 09/30/2013 11/27/2013 | 2013004-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain design Control of the Power Supplies for the Emergency Switchgear and Battery Room Fire Dampers |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.18 | The inspectors reviewed a self-revealing Green non-cited violation of Facility Operating License Condition 2.C (41), "Fire Protection Program," involving the failure to maintain design control of the power supplies for the emergency switchgear and battery
Region: IV | Grand Gulf | 30884 | 09/30/2013 11/27/2013 | 2013004-05 | NRC | NCV | Public Radiation Safety | Green | Failure to Implement the Offsite Dose Calculation Manual |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 71124.06 | Inspectors identified three examples of a non-cited violation of Technical Specification 5.5, "Programs and Manuals," for failure to maintain and implement requirements of the offsite dose calculation manual (ODCM). Specifically, the licensee failed to: (
Region: IV | Grand Gulf | 30885 | 09/30/2013 11/27/2013 | 2013004-06 | NRC | NCV | Public Radiation Safety | Green | Failure to Include Some Solid Radwaste Released in the 2012 Regulatory Guide 1.21 Annual Effluent Report |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 71124.08 | Inspectors identified a non-cited violation of Technical Specification 5.6.3 because the licensee failed to include in the 2012 Annual Radiological Effluent Release Report some solid radioactive waste released to an offsite waste processor. The failur
Region: IV | Grand Gulf | 30888 | 09/30/2013 11/27/2013 | 2013004-07 | NRC | FIN | Initiating Events | Green | Failure to Follow Alarm Response Steps to Restore the TSE Following Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a Green self-revealing finding for the failure to follow Procedure 04-1-02-1H13-P680-9A, "TSE INFL OFF," Revision 36; in that operations personnel did not verify steps were followed per this alarm response procedure prior to return
Region: IV | Grand Gulf | 30865 | 06/28/2013 08/12/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement a Compensatory Fire Watch per Station Fire Protection Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | The inspectors identified a non-cited violation of Facility Operating License Condition 2.C(41) for the failure to properly implement a compensatory fire watch per the station fire protection program. Following an inadvertent release of carbon dioxide fro
Region: IV | Grand Gulf | 30871 | 06/28/2013 08/12/2013 | 2013003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Nonconforming Condition with the Standby Diesel Generator Inlet Plenum Turning Vanes |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.17T | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, that "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, def
Region: IV | Grand Gulf | 30872 | 06/28/2013 08/12/2013 | 2013003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Nonconforming Condition in the Train B Starting Circuit |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.17T | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, that "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, def
Region: IV | Grand Gulf | 30873 | 06/28/2013 08/12/2013 | 2013003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Residual Heat Removal B System was Full of Water Within its Specified Frequency |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | Green. The inspectors identified a non-cited violation of Technical Specification Surveillance Requirement SR 3.5.1.1 for the failure to verify the residual heat removal B system was full of water within its specified frequency. The inspectors reviewed a
Region: IV | Grand Gulf | 29923 | 03/31/2013 05/15/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Seal Safety-related Manholes |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71111.06 | The inspectors identified a non-cited violation of License Condition 2.C(41), "Fire Protection Program," involving the failure to ensure that manhole MH01 was properly sealed to prevent entry of flammable liquid. Specifically, on February 20, 2013, four m
Region: IV | Grand Gulf | 29928 | 03/31/2013 05/15/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor for Ice on Standby Service Water Towers |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, for the licensee's failure to monitor for ice accumulation on the standby service water cooling towers in accordance with station procedures. On January 17, 2013, the p
Region: IV | Grand Gulf | 29929 | 03/31/2013 05/15/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for Setpoint Calculations |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to maintain design control, incorporate, verify, and check new instrument drift values, and translate the design bas
Region: IV | Grand Gulf | 29930 | 03/31/2013 05/15/2013 | 2013002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Scaffold Affecting Fire Brigade Access |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors identified a non-cited violation of License Condition 2.C(41), "Fire Protection Program," for the failure to identify and correct a condition adverse to fire protection. Specifically, the licensee failed to ensure that fire brigade members
Region: IV | Grand Gulf | 29931 | 03/31/2013 05/15/2013 | 2013002-05 | Self - Revealed | FIN | Initiating Events | Green | Reactor Scram Due to Ground Fault |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing finding for the failure to ensure the current transformer structure, the neutral bus housing, and the associated mounting hardware were installed with adequate clearance to accommodate thermal expansion. This failu
Region: IV | Grand Gulf | 29932 | 03/31/2013 05/15/2013 | 2013002-06 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure for Removal of a Foreign Material Exclusion Plug |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50 Appendix B Criterion V, for the failure to provide adequate instructions to remove foreign material from the exhaust port of relief valve 1B21F047A. As a result, the valve fa
Region: IV | Grand Gulf | 30854 | 03/31/2013 05/15/2013 | 2013002-07 | Self - Revealed | FIN | Initiating Events | Green | Reactor Scram Due to Moisture in Isophase Bus Duct |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing finding for the failure to identify a degraded isophase bus duct view port window, which allowed water to intrude into the duct and caused an automatic reactor scram on January 14, 2013. The licensee took correctiv
Region: IV | Grand Gulf | 30860 | 03/31/2013 05/15/2013 | 2013002-08 | NRC | NCV | Initiating Events | Green | Failure to Revise the Scram Procedure After Temporary Modification |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the failure to revise the scram procedure after temporarily modifying the division-2 circuits that sense first-stage turbine pressure. Specifically, after a steam sens
Region: IV | Grand Gulf | 30862 | 02/27/2013 03/28/2013 | 2012301-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Aligning Nitrogen Backup to Automatic Deressurization System |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | NONE | -Green. The team identified a Green non-cited violation (NCV) of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings." Specifically, the licensee's procedures for aligning portable nitrogen bottles to the Instrument Air
Region: IV | Grand Gulf | 29908 | 12/31/2012 02/11/2013 | 2012005-01 | NRC | NCV | Barrier Integrity | Green | Failure to Make Timely Corrective Actions to Repair the Degraded Auxiliary Building Water Intrusion Barrier |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," involving the failure to correct a condition adverse to quality in a timely manner. Specifically, the licensee failed to correct multiple
Region: IV | Grand Gulf | 29910 | 12/31/2012 02/11/2013 | 2012005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Monitor the Condition of the Auxiliary Building Water Intrusion Barrier |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2), for the failure to evaluate the condition of the auxiliary building water intrusion barrier. The licensee entered this issue into their corrective action program as Condition Re
Region: IV | Grand Gulf | 29911 | 12/31/2012 02/11/2013 | 2012005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Adequate Procedure Instructions to Perform Preventive Maintenance Requiring The Periodic Replacement of the Control Relays in the GE Magne Blast Circuit Breakers |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | Green. The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to complete preventive maintenance tasks on the high pressure core spray divisi
Region: IV | Grand Gulf | 29912 | 12/31/2012 02/11/2013 | 2012005-04 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Adequately Plan and Control Work Activities to Maintain ALARA |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 71124.02 | Green. The inspector reviewed a self-revealing finding of very low safety significance because during the refueling outage 18 extended power upgrade, the licensee did not adequately plan and control work activities for the design and replacement of the ne
Region: IV | Grand Gulf | 29916 | 12/31/2012 02/11/2013 | 2012005-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure To Follow the Radiation Work Permit Requirements During Reactor Cavity High Water Operations |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 71124.02 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1 for failure to comply with radiological exposure controls specified in Radiation Work Permit 2012-1402, "Refuel Floor High Water Activities." Specifically
Region: IV | Grand Gulf | 29917 | 12/31/2012 02/11/2013 | 2012005-06 | NRC | NCV | Initiating Events | Green | Failure to Evaluate the Risk Significances and Develop Action Plans to Address Equipment Identified During Extent of Condition Review for a Post Scram Root Cause Analysis |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to follow procedure EN-LI-118, "Root Cause Evaluation Process," Revision 18, in that t
Region: IV | Grand Gulf | 29921 | 12/31/2012 02/11/2013 | 2012005-07 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Gain Settings on APRM and LPRM Instruments in Accordance with Design Requirements |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to establish the gain settings used on the power range neutron monitoring system in accordance with design require
Region: IV | Grand Gulf | 29886 | 09/21/2012 11/01/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Inadequate Operability Determinations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | Green. The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure EN-OP-104, "Operability
Region: IV | Grand Gulf | 29887 | 09/10/2012 10/09/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Preconditioning of 4160 Vac Circuit Breakers for As-Found Tests |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and com
Region: IV | Grand Gulf | 29894 | 09/10/2012 10/09/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Testing Program for Safety Related 125 Vdc Circuit Breakers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, an
Region: IV | Grand Gulf | 29895 | 09/10/2012 10/09/2012 | 2012008-03 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain NRC Approval for a Change to Credible Passive Failures in the Standby Service Water System |  |  | TE?: Y SL-IV-NCVIV | 05000416 Grand Gulf 1 |  | 7111121 | Severity Level IV. The team identified a Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests and Experiments" which states, in part, that "a licensee shall obtain a license amendment pursuant to Section 50.90 prior to implementing a pro
Region: IV | Grand Gulf | 29901 | 09/10/2012 10/09/2012 | 2012008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Enter an NRC Violation Regarding the Standby Service Water System into the Corrective Action Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, that "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctio
Region: IV | Grand Gulf | 29902 | 09/10/2012 10/09/2012 | 2012008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Operability Determination Process Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" which states, in part, that "Activities affecting quality shall be prescribed by documented instructions, procedure
Region: IV | Grand Gulf | 29905 | 09/10/2012 10/09/2012 | 2012008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Test and Inspection Requirements for 4160 Vac Circuit Breakers into Preventive Maintenance Procedures |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | Green. The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and com
Region: IV | Grand Gulf | 29861 | 06/30/2012 08/01/2012 | 2012003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure Materials are Stored Properly in the 500 KV Switchyard |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.01 | The inspectors identified a finding for the licensee's failure to ensure that materials or equipment were not stored under energized lines or near energized equipment in accordance with station procedures. On May 21, 2012, the inspectors were performing a
Region: IV | Grand Gulf | 29866 | 06/30/2012 08/01/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions to Address Configuration Control of Previous Non-cited Violation |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The inspectors identified a non-cited violation of very low safety significance of 10 CFR Appendix B, Criterion XVI, "Corrective Action," for failure to implement adequate corrective actions for a previous NRC-identified non-cited violation. The pr
Region: IV | Grand Gulf | 29862 | 06/30/2012 08/01/2012 | 2012003-03 | Self - Revealed | FIN | Mitigating Systems | Green | Loss of Alternate Method of Decay Heat Removal Due to Reactor Water Clean Up Pumps Tripping on Low Suction Flow Signal |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | Green. The inspectors reviewed a self-revealing finding for the licensee's failure to identify that de-energizing non-safety electrical bus 13BD1 and 13BD2 would cause the reactor water clean-up pumps A and B to trip on a low suction flow signal. On April
Region: IV | Grand Gulf | 29867 | 06/30/2012 08/01/2012 | 2012003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement a Surveillance Requirement to Assure that the Limiting Condition for Operation Will be Met |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50.36, "Technical Specifications," involving the failure to implement a surveillance requirement to assure that the limiting conditions for operation of the ultimate heat sink will be m
Region: IV | Grand Gulf | 29870 | 06/30/2012 08/01/2012 | 2012003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow a Post-Modification Test Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to follow a post-modification test procedure for the interconnecting siphon line
Region: IV | Grand Gulf | 29857 | 06/30/2012 08/01/2012 | 2012003-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Results in Loss of Decay Heat Removal to the Spent Fuel Pool |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specifications 5.4.1(a), involving a loss of decay heat removal in the spent fuel pool due to station personnel failing to correctly follow operation of pool gate seal air su
Region: IV | Grand Gulf | 29871 | 06/30/2012 08/01/2012 | 2012003-07 | NRC | NCV | MISC | Green | Inappropriate Use of Waivers to Allow Workers to Exceed the Minimum Day Off Rule |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | Green. The inspectors identified a non-cited violation of 10 CFR 26, Subpart I, "Managing Fatigue," Subsection 207, "Waivers and Exceptions," when the licensee inappropriately used waivers to allow workers to exceed the minimum day off rule. While reviewi
Region: IV | Grand Gulf | 29858 | 06/30/2012 08/01/2012 | 2012003-08 | Self - Revealed | NCV | Initiating Events | Green | Failure of Hot Work Fire Watch to Follow Procedural Requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of Technical Specifications 5.4.1(a), for failure of the hot-work fire watch to follow procedural requirements, which resulted in a fire in main condenser A. On April 11, 2012, at 6:11 p.m., hot
Region: IV | Grand Gulf | 29841 | 03/23/2012 05/04/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions Associated with Division 1 and 2 Standby Service Water Safety Related Cables that were Partially Submerged in Cable Manhole/Vault |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.06 | Green . The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take timely corrective actions to correct a condition adverse to quality associated with divisi
Region: IV | Grand Gulf | 29844 | 03/23/2012 05/04/2012 | 2012002-02 | Self - Revealed | FIN | Initiating Events | Green | Manual Reactor Scram Caused by Failure to Ensure the Main Steam Supply Valve to Reactor Feed Pump Turbine B was Full Open |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.11Q | Green . The inspectors reviewed a Green self-revealing finding for the failure to ensure the correct position (full open) of the main steam supply valve 1N11-F014B to reactor feed pump turbine B, which resulted in a manual reactor scram due to decreasing
Region: IV | Grand Gulf | 29845 | 03/23/2012 05/04/2012 | 2012002-03 | NRC | NCV | Initiating Events | Green | Failure to Perform an Online Risk Assessment Per Severe Weather Off Normal Procedure Due to a Declared Tornado Warning Affecting Grand Gulf Nuclear Station |  | H.2(d) Facilities & Equipment | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | Green. The inspectors identified a Green non-cited violation of Technical Specifications 5.4.1.a for the failure to perform an online risk assessment per severe weather off normal procedure due to a declared tornado warning affecting Grand Gulf Nuclear St
Region: IV | Grand Gulf | 29853 | 03/23/2012 05/04/2012 | 2012002-04 | NRC | NCV | Barrier Integrity | Green | Modification of the Spent Fuel Pool without Prior NRC Approval |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | SLIV. The inspectors identified a Severity Level IV non-cited violation of 10 CFR 50.59, "Changes, Tests and Experiments," when the licensee failed to obtain a license amendment prior to implementing a proposed change to the plant that required a change t
Region: IV | Grand Gulf | 29851 | 03/23/2012 05/04/2012 | 2012002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Fire Protection, in That the Licensee Failed to Adequately Provide Contingency Lighting in the Fire Brigade Dress Out Area While Normal Lighting was Inoperabl |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors identified a Green non-cited violation of Facility Operating License Condition 2.C(41), for the failure to correct a condition adverse to fire protection. Specifically, the licensee failed to adequately provide contingency lighting i
Region: IV | Grand Gulf | 29830 | 12/31/2011 02/02/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Inspection of Probable Maximum Precipitation Door Seals Protecting Safety Related Equipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | Green. The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to perform an adequate inspection of probable maximum precipitation door seals protecting safety related equ
Region: IV | Grand Gulf | 29831 | 10/21/2011 01/13/2012 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions for Reactor Core Isolation Cooling System Venting |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The team identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct an inadequate venting procedure for the reactor core isolation cooling system. Corrective
Region: IV | Grand Gulf | 29833 | 10/21/2011 01/13/2012 | 2011006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Document a Condition as a Significant Condition Adverse to Quality |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The team identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions," for the failure to identify and document a significant condition adverse to quality and report the condition to appropriate levels of manag
Region: IV | Grand Gulf | 29839 | 10/21/2011 01/13/2012 | 2011006-04 | NRC | VIO | Mitigating Systems | Green | Inadequate Corrective Action for a Leak on the Division II Emergency Diesel Generator Lube Oil Sump | EA Case: 2012015 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The team identified a Green cited violation of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct a leak on the Division II emergency diesel generator lube oil sump. Despite identification of
Region: IV | Grand Gulf | 29818 | 09/27/2011 11/09/2011 | 2011004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure Correct Fuses were Installed in the Hydrogen Igniter Control Circuits |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | Green. The inspectors reviewed a self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to install the correct amperage fuses in the hydrogen igniter control circuit. On August 4, 2011, the inspe
Region: IV | Grand Gulf | 29819 | 09/27/2011 11/09/2011 | 2011004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Perform Preventative Maintenance on the Fuel Handling Bridge Paddle Switch |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. The inspectors reviewed a self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for inadequate preventative maintenance instructions, which resulted in the loss of control of the fu
Region: IV | Grand Gulf | 29825 | 09/27/2011 11/09/2011 | 2011004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance for Components Used in Critical Applications |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a for the licensee's failure to follow a procedure that required them to evaluate components of critical systems in order to establish a preventive mainte
Region: IV | Grand Gulf | 29826 | 08/30/2011 09/22/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure To Provide An Adequate Alternative Shutdown Procedure |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | -Green. The team identified a noncited violation of License Condition 2.C(41), "Fire Protection Program," for failing to ensure that the postfire safe shutdown procedure for fires requiring control room evacuation could be performed within the critical ti
Region: IV | Grand Gulf | 29827 | 08/30/2011 09/22/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Failure To Assure Equipment Required For Postfire Safe Shutdown Was Protected Against Fire Damage |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | Green. The team identified a noncited violation of License Condition 2.C(41), "Fire Protection Program," for failing to assure that equipment relied upon for safe shutdown following a fire in the control room was protected against fire damage. Specificall
Region: IV | Grand Gulf | 29828 | 08/30/2011 09/22/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions to Protect Safe Shutdown Equipment From Fire Damage |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | Green. The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take timely corrective action to modify the control circuits for 33 motor operated valves that are relied upon during safe shutd
Region: IV | Grand Gulf | 29829 | 08/30/2011 09/22/2011 | 2011007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions To Assure Postfire Safe Shutdown |  |  | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, for inadequate corrective actions to address the potential for fire induced hot shorts to impact the ability to trip a control rod group as described in Information
Region: IV | Grand Gulf | 28566 | 06/27/2011 08/05/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Inspection of Probable Maximum Precipitation Door Seals Protecting Safety Related Equipment |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 71111.01 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to perform an adequate inspection of probable maximum precipitation door seals protecting safety relate
Region: IV | Grand Gulf | 28567 | 06/27/2011 08/05/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Scaffold Control Procedure |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to adequately implement scaffolding control procedural requirements related to post-installation in
Region: IV | Grand Gulf | 28574 | 06/27/2011 08/05/2011 | 2011003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Conditions Adverse to Fire Protection |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | Green. The inspectors identified a noncited violation of License Condition 2.C(41) for the failure to identify conditions adverse to the fire protection program. Specifically, during required inspections of the material condition of the sprinkler system,
Region: IV | Grand Gulf | 28575 | 06/27/2011 08/05/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that Safety Related Manholes were Properly Sealed to Prevent the Entry of Flammable Liquid |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.06 | Green. The inspectors identified a noncited violation of Facility Operating License Condition 2.C(41), involving the failure to ensure that manholes MH01, MH20 and MH21 were properly sealed to prevent the entry of flammable liquid. During the performance
Region: IV | Grand Gulf | 28576 | 06/27/2011 08/05/2011 | 2011003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedures for High Pressure Core Spray Minimum Flow Valve Surveillance Testing |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the licensee's failure to provide adequate testing procedures, which resulted in the high pressure core spray minimum flow valve inadvertently stroki
Region: IV | Grand Gulf | 28579 | 06/27/2011 08/05/2011 | 2011003-06 | Self - Revealed | NCV | Mitigating Systems | Green | Loose Fuse Clips in Division 3 Emergency Diesel Generator |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions for a significant condition adverse to quality associated
Region: IV | Grand Gulf | 29810 | 06/27/2011 08/05/2011 | 2011003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Assure Configuration Control of Safety Related Systems |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to review the suitability of leaving test fittings on reactor coolant system flow transmitter equalizing block drain port
Region: IV | Grand Gulf | 29811 | 06/27/2011 08/05/2011 | 2011003-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow a Procedure Resulting in the Inoperability of the Reactor Core Isolation Cooling System Primary Containment Isolation Valve |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | Green. The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, for failure to follow a procedure resulting in the inoperability of the reactor core isolation cooling system primary containment isolation valve. This
Region: IV | Grand Gulf | 28553 | 03/27/2011 05/10/2011 | 2011002-01 | NRC | NCV | Barrier Integrity | Green | Transient Combustible Stored in the Fire Exclusion Zone Near the Independent Spent Fuel Storage Installation |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | Green . The inspectors identified a noncited violation of Facility Operating License Condition 2.C(41), involving the failure to ensure that transient combustible were not stored in the fire exclusion zone near the independent spent fuel storage installa
Region: IV | Grand Gulf | 28555 | 03/27/2011 05/10/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Demonstrate Maintenance Effectiveness of Train B Control Room Air Conditioner |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors identified a noncited violation of 10 CFR Part 50.65(a)(2) for the licensee's failure to demonstrate that the performance of the train B control room air conditioner was being effectively controlled through the performance of appropr
Region: IV | Grand Gulf | 28558 | 03/27/2011 05/10/2011 | 2011002-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to use a qualified radiation protection technician to provide direct continuous coverage of work in a locked high radiation area |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71124.01 | Green. The inspectors identified a noncited violation of Technical Specification 5.7.2, resulting from the licensee's failure to use a qualified radiation protection technician to provide direct continuous coverage of work in a locked high radiation area.
Region: IV | Grand Gulf | 28556 | 03/27/2011 05/10/2011 | 2011002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent Recurrence of Control Room Air Conditioner Compressor Tripping Due to Low Oil Pressure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, after the licensee failed to determine the cause and prevent recurrence of a significant condition adverse to quality assoc
Region: IV | Grand Gulf | 28557 | 03/27/2011 05/10/2011 | 2011002-06 | NRC | FIN | Barrier Integrity | Green | Inadequate Design Control for the Mitigation Monitoring System Modification |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing, Green finding of EN-DC-115, "Engineering Change Process," involving the failure to maintain adequate design control measures associated with the installation of the mitigation monitoring system. On November
Region: IV | Grand Gulf | 28539 | 12/31/2010 02/10/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation Following a Spurious Actuation of the Standby Service Water Pump House Ventilation Fan |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | Green. The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion V, involving a failure to follow procedures, which resulted in an inadequate operability evaluation. On December 5, 2010, a spurious actuation of the standby se
Region: IV | Grand Gulf | 28537 | 12/31/2010 02/10/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Address the deficiencies in the RCIC Flow Control System |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | Green. The inspectors reviewed a self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified associated with the licensee's failure to take timely corrective actions to correct a condition adverse to qua
Region: IV | Grand Gulf | 28545 | 12/31/2010 02/10/2011 | 2010005-03 | NRC | VIO | Emergency Preparedness | Green | Failure to Have Guidelines for the Choice of Protective Actions During an Emergency Consistent with Federal Guidance |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71114.05 | Green. A cited violation of 10 CFR 50.47(b)(10) was identified for failure to develop and have in place guidelines for the choice of protective actions during an emergency that were consistent with federal guidance. Federal guidance for the choice of prot
Region: IV | Grand Gulf | 28538 | 12/31/2010 02/10/2011 | 2010005-04 | NRC | NCV | Initiating Events | Green | Inadequate Reactor Shutdown Procedure Causes Power and Level Oscillations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. The inspectors identified a green, noncited violation of 10 CFR 50 Appendix B, Criterion V, for an inadequate shutdown procedure resulting in power and level oscillations in the reactor. The revised procedure failed to require the plant to be place
Region: IV | Grand Gulf | 28546 | 12/31/2010 02/10/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that Quality Control verification inspections were consistently included and correctly specified in quality-affecting procedur
Region: IV | Grand Gulf | 28547 | 12/31/2010 02/10/2011 | 2010005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. Inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement the experience and qualification requirements of the Quality Assurance Program. As a result, the licensee f
Region: IV | Grand Gulf | 28530 | 09/27/2010 11/09/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Door Barrier Protecting the Safeguards Switchgear Rooms |  | H.2(d) Facilities & Equipment | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | Green. The inspectors identified a Green noncited violation of Facility Operating License Condition 2.C(41) involving the failure to ensure that fire barriers protecting safety-related areas were functional during monthly fire barrier inspections. The ins
Region: IV | Grand Gulf | 28529 | 09/27/2010 11/09/2010 | 2010004-02 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment for Switchyard Battery Replacement |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for failure to properly assess the risk impact of maintenance on the switchyard batt
Region: IV | Grand Gulf | 28531 | 09/27/2010 11/09/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Remove Foreign Material from the Control Room Air Conditioning Systems |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion XVI, for the failure to remove foreign material from the control room air conditioning oil and Freon subsystems. The pencil strainer on the compressor was found
Region: IV | Grand Gulf | 28533 | 09/27/2010 11/09/2010 | 2010004-04 | Self - Revealed | NCV | Emergency Preparedness | Green | Primary Meteorological Tower Inoperable Without Compensatory Actions in Place |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. A self-revealing non-cited violation of 10 CFR 50.47(b)(8), was identified when the Grand Gulf Nuclear Station Primary Meteorological Tower was rendered inoperable without compensatory actions from July 6 through July 27, 2010. The primary meteorol
Region: IV | Grand Gulf | 28552 | 09/27/2010 11/09/2010 | 2010004-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow the Radiological Protection Job Coverage Procedure |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 71124.04 | Green. The inspectors reviewed a self-revealing Green noncited violation of Technical Specification 5.4.1.a for a procedure violation. Radiation Work Permit 20101704 covered work on Valve 1G33F253 in the reactor water cleanup room. Work on this valve was
Region: IV | Grand Gulf | 28532 | 09/27/2010 11/09/2010 | 2010004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement an Adequate Structural Monitoring Program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B Criterion V for failure to perform required inspection of safety-related plant structures. Specifically, the inspectors found inspections that had been only partially perf
Region: IV | Grand Gulf | 28528 | 06/27/2010 07/19/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Risk Assessment for Emergent Work Activities |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | NONE | -Green. The inspectors identified a noncited violation of 10 CFR 50.65 a(4) for failure to perform adequate risk assessments prior to flushing the reactor heat removal systems suction piping and filling and venting of the alternate decay heat removal syst
Region: IV | Grand Gulf | 28527 | 06/27/2010 07/19/2010 | 2010003-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedure Results in Loss of Decay Heat Removal to the Spent Fuel Pool |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | NONE | Green. The inspectors reviewed a self-revealing noncited violation of Technical Specifications 5.4.1(a), involving a loss of decay heat removal in the spent fuel pool due to station operators failing to follow the fuel pool cooling and cleanup system oper
Region: IV | Grand Gulf | 28523 | 03/27/2010 05/04/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Restore Control Room Air Conditioning Subsystem B to Operable Status Within the Required Time of 30 days (Section 1R07) |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.07A | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 3.7.4 for failing to restore control room air conditioning subsystem B to operable status within the required time of 30 days. Specifically, between March 28, 2
Region: IV | Grand Gulf | 28524 | 03/27/2010 05/04/2010 | 2010002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Work Instructions Results in Loss of Buss and a Plant Transient (Section 4OA3) |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing finding for a failure to follow work instructions resulting a in loss of 480V power to a bus and a plant transient. Specifically, contract workers were directed by work instructions to enter into a motor con
Region: IV | Grand Gulf | 28525 | 03/27/2010 05/04/2010 | 2010002-03 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Actions in Response to a Steam Leak Result in an Automatic Reactor Scram (Section 4OA3) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing finding involving the failure of site management to ensure that adequate corrective actions were implemented to resolve the effects of a large steam leak in the turbine building. Specifically, the reactor ex
Region: IV | Grand Gulf | 28526 | 03/27/2010 05/04/2010 | 2010002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Operator Failed to Move a Fuel Assembly in Accordance with Station Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1a when a fuel handling platform operator failed to move a fuel assembly in accordance with station procedures. Specifically, a new fuel assembly and the fu
Region: IV | Grand Gulf | 28518 | 12/03/2009 01/14/2010 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Used to Vent the Reactor Core Isolation Cooling System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | Green. The team identified a noncited violation of Technical Specification Surveillance Requirement 3.5.3.1 because the licensee failed to establish an adequate procedure to demonstrate compliance with this surveillance requirement. This surveillance requ
Region: IV | Grand Gulf | 28520 | 12/03/2009 01/14/2010 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Oil-Impregnated Insulation on Pump Turbines |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71152B | Green. A noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," was revealed on October 26, 2009, when potentially oil-impregnated insulation on the reactor core isolation cooling pump turbine began smoking during a monthly surve
Region: IV | Grand Gulf | 28510 | 09/23/2009 10/29/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Performance of a Maintenance Rule Scoped System |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | Green. The inspectors identified a Green noncited violation of 10 CFR Part 50.65(a)(2) involving the failure to adequately monitor the performance of a maintenance rule scoped system. The licensee's maintenance rule program required evaluation of the area
Region: IV | Grand Gulf | 28515 | 09/23/2009 10/29/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Operator Response Times to Fires |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | Green. The inspectors identified a Green non-cited violation of Technical Specification 5.4.1(a), for failure to ensure that operators can respond in timely manner to safe shutdown panels in the auxiliary building with a fire in the main control room. The
Region: IV | Grand Gulf | 28502 | 06/23/2009 07/28/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Changes to Protect the Standby Service Water Slab |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion III involving the failure to incorporate design changes required to limit dynamic loads on the standby service water basin slab. In 1997, the plant experienced damage
Region: IV | Grand Gulf | 28503 | 06/23/2009 07/28/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Debris Left in the Condensate Storage Tank |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V involving a failure to follow procedures which resulted in an inadequate operability evaluation. During the week of May 18, 2009, the site conducted debris remo
Region: IV | Grand Gulf | 28504 | 06/23/2009 07/28/2009 | 2009003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Fully Close a LPCS Manual Valve Resulted in Leakage of Water into the Condensate and Refueling Water Storage System |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors reviewed a self-revealing Green noncited violation of Technical Specification 5.4.1(a) involving a failure to implement the low pressure core spray system operating instruction correctly. On April 20, 2009, the site was performing a low pre
Region: IV | Grand Gulf | 28508 | 06/23/2009 07/28/2009 | 2009003-04 | NRC | FIN | Mitigating Systems | Green | Failure to Perform a Timely Operability Evaluation Following the Discovery of a SSW Fan Failure Mechanism |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green finding involving the failure to perform an operability determination after a new failure mechanism was discovered for standby service water Fan B. The inspectors were performing a follow up review of a condition report t
Region: IV | Grand Gulf | 28509 | 06/23/2009 07/28/2009 | 2009003-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Respond to Control Room Alarms in Accordance with Plant Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1(a) was reviewed involving a failure to follow the fire alarm response procedure during a fire in the reactor feedwater pump area. The operators failed to investigate the source of a smok
Region: IV | Grand Gulf | 28485 | 04/02/2009 04/30/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Preconditioning of Division II Standby Diesel Generator Jacket Water Heat Exchanger |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for failure to comply with the licensee's Generic Letter 89 13 program, which specifically states that cleaning of heat exchangers covered by this progra
Region: IV | Grand Gulf | 28486 | 04/02/2009 04/30/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Non-conservative Bias in Instrumentation Used for Standby Service Water Leak Detection |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to establish adequate measures for the selection and review for suitability of equipment and processes that are essential to the safety-re
Region: IV | Grand Gulf | 28492 | 04/02/2009 04/30/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Motor-Operated Valve Calculations Used Non-Conservative Inputs and Methodologies |  | P.3(a) Self-Assessment | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for failing to assure that applicable regulatory requirements and the design basis are correctly translated into specifications, drawings, procedures,
Region: IV | Grand Gulf | 28493 | 04/02/2009 04/30/2009 | 2009006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions fo rReplacement of Safety-Related Batteries |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for failure to identify and correct a condition adverse to quality related to the seismic qualification of the Division III High Pressure Core Spr
Region: IV | Grand Gulf | 28494 | 04/02/2009 04/30/2009 | 2009006-05 | NRC | NCV | Mitigating Systems | Green | Two Examples of a Failure to Meet 10 CFR Part 50, Appendix B, Criterion XI, "Test Control" |  | P.3(a) Self-Assessment | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," with two examples. Specifically, the team identified that the licensee failed to develop and implement adequate testing programs for Class 1E molded-case
Region: IV | Grand Gulf | 28498 | 04/02/2009 04/30/2009 | 2009006-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Standby Service Water Pump Cables and Electrical Vaults |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to adequately demonstrate operability for the 4160 volt Standby Service Water Pump kerite cables through adequate testing and analysis in
Region: IV | Grand Gulf | 28499 | 03/31/2009 05/08/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedures to Maintain Drains on Safety Related Buildings |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.01 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V, involving the failure to properly clean and inspect the rooftop and associated water drainage systems of the safety-related diesel generator building. The insp
Region: IV | Grand Gulf | 28500 | 03/31/2009 05/08/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Standby Service Water Cooling Tower Drift Eliminators |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, involving a failure to perform an adequate operability evaluation. The inspectors identified non-conservatisms in the evaluation with regards to standby servi
Region: IV | Grand Gulf | 28501 | 03/31/2009 05/08/2009 | 2009002-03 | NRC | NCV | Barrier Integrity | Green | Failure to Enter a Limiting Condition for Operation for Primary Containment Isolation Valves |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors identified a Green noncited violation of Grand Gulf Nuclear Station Technical Specifications 3.6.1.3, for failure to enter a limiting condition for operation action statement for primary containment isolation valves. As a result, the limiti
Region: IV | Grand Gulf | 28477 | 02/12/2009 03/23/2009 | 2009007-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Procedure Requirements for Preventive Maintenance Strategy Development |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | A Green self revealing finding was identified for the failure to implement maintenance procedure requirements. Specifically, in June 2007, an incorrect preventive maintenance template was applied to the main transformer auxiliary power transfer switch res
Region: IV | Grand Gulf | 28478 | 02/12/2009 03/23/2009 | 2009007-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Procurement Engineering Procedure Requirements |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | A Green self revealing finding was identified for the failure of engineering and maintenance personnel to implement procurement engineering procedure requirements. Specifically, in January, 2007 a procurement engineering evaluation determined that a diffe
Region: IV | Grand Gulf | 28484 | 02/12/2009 03/23/2009 | 2009007-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Preventive Maintenance Procedure Requirements |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 95001 | A Green self revealing finding was identified for the failure of to implement maintenance procedure requirements. Specifically, between 2002 and 2008, neither the preventive maintenance optimization program, nor the turbine 10-year plan prescribed a preve
Region: IV | Grand Gulf | 28465 | 12/31/2008 02/09/2009 | 2008005-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Fire Drill Critique |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05A | The inspectors identified a finding for fire brigade performance deficiencies that were not identified by the licensee during a fire drill critique. The inspectors identified several deficiencies during the drill including issues relating to command and c
Region: IV | Grand Gulf | 28466 | 12/31/2008 02/09/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Performance of the Engineering Safety Features Electrical Switchgear and Battery Room Ventilation System |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2) for the failure to adequately monitor the performance of the engineering safety features electrical switchgear and battery room ventilation system. The inspectors identified a condition
Region: IV | Grand Gulf | 28467 | 12/31/2008 02/09/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Two Examples of Inadequate Operability Evaluations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V involving two examples of a failure to follow procedures which resulted in inadequate operability evaluations. The first example involved an inadequate evaluati
Region: IV | Grand Gulf | 28468 | 12/31/2008 02/09/2009 | 2008005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Correct Leaking Reactor Water Cleanup System Primary Containment Isolation Valves |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion XVI, involving the failure to correct leaking reactor water cleanup system primary containment isolation valves. During refuelling Outage 16, plant personnel were
Region: IV | Grand Gulf | 28469 | 12/31/2008 02/09/2009 | 2008005-05 | Self - Revealed | FIN | Initiating Events | Green | Trip of a Reactor Recirculation Pump During Pump Up-shift to Fast Speed Due to Ineffective Corrective Actions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors reviewed a self-revealing Green finding involving a recirculation pump trip during pump up-shift to fast speed due to ineffective corrective actions. The plant had recently replaced the recirculation motor on Pump A during the refuelling ou
Region: IV | Grand Gulf | 28470 | 12/31/2008 02/09/2009 | 2008005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Recurrence of Standby Service Water Corrosion |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, involving a failure to take corrective actions to prevent recurrence of severe corrosion in piping hangers, piping supports, and piping in the standby service wat
Region: IV | Grand Gulf | 28471 | 12/31/2008 02/09/2009 | 2008005-07 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions Following Identification of Degrading Standby Service Water Supports |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion XVI, involving the failure to take timely corrective actions for corrosion on distribution beam structural support posts in the standby service water basin coolin
Region: IV | Grand Gulf | 28472 | 12/31/2008 02/09/2009 | 2008005-08 | Self - Revealed | FIN | Initiating Events | Green | Automatic Reactor Scram Caused by an Operator Inadvertently Closing Steam Supply Valves to the Reactor Feed Pump Turbine |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing Green finding involving an automatic reactor scram caused by an operator inadvertently closing steam supply valves to the reactor feed pump turbine. Site personnel investigating the scram determined that an operato
Region: IV | Grand Gulf | 28476 | 12/31/2008 02/09/2009 | 2008005-09 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Monitor Plant Parameters to Control Reactor Coolant System Cooldown Rate |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a Green finding involving the failure to demonstrate proper monitoring of plant parameters to control reactor coolant system cooldown rate to within expected management standards. The plant experienced a reactor scram from approx
Region: IV | Grand Gulf | 28462 | 11/06/2008 12/18/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | B.5.b. Phase 2 and 3 Mitigating Strategy |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 2515/171 | This finding, affecting the Mitigating Systems Cornerstone, is related to mitigative measures developed to cope with losses of large areas of the plant; in response to Section B.5.b. of the February 25, 2002, Interim Compensatory Measures (ICM) Order (EA-
Region: IV | Grand Gulf | 28459 | 09/21/2008 10/17/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Performance of Four Maintenance Rule Systems. |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.12 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(2) involving the failure to adequately monitor the performance of four Maintenance Rule systems. Several discrepancies in the Maintenance Rule Program were discovered by the inspector
Region: IV | Grand Gulf | 28460 | 09/21/2008 10/17/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Risk Assessment during Adverse Weather Conditions. |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65 (a)(4), involving the failure to perform risk assessments following multiple declared tornado watches affecting Grand Gulf Nuclear Station during the landfall of Hurricane Gustav. On the
Region: IV | Grand Gulf | 28461 | 09/21/2008 10/17/2008 | 2008004-03 | NRC | VIO | Mitigating Systems | Green | Failure to Perform an Adequate Inspection of PMP Door Seals Protecting Safety Related Equipment. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to perform an adequate inspection of probable maximum precipitation door seals protecting safety r
Region: IV | Grand Gulf | 28438 | 06/21/2008 07/24/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fireproofing on Fire Barrier Protecting the Safeguards Switchgear Room |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05Q | The inspectors identified a Green noncited violation of Facility Operating License Condition 2.C(41) involving the failure to ensure that fire barriers protecting safety-related areas were functional. The inspectors identified an 8-foot length of structur
Region: IV | Grand Gulf | 28439 | 06/21/2008 07/24/2008 | 2008003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Recognize the Division III Diesel Generator being Non-Functional. |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a self-revealing Green noncited violation of Technical Specification 5.4.1(a) involving the failure to follow a system operating instruction. While shutting down the Division III diesel generator, operators failed to place the outs
Region: IV | Grand Gulf | 28445 | 06/21/2008 07/24/2008 | 2008003-03 | Self - Revealed | FIN | Initiating Events | Green | Ineffective Corrective Actions in Response to Plant Transients Resulting from Animal Intrusions. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a self-revealing Green finding involving ineffective corrective actions that resulted in an unplanned down power caused by an animal intrusion. The plant experienced a loss of the balance of plant Transformer 23 with a loss of powe
Region: IV | Grand Gulf | 28446 | 06/21/2008 07/24/2008 | 2008003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Procedures Causing a Loss of Decay Heat Removal to the Spent Fuel Pool. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1(a) involving the failure of operators to follow a safety-related off normal event procedure resulting in a loss of decay heat removal to the spent fuel pool. The operato
Region: IV | Grand Gulf | 28448 | 04/18/2008 07/30/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Fire Wrap Testing Discrepancies |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | A noncited violation of License Condition 2.C(41), "Fire Protection Program," was identified because the licensee failed to evaluate vendor fire test results to ensure that deviations from the acceptance criteria did not result in a reduction in the effec
Region: IV | Grand Gulf | 28451 | 04/18/2008 07/30/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Fire Brigade Members Assigned Responsibilities That Conflicted with Fire Brigade Responsibilities. |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | A noncited violation of License Condition 2.C.(41) was identified for failure to maintain required staffing available to respond to a fire. Specifically, the approved Fire Protection Program requires that a five-person fire brigade be available onsite at
Region: IV | Grand Gulf | 28452 | 04/18/2008 07/30/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Plant Modification Blocked Access for Manual Firefighting. |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | A noncited violation of License Condition 2.C.(41), "Fire Protection Program," was identified related to making a plant change that negatively impacted the effectiveness of the approved Fire Protection Program. The team identified that the licensee had pe
Region: IV | Grand Gulf | 28453 | 04/18/2008 07/30/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure That Potential Damage to Motor-Operated Valve Circuits Would Not Prevent Safe Shutdown. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05T | A noncited violation of 10 CFR Part 50, Appendix R, Section III.G.1.a was identified because the licensee failed to evaluate the impact of a potential motor operated valve failure mechanism on the ability to implement post-fire safe shutdown following a c
Region: IV | Grand Gulf | 28425 | 03/22/2008 05/08/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Inspection of Probable Maximum Precipitation (PMP) Door Seals Protecting Safety Related Equipment. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71111.01 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to perform an adequate inspection of probable maximum precipitation door seals protecting safety related
Region: IV | Grand Gulf | 28426 | 03/22/2008 05/08/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement an Adequate Compensatory Fire Watch per Station Fire Protection Procedures. |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05A | The inspectors identified a noncited violation of Facility Operating License Condition 2.C.41 for the failure to properly implement a compensatory fire watch per the station fire protection program. The inspectors performed a fire inspection of the auxili
Region: IV | Grand Gulf | 28431 | 03/22/2008 05/08/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Failure of Licensed Senior Reactor Operators to Maintain the Required Proficiency to Maintain Their License Current. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a noncited violation of 10 CFR 55.53.e, "Conditions of License," for failure of licensed senior reactor operators to maintain the required proficiency to maintain their license current. Senior reactor operators standing the shift
Region: IV | Grand Gulf | 28432 | 03/22/2008 05/08/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Required Technical Specification Surveillance. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specifications 3.8.1, "AC Sources-Operating," for the failure to perform a required surveillance following the loss of a required offsite power source. The plant suffered a loss of power from the
Region: IV | Grand Gulf | 28433 | 03/22/2008 05/08/2008 | 2008002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Cracks in Standby Service Water Pump House Structure. |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion XVI, for failing to implement effective corrective actions after identifying concrete cracking in the standby service water pump houses. The inspectors determined that
Region: IV | Grand Gulf | 28434 | 03/22/2008 05/08/2008 | 2008002-06 | NRC | FIN | Initiating Events | Green | Ineffective Corrective Actions in Response to Resin in the Electro-hydraulic Control System. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a finding involving ineffective corrective actions in response to resin intrusion in the electro-hydraulic control system. The inspectors reviewed the corrective actions from a condition report involving a resin intrusion into th
Region: IV | Grand Gulf | 28437 | 03/22/2008 05/08/2008 | 2008002-07 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Design Control of HPCS Minimum Flow Valve Motor-Operated Valve Over Current Setpoint. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors identified a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to properly set the over current trip setpoint for the high pressure core spray minimum flow motor operated valve. Th
Region: IV | Grand Gulf | 28447 | 01/24/2008 02/05/2008 | 2007008-04 | NRC | URI | Mitigating Systems | Green | Verify Continued Operability of RHR Heat Exchanger B Due to Fouling. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | NONE
Region: IV | Grand Gulf | 28409 | 12/31/2007 02/07/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Venting Procedure for the Reactor Core Isolation Cooling System |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors identified a noncited violation of Criterion V, "Instructions, Procedures, and Drawings," of 10 CFR Part 50, Appendix B for the failure to demonstrate compliance with Technical Specification Surveillance Requirement 3.5.3.1 due to an inadeq
Region: IV | Grand Gulf | 28410 | 12/31/2007 02/07/2008 | 2007005-02 | NRC | FIN | Initiating Events | Green | Improper Control of Troubleshooting Causes a Loss of Condenser Vacuum |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a finding involving a loss of condenser vacuum caused by improper troubleshooting of the seal steam pressure controller. Specifically, the licensee failed to provide adequate work instructions and procedural limitations during tr
Region: IV | Grand Gulf | 28411 | 12/31/2007 02/07/2008 | 2007005-03 | NRC | FIN | Initiating Events | Green | Inadequate Engineering Review of Plant Service Water Modification |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | A self-revealing finding was identified involving the failure of a plant service water piping flange due to an improper flow control valve design modification. Specifically, the licensee failed to perform an adequate review of an engineering modification
Region: IV | Grand Gulf | 28412 | 12/31/2007 02/07/2008 | 2007005-04 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure Results in Loss of Condener Vacuum |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | A self-revealing finding was identified involving a loss of condenser vacuum caused by plant operators improperly removing a steam jet air ejector from service. Specifically, the licensee failed to isolate the steam jet air ejector from service as delinea
Region: IV | Grand Gulf | 28415 | 12/31/2007 02/07/2008 | 2007005-05 | NRC | FIN | Occupational Radiation Safety | Green | Inadequate Procedure |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 7112102 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for the failure to provide a detailed work order package to perform vent and fill operations on a pressure transmitter. Specifically, the licensee did not provi
Region: IV | Grand Gulf | 28416 | 12/30/2007 02/05/2008 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Failure to perform a root cause analysis for RHR heat exchanger B fouling, and implement corrective action to prevent recurrence |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | NONE | A noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, was identified for failure to perform an adequate cause analysis for fouling of the Residual Heat Removal Heat Exchanger B on the standby service water side, and implement corrective actio
Region: IV | Grand Gulf | 28417 | 12/30/2007 02/05/2008 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Inadequate thermal performance testing of the residual heat removal heat exchangers |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 7111107B | A noncited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," was identified because the licensee's thermal performance test procedures for the residual heat removal heat exchangers were inadequate to ensure the quality of the test results.
Region: IV | Grand Gulf | 28219 | 09/30/2007 11/02/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor Performance of the Control Rod Drive System. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a Green noncited violation (NCV) of 10 CFR Part 50.65(a)(2) for the failure to adequately monitor the performance of the control rod drive system. Specifically, the licensee failed to adequately perform a functional failure deter
Region: IV | Grand Gulf | 28226 | 09/30/2007 11/02/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish a Formal Procedure to Monitor Outdoor Air Temperatures. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 7111117A | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to translate a design basis limit for outdoor air temperature into an instruction or procedure. The licensee established a new U
Region: IV | Grand Gulf | 28227 | 09/30/2007 11/02/2007 | 2007004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures Caused Loss of Decay Heat Removal in the Spent Fuel Pool. |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | A self-revealing Green non-cited violation of Technical Specifications 5.4.1(a) was identified involving the failure to adequately follow procedure to align valves in the fuel pool cooling and cleanup system. The valves were aligned in the wrong sequence,
Region: IV | Grand Gulf | 28405 | 09/30/2007 11/02/2007 | 2007004-04 | Self - Revealed | FIN | Initiating Events | Green | Reactor SCRAM due to Turbine Trip caused by Loss of Condenser Vacuum |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | A self-revealing finding was identified involving the failure to properly calibrate the main condenser hydraulic vacuum switch that established a higher trip setpoint that would prematurely actuate an automatic turbine trip and reactor scram for a degrade
Region: IV | Grand Gulf | 28406 | 09/14/2007 10/11/2007 | 2007007-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Provide Function-Specific Training to Hazardous Material Workers. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 7112202 | The team identified a noncited violation (NCV) of 10 CFR 71.5 because the licensee failed to provide required training to hazardous material workers involved in the shipment of radioactive material. Specifically, the licensee did not provide function-spec
Region: IV | Grand Gulf | 28209 | 06/30/2007 08/02/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of the Leakage Detection System |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a Green noncited violation involving the failure to adequately monitor the performance of the leakage detection system in accordance with 10CFR50.65(a)(2). Specifically, the licensee failed to account for the functional failure o
Region: IV | Grand Gulf | 28210 | 06/30/2007 08/02/2007 | 2007003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Repair Crack in Containment Building Structure |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, involving the failure to correct a crack in the ceiling of the reactor water cleanup heat exchanger room internal to the containment building structure. Spe
Region: IV | Grand Gulf | 28203 | 06/30/2007 08/02/2007 | 2007003-03 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Foreign Material Controls During Reactor Feed Pump Maintenance |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | A self-revealing Green finding was identified for inadequate foreign material controls during maintenance. Specifically, a foreign material exclusion device was left inside the reactor feed Pump B lube oil system following maintenance activities, which pr
Region: IV | Grand Gulf | 28216 | 06/30/2007 08/02/2007 | 2007003-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Evaluate the Radiological Hazard Caused by Foreign Material Retrieval from the Reactor Vessel |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of 10 CFR Part 20.1501(a) because the licensee failed to evaluate the radiological hazard of foreign material retrieval from the reactor vessel. A contract radiation protection technician misint
Region: IV | Grand Gulf | 28217 | 06/30/2007 08/02/2007 | 2007003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Post and Control a High Radiation Area |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.7.1 resulting from a failure to post and control a high radiation area. Room 0R123 on the 93-foot elevation of the radwaste building had dose rates as high as 265 mi
Region: IV | Grand Gulf | 28218 | 06/30/2007 08/02/2007 | 2007003-06 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Safety-Related Breaker Inspections |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1(a) involving the failure to identify loose and missing fasteners on the standby service water Train B bus feeder breaker. The licensee entered this issue in their correc
Region: IV | Grand Gulf | 28191 | 03/31/2007 05/01/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Resulting in an Inadequate Operability Evaluation. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V involving the failure to follow procedures resulted in an inadequate operability evaluation for a degraded switchgear ventilation system. Specifically, the eval
Region: IV | Grand Gulf | 28195 | 03/31/2007 05/01/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Ineffective Command and Control Results in Inappropriate Valve Manipulations. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000416 Grand Gulf 1 |  | 71111.22 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1(a) for failure to meet procedural requirements involving command and control in the control room. Specifically, the control room supervisor was not informed of a system
Region: IV | Grand Gulf | 28196 | 03/31/2007 05/01/2007 | 2007002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedural Guidance and Radiation Work Instructions While Supporting Radiograpy Operations |  | H.3(b) Work Activity Coordination | TE?: N | 05000416 Grand Gulf 1 |  | 7112101 | A self-revealing, Green noncited violation of Technical Specification 5.4.1 was identified for the failure to follow procedural guidance and radiation work instructions while supporting radiography operations. All entrances to the area in which radiograph
Region: IV | Grand Gulf | 28197 | 03/31/2007 05/01/2007 | 2007002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions Prohibiting High Radiation Area Entry. |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 7112101 | A self-revealing Green noncited violation of Technical Specification 5.4.1 was identified for the failure to follow radiation work permit instructions prohibiting high radiation area entry. Two outage workers entered a high radiation area on the 139-foot
Region: IV | Grand Gulf | 28198 | 03/31/2007 05/01/2007 | 2007002-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Evaluate the Radiological Hazard Caused by Water Leaking in the Drywell. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 7112101 | The inspector identified a Green noncited violation of 10 CFR 20.1501(a) because the licensee failed to adequately evaluate the radiological hazard caused by water leaking from a valve in the drywell. The licensee failed to maintain knowledge of changing
Region: IV | Grand Gulf | 28199 | 03/31/2007 05/01/2007 | 2007002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Resulting in Isolation of Switchgear Room Ventilation. |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | A self-revealing Green noncited violation of Technical Specification 5.4.1(a) was identified for the failure to follow a surveillance procedure resulting in the inadvertent isolation of ventilation to the Division 1 and Division 3 safety-related switchgea
Region: IV | Grand Gulf | 28200 | 03/31/2007 05/01/2007 | 2007002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Standby Service Water System Leakage. |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI for the failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to take adequate corrective actions in res
Region: IV | Grand Gulf | 28201 | 03/12/2007 05/18/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Recurrence of High Standby Diesel Generator Temperatures (Section 3.0). |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving the failure to identify and correct the cause of elevated temperatures adversely affecting the safety function of the Division I standby
Region: IV | Grand Gulf | 28202 | 03/12/2007 05/18/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alarm Response Instruction for SDG High Jacket Water Temperature (Section 4.0). |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team identified a noncited violation of Technical Specification 5.4.1 (a) involving the failure to maintain an adequate alarm response instruction for standby diesel generator high jacket water temperature. Specifically, Procedure 04-1-02-1H22-P400, "
Region: IV | Grand Gulf | 28207 | 03/12/2007 05/18/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify a Degraded Condition (Section 5.0). |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving the failure to promptly identify a condition adverse to quality. Between February 2-15, 2007, the licensee failed to promptly identify th
Region: IV | Grand Gulf | 28208 | 03/12/2007 05/18/2007 | 2007006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Resulting in an Inadequate Operability Evaluation (Section 5.0). |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a failure to follow procedures which resulted in an inadequate operability evaluation. Specifically, the evaluati
Region: IV | Grand Gulf | 28189 | 12/31/2006 02/05/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Station Procedures for Conducting Maintenance Activities |  | H.4(a) Human Error Prevention | TE?: N | 05000416 Grand Gulf 1 |  | 71111.19 | The inspectors reviewed a Green, self-revealing noncited violation of Technical Specification 5.4.1(a) for failure to follow station maintenance procedures while troubleshooting the control rod drive Pump A hand switch green indicating light socket. The l
Region: IV | Grand Gulf | 28190 | 12/31/2006 02/05/2007 | 2006005-02 | NRC | FIN | Initiating Events | Green | Insufficient Preventive Maintenance of Bus Duct Cooling System Results in Unplanned Power Reduction |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71153 | The inspectors reviewed a Green, self-revealing finding for failure to implement preventive maintenance on the bus duct cooling system components prior to system failures, causing a plant transient. The licensee entered this into their corrective action p
Region: IV | Grand Gulf | 28182 | 09/30/2006 11/06/2006 | 2006004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Design Control of Leakage Detection Sensing Lines |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to maintain the original design configuration of a leakage detection instrument sensing line in the fuel pool cooling and
Region: IV | Grand Gulf | 28183 | 09/30/2006 11/06/2006 | 2006004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Monitor Containment Pool Liner Leakage |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.04Q | The inspectors identified a Green noncited violation of Technical Specification 5.4.1(a) involving the failure of the licensee to take actions required by operator rounds in response to containment pool liner leakage. The licensee entered this issue into
Region: IV | Grand Gulf | 28184 | 09/30/2006 11/06/2006 | 2006004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Control Loose Items in Safety Related Areas |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.05A | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for a failure to control loose items in safety related structures. Between July 25 and September 13, 2006, the inspec
Region: IV | Grand Gulf | 28187 | 09/30/2006 11/06/2006 | 2006004-04 | NRC | FIN | Initiating Events | Green | Failure to Document Deficiencies in the Corrective Action Program |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000416 Grand Gulf 1 05000416 Grand Gulf 1 |  | 71153 | A finding was identified for failure to implement adequate controls to maintain the integrity of the 34.5 kV switchyard animal intrusion fence and for failure to initiate condition reports when the fence was found de-energized or the gate found open. The
Region: IV | Grand Gulf | 28188 | 08/07/2006 08/28/2006 | 2006010-01 | Self - Revealed | NCV | Mitigating Systems | Green | Standby Diesel Generator Cylinder Head Failures |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 93812 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of licensee personnel to preclude repetition of a significant condition adverse to quality. Specifically, the licensee f
Region: IV | Grand Gulf | 28173 | 06/30/2006 07/17/2006 | 2006003-01 | NRC | NCV | Barrier Integrity | Green | Improper Reactor Recirculation Pump Speed Change |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.2 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1(a) for the failure to follow the procedure for reactor recirculation pump speed changes. Operators attempted to shift Recirculation Pump A to fast speed without verifyin
Region: IV | Grand Gulf | 28175 | 04/11/2006 05/08/2006 | 2006002-02 | NRC | NCV | Initiating Events | Green | Failure to Perform an Adequate Risk Assessment |  | H.3(a) Work Planning | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors identified two examples of a noncited violation of 10 CFR 50.65, "Maintenance Rule," for failing to include maintenance that could increase the likelihood of an initiating event in the plant risk assessment. On February 2, 2006 and again on
Region: IV | Grand Gulf | 28176 | 04/11/2006 05/08/2006 | 2006002-03 | NRC | FIN | Initiating Events | Green | Plant Service Water Leak During Excavation |  | H.4(b) Procedural Compliance | TE?: N | 05000416 Grand Gulf 1 |  | 71111.13 | The inspectors reviewed a self-revealing finding for a failure to follow procedure that resulted in a significant plant service water header leak. The licensee failed to review adequate documents to identify potential hazards as required by Procedure EN-S
Region: IV | Grand Gulf | 28180 | 04/11/2006 05/08/2006 | 2006002-04 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions Associated with Condensate Storage Tank Level Instrumentation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000416 Grand Gulf 1 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI for the failure to take prompt corrective actions to address a design deficiency involving condensate storage tank level instrumentation. The licensee identi
Region: IV | Grand Gulf | 28181 | 04/11/2006 05/08/2006 | 2006002-05 | NRC | NCV | Mitigating Systems | Green | Alternate Shutdown Cooling Mode Not Properly Implemented in Alternate Shutdown Procedure. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | NONE | The inspectors identified a Green noncited violation for failure to have an alternative shutdown procedure to restore power following a control room evacuation with loss of offsite power that was independent of the control room. The licensee entered this
Region: IV | Grand Gulf | 28165 | 03/27/2006 04/13/2006 | 2006008-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement a testing program to demonstrate the ability of standby service water-cooled heat exchangers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, Test Control, for the failure to implement a testing program to demonstrate the ability of standby service water-cool
Region: IV | Grand Gulf | 28172 | 03/27/2006 04/13/2006 | 2006008-02 | NRC | NCV | Mitigating Systems | Green | Failure to translate all design basis information into specifications and procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000416 Grand Gulf 1 |  | 7111121 | The team identified a finding of very low safety significance for a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to translate all design basis information into specifications and procedures were not adeq
Region: IV | Grand Gulf | 125947 | 10/28/2019 |  | Licensee - Identified | LIV |  | Green | Failure to ensure that armed security officers who are on duty and have exited the protected area may re-enter the protected area without being searched for firearms. |  |  | TE?: N | 05000416 Grand Gulf 1 |  | 71130.05
Region: IV | Palo Verde | 125953 | 09/30/2019 11/05/2019 | 2019003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Incorporate Design Requirements to Inspect and Dewater Manholes for the DG Fuel Oil Storage Vaults into the Preventive Maintenance Program |  | P.2 - Evaluation | TE?: N | 05000530 Palo Verde 3 | Design Control | 71111.01 | The inspectors reviewed a self-revealed Green and associated non-cited violation of 10 CFR 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to correctly translate the design basis of the facility into procedures. Specifically, t
Region: IV | Palo Verde | 124987 | 06/30/2019 08/07/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Develop Testing Program for Fuel Transfer Tubes |  | NONE | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control." Specifically, the licensee did not establish testing requirements and acceptance limits to detect degradation of the fuel transfer tubes as
Region: IV | Palo Verde | 124612 | 05/17/2019 05/10/2019 | 2019011-02 | NRC | NCV | Barrier Integrity | Green | Failure to Correct MSIV Actuator Hydraulic Fluid Viscosity Sensitivity to Low Temperature |  | H.12 - Avoid Complacency | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.21M | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to correct a condition adverse to quality associated with a known latent condition of the main steam isola
Region: IV | Palo Verde | 124611 | 04/17/2019 05/10/2019 | 2019011-01 | NRC | NCV | Barrier Integrity | Green | Failure to Evaluate Unit 1 MSIV Actuator Trains for 50.65(a)(1) Status in the Maintenance Rule Program |  | H.13 - Consistent Process | TE?: N | 05000528 Palo Verde 1 | SSC and Barrier Performance | 71111.21M | The inspectors identified a Green, non-cited violation of 10 CFR 50.65 (a)(1) for the failure to monitor the performance of Unit 1 main steam isolation valve (MSIV) actuators and the failure to take corrective action when the performance did not meet esta
Region: IV | Palo Verde | 124766 | 04/17/2019 05/10/2019 | 2019011-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage the Risk Involved with Various Risk Significant Maintenance Windows |  | H.1 - Resources | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.21M | The inspectors identified a Green, non-cited violation of 10 CFR 50.65 (a)(4) for the licensee’s failure to complete adequate risk assessments prior to performing maintenance activities because the probabilistic risk assessment (PRA) tools were not mainta
Region: IV | Palo Verde | 25898 | 12/31/2018 01/29/2019 | 2018004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Properly Preplan Corrective Maintenance |  | H.5 - Work Management | TE?: N | 05000529 Palo Verde 2 | Human Performance | 71111.13 | The inspectors reviewed a Green, self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to properly preplan maintenance that can affect the performance of safety-related equipment. Specifically, while planning
Region: IV | Palo Verde | 25897 | 12/31/2018 01/29/2019 | 2018004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Adequate Procedure for Control of Potential Tornado Borne Missiles |  | H.3 - Change Management | TE?: N | 05000529 Palo Verde 2 | Protection Against External Factors | 71111.2 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to prescribe instructions appropriate to the circumstances for the control and monito
Region: IV | Palo Verde | 24411 | 09/30/2018 11/14/2018 | 2018003-01 | NRC | FIN | Initiating Events | Green | Failure to Maintain Command and Control During a Feedwater Control Valve Malfunction |  | NPP | TE?: N | 05000530 Palo Verde 3 |  | 71153 | While reviewing the licensee response to a Unit 3 feedwater pump trip, reactor cutback, reactor trip, and main steam isolation system actuation on June 27, 2018, the inspectors identified that the licensee did not meet the command and control standards in
Region: IV | Palo Verde | 24642 | 09/14/2018 10/16/2018 | 2018008-01 | NRC | UNKN | Mitigating Systems | Green | Inadequate Corrective Actions For Missing Control Room Hand-Switch Operator Knobs |  | H.12 - Avoid Complacency | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The team reviewed a Green, NRC identified, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly identify and correct the failures of multiple control room hand-switch operator knobs.
Region: IV | Palo Verde | 24123 | 06/30/2018 08/06/2018 | 2018002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Rebaseline Valve Stroke Times as Required by ASME OM Code |  | H.1 - Resources | TE?: N | 05000528 Palo Verde 1 |  | 71111.12 | The inspectors identified a Green, non-cited violation of Palo Verde Technical Specification 5.5.8, “Inservice Testing Program,” which requires inservice testing of ASME Code Class 1, 2, and 3 components in accordance with the ASME Code for Operation and
Region: IV | Palo Verde | 24122 | 06/30/2018 08/06/2018 | 2018002-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement and Maintain Procedures Regarding Breathing Air Quality |  | H.4 - Teamwork | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71124.03 | The inspectors identified a Green, non-cited violation of 10 CFR 20.1703 for failing to implement and maintain written procedures to ensure that respiratory protection equipment (air compressors and bubble hood suites) supplied respirable air of grade D q
Region: IV | Palo Verde | 24134 | 06/30/2018 08/06/2018 | 2018002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Assess the Operability of a Degraded or Nonconforming Structure, System, or Component |  | H.13 - Consistent Process | TE?: N | 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to evaluate conditions adverse to quality for impacts on the operability of the essenti
Region: IV | Palo Verde | 23509 | 03/31/2018 05/07/2018 | 2018001-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Test Instructions for Diesel Fuel Oil Transfer Pump |  | H.12 - Avoid Complacency | TE?: N | 05000528 Palo Verde 1 |  | 71111.12 | The inspectors reviewed a self-revealed, Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to prescribe appropriate work instructions for maintenance on the Unit 1 diesel fuel
Region: IV | Palo Verde | 24358 | 02/15/2018 03/16/2018 |  | NRC | FIN | Mitigating Systems | Green | Failure to provide adequate guidance to personnel to assure degraded or deficient emergency lighting required for post-fire safe shutdown was corrected in a timely manner. |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.05T | The inspectors identified a Green finding for failure to provide adequate guidance to assure degraded or deficient emergency lighting required for post-fire safe shutdown is corrected in a timely manner. Specifically, the licensee failed to specify that f
Region: IV | Palo Verde | 22622 | 12/31/2017 01/30/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to incorporate vendor overhaul recommendations for Class 1E medium voltage circuit breaker preventive maintenance program |  | NPP | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.19 | DRAFT: The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a “Procedures” for failure to incorporate vendor service recommendations into the preventive maintenance program. As a result of not incorporating those
Region: IV | Palo Verde | 22300 | 09/30/2017 11/13/2017 | 2017003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Initiate Corrective Actions for Thermography Tests |  | P.1 - Identification | TE?: N | 05000530 Palo Verde 3 |  | 71111.12 | The inspectors reviewed a self-revealed, Green finding for the licensee’s failure to initiate corrective actions to address elevated temperature measurements identified during thermography inspections of the Unit 3 Phase C main transformer control cabinet
Region: IV | Palo Verde | 21649 | 09/30/2017 11/13/2017 | 2017003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Loss of Refrigerant Failure of Essential Chiller Unit due to Installation of Incorrect Parts |  | H.12 - Avoid Complacency | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 3.7.10 Condition A for exceeding the allowed outage time of 72 hours to restore one inoperable train of essential chilled water system to an operable status. Sp
Region: IV | Palo Verde | 21650 | 09/30/2017 11/13/2017 | 2017003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Conduct of Operations Procedure |  | H.12 - Avoid Complacency | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a. "Procedures," for the licensee’s failure to implement their Conduct of Operations procedure. Specifically, licensee personnel improperly performed a re
Region: IV | Palo Verde | 21651 | 09/30/2017 11/13/2017 | 2017003-04 | Self - Revealed | NCV | Initiating Events | Green | Reactor Trip due to Pressurizer Spray Valve Failing Open due to Volume Booster Internals Not Environmentally Qualified for Anticipated Ambient Operating Temperatures |  | H.13 - Consistent Process | TE?: N | 05000530 Palo Verde 3 |  | 71153 | The inspectors reviewed a self-revealed, Green, non-cited violation of Technical Specification 5.4.1.a "Procedures," for the licensee’s failure to follow station procedure 73DP-0EE05, "Engineering Preventive Maintenance Program." The licensee did not cons
Region: IV | Palo Verde | 13969 | 06/30/2017 08/08/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | Inoperable Containment Isolation Valve Due to Not Operating Valve in Accordance with Station Procedures |  | H.7 Documentation | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors reviewed a Green self-revealing non-cited violation of Technical Specification 3.6.3 Condition C for exceeding the allowed outage time of 4 hours to isolate the flow path of an inoperable containment isolation valve. Specifically, Unit 1 co
Region: IV | Palo Verde | 13968 | 05/10/2017 05/10/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish station procedure instructions for denial work authorizations |  | H.5 Work Management | TE?: N | 05000529 Palo Verde 2 |  | 71111.13 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the failure to establish procedure instructions for work authorization denials or deferrals. Specifically, this led to a 60 day extended unavailab
Region: IV | Palo Verde | 22628 | 03/03/2017 04/06/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze Shutdown Cooling and Feedwater Lines for High-Energy Line Break Pipe Whip Effects |  | NPP | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.17T | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” which states, in part, “Measures shall be established to assure that applicable regulatory requirements and the design basis, as defined in § 5
Region: IV | Palo Verde | 13967 | 12/29/2016 02/01/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate monitoring of MSIV nitrogen pre-charge pressure |  | H.4 Teamwork | TE?: N | 05000529 Palo Verde 2 |  | 71153 | Green. The inspectors reviewed a self-revealing non-cited violation of Technical Specification 3.7.2 for exceeding the Condition A completion time for an inoperable main steam isolation valve (MSIV) single actuator train and not immediately declaring the
Region: IV | Palo Verde | 13966 | 09/28/2016 11/10/2016 | 2016003-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Advance Work Authorization Procedure |  | H.5 Work Management | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.18 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee failed to accomplish activities affecting quality in accordance with documented procedures. S
Region: IV | Palo Verde | 13947 | 09/01/2016 10/06/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Maintenance Activities and Instructions for Gas Turbine Generator Station Blackout Batteries |  | P.3 Resolution | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current," which states, in part, "The alternate AC power source, as defined in 10 CFR 50.2, will constitute acceptable capability to withstand station blackout prov
Region: IV | Palo Verde | 13948 | 09/01/2016 10/06/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Information from Design Modification into Design Documentation, Operating Procedures, and Operator Training |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | . The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis, for those stru
Region: IV | Palo Verde | 13955 | 09/01/2016 10/06/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Ability to Isolate the Safety-Related Condensate Storage Tank from Non-Safety Piping |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis for those structu
Region: IV | Palo Verde | 13956 | 09/01/2016 10/06/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Pipe Welds Not Incorporated into the Inservice Inspection Program |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50.55a(g)4, "Inservice Inspection Standards Requirement for Operating Plants," which states, in part, "Throughout the service life of a pressurized water-cooled nuclear power facility, components
Region: IV | Palo Verde | 13941 | 04/20/2016 08/05/2016 | 2016002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Implement High Radiation Area Controls in an Area with a Dose Rates Greater Than 1 rem per hour |  | H.1 Resources | TE?: N | 05000528 Palo Verde 1 |  | 71124.01 | The inspectors reviewed a Green, self-revealing, non-cited violation of Technical Specification 5.7.2, which was caused by the licensee's failure to control a high radiation area with radiation levels greater than 1 rem per hour in the Unit 1 containment.
Region: IV | Palo Verde | 13942 | 04/20/2016 08/05/2016 | 2016002-03 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Engineering and Radiological Controls Resulting in a Unit 1 Containment Building Airborne Radioactivity Event with Unplanned Intakes |  | H.1 Resources | TE?: N | 05000528 Palo Verde 1 |  | 71124.03 | The inspectors identified a non-cited violation of 10 CFR 20.1701 due to the licensee's failure to implement adequate processes and engineering controls necessary to reduce airborne radioactivity and prevent internal dose to workers in Unit 1. On April 20
Region: IV | Palo Verde | 13934 | 03/30/2016 04/25/2016 | 2016001-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to use adequate engineering and radiological controls resulting in two unplanned intakes |  | H.14 Conservative Bias | TE?: N | 05000530 Palo Verde 3 |  | 71124.04 | A self-revealing non-cited violation of 10 CFR 20.1701 was identified for the licensee's failure to implement adequate processes or engineering controls to control the concentration of radioactive material in air and prevent internal dose to workers. Spec
Region: IV | Palo Verde | 13935 | 03/30/2016 04/25/2016 | 2016001-02 | Self - Revealed | NCV | Mitigating Systems | Green | Fatigue failure of pneumatic fitting due to excessive vibrations |  | H.12 Avoid Complacency | TE?: N | 05000530 Palo Verde 3 |  | 71153 | The inspectors documented a self-revealing non-cited violation of Technical Specification 3.7.2 Condition A for exceeding the allowed outage time of seven days. Specifically Unit 3's MSIV-181 actuator B was found to be inoperable from May 1, 2015 until Au
Region: IV | Palo Verde | 13936 | 03/24/2016 05/06/2016 | 2016008-01 | NRC | NCV | Mitigating Systems | Green | Operations Department Failure to Document Conditions Adverse to Quality in Condition Reports |  | P.3 Resolution | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to document conditions adverse to quality in the corrective action program. Previous similar failures to initiate condition reports le
Region: IV | Palo Verde | 13933 | 01/15/2016 02/05/2016 | 2015008-01 | NRC | NCV | Initiating Events | Green | Inadequate Loop Flow Test Procedure |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.05T | The team identified a Green non-cited violation of License Conditions 2.C.7, 2.C.6, and 2.F for Units 1, 2, and 3, respectively, because the licensee had not established criteria for determining when a fire main loop had degraded and had not properly test
Region: IV | Palo Verde | 13920 | 06/30/2015 08/13/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Design of the Essential Spray Pond System Crosstie Valves |  |  | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, involving the failure to maintain adequate design control measures associated with the ultimate heat sink. Specifically, the essential spray
Region: IV | Palo Verde | 13921 | 06/30/2015 08/13/2015 | 2015002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Take Timely Corrective Actions to Prevent Charging Pump Discharge Bladder Failure |  | H.9 Training | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors documented a finding for the failure to take timely corrective actions associated with failure of the discharge pulsation dampener poppet valves in the positive displacement pump charging system. Specifically, following the investigation of
Region: IV | Palo Verde | 13922 | 06/30/2015 08/13/2015 | 2015002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Engineered Safety Features Actuation System Steam Generator Differential Pressure Setpoint Drift |  | H.3 Change Management | TE?: N | 05000529 Palo Verde 2 |  | 71153 | The inspectors reviewed a Green self-revealing non-cited violation of Technical Specification 5.4.1.a for failure to establish and implement procedures recommended by Regulatory Guide 1.33 Appendix A, Item 5.0, "Abnormal, Off-Normal and Alarm Conditions."
Region: IV | Palo Verde | 13931 | 06/30/2015 08/13/2015 | 2015002-05 | NRC | NCV | Initiating Events | Green | Failure to Establish Adequate Procedures to Respond to a Total Loss of Charging Event |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71153 | The inspectors documented a non-cited violation of Technical Specification 5.4.1.a, Regulatory Guide 1.33, Revision 2, Appendix A, Section 6.t, February 1978. Specifically, the licensee failed to establish adequate procedures for combating emergencies and
Region: IV | Palo Verde | 13932 | 03/31/2015 05/13/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to conduct required in-service testing in accordance with ASME OM Code |  | H.4 Teamwork | TE?: N | 05000528 Palo Verde 1 |  | 71111.19 | The inspectors identified a Green, non-cited violation of Palo Verde Technical Specification 5.5.8 "Inservice Testing Program" which requires the in-service testing of ASME Code Class 1, 2, and 3 components in accordance with the ASME Code for Operation a
Region: IV | Palo Verde | 13899 | 12/31/2014 02/12/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy of the Design of the Diesel Fuel Oil Cooler |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.19 | Green. The inspectors reviewed a self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control" for the station's failure to adequately review the suitability of materials of the diesel fuel oil cooler. Specificall
Region: IV | Palo Verde | 13897 | 09/30/2014 11/12/2014 | 2014004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Requirements for Establishing Operability of Spray Pond System |  | H.7 Documentation | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | Green. The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly translate the mission time of the essential spray pond system into a procedure used to determine oper
Region: IV | Palo Verde | 13896 | 09/30/2014 11/12/2014 | 2014004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Technical Justification for Operability |  | H.14 Conservative Bias | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | Green. The inspectors identified a Green non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to provide an adequate t
Region: IV | Palo Verde | 13898 | 09/30/2014 11/12/2014 | 2014004-03 | NRC | NCV | Mitigating Systems | Green | Component Design Basis Inspection |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | Green. The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to assure the adequacy of degraded voltage relay setpoints. Specifically, the team identified that the licens
Region: IV | Palo Verde | 38849 | 06/30/2014 08/13/2014 | 2014003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operator Challenges Procedure |  | H.11 Challenge the Unknown | TE?: N | 05000530 Palo Verde 3 |  | 71152 | Green. The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow station procedures to ensure that appropriate contingency acti
Region: IV | Palo Verde | 38823 | 04/02/2014 04/15/2014 | 2013009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Requirements for Establishing Operability of the Spray Pond System |  | H.7 Documentation | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, are correctly tr
Region: IV | Palo Verde | 38836 | 04/02/2014 04/15/2014 | 2013009-02 | NRC | NCV | Mitigating Systems | Green | Deficiencies in Emergency Diesel Generator Engine Room and Control Room Ventilation Air Flow Testing and Evaluation |  | H.14 Conservative Bias | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and comp
Region: IV | Palo Verde | 38837 | 04/02/2014 04/15/2014 | 2013009-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for an Alternate Source of Spray Pond Inventory |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of Technical Specification 5.4.1, which states, in part, "Written procedures shall be established, implemented, and maintained covering the following activities: Part a. The applicable procedures recommende
Region: IV | Palo Verde | 38843 | 04/02/2014 04/15/2014 | 2013009-04 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Surveillance Testing Procedure |  | H.1 Resources | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | Palo Verde | 38844 | 04/02/2014 04/15/2014 | 2013009-05 | NRC | NCV | Mitigating Systems | Green | Improper Extension of Surveillance Interval for Surveillance Requirements Associated with the Engineered Safety Features Actuation Signal (ESFAS) Sequencer and Relays |  | H.3 Change Management | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green, non-cited violation of Technical Specification 5.5.18, "Surveillance Frequency Control Program" which states, in part, "This program provides controls for Surveillance Frequencies. The program shall ensure that Surveillance Re
Region: IV | Palo Verde | 38810 | 03/31/2014 05/14/2014 | 2014002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Protected Equipment Procedures |  | H.9 Training | TE?: N | 05000528 Palo Verde 1 |  | 71111.13 | The inspectors reviewed a Green self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of Projects personnel to follow station procedures which required obtaining permission
Region: IV | Palo Verde | 38811 | 03/31/2014 05/14/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification 3.7.2 |  | H.13 Consistent Process | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification Limiting Condition for Operation 3.7.2, Condition G, for the failure of plant personnel to follow the actions specified in Technical Specification 3.7.2 for one main steam isolatio
Region: IV | Palo Verde | 38814 | 03/31/2014 05/14/2014 | 2014002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Performing Nitrogen Pre-Charge Checks |  | P.5 Operating Experience | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to prescribe activities affecting quality by documented procedures of a type app
Region: IV | Palo Verde | 38815 | 03/31/2014 05/14/2014 | 2014002-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Declare an Unusual Event |  | H.13 Consistent Process | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR 50.54(q) for the failure of operations personnel to implement the emergency plan in response to a certain emergent event. Specifically, on November 6, 2013, after the hydraulic reservoir for main s
Region: IV | Palo Verde | 38816 | 03/28/2014 05/14/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure To Provide Adequate Technical Justification For Operability of Containment Spray and Diesel Fuel Oil Systems |  | H.13 Consistent Process | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified multiple examples of a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow station procedures used to perform operabili
Region: IV | Palo Verde | 38822 | 03/28/2014 05/14/2014 | 2014007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Station Process for Root Cause Evaluation |  | H.13 Consistent Process | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a Green finding for the failure of station personnel to follow procedures to implement root cause evaluations. Specifically, approximately one third of the root cause evaluations reviewed by inspectors resulted in a probable caus
Region: IV | Palo Verde | 38805 | 12/31/2013 02/13/2014 | 2013005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Modification of Safety Related Accumulators |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.18 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for the failure to assure that a modification to the main steam and main feedwater isolation valve accumulators was suitable for the reliabl
Region: IV | Palo Verde | 38809 | 12/31/2013 02/13/2014 | 2013005-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Replace Oil Soaked Insulation Results in a Fire |  | P.2(b) Implementing Operating Experience | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors reviewed a Green self-revealing finding for the licensee's failure to promptly identify and correct an adverse condition. Specifically, the licensee failed to identify that operating limits for main feedwater pump (MFP) vapor extractors d
Region: IV | Palo Verde | 38803 | 09/30/2013 11/13/2013 | 2013004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain an effective Emergency Plan for a Seismic Event |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50.54 (q)(2) for the failure to maintain an effective emergency plan action level scheme in accordance with 50.47(b)(4). Specifically, the Alert threshold for HA1.1, "Natural or Destructive Phenome
Region: IV | Palo Verde | 38804 | 09/30/2013 11/13/2013 | 2013004-02 | NRC | FIN | Initiating Events | Green | Failure to Include Requirements in Preventative Maintenance Basis |  | P.2(b) Implementing Operating Experience | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71153 | The inspectors identified a Green finding for the failure of licensee personnel to follow Procedure 30DP-9MP08, "Preventive Maintenance Program." Specifically, plant personnel did not ensure that requirements for performing inspection and replacement of d
Region: IV | Palo Verde | 38797 | 06/30/2013 08/09/2013 | 2013003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Operability Determination Procedure for Maintaining Administrative Limits |  | H.1(c) Communication of Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to perform operability determina
Region: IV | Palo Verde | 38795 | 06/30/2013 08/09/2013 | 2013003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent Recurrence of a Significant Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000529 Palo Verde 2 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," occurred because the licensee failed to correct and prevent recurrence of a significant condition adverse to quality associated with the emergency diese
Region: IV | Palo Verde | 38796 | 06/30/2013 08/09/2013 | 2013003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Corrective Action for Embedded Operator Work Around |  |  | TE?: N | 05000530 Palo Verde 3 |  | 71152 | A self-revealing finding occurred because the licensee did not take action to correct an embedded operator work around in the condensate system. Specifically, the licensee did not evaluate and develop a plan to correct the practice of throttling the conde
Region: IV | Palo Verde | 38790 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Multiple Failures to Identify Conditions Adverse to Quality |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified two examples of a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI "Corrective Action," for the failure of the licensee to promptly identify and correct conditions adverse to quality. Specifically, on July 19, 2012, personn
Region: IV | Palo Verde | 38789 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Technical Justification for Operability |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to provide an adequate technical justification
Region: IV | Palo Verde | 38791 | 03/31/2013 05/14/2013 | 2013002-03 | NRC | NCV | Emergency Preparedness | Green | Failure to identify weak preformance during an exercise |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71114.01 | The inspectors identified a Green NCV of 10 CFR 50.47(b)(14) for the licensee's failure to identify and correct a performance deficiency during an evaluated exercise. Specifically, the licensee failed to identify that the Emergency Director in the Simulat
Region: IV | Palo Verde | 38792 | 03/31/2013 05/14/2013 | 2013002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self-revealing, Green NCV of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.4 was identified after Unit 2 operators entered a mode with a limiting condition for operation not met. Specifically, following maintenance on auxiliary
Region: IV | Palo Verde | 38793 | 03/31/2013 05/14/2013 | 2013002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Shutdown Cooling Piping Failure |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self-revealing, Green NCV of 10 CFR Part 50, Appendix B, Criterion III "Design Control," was identified for the failure of the licensee to assure that applicable regulatory requirements and the design basis are correctly translated into specifications,
Region: IV | Palo Verde | 38781 | 12/31/2012 02/07/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Fire Protection |  | P.3(a) Self-Assessment | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.05Q | The inspectors identified a Green non-cited violation of License Conditions 2.C.7, 2.C.6, and 2.F for Palo Verde Units 1, 2, and 3 for the licensee's failure to identify and correct a condition adverse to fire protection. Specifically, on November 19, 201
Region: IV | Palo Verde | 38782 | 12/31/2012 02/07/2013 | 2012005-02 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Pressure Testing of the Reactor Vessel Flange Leak-Off Lines |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.08P | Inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4) involving the licensee's failure to perform a system pressure test of the reactor vessel flange leak off-line of Units 1, 2, and 3 in accordance with the applicable edition of Section XI o
Region: IV | Palo Verde | 38783 | 12/31/2012 02/07/2013 | 2012005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.3(a) Work Planning | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure the integrity of the licensed operator biennial written examinations. During the 2012 biennial written examin
Region: IV | Palo Verde | 38784 | 12/31/2012 02/07/2013 | 2012005-04 | NRC | NCV | Barrier Integrity | Green | Inadequate Tracking of a Functional Assessment for Spent Fuel Pool Heat Load |  | H.1(c) Communication of Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to perform operability determin
Region: IV | Palo Verde | 38787 | 12/31/2012 02/07/2013 | 2012005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Classify and Evaluate a Condition Adverse to Quality |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of Palo Verde Unit 1 License Condition 2.C.7 for the failure of plant personnel to follow station procedures to classify and evaluate a condition adverse to quality. Specifically, after identifying mov
Region: IV | Palo Verde | 38788 | 12/31/2012 02/07/2013 | 2012005-06 | Self - Revealed | NCV | Emergency Preparedness | Green | Technical Support Center Diesel Generator Not Restored Following Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | A self revealing Green non-cited violation of 10 CFR 50.47(b)(8) was identified for the failure to maintain adequate facilities to support emergency response. Specifically, the licensee found the technical support center battery disconnect switch had not
Region: IV | Palo Verde | 38766 | 09/30/2012 11/14/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Scupper Obstruction |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.01 | The inspectors identified a Green non-cited violation of 10 CFR Part 50 Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to correct a condition adverse to quality. Specifically, on November 7, 2011, after the inspectors noti
Region: IV | Palo Verde | 38775 | 09/30/2012 11/14/2012 | 2012004-02 | NRC | NCV | Initiating Events | Green | Untimely Corrective Action for Condition Adverse to Fire Protection |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000529 Palo Verde 2 |  | 71111.05Q | The inspectors identified a Green non-cited violation of License Conditions 2.C.7, 2.C.6, and 2.F for Palo Verde Units 1, 2, and 3 for the licensee's failure to take timely corrective actions for a condition adverse to fire protection. Specifically, in 20
Region: IV | Palo Verde | 38776 | 09/30/2012 11/14/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Boric Acid Evaluation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to follow Procedure 70TI-9ZC01, "Boric Acid Walkdown Leak Detection," to p
Region: IV | Palo Verde | 38777 | 09/30/2012 11/14/2012 | 2012004-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination for ARD Relay Failures |  | H.1(c) Communication of Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to provide an adequate technic
Region: IV | Palo Verde | 38779 | 09/30/2012 11/14/2012 | 2012004-05 | NRC | NCVIV | Emergency Preparedness | Green | Failure to Perform 50.54(q) Evaluation |  | H.4(c) Supervisory & Management Oversight | TE?: Y SL-IV-NCVIV | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | Inspectors identified a Severity Level IV, non-cited violation of 10 CFR 50.54 (q), "Conditions of licenses," and an associated Green finding for the licensee's failure to perform an appropriate design scope change, which resulted in the reduction in effe
Region: IV | Palo Verde | 38780 | 09/30/2012 11/14/2012 | 2012004-06 | NRC | NCV | Emergency Preparedness | Green | Failure to Declare an Unusual Event |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71153 | The inspectors identified a Green non-cited violation of 10 CFR 50.54(q) for the failure of operations personnel to adequately implement the emergency plan. Specifically, on August 26, 2012, auxiliary operators felt vibratory ground motion inside the prot
Region: IV | Palo Verde | 38747 | 06/30/2012 08/10/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Hot Work Permit Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 71111.05Q | The inspectors identified a non-cited violation of technical specification 5.4.1.d for the failure of the licensee to follow Procedure 14DP-0FP36, "Hot Work Permit." Specifically, the licensee failed to implement all requirements of the hot work permit an
Region: IV | Palo Verde | 38748 | 06/30/2012 08/10/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | The inspectors identified a Green non-cited violation of Technical Specification Limiting Condition for Operation (LCO) 3.0.3 for the failure of plant personnel to place Unit 2 in Mode 3 within 7 hours after discovering a condition not permitted by Techni
Region: IV | Palo Verde | 38749 | 06/30/2012 08/10/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Post Maintenance Test of the Diesel Fuel Oil Transfer Pump |  | H.4(a) Human Error Prevention | TE?: N | 05000529 Palo Verde 2 |  | 71111.19 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," for the failure to assure that testing to demonstrate that the diesel fuel oil transfer pumps would perform satisfactory in service was performed in ac
Region: IV | Palo Verde | 38754 | 06/30/2012 08/10/2012 | 2012003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Boric Acid Evaluation |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000530 Palo Verde 3 |  | 71111.2 | The inspectors identified a non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to follow Procedure 70TI-9ZC01 "Boric Acid Walkdown Leak Detection," to provide a
Region: IV | Palo Verde | 38755 | 06/30/2012 08/10/2012 | 2012003-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedures and Radiation Exposure Permit Requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1, because workers failed to follow radiation exposure permit requirements and entered high radiation area without authorization by entering the wrong room. As cor
Region: IV | Palo Verde | 38756 | 06/30/2012 08/10/2012 | 2012003-06 | NRC | NCV | Public Radiation Safety | Green | Failure to Verify a Transferee was Licensed to Receive Byproduct Material |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The inspector identified a non-cited violation of 10 CFR 30.41 because the licensee failed to verify a transferee was authorized to receive byproduct material before transferring it. This finding was entered in the licensee's corrective action program as
Region: IV | Palo Verde | 38723 | 03/31/2012 05/15/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Program Procedure |  | H.4(b) Procedural Compliance | TE?: N | 05000529 Palo Verde 2 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after Arizona Public Service failed to follow station procedures and enter issues into the corrective action program. Specifica
Region: IV | Palo Verde | 38726 | 03/31/2012 05/15/2012 | 2012002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Assess and Manage Risk Prior to Troubleshooting on 4.16 kV Bus Supply Breaker Hand Switch |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000529 Palo Verde 2 |  | 71111.13 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50.65a(4), for the licensee's failure to assess and manage an increase in risk prior to planned maintenance activities. Specifically, on January 25, 2012, the licensee failed to includ
Region: IV | Palo Verde | 38727 | 03/31/2012 05/15/2012 | 2012002-03 | NRC | NCVIV | Initiating Events | Green | Failure to Obtain NRC Approval for a Change Adverse to Safe Shutdown |  |  | TE?: Y SL-IV-NCVIV | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a Severity Level IV non-cited violation of License Conditions 2.C.7, 2.C.6, and 2.F for Palo Verde Units 1, 2, and 3, respectively, for the licensee's failure to maintain the reactor coolant pumps in compliance with fire protecti
Region: IV | Palo Verde | 38728 | 03/31/2012 05/15/2012 | 2012002-04 | NRC | NCV | Emergency Preparedness | Green | Failure in the Choice of Protective Actions Consistent with Federal Guidance |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.47(b)(10) for the licensee's failure to develop and have in-place guidelines for the choice of protective actions during an emergency that were consistent with federal guidance. Specifically, th
Region: IV | Palo Verde | 38733 | 03/31/2012 05/15/2012 | 2012002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Essential Chilled Water System Gas Accumulation |  | P.1(b) Trend Performance CAP | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality associated with essential chilled wa
Region: IV | Palo Verde | 38734 | 03/31/2012 05/15/2012 | 2012002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Operating Procedure for Cold-Leg Boration |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 |  | 71152 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion V, for the failure of the licensee to provide an adequate operating procedure for cold leg boration. Specifically, on November 19, 2011, Unit 1 operators excee
Region: IV | Palo Verde | 38735 | 03/31/2012 05/15/2012 | 2012002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Functionality Assessment for Safety-Related Buildings |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to provide a technical justification
Region: IV | Palo Verde | 38737 | 03/31/2012 05/15/2012 | 2012002-08 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Into Drawings and Calculations for Safety-related Roof Drainage Capability |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to translate the safety-related roof drainage capability design basis into drawings and calculations. Specifica
Region: IV | Palo Verde | 38722 | 12/31/2011 02/09/2012 | 2011005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Evaluate a Radiological Hazard |  | H.3(a) Work Planning | TE?: N | 05000528 Palo Verde 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR 20.1501(a), resulting from the licensee's failure to evaluate the hazard associated with breaching a contaminated system. On October 18, 2011, before and during work on Unit 1 in the
Region: IV | Palo Verde | 38714 | 12/31/2011 02/09/2012 | 2011005-02 | NRC | NCV | Initiating Events | Green | Failure to Identify and Perform Testing for the Gaseous Radwaste System |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the failure of the licensee to assure that all required testing for the gaseous radwaste (GR) system was identified and performed in accordanc
Region: IV | Palo Verde | 38721 | 12/31/2011 02/09/2012 | 2011005-03 | NRC | FIN | Initiating Events | Green | Failure of Unit 1 Reactor Coolant Pump 2A Motor Junction Box Due to Inadequate Maintenance |  | P.2(b) Implementing Operating Experience | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors reviewed a self-revealing finding that occurred during maintenance associated with the Unit 1 reactor coolant pump 2A 13.8 kilovolt motor termination enclosure. Specifically, work instructions were inadequate to ensure the enclosure maintai
Region: IV | Palo Verde | 38764 | 08/18/2011 11/10/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination for Essential Chilled Water System Gas Voids |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures and complete a prompt operability dete
Region: IV | Palo Verde | 38765 | 07/27/2011 11/10/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Operation of Essential Chillers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality associated with Unit 3 essential chiller A o
Region: IV | Palo Verde | 38703 | 06/30/2011 08/11/2011 | 2011003-01 | NRC | NCV | Barrier Integrity | Green | Failure to Include Screening Criteria in the Boric Acid Corrosion Control Program |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.08P | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, that "Instructions, procedures, or drawings shall include appropriate quantitative or qualita
Region: IV | Palo Verde | 38704 | 06/30/2011 08/11/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Complete an Immediate Operability Determination for Code System Leakage Test |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.08P | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states "Activities affecting quality shall be prescribed by documented instructions, procedures, or drawings,
Region: IV | Palo Verde | 38697 | 06/30/2011 08/11/2011 | 2011003-04 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique a Weakness during a Biennial Exercise |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71114.01 | The inspectors identified a Green noncited violation for failure to critique weak performance in the Technical Support Center during a biennial exercise conducted March 1, 2011, as required by 10 CFR Part 50, Appendix E, IV(F)(2)(g). Specifically, the lic
Region: IV | Palo Verde | 38713 | 06/30/2011 08/11/2011 | 2011003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Have Adequate Documentation for Verification of ASME Code Compliance |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion VII "Control of Purchased Material, Equipment, And Services" for the failure of licensee personnel to maintain radiographs onsite for the verification of ASME Co
Region: IV | Palo Verde | 38712 | 06/30/2011 08/11/2011 | 2011003-06 | Self - Revealed | FIN | Initiating Events | Green | Failure of 13.8kV Splice due to Inadequate Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | Inspectors reviewed a Green self-revealing finding for failure to properly repair a 13.8kV cable associated with the AENANX02 startup transformer. Specifically, the work performed failed to achieve an acceptable level of quality as required by Procedure 3
Region: IV | Palo Verde | 38694 | 03/31/2011 05/12/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Program Procedure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," after the licensee failed to promptly evaluate a nonconforming condition for operability as required by Procedure 01PR-0AP0
Region: IV | Palo Verde | 38695 | 03/31/2011 05/12/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures to Control Essential Chiller Compressor Oil Level |  | P.2(b) Implementing Operating Experience | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.4.1, "Procedures," for the failure of operations, engineering, and maintenance personnel to establish and implement procedures recommended in Regulatory Guide 1.33. Specifically,
Region: IV | Palo Verde | 38688 | 03/31/2011 05/12/2011 | 2011002-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Have Adequate Procedures to Prevent Resin Contamination into the Auxiliary Building Exhaust Ventilation System |  |  | TE?: N | 05000530 Palo Verde 3 |  | 71124.06 | Inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1 for failure to have adequate procedures to prevent resin contamination of the auxiliary building exhaust ventilation system while filling and venting the pre-holdup i
Region: IV | Palo Verde | 38693 | 03/31/2011 05/12/2011 | 2011002-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Work Instructions for Condenser Coating |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000530 Palo Verde 3 |  | 71153 | The inspectors identified a self-revealing finding after Palo Verde Nuclear Generating Station failed to adequately perform maintenance activities associated with main condenser tube sheet coatings in Unit 3. As a result, a degraded tube was not replugged
Region: IV | Palo Verde | 38759 | 02/25/2011 11/10/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Classify and Evaluate Conditions Adverse to Quality |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow station procedures and perform an adequate classification and evaluation of two condit
Region: IV | Palo Verde | 38667 | 12/17/2010 01/28/2011 | 2010008-01 | NRC | VIO | Mitigating Systems | Green | Failure to Correct and Prevent Recurrence of a Significant Condition Adverse to Quality Associated with the Emergency Diesel Generator Fuel Oil Transfer Pumps | EA Case: 2011006 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000529 Palo Verde 2 |  | 71152B | Inspectors identified a Green cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action", for the failure of the licensee to correct a significant condition adverse to quality associated with the emergency diesel generator fuel oil
Region: IV | Palo Verde | 38686 | 11/15/2010 02/08/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality for the Essential Cooling Water Room Cooler |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of engineering personnel to promptly correct a condition adverse to quality associated with room cooler AHU-3MHAAZ05 blower s
Region: IV | Palo Verde | 38659 | 09/30/2010 11/03/2010 | 2010004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Work Instruction to Replace Emergency Diesel Generator Starting Air Turning Gear Interlock Valves |  | P.2(b) Implementing Operating Experience | TE?: N | 05000530 Palo Verde 3 |  | 71111.12 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure of maintenance personnel to adequately establish and implement work order instructions associated with
Region: IV | Palo Verde | 38660 | 09/30/2010 11/03/2010 | 2010004-03 | NRC | NCV | Barrier Integrity | Green | Failure to Assess Risk Prior to Maintenance on Containment Hatch |  | H.3(b) Work Activity Coordination | TE?: N | 05000528 Palo Verde 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65 a(4), for the failure of work management personnel to assess and manage an increase in risk prior to planned maintenance activities. Specifically, on May 1, 2010, the licensee failed to includ
Region: IV | Palo Verde | 38661 | 09/30/2010 11/03/2010 | 2010004-04 | NRC | NCV | Mitigating Systems | Green | Unqualified Coatings in Containment |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V," Instructions, Procedures, and Drawings," for an inadequate procedure for the application of coatings in containment. Specifically, during construction, Specificati
Region: IV | Palo Verde | 38680 | 09/10/2010 02/08/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Operator Licensing Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure that the integrity of an operating test administered to licensed operators was maintained. During the week of
Region: IV | Palo Verde | 38685 | 09/09/2010 02/08/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures for Medical Examinations of Licensed Operators |  | H.4(a) Human Error Prevention | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of the licensee to follow their quality procedure 01DP-0EM13, "Licensed Operator Medical Examinations," Re
Region: IV | Palo Verde | 38658 | 08/21/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality for Foreign Material in the Pneumatic Supply Lines to the Atmospheric Dump Valves Actuators |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of engineering personnel to promptly identify and correct a condition adverse to quality associated with foreign material in
Region: IV | Palo Verde | 38656 | 05/02/2010 08/03/2010 | 2010003-01 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Post Maintenance Test Results with an Inoperable Containment. |  | H.4(a) Human Error Prevention | TE?: N | 05000528 Palo Verde 1 |  | 71111.12 | A self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," was identified for the failure of maintenance personnel to follow work instructions during the 1R15 refueling outage. Specifically, on May 2, 2010, maintenance personnel w
Region: IV | Palo Verde | 38646 | 03/31/2010 05/05/2010 | 2010002-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Take Corrective Actions for an Identified Adverse Condition |  |  | TE?: N | 05000530 Palo Verde 3 |  | 71111.15 | A self-revealing finding was identified for the failure of engineering personnel to follow procedures and adequately evaluate an identified adverse condition for corrective actions associated with containment isolation valve UV002 as required by Procedure
Region: IV | Palo Verde | 38645 | 03/31/2010 05/05/2010 | 2010002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Mispositioning of Valve Renders Essential Chiller Inoperable |  | H.4(a) Human Error Prevention | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | A self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," was identified for the failure of operations personnel to adequately implement Procedure 40DP-9OP19, "Locked Valve, Breaker, and Component Tracking." Specifically, between
Region: IV | Palo Verde | 38647 | 03/31/2010 05/05/2010 | 2010002-03 | Self - Revealed | NCV | Mitigating Systems | Green | ADV Drop Test Failure Due to Foreign Material |  |  | TE?: N | 05000530 Palo Verde 3 |  | 71111.22 | A self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure of maintenance personnel to prevent the introduction of foreign material into the atmospheric dump valve ni
Region: IV | Palo Verde | 38657 | 03/22/2010 08/03/2010 | 2010003-03 | NRC | NCV | Emergency Preparedness | Green | Inadequate Emergency Action Level Declaration. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR 50.47(b)(4) for the failure of operations personnel to adequately implement the emergency plan. Specifically, on March 22, 2010, leakage from the packing of a main pressurizer spray valve at a rate
Region: IV | Palo Verde | 38655 | 03/07/2010 08/03/2010 | 2010003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Establish Procedures to Restore the Required Configuration of 13.8kV Electrical Bus Ducting. |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000528 Palo Verde 1 |  | 71152 | A self-revealing finding was identified for the failure of maintenance personnel to provide adequate procedures and ensure work was performed properly for installation of the ducting for the 13.8 kV bus to ensure it was weather tight. Specifically, on Mar
Region: IV | Palo Verde | 38630 | 12/31/2009 02/09/2010 | 2009005-01 | NRC | VIO | Mitigating Systems | Green | Failure to Establish Adequate Procedures to Control Potential Tornado Borne Missile Hazards Near the Essential Spray Ponds | EA Case: 2009330 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | Inspectors identified a Green cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action", for the failure of the licensee to correct a significant condition adverse to quality associated with the emergency diesel generator fuel oil
Region: IV | Palo Verde | 38631 | 12/31/2009 02/09/2010 | 2009005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Containment Closure Capability |  | H.3(b) Work Activity Coordination | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified for the failure of maintenance personnel to maintain containment closure capability as required by Procedure 70DP-0RA01, "Shutdown Risk Assessments." Spec
Region: IV | Palo Verde | 38632 | 12/31/2009 02/09/2010 | 2009005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply with High Radiation Area Entry Requirements |  | H.4(b) Procedural Compliance | TE?: N | 05000529 Palo Verde 2 |  | 7112101 | A self-revealing noncited violation of Technical Specification 5.7.1, "High Radiation Areas," was identified for the failure of radiological protection personnel to perform a prejob briefing to ensure workers are aware of radiological conditions in a high
Region: IV | Palo Verde | 38622 | 12/31/2009 02/09/2010 | 2009005-05 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedures to Diagnose and Mitigate a Loss of Instrument Air to the Containment |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure of operations personnel to adequately establish and implement procedures associated with a loss of ins
Region: IV | Palo Verde | 38613 | 10/08/2009 11/19/2009 | 2009008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Evaluation for the Condensate Storage Tank |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to perform an adequate operability evaluation for the condensate storage tank as required by site procedur
Region: IV | Palo Verde | 38619 | 10/08/2009 11/19/2009 | 2009008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Vendor Information for Reactor Trip Breakers |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with programmatic implications for the licensee's failure to follow site procedures and incorporate updated vendor informa
Region: IV | Palo Verde | 38612 | 10/08/2009 11/19/2009 | 2009008-04 | NRC | NCV | Mitigating Systems | Green | Ineffective Corrective Actions for Vaults Containing Station Blackout Cables |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a noncited violation of very low safety significance for failure to effectively implement the corrective action requirements of Regulatory Guide 1.155, "Station Blackout," Appendix A, Criterion 8, "Corrective Action," which were adopte
Region: IV | Palo Verde | 38604 | 09/30/2009 10/30/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality with the Emergency Diesel Generator Train A K-4 Relay in a Timely Manner |  |  | TE?: N | 05000530 Palo Verde 3 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to correct a deficiency associated with the emergency diesel generator voltage regulator K-4 relay in a timel
Region: IV | Palo Verde | 38605 | 09/30/2009 10/30/2009 | 2009004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality with the Emergency Diesel Generator Train B Fuel Oil Transfer Pump in a Timely Manner |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure of maintenance personnel to promptly identify and correct a deficiency associated with the Unit 2 emergency diesel genera
Region: IV | Palo Verde | 38611 | 09/30/2009 10/30/2009 | 2009004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures Results in Loss of Ventilation to Safety-Related Equipment |  | H.4(a) Human Error Prevention | TE?: N | 05000528 Palo Verde 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified for failure of fire protection personnel to adequately implement a functional test procedure. Specifically, on September 21, 2009, fire protection personn
Region: IV | Palo Verde | 38603 | 08/12/2009 09/02/2009 | 2009010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Foreign Material Exclusion Requirements |  | H.1(c) Communication of Decisions | TE?: N | 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to adequately implement foreign material controls during maintenance. Specifically, on May 21, 2008, maintenance
Region: IV | Palo Verde | 38588 | 06/30/2009 08/03/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inoperable Fire Barrier Door for Emergency Diesel Generator Train B |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 |  | 71111.05Q | The inspectors identified a non-cited violation of License Condition 2.C.(7), "Fire Protection Program," for the failure of fire protection personnel to implement fire protection plan requirements. Specifically, from June 8, 2009 to June 12, 2009, fire pr
Region: IV | Palo Verde | 38589 | 06/30/2009 08/03/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Develop an Adequate Procedure to Ensure Operability of the Essential Cooling Water Heat Exchangers |  | H.1(c) Communication of Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.07A | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations, chemistry, and engineering personnel to develop a procedure with appropriate quantitative o
Region: IV | Palo Verde | 38587 | 06/30/2009 08/03/2009 | 2009003-04 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Decrease of Pressurizer Level Due to Personnel Error |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000530 Palo Verde 3 |  | 71111.2 | A self-revealing non-cited violation of Technical Specification 5.4.1(a), "Procedures," was identified for the failure of operations personnel to follow procedural requirements during a planned plant startup. Specifically, on May 27, 2009, operations pers
Region: IV | Palo Verde | 38576 | 03/31/2009 05/05/2009 | 2009002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Correct Deficient Condition for the Essential Spray Pond Chemical Addition System Valves High Failure Rate |  | H.1(c) Communication of Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.12 | The inspectors identified a finding for the failure of engineering and maintenance personnel to adequately implement timely corrective actions for deficiencies associated with the essential spray pond sodium hypochlorite chemical addition system. Specific
Region: IV | Palo Verde | 38577 | 03/31/2009 05/05/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Determination for High Chlorine in the Essential Spray Pond |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow procedures to declare the essential spray pond inoperable. Specifically
Region: IV | Palo Verde | 38578 | 03/31/2009 05/05/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Inspect or Test, and Repair Fire Penetration Seals |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified 5 examples of a non-cited violation of License Condition 2.C.(7), 2.C.(6), and 2.F for Unit 1, Unit 2, and Unit 3, respectively, for the failure of engineering and maintenance personnel to follow procedures to adequately inspect
Region: IV | Palo Verde | 38555 | 02/27/2009 03/20/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation for Potential Emergency Diesel Generator Slow Start Issue |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when, on November 8, 2008, Palo Verde Nuclear Generating Station did not adequately test the emergency diesel generator to
Region: IV | Palo Verde | 38556 | 02/27/2009 03/20/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Screening Significant Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to follow procedures for identifying the significance of a significant condition adverse t
Region: IV | Palo Verde | 38565 | 02/27/2009 03/20/2009 | 2009006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform 10 CFR 50.59 Screenings on Scaffolds Installed for Greater than 90 Days |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when, on February 10, 2009, it was determined that 62 scaffolds that did not comply with the engineering installation spec
Region: IV | Palo Verde | 38566 | 02/27/2009 03/20/2009 | 2009006-04 | NRC | VIO | Mitigating Systems | Green | Failure to Implement Adequate Design Controls | EA Case: 2009057 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of engineering personnel to translate the design basis maximum condensate storage tank temperature requirements into procedures to
Region: IV | Palo Verde | 38567 | 02/27/2009 03/20/2009 | 2009006-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Age-Related Degradation of Safety-Related Inverters |  | P.2(b) Implementing Operating Experience | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to incorporate
Region: IV | Palo Verde | 38572 | 02/27/2009 03/20/2009 | 2009006-06 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Corrective Action Process for Potential Operability Issues with the Safety Related Systems and Systems Important to Safety |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow the corrective action program to ensure that degraded and nonconforming
Region: IV | Palo Verde | 38573 | 02/27/2009 03/20/2009 | 2009006-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Performing Operability Determinations |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow the corrective action program to ensure that degraded and nonconforming
Region: IV | Palo Verde | 38574 | 02/27/2009 03/20/2009 | 2009006-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality with the Emergency Core Cooling System Piping |  |  | TE?: N | 05000528 Palo Verde 1 |  | 71152B | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure of the licensee to promptly identify and correct a condition adverse to quality associated with the high pressure safety
Region: IV | Palo Verde | 38552 | 12/31/2008 02/11/2009 | 2008005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Promptly Identify and Correct Degraded Hydrostatic Penetration Seals |  | P.2(b) Implementing Operating Experience | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.06 | The inspectors identified a finding at Palo Verde Nuclear Generating Station Procedure 01DP-0AP10, "Corrective Action Program," Revision 1, for the failure of operations and engineering personnel to promptly identify and correct a condition adverse to qua
Region: IV | Palo Verde | 38554 | 12/31/2008 02/11/2009 | 2008005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Adequately Implement Procedure Requirements for Refueling Machine Operation |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 |  | 71111.2 | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the failure of refueling services personnel to follow procedures to address refueling machine fault indications. S
Region: IV | Palo Verde | 38549 | 09/30/2008 11/12/2008 | 2008004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Requirements to Implement Technical Specification 5.5.2.b |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.04S | The inspectors identified a noncited violation of Technical Specification 5.5.2.b, "Primary Coolant Sources Outside Containment," for the failure of engineering and maintenance personnel to implement a program to verify integrated leak test requirements f
Region: IV | Palo Verde | 38542 | 09/30/2008 11/12/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Procedure to Control Essential Spray Pond Missile Hazards |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000528 Palo Verde 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of engineering personnel to establish adequate procedures to ensure evaluation and approval of transient mi
Region: IV | Palo Verde | 38543 | 09/30/2008 11/12/2008 | 2008004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination for High Chlorine in the Essential Spray Pond |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000529 Palo Verde 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and chemistry personnel to follow the corrective action program to ensure that potentially n
Region: IV | Palo Verde | 38548 | 09/30/2008 11/12/2008 | 2008004-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality with the Refueling Water Tank Instruments in a Timely Manner |  |  | TE?: N | 05000528 Palo Verde 1 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to correct a deficiency associated with the refueling water tank instrument pit in a timely manner. Specifica
Region: IV | Palo Verde | 38526 | 06/30/2008 08/14/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Reinstallation of Constant Support Hanger |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000529 Palo Verde 2 |  | 71111.12 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for the failure to establish and implement adequate maintenance procedures. These inadequate instructions resulted in the failure to install required washers
Region: IV | Palo Verde | 38524 | 06/30/2008 08/14/2008 | 2008003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Resolve Discrepancies Between Installed Equipment and Work Instructions Results in Mis-positioning Event |  | H.4(a) Human Error Prevention | TE?: N | 05000529 Palo Verde 2 |  | 71111.12 | A self-revealing finding was identified for the failure of operations and maintenance personnel to follow Procedure 01DP-9ZZ01, "Systematic Troubleshooting," and resolve a discrepancy with a work instruction prior to proceeding with troubleshooting. Speci
Region: IV | Palo Verde | 38525 | 06/30/2008 08/14/2008 | 2008003-03 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Decrease in Reactor Water Level Due to Personnel Error |  | H.4(a) Human Error Prevention | TE?: N | 05000529 Palo Verde 2 |  | 71111.22 | A self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," was identified for the failure of operations personnel to adequately implement Procedure 40DP-9OP19, "Locked Valve, Breaker, and Component Tracking." Specifically, on May
Region: IV | Palo Verde | 38531 | 06/30/2008 08/14/2008 | 2008003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prevent Recurrence of a Significant Condition Adverse to Quality for the Feedwater Isolation Valves |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of engineering personnel to implement adequate corrective actions to preclude recurrence of a significant condition adve
Region: IV | Palo Verde | 38523 | 06/30/2008 08/14/2008 | 2008003-05 | Self - Revealed | NCV | Initiating Events | Green | Fire in Pressurizer Cubicle due to Poor Work Practices |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self-revealing noncited violation of License NPF-51, Condition 2.C. (6), was identified involving the failure to follow procedures for proper control of ignition sources. Specifically, contract welding personnel failed to deenergize welding equipment an
Region: IV | Palo Verde | 38530 | 06/30/2008 08/14/2008 | 2008003-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Adequately Implement Procedural Requirements for Open Doors, Hatches, and Floor Plugs |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000528 Palo Verde 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified for the failure of maintenance personnel to adequately implement procedural guidance. Specifically, on May 9, 2008, maintenance personnel failed to ensure
Region: IV | Palo Verde | 38529 | 06/30/2008 08/14/2008 | 2008003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Take Timely Corrective Actions for a Condition Adverse to Quality Resulting in the '1A' Safety Injection Tank being declared Inoperable |  | H.3(b) Work Activity Coordination | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of operations and maintenance personnel to promptly identify and correct a condition adverse to quality. Specifically, from A
Region: IV | Palo Verde | 38522 | 06/30/2008 08/14/2008 | 2008003-08 | Self - Revealed | FIN | Initiating Events | Green | Failure to Evaluate Design Changes Leads to a Manual Reactor Trip |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self revealing finding of Procedure 81DP-0DC13, "Deficiency Work Order," Revision 13, was identified for the failure of engineering personnel to ensure modifications do not inadvertently affect design basis plant conditions. Specifically, between Januar
Region: IV | Palo Verde | 38541 | 06/30/2008 08/14/2008 | 2008003-09 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct a Risk Significant Planning Standard | EA Case: 2008003 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The inspectors identified a noncited violation (NCV) of 10 CFR 50.54(q) and 10 CFR Part 50, Appendix E.IV.F.2.g, for the licensee's failure to correct an identified risk significant planning standard weakness between May 2, 2007 and October 28, 2007. Spec
Region: IV | Palo Verde | 38511 | 03/31/2008 05/09/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Preventative Maintenance Procedures for Emergency Diesel Generator Fuel Oil Injection Pump O-Rings |  | P.2(b) Implementing Operating Experience | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for the failure of operations and engineering personnel to establish and implement maintenance procedures for inspection and replacement of items that have a specific lifet
Region: IV | Palo Verde | 38512 | 03/31/2008 05/09/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Two Examples of a Failure to Properly Implement the Systematic Troubleshooting Process |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000530 Palo Verde 3 |  | 71111.19 | The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations, engineering, and maintenance personnel to follow procedures for troubleshoo
Region: IV | Palo Verde | 38513 | 03/31/2008 05/09/2008 | 2008002-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedure to Evaluate Foreign Material in the Spent Fuel Pool |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of fuels services personnel to evaluate leaving foreign material in the Unit 2 spent fuel pool in accorda
Region: IV | Palo Verde | 38497 | 03/31/2008 05/09/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Staffing Levels Results in Heavy Use of Overtime to Maintain Adequate Shift Coverage |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.2.2.d involving the routine use of excessive overtime for operations personnel that performed safety-related functions. Specifically, between January 1 and December 31, 2007, ope
Region: IV | Palo Verde | 38519 | 03/31/2008 05/09/2008 | 2008002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Corrective Action Process for Potential Operability Issues with the Class 1E 125 V DC System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to ensure that potentially nonconforming conditions associated with the Class 1E
Region: IV | Palo Verde | 38520 | 03/31/2008 05/09/2008 | 2008002-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures Resulted in Water Transfer from the Spent Fuel Pool |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 71152 | A self-revealing non-cited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedures. Specifically, on January 13, 2008, operations personnel failed to properly implement Procedure 40OP-9PC06,
Region: IV | Palo Verde | 38521 | 03/31/2008 05/09/2008 | 2008002-07 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify Inoperable Feedwater Isolation Valve Exceeds Technical Specification Allowed Outage Time |  |  | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self-revealing non-cited violation of Technical Specification 3.7.3.c was identified for the failure of operations personnel to perform the actions required for an inoperable main feedwater isolation valve. Specifically, on July 17, 2006, operations per
Region: IV | Palo Verde | 38458 | 12/31/2007 02/04/2008 | 2007005-01 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO TAKE ADEQUATE CORRECTIVE ACTIONS TO PREVENT RECURRENCE OF A SIGNIFICANT CONDITION ADVERSE TO QUALITY |  | H.3(b) Work Activity Coordination | TE?: N | 05000528 Palo Verde 1 |  | NONE | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of engineering personnel to promptly correct a significant condition adverse to quality. Specifically, on September 17,
Region: IV | Palo Verde | 38459 | 12/31/2007 02/04/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | TWO EXAMPLES OF FAILURE TO PROPERLY IMPLEMENT THE OPERABILITY DETERMINATION PROCESS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 |  | 71111.15 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations personnel to follow procedures and adequately evaluate degraded and nonconfor
Region: IV | Palo Verde | 38461 | 12/31/2007 02/04/2008 | 2007005-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO POST AND CONTROL A HIGH RADIATION AREA |  | H.3(a) Work Planning | TE?: N | 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7112101 | The inspectors reviewed two examples of a self-revealing, noncited violation of Technical Specification 5.7.1 resulting from a failure to control a high radiation area. Specifically, the first example occurred on February 14, 2007, while preparing to perf
Region: IV | Palo Verde | 38465 | 12/31/2007 02/04/2008 | 2007005-04 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO EVALUATE THE RADIOLOGICAL HAZARD CAUSED BY DECONTAMINATION |  | H.3(a) Work Planning | TE?: N | 05000528 Palo Verde 1 |  | 7112101 | The inspectors identified a noncited violation of 10 CFR 20.1501(a) because the licensee failed to completely evaluate the radiological hazard associated with the decontamination of the temporary reactor head. This failure lead to internal exposure of two
Region: IV | Palo Verde | 38466 | 12/31/2007 02/04/2008 | 2007005-05 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO FOLLOW PROCEDURAL GUIDANCE AND RADIATION WORK INSTRUCTIONS |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 7112101 | The inspectors identified a noncited violation of Technical Specification 5.4.1 resulting from a failure to follow radiation exposure permit instructions. Specifically, while touring the Unit 3 containment on October 23, 2007, the inspectors questioned si
Region: IV | Palo Verde | 38460 | 12/31/2007 02/04/2008 | 2007005-06 | NRC | NCV | Barrier Integrity | Green | INADEQUAT DESIGN CONTROLS FOR REFUELING MACHINE |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Criterion III, "Design Control," for the failure of engineering personnel to ensure that the design bases of the refueling machine were adequately translated into specificat
Region: IV | Palo Verde | 38494 | 11/02/2007 02/01/2008 | 2007012-11 | NRC | NCV | Initiating Events | Green | Inadequate Implementation of Risk Management Actions and Risk Assessments for the Switchyard |  | H.3(a) Work Planning | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 50.65(a)(4) for the failure to adequately assess the increase in risk and effectively implement risk mitigation actions for maintenance activities in the switchyard. Specifically, the switchyard wa
Region: IV | Palo Verde | 38507 | 11/02/2007 02/01/2008 | 2007012-19 | NRC | URI | Mitigating Systems | Green | routine use of heavy amounts of overtime for operations personnel |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 95003 | The inspectors identified a noncited violation of Technical Specification 5.2.2.d involving the routine use of excessive overtime for operations personnel that performed safety-related functions. Specifically, between January 1 and December 31, 2007, oper
Region: IV | Palo Verde | 38467 | 10/26/2007 02/01/2008 | 2007012-01 | NRC | NCV | Mitigating Systems | Green | Eight Examples of the Failure to Implement the operability Determination Process |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 05000530 Palo Verde 3 05 |  | 95003 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," with eight examples for the failure of the licensee to adequately evaluate degraded and unanalyzed conditions to support
Region: IV | Palo Verde | 38498 | 10/25/2007 02/01/2008 | 2007012-14 | NRC | NCV | Mitigating Systems | Green | Failure to Establish maintenance Rule Goals for the Safety Injection System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 50.65, for the failure of engineering personnel to establish goals and monitor the performance of the safety injection system. Specifically, on March 22, 2007, engineering personnel failed to estab
Region: IV | Palo Verde | 38473 | 10/10/2007 02/01/2008 | 2007012-04 | NRC | NCV | Mitigating Systems | Green | Six Examples of a Failure to Implement the Corrective Action Program Requirements |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 05000530 Palo Verde 3 05 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," with six examples for the failure of the licensee to identify, evaluate, or correct conditions adverse to quality between 1988 and October 10, 20
Region: IV | Palo Verde | 38477 | 10/10/2007 02/01/2008 | 2007012-05 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Performance Monitoring Criteria for the Auxiliary Feedwater System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 50.65(a)(2) for the failure of maintenance rule and engineering personnel to demonstrate that the performance or condition of structures, systems, or components was being effectively controlled thr
Region: IV | Palo Verde | 38500 | 10/08/2007 02/01/2008 | 2007012-16 | NRC | NCV | Emergency Preparedness | Green | Inability to Implement Two Emergency Action Levels |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a Green noncited violation of 10 CFR 50.54(q) and º50.47(b)(4), for the failure of the licensee to be able to implement EAL 3-12 and EAL7-1. Specifically, area radiation Monitor RU-18 could not be utilized in the vicinity of the
Region: IV | Palo Verde | 38471 | 10/04/2007 02/01/2008 | 2007012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Adequate Design Controls for Condensate Storage Tank Temperature |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with for the failure to translate design basis requirements into procedures to ensure the plant is operated within its design basis. Specifical
Region: IV | Palo Verde | 38491 | 10/03/2007 02/01/2008 | 2007012-10 | NRC | NCV | Mitigating Systems | Green | Failure to Follow procedures for Temporary Shielding Installation |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of Technical Specification 5.4.1.a for the failure of radiation protection personnel to follow procedures for installing temporary shielding at the 87 foot elevation of the auxiliary building west penetratio
Region: IV | Palo Verde | 38505 | 10/03/2007 02/01/2008 | 2007012-17 | NRC | NCV | Occupational Radiation Safety | Green | Inadequate Briefings of Radiological Conditions |  | H.1(c) Communication of Decisions | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 19.12, "Instructions to Workers," for the failure of radiation protection personnel to provide adequate information regarding radiological conditions and precautions to minimize exposure during pre
Region: IV | Palo Verde | 38472 | 10/02/2007 02/01/2008 | 2007012-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Installation of Fire Sprinklers |  |  | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of License Condition 2.C(6) for the failure to install sprinkler heads in accordance with the fire protection program. Specifically, on October 2, 2007, the team identified several upright fire sprinkler hea
Region: IV | Palo Verde | 38489 | 10/02/2007 02/01/2008 | 2007012-08 | NRC | NCV | Initiating Events | Green | Two Examples of a Failure to maintain Control of Transient Combustibles |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of Technical Specification 5.4.1.d for the failure of fire protection personnel to follow Procedure 14DP-0FP33, "Control of Transient Combustibles," Revision 15. Specifically, the team identified that on the
Region: IV | Palo Verde | 38490 | 10/02/2007 02/01/2008 | 2007012-09 | NRC | FIN | Mitigating Systems | Green | Failure to Install Emergency Lighting in Containment Prior to Work Commencement |  | H.3(a) Work Planning | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a finding for the failure of maintenance personnel to install emergency lighting in containment in support of the refueling outage per repetitive maintenance work Order 2935399 and work Instruction WSL 24436. As a result, work b
Region: IV | Palo Verde | 38495 | 10/02/2007 02/01/2008 | 2007012-12 | NRC | NCV | Barrier Integrity | Green | Incorrect Rigging of Personal Airlock Door |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to properly rig the Unit 3 100 foot elevation inner personnel airlock door in accorda
Region: IV | Palo Verde | 38496 | 10/02/2007 02/01/2008 | 2007012-13 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Configuration Control of Pressurizer Instrument Condensing Pot Support Brackets |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of maintenance and engineering personnel to maintain proper configuration of the support brackets for the
Region: IV | Palo Verde | 38456 | 09/30/2007 11/08/2007 | 2007004-01 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO IDENTIFY AND CRITIQUE AN EVENT CLASSIFICATION WEAKNESS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71114.07 | The inspectors identified a noncited violation of 10 CFR 50.54(q) for failure of the emergency planning organization's emergency exercise critique process to identify for correction an emergency plan weakness associated with a risk significant planning st
Region: IV | Palo Verde | 38457 | 09/30/2007 11/08/2007 | 2007004-02 | NRC | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURE RESULTS IN PARTIAL VACUUM OF THE RCS |  | H.4(a) Human Error Prevention | TE?: N | 05000528 Palo Verde 1 |  | 71153 | . A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedures to establish appropriate conditions prior to lowering pressurizer level, resulting in a partial vacuum con
Region: IV | Palo Verde | 38478 | 09/27/2007 02/01/2008 | 2007012-06 | NRC | NCV | Barrier Integrity | Green | Failure to Meet Technical Specification Surveillance Requirement 3.6.6.6 |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 95003 | Green. The team identified a noncited violation of Technical Specification Surveillance Requirement 3.6.6.6, for the failure to verify that each containment spray nozzle was unobstructed. Specifically, the last completed surveillance test conducted on eac
Region: IV | Palo Verde | 38479 | 09/27/2007 02/01/2008 | 2007012-07 | NRC | NCV | Barrier Integrity | Green | Failure to Meet Technical Specification Surveillance Requirement 3.0.3 |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 |  | 95003 | Green. The team identified a noncited violation of Technical Specification Surveillance Requirement 3.0.3 for the failure of operations personnel to conduct an assessment and manage the risk for a missed surveillance test. On September 27, 2007, the team
Region: IV | Palo Verde | 38508 | 08/17/2007 09/18/2007 | 2007008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate procedure for safe shutdown from outside the control room |  | H.2(d) Facilities & Equipment | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.05T | Green. The team identified a noncited violation of License Conditions 2.C.(7), 2.F and 2.C.(6) for Units 1, 2, and 3, respectively. Specifically, procedures required by 10 CFR Part 50, Appendix R, Section III.G.3 and III.L.3 had deficiencies that might im
Region: IV | Palo Verde | 38443 | 06/30/2007 07/20/2007 | 2007003-01 | NRC | NCV | Initiating Events | Green | FAILURE TO SCOPE CONDENSATE DEMINERALIZER VALVE INTO MAINTENANCE RULE |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.12 | A self-revealing noncited violation of 10 CFR 50.65(b) was identified for the failure of engineering personnel to place some components of the condensate demineralizer system into the scope of its program for monitoring the effectiveness of maintenance. S
Region: IV | Palo Verde | 38448 | 06/30/2007 07/20/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY DEGRADED STRUCTURAL SUPPORTS |  | P.2(b) Implementing Operating Experience | TE?: N | 05000530 Palo Verde 3 |  | 71153 | A self-revealing noncited violation of 10 CFR 50.65(a)(3) was identified for failure of the licensee to incorporate internal and external industry operating experience into preventative maintenance activities that could have prevented a maintenance rule f
Region: IV | Palo Verde | 38449 | 06/30/2007 07/20/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO APPLY INDUSTRY OPERATING EXPERIENCE TO MAINTENANCE ACTIVITIES RESULTS IN A PLANT TRANSIENT |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure of inservice inspection personnel to promptly identify and correct a condition adverse to quality. Specifically, since April
Region: IV | Palo Verde | 38450 | 06/30/2007 07/20/2007 | 2007003-04 | NRC | NCV | Barrier Integrity | Green | FAILURE TO PERFORM EVENT RECOVERY CHECKLIST |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and refueling personnel to follow Procedure 40DP-9OP02, "Conduct of Shift Operations," Revis
Region: IV | Palo Verde | 38436 | 05/25/2007 05/30/2007 | 2007011-01 | NRC | FIN | Mitigating Systems | Green | Ineffective Demonstration of Conformance to Design for the Alternate ac Power Sources |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The team identified a finding involving the implementation of Regulatory Guide 1.155, Station Blackout, Appendix A, for the demonstration of the station backout generator design and system readiness requirements. Specifically, established preventive maint
Region: IV | Palo Verde | 38437 | 05/25/2007 05/30/2007 | 2007011-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Control of Design Information for the Station Blackout System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The team identified a noncited violation of very low safety significance for the failure to implement the design control requirements of Regulatory Guide 1.155, Station Blackout, Appendix A, Criterion 1, Design Control and Procurement Control, to 10 CFR 5
Region: IV | Palo Verde | 38440 | 05/25/2007 05/30/2007 | 2007011-03 | NRC | NCV | Mitigating Systems | Green | Non-conservative Containment Sump Level Analysis |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The team identified a noncited violation of very low safety significance of 10 CFR Part 50, Appendix B, Criterion III, Design Control. Specifically, the design calculation that determined the minimum containment flood level following a loss-of-coolant acc
Region: IV | Palo Verde | 38441 | 05/25/2007 05/30/2007 | 2007011-04 | NRC | NCV | Mitigating Systems | Green | Ineffective Maintenance on Target Rock Solenoid-Operated Valves |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111121 | The team identified a noncited violation of very low safety significance of 10 CFR Part 50, Criterion XVI, Corrective Actions, for the failure to identify and correct significant conditions adverse to quality involving Target Rock valve failures. The lice
Region: IV | Palo Verde | 38420 | 03/31/2007 04/26/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Change to Emergency Diesel Generator Intake Air Oil Bath Filter Standby Oil Level Specification |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of engineering personnel to verify or check the adequacy of design for maintaining the emergency diesel generator air intake oil
Region: IV | Palo Verde | 38421 | 03/31/2007 04/26/2007 | 2007002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Operability Determination Process |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of engineering and operations personnel to follow procedures and adequately evaluate degraded and nonconfor
Region: IV | Palo Verde | 38426 | 03/31/2007 04/26/2007 | 2007002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Misalignment of Spring Cans |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of inservice inspection personnel to promptly identify misalignment of spring cans on safety-related piping. Specifically, be
Region: IV | Palo Verde | 38427 | 03/31/2007 04/26/2007 | 2007002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Monitoring of CEA Position Results in Technical Specification Violation |  | H.4(a) Human Error Prevention | TE?: N | 05000529 Palo Verde 2 05000529 Palo Verde 2 |  | 71111.22 | A self-revealing noncited violation of Technical Specification 3.1.6 was identified during the performance of surveillance testing of the control element assemblies when more than one shutdown control element assembly was less than 144.75 inches withdrawn
Region: IV | Palo Verde | 38428 | 03/31/2007 04/26/2007 | 2007002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Results in Declaring Both Actuator Trains of Main Steam Isolation Valve MSIV-170 Inoperable |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 |  | 71111.22 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedure which resulted in declaring both actuator trains for main steam isolation Valve MSIV-170 inoperable. Specific
Region: IV | Palo Verde | 38434 | 03/31/2007 04/26/2007 | 2007002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain EDG Train B Operable |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors identified a noncited violation of Technical Specification 3.8.1 for exceeding the allowed outage time for the Unit 2 emergency diesel generator, Train B. Specifically, for the period between May 14, 2005 and November 3, 2005, the licensee
Region: IV | Palo Verde | 38442 | 02/22/2007 03/16/2007 | 2007010-01 | NRC | NCV | Public Radiation Safety | Green | Failure to control the release of radioactive material |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | A self-revealing, noncited violation of Technical Specification 5.4.1 was reviewed regarding the failure to control the release of radioactive material. On February 2, 2006, the licensee was notified by another site that equipment received was labeled as
Region: IV | Palo Verde | 38415 | 02/09/2007 04/24/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Technical Evaluation of HPSI Pump Bearing Oil Leaks |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | A noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," with two examples was identified for two inadequate operability evaluations. Prompt operability determinations in CRDRs 2941494 and 2303499 incorrect
Region: IV | Palo Verde | 38419 | 02/09/2007 04/24/2007 | 2007007-02 | NRC | FIN | Mitigating Systems | Green | Preventive Maintenance Change Backlog Was Not Tracking Due Dates |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152B | A finding was identified for failure to schedule and perform preventive maintenance tasks that were in the preventive maintenance change process. The team identified that a backlog of over 2500 preventive maintenance changes existed which resulted in thes
Region: IV | Palo Verde | 38404 | 12/31/2006 02/06/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | SCAFFOLDING ERECTED WITH INADEQUATE CLEARANCES AND NO ENGINEERING EVALUATION |  | H.3(b) Work Activity Coordination | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure of maintenance and engineering personnel to follow Procedure 30DP-9WP11, "Scaffolding Instructions," Revision 13, and associated engineering specifications g
Region: IV | Palo Verde | 38405 | 12/31/2006 02/06/2007 | 2006005-02 | NRC | NCV | Mitigating Systems | Green | TWO EXAMPLES OF FAILURE TO PROPERLY IMPLEMENT OPERABILITY DETERMINATION PROCESS |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000528 Palo Verde 1 |  | 71111.15 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of engineering and operations personnel to adequately evaluate degraded and nonconforming c
Region: IV | Palo Verde | 38379 | 12/31/2006 02/06/2007 | 2006005-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN SEISMIC QUALIFICATION OF POST ACCIDENT MONITORING INSTRUMENTATION |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the improper control of design parameters for post accident monitoring instrumentation by operations personnel. Specifically, prior to Novem
Region: IV | Palo Verde | 38410 | 12/31/2006 02/06/2007 | 2006005-04 | NRC | NCV | Barrier Integrity | Green | INADEQUATE ACCEPTANCE TESTING FOR THE UPGRADED REFUELING EQUIPMENT |  |  | TE?: N | 05000529 Palo Verde 2 |  | 7111117A | The inspectors identified a noncited violation of 10 CFR Part 50, Criterion III, "Design Control," for the failure of engineering personnel to implement an adequate procedure for acceptance testing of the upgraded refueling equipment resulting in several
Region: IV | Palo Verde | 38411 | 12/31/2006 02/06/2007 | 2006005-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PERFORM AN ADEQUATE ROOT CAUSE ANALYSIS FOR VALVE SI-225 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000529 Palo Verde 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of the licensee to adequately evaluate and identify the cause for a degraded material condition associated with Unit 2 Valve
Region: IV | Palo Verde | 38412 | 12/31/2006 02/06/2007 | 2006005-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MAINTAIN PROCEDURES AND INSTRUCTIONS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct a condition adverse to quality. Specifically, since 1992, the licensee failed to maintain p
Region: IV | Palo Verde | 38413 | 12/31/2006 02/06/2007 | 2006005-07 | Self - Revealed | NCV | Initiating Events | Green | INADEQUATE PROCEDURE USED FOR MAINTENANCE RESULTS IN REACTOR TRIP |  | H.3(b) Work Activity Coordination | TE?: N | 05000529 Palo Verde 2 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of maintenance personnel to use an adequate procedure for the repairs and restoration of control Valve 2, resulting in a reactor trip during main turbine
Region: IV | Palo Verde | 38414 | 12/31/2006 02/06/2007 | 2006005-08 | Self - Revealed | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES RESULTS IN LOSS OF PLANT CONFIGURATION CONTROL |  | H.3(b) Work Activity Coordination | TE?: N | 05000529 Palo Verde 2 |  | 71153 | Two examples of a self-revealing noncited violation of Technical Specification 5.4.1.a were identified for the failure of operations personnel to properly implement procedures to ensure the correct configuration of equipment during plant evolutions. Speci
Region: IV | Palo Verde | 38394 | 11/30/2006 12/06/2006 | 2006012-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IMPLEMENT THE OPERABILITY DETERMINATION PROCESS |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The team identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to perform operabilty determinations. In both examples, the licensee failed to perform an operab
Region: IV | Palo Verde | 38382 | 11/03/2006 11/13/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE CORRECTIVE ACTIONS TO PRECLUDE WATER INTRUSION AND CORROSION OF UNDERGROUND PIPING AT THE FACILITY |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The inspectors identified multiple examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failing to promptly correct water intrusion problems in multiple areas in the facility, that were identified and exa
Region: IV | Palo Verde | 38385 | 11/03/2006 11/13/2006 | 2006004-02 | NRC | NCV | Initiating Events | Green | UNINTENTIONAL BORATION OF REACTOR COOLANT SYSTEM DUE TO INAPPROPRIATE WORK PERMIT |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 |  | NONE | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to have adequate work control procedures that resulted in an inadvertent boration of the Unit 1 reactor coolant system. Specifica
Region: IV | Palo Verde | 38386 | 11/03/2006 11/13/2006 | 2006004-03 | NRC | NCV | Initiating Events | Green | UNINTENTIONAL TRANSFER OF CVCS INVENTORY TO HIGH ACTIVITY SPENT RESIN TANK |  | H.4(b) Procedural Compliance | TE?: N | 05000530 Palo Verde 3 |  | NONE | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedures that resulted in an unintended transfer of water from the chemical volume and control system to the high act
Region: IV | Palo Verde | 38387 | 11/03/2006 11/13/2006 | 2006004-04 | NRC | NCV | Mitigating Systems | Green | TESTING PERFORMED BEYOND THE SCOPE OF THE FUNCTIONAL RELEASE |  | H.4(b) Procedural Compliance | TE?: N | 05000530 Palo Verde 3 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure of operations personnel to follow procedures for plant modifications when performing a surveillance test that impacted a component that had been recently mod
Region: IV | Palo Verde | 38388 | 11/03/2006 11/13/2006 | 2006004-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY CONDITIONS ADVERSE TO QUALITY FOR THE EMERGENCY DIESEL GENERATORS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71152 | The inspectors identified multiple examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failing to identify degraded material conditions on the emergency diesel generators. Between July and September 2006
Region: IV | Palo Verde | 38395 | 09/26/2006 09/28/2006 | 2006011-01 | NRC | NCV | Mitigating Systems | Green | ESSENTIAL COOLING WATER TRAIN 2B INOPERABLE LONGER THAN ALLOWED OUTAGE TIME DUE TO FOULING - RECHARACTERIZED IN FINAL SIGNIFICANCE DETERMINATION LETTER TO BE A GREEN NCV. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000529 Palo Verde 2 |  | 93812 | Green. A noncited violation of Technical Specification 3.7.7 was identified because Train B of the essential cooling water system in Unit 2 was not capable of performing its safety function for approximately 78 days ending on September 27, 2003. The degra
Region: IV | Palo Verde | 38400 | 09/26/2006 09/28/2006 | 2006011-02 | NRC | NCV | Mitigating Systems | Green | INADEQUATE TEST CONTROL TO PROMPTLY IDENTIFY UNACCEPTABLE HEAT EXCHANGER PERFORMANCE TEST RESULTS - RECHARACTERIZED IN FINAL SIGNIFICANCE DETERMINATION LETTER TO BE A GREEN NCV. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111107B | Green. A noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified. Test Procedure 70TI-9EW01, "Thermal Performance Testing of Essential Cooling Water Heat Exchangers," and Procedure 73DP-9ZZ10, "Guidelines for Heat Ex
Region: IV | Palo Verde | 38402 | 09/26/2006 09/28/2006 | 2006011-04 | NRC | NCV | Mitigating Systems | Green | INADEQUATE IDENTIFICATION AND CORRECTIVE ACTION FOR DEGRADED ESSENTIAL COOLING WATER HEAT EXCHANGER PERFORMANCE - RECHARACTERIZED IN FINAL SIGNIFICANCE DETERMINATION LETTER TO BE A GREEN NCV |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 05000529 Palo Verde 2 05000529 Palo Verde 2 05000530 Palo Verde 3 05000530 Palo Verde 3 |  | 7111107B | Green. A noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified. On March 19, 2002, performance testing for Essential Cooling Water Heat Exchanger 2B indicated that the system would not be capable of performi
Region: IV | Palo Verde | 38403 | 09/26/2006 09/28/2006 | 2006011-05 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DESIGN CONTROL TO ENSURE NO ESSENTIAL COOLING WATER HEAT EXCHANGER SCALING - RECHARACTERIZED IN FINAL SIGNIFICANCE DETERMINATION LETTER TO BE A GREEN NCV. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 7111107B | Green. A noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for failure to correctly evaluate the scaling potential of the safety-related heat exchangers cooled by the emergency spray pond during a design bas
Region: IV | Palo Verde | 38380 | 09/26/2006 09/28/2006 | 2006011-06 | NRC | NCV | Mitigating Systems | Green | TWO EXAMPLES OF FAILURE TO TRANSLATE SPRAY POND DESIGN ASSUMPTIONS INTO PLANT PROCEDURES CONTROL |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 93812 | Two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," were identified involving the failure to adequately translate the design basis of the spray ponds into procedures. Design Calculation 13-MC-SP-0307, "SP/E
Region: IV | Palo Verde | 38381 | 09/26/2006 09/28/2006 | 2006011-07 | NRC | NCV | Mitigating Systems | Green | MULTIPLE EXAMPLES OF INADEQUATE OPERABILITY ASSESSMENTS FOR HEAT EXCHANGER DEGRADATION |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 93812 | A noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," with multiple examples was identified for failure to adequately assess the impact to operability of degraded heat exchangers in the emergency diesel
Region: IV | Palo Verde | 38360 | 06/30/2006 07/24/2006 | 2006003-01 | Self - Revealed | NCV | Initiating Events | Green | EMERGENCY DIESEL TRIP DURING TESTING |  | H.4(b) Procedural Compliance | TE?: N | 05000530 Palo Verde 3 |  | 7111114 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of maintenance personnel to follow procedures. Specifically, on April 2, 2006, maintenance personnel failed to follow Procedure 73ST-9DG02, "Class 1E Die
Region: IV | Palo Verde | 38369 | 06/30/2006 07/24/2006 | 2006003-02 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW PROCEDURES RESULTING IN SPENT FUEL POOL DRAIN DOWN AND SPILL IN THE FUEL BUILDING |  | H.4(a) Human Error Prevention | TE?: N | 05000530 Palo Verde 3 |  | 7111114 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedures. Specifically, between April 7 and April 12, 2006, operations personnel did not follow Procedure 40OP-9PC06,
Region: IV | Palo Verde | 38370 | 06/30/2006 07/24/2006 | 2006003-03 | NRC | NCV | Initiating Events | Green | FAILURE TO PRECLUDE A SIGNIFICANT CONDITION ADVERSE TO QUALITY |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 05000528 Palo Verde 1 |  | 7111114 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of licensee personnel to preclude repetition of a significant condition adverse to quality. Specifically, on April 17, 2
Region: IV | Palo Verde | 38371 | 06/30/2006 07/24/2006 | 2006003-04 | Self - Revealed | NCV | Initiating Events | Green | FAILURE TO FOLLOW GTG SURVEILLANCE PROCEDURE CAUSES LOSS OF POWER TO SAFETY-RELATED BUS |  | H.4(b) Procedural Compliance | TE?: N | 05000530 Palo Verde 3 |  | 7111114 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure of operations personnel to follow procedure. Specifically, on May 6, 2006, operations personnel failed to achieve a current of approximately zero amperes
Region: IV | Palo Verde | 38373 | 06/30/2006 07/24/2006 | 2006003-05 | NRC | NCV | Mitigating Systems | Green | FAILED UNIT 1 CS TRAIN B PUMP ROOM FLOOD LEVEL SWITCH DUE TO NONCONFORMING DRAIN HOSE MANIFOLD BOXES |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of operations personnel to verify or check the adequacy of the design of drain hose manifold boxes. Specifically, between 1997 a
Region: IV | Palo Verde | 38374 | 06/30/2006 07/24/2006 | 2006003-06 | NRC | NCV | Mitigating Systems | Green | FAILURE TO EVALUATE DEGRADED CONDITIONS TO ENSURE OPERABILITY |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 05000530 Palo Verde 3 |  | 71111.13 | The inspectors identified two examples of a noncited violation of Technical Specification 5.4.1.a for the failure of engineering personnel to follow procedures. On April 17, 2006, engineering personnel failed to follow Procedure 81DP-0DC13, "Deficiency Wo
Region: IV | Palo Verde | 38375 | 06/30/2006 07/24/2006 | 2006003-07 | NRC | NCV | Mitigating Systems | Green | THREE EXAMPLES OF A TECHNICAL SPECIFICATION 3.0.4 VIOLATION |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 |  | 71111.2 | The inspectors identified three examples of a Green noncited violation of Technical Specification 3.0.4 for the failure of operations personnel to ensure the operability of required equipment prior to entry into a mode or other specified condition in the
Region: IV | Palo Verde | 38376 | 06/30/2006 07/24/2006 | 2006003-08 | NRC | NCV | Mitigating Systems | Green | FAILURE TO FOLLOW PROCEDURES RESULTED IN DECLARING BOTH TRAINS OF LOW PRESSURE SAFETY INJECTION INOPERABLE |  | H.4(b) Procedural Compliance | TE?: N | 05000530 Palo Verde 3 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure of operations personnel to follow Procedure 73ST-9SI03, Leak Test of SI/RCS Pressure Isolation Valves, which resulted in declaring both trains of low pressur
Region: IV | Palo Verde | 38377 | 06/30/2006 07/24/2006 | 2006003-09 | NRC | NCV | Mitigating Systems | Green | INOPERABLE INVERTER DUE TO DEGRADED CAPACITORS |  |  | TE?: N | 05000528 Palo Verde 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 3.8.7, "Inverters - Operating," was identified for the failure to maintain two operable trains of inverters. On October 20, 2005, Inverter 1EPNBN12 failed. The licensee's evaluation determined
Region: IV | Palo Verde | 38356 | 03/31/2006 05/03/2006 | 2006002-01 | NRC | NCV | Mitigating Systems | Green | INADEQUATE DIESEL FIRE PUMP BATTERY SURVEILLANCE |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71111.05A | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for an inadequate surveillance test for the diesel fire pump batteries. Specifically, since 1995, the method described in Procedure 38FT-9FP02, "Fire Protection System Month
Region: IV | Palo Verde | 38359 | 03/31/2006 05/03/2006 | 2006002-02 | NRC | NCV | Emergency Preparedness | Green | FAILURE TO TRAIN EMERGENCY RESPONSE PERSONNEL |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000528 Palo Verde 1 |  | 7112101 | The inspector identified a noncited violation of 10 CFR 50.47(b)(15) and 10 CFR Part 50, Appendix E, IV(F)(1), for the failure to provide requalification training during 2005 to Arizona Public Service Corporate Public Information personnel as required by
Region: IV | Palo Verde | 38358 | 03/31/2006 05/03/2006 | 2006002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | FAILURE TO FOLLOW RADIATION EXPOSURE PERMIT INSTRUCTIONS |  | H.4(b) Procedural Compliance | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | The inspector reviewed a self-revealing, noncited violation of Technical Specification 5.4.1.a, resulting from two radiation workers' failure to follow radiation exposure permit instructions. On November 22, 2005, two radiation workers, without notifying
Region: IV | Palo Verde | 38350 | 02/03/2006 05/10/2006 | 2006008-01 | Self - Revealed | NCV | Mitigating Systems | Green | UNTIMELY CORRECTIVE ACTIONS FOR FEEDWATER PUMP RESISTOR FAILURES |  |  | TE?: N | 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | A self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for failure to correct, and preclude repetition of, a significant condition adverse to quality involving the failure of the turbine driv
Region: IV | Palo Verde | 38351 | 02/03/2006 05/10/2006 | 2006008-02 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PROMPTLY CORRECT AN ADVERSE TREND OF CONTAMINATED OIL SAMPLES |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | A noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to correct an adverse trend of contaminated oil samples in a timely manner. Specifically, on April 1, 2005, the licensee identified an i
Region: IV | Palo Verde | 38352 | 02/03/2006 05/10/2006 | 2006008-03 | NRC | NCV | Mitigating Systems | Green | FAILURE TO MEET MAINTENANCE TEST REQUIREMENTS |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | A noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," was identified for failure to perform required testing of the Unit 3 essential cooling water system Pump EWP01 breaker in accordance with requirements and acceptance limits.
Region: IV | Palo Verde | 38353 | 02/03/2006 05/10/2006 | 2006008-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY AND CORRECT AN ADVERSE CONDITION ASSOCIATED WITH THE BOP-ESFAS SEQUENCER |  |  | TE?: N | 05000528 Palo Verde 1 |  | NONE | A noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for failure to identify and correct the adverse impact of auto-testing on safety-related relays. Specifically, for approximately 100 days, between May 5
Region: IV | Palo Verde | 38354 | 02/03/2006 05/10/2006 | 2006008-05 | NRC | NCV | Mitigating Systems | Green | FAILURE TO IDENTIFY A MAINTENANCE RULE FUNCTIONAL FAILURE |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | NONE | A noncited violation of 10 CFR 50.65(a)(2) was identified for the failure to demonstrate that the performance or condition of the low pressure safety injection/shutdown cooling Pump 2A was adequate. Specifically, in May 2005, the licensee failed to accura
Region: IV | Palo Verde | 24643 | 10/16/2018 |  | Licensee - Identified | NCV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71153 | Violation: 10 CFR Part 50, Appendix B, Criterion V requires, in part, that activities affecting quality shall be prescribed by documented instructions, procedures, or drawings, of a type appropriate to the circumstances and shall be accomplished in accord
Region: IV | Palo Verde | 24644 | 10/16/2018 |  | Licensee - Identified | NCV |  | Green | Licensee-Identified Non-Cited Violation |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71153 | Violation: 10 CFR 50.73(a)(2)(i)(B) requires, in part, that the holder of an operating license shall submit an licensee event report within 60 days of discovery of the event, which includes any operation or condition which was prohibited by technical spec
Region: IV | Palo Verde | 125735 | 10/21/2019 |  | Licensee - Identified | LIV |  | Green | (OUO-SRI) Licensee identified multiple security officers failed to provide an equivalent level of protection when assigned as a compensatory measure for an inoperable SOCA IDS. |  |  | TE?: N | 05000528 Palo Verde 1 05000529 Palo Verde 2 05000530 Palo Verde 3 |  | 71130.02
Region: IV | River Bend | 126467 | 12/31/2019 02/06/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain the Ability of a Fire Door to Close |  | P.3 - Resolution | TE?: N | 05000458 River Bend Station 1 | Protection Against External Factors | 71111.13 | The inspectors identified a Green, non-cited violation of River Bend Station, Unit 1, Renewed Facility Operating License, Section C(10), with two examples, for failure to implement the fire protection program when the licensee degraded a fire barrier by o
Region: IV | River Bend | 126334 | 12/31/2019 02/06/2020 | 2019004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Periodically Calibrate Radiation Monitoring Equipment |  | H.3 - Change Management | TE?: N | 05000458 River Bend Station 1 | Plant Facilities/Equipment and Instrumentation | 71152 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1 for failure to periodically calibrate and maintain area, process, and effluent radiation monitors as required by 10 CFR Part 20, the Updated Final Safety Analysis Repo
Region: IV | River Bend | 125818 | 09/30/2019 10/31/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Ability of a Fire Door to Close |  | H.5 - Work Management | TE?: N | 05000458 River Bend Station 1 | Protection Against External Factors | 71111.05Q | The inspectors identified a Green non-cited violation of Facility Operating License, Section C(10), when the licensee failed to implement the fire protection program. Specifically, the licensee degraded a fire barrier by obstructing a fire door without i
Region: IV | River Bend | 125775 | 09/30/2019 10/31/2019 | 2019003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Preventively Maintain Circuit Component in Unmonitored System Leads to Inoperability of Containment Unit Cooler |  | NPP | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71111.12 | A self-revealed Green non-cited violation of 10 CFR 50.65, “Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants,” was identified when the licensee failed to monitor the condition of a safety-related component whose conditi
Region: IV | River Bend | 125873 | 09/30/2019 10/31/2019 | 2019003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow the Corrective Action Process Procedure |  | NPP | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71153 | A self-revealed Green finding was identified for failure to follow Entergy Nuclear Procedure EN-LI-102, “Corrective Action Process,” Revision 19. Specifically, station personnel failed to issue appropriate corrective actions to preclude repetition (CAPRs)
Region: IV | River Bend | 125876 | 09/30/2019 10/31/2019 | 2019003-04 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Design Change Leads to Division III Undervoltage Relay Setpoints Drifting Outside of Technical Specification Allowable Values |  | H.3 - Change Management | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71153 | A self-revealed Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” was identified when the licensee failed to establish measures to assure that the design basis is correctly translated into plant specifications. Spec
Region: IV | River Bend | 125243 | 06/30/2019 08/08/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Place a Division of Reactor Protection System in Trip After Falling below the Minimum Required Intermediate Range Monitor Channels During Startup |  | H.14 - Conservative Bias | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71111.15 | The inspectors identified a Green, non-cited violation of Technical Specification (TS) 3.3.1.1, "RPS Instrumentation," for the licensee's failure to take required actions for inoperable intermediate range monitors (IRM). Specifically, while operating in
Region: IV | River Bend | 124640 | 03/31/2019 05/10/2019 | 2019001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Appropriate Surveillance and Maintenance Procedures for the Division III Emergency Diesel Generator |  | H.11 - Challenge the Unknown | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to prescribe instructions appropriate to the circumstances, including appropriate quant
Region: IV | River Bend | 124639 | 03/31/2019 05/10/2019 | 2019001-02 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Initiation of Reactor Core Isolation Cooling due to Personnel Error |  | H.5 - Work Management | TE?: N | 05000458 River Bend Station 1 | Human Performance | 71153
Region: IV | River Bend | 25941 | 12/31/2018 01/29/2019 | 2018004-01 | NRC | FIN | Public Radiation Safety | Green | Failure to Disposition Adverse Conditions Associated with the Offgas System as Required by Procedures |  | H.4 - Teamwork | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a finding for the licensee’s failure to disposition adverse conditions as required by Procedure EN-LI-102, “Corrective Action Program,” Revision 35. Specifically, the licensee did not categorize conditions associated with the off
Region: IV | River Bend | 25942 | 12/31/2018 01/29/2019 | 2018004-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Entrance Into a High Radiation Area |  | H.11 - Challenge the Unknown | TE?: N | 05000458 River Bend Station 1 | Material Control and Accounting | 71124.01 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.7.1, “High Radiation Area,” for the licensee’s failure to control activities in a high radiation area. Specifically, a worker entered into the lower area of the reac
Region: IV | River Bend | 25943 | 12/31/2018 01/29/2019 | 2018004-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Risk Mitigation Actions in Work Procedure Leads to Inadvertent High Pressure Core Spray Initiation |  | H.12 - Avoid Complacency | TE?: N | 05000458 River Bend Station 1 | Equipment Performance | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to implement a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, dated February 1978. Specifically, the licensee
Region: IV | River Bend | 25944 | 12/31/2018 01/29/2019 | 2018004-04 | Self - Revealed | NCV | Barrier Integrity | Green | Control Room Fresh Air Surveillance Procedures Inappropriate to the Circumstances |  | H.14 - Conservative Bias | TE?: N | 05000458 River Bend Station 1 | Procedure Quality | 71153 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” which occurred because the licensee did not prescribe procedures for performing surveillance tests on the ma
Region: IV | River Bend | 25945 | 12/31/2018 01/29/2019 | 2018004-05 | Self - Revealed | NCV | Mitigating Systems | Green | Inappropriate Maintenance Procedure Leads to Water Intrusion into Division II Emergency Diesel Generator Lube Oil System |  | H.5 - Work Management | TE?: N | 05000458 River Bend Station 1 | Procedure Quality | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to implement a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, dated February 1978. Specifically, the licensee
Region: IV | River Bend | 25873 | 08/22/2018 09/10/2018 | 2018301-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Shutdown Operations Protection Plan |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | ES-301 | The team reviewed a self-revealed Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the failure to provide accurate qualitative procedural guidance to determine Shutdown Cooling Safety Func
Region: IV | River Bend | 25874 | 08/22/2018 09/10/2018 | 2018301-02 | Self - Revealed | NCV | Mitigating Systems | Green | Exam Security Compromise While Administering Simulator JPM |  | P.2 - Evaluation | TE?: N | 05000458 River Bend Station 1 |  | ES-301 | The team reviewed a self-revealed Green non-cited violation of 10 CFR Part 55.49, “Integrity of examinations and tests,” for the licensee’s compromise of a simulator JPM during exam administration. Specifically, on June 8, 2018, during a review of the dra
Region: IV | River Bend | 24151 | 07/16/2018 07/18/2018 |  | NRC | NCV | Mitigating Systems | Green | Failure to Develop an Adequate Operational Decision-Making Issue for Compensatory Measures Related to a Degraded Condition of the Feedwater System Sparger Nozzles |  | H.3 - Change Management | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to develop an adequate Operational Decision-Making Issue (ODMI) document per Procedure EN-OP-111, "
Region: IV | River Bend | 24152 | 07/16/2018 07/18/2018 |  | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedures for Post-Scram Recovery |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | 71111.18 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to establish, implement and maintain a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, dated February 1978. Sp
Region: IV | River Bend | 24153 | 07/16/2018 07/18/2018 |  | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Identify and Correct a Broken Feedwater Chemistry Probe |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | 71152 | Two examples of a self-revealed Green finding and associated NCV of 10 CFR Part 50, Appendix B, Criterion XVI, were identified for the licensee’s failure to identify that a broken chemistry probe in the feedwater system had the potential to cause an adver
Region: IV | River Bend | 24154 | 07/16/2018 07/18/2018 |  | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Procedural Guidance for Determining Core Flow During Unanticipated Single Loop Operations |  | P.3 - Resolution | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee’s failure to establish appropriate instructions in the abnormal operating procedure for ther
Region: IV | River Bend | 24383 | 07/16/2018 07/18/2018 |  | NRC | FIN | Initiating Events | Green | Failure to Conduct Adequate Transient Snap Shot Assessment Following Recirculation Pump Trip |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a Green finding for the licensee’s failure to adequately validate simulator response during a transient snap shot assessment following an unexpected trip of reactor recirculation pump A on December 19, 2012. The licensee’s failur
Region: IV | River Bend | 24017 | 03/31/2018 05/08/2018 | 2018001-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Implement Procedure for Storage of Material in the Pools |  | H.4 - Teamwork | TE?: N | 05000458 River Bend Station 1 |  | 71124.02 | The inspector identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee’s failure to implement written procedures for activities referenced in Appendix A of Regulatory Guide 1.33, Revision 2, dated February 1978. Specifically,
Region: IV | River Bend | 24016 | 03/31/2018 05/08/2018 | 2018001-02 | Self - Revealed | FIN | Initiating Events | Green | Installation of an Incorrectly Specified Relay Causes Plant Transient and Reactor Scram |  | H.5 - Work Management | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed two examples of a self-revealed finding for the licensee’s installation of an incorrectly specified relay in 1) the control circuitry for the feedwater level control system and 2) the turbine generator voltage regulator circuitry.
Region: IV | River Bend | 22667 | 12/31/2017 02/08/2018 | 2017004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Loss of High Pressure Core Spray Safety Function during Surveillance Due to Malfunction of Test Return Valve |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 5.4, "Procedures," associated with the licensee’s failure to properly pre-plan and perform maintenance on safety-related components in accordance with documented instr
Region: IV | River Bend | 21662 | 09/30/2017 11/13/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Delayed Closure of Isolation Valves in the Ultimate Heat Sink Inventory Analysis |  | H.6 - Design Margins | TE?: N | 05000458 River Bend Station 1 |  | 71111.07T | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, as defined in Sec
Region: IV | River Bend | 22624 | 09/30/2017 11/13/2017 | 2017003-02 | Self - Revealed | FIN | Initiating Events | Green | Manual Reactor Scram Initiated in Response to Increase in Steam Pressure during Steam Leak Troubleshooting |  | H.5 - Work Management | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealed finding for the licensee’s failure to properly complete steps of an approved procedure during the installation of a modification to the turbine electro-hydraulic control system. Specifically, the licensee failed to
Region: IV | River Bend | 22621 | 08/03/2017 08/03/2017 | 2017002-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Operability of the Division I Control Room Fresh Air System While Changing Reactor Modes |  | H.11 - Challenge the Unknown | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed multiple examples of a self-revealing, non-cited violation of Technical Specification 3.0.4, "Limiting Condition for Operation Applicability," for the licensee’s failure to restore safety-related equipment to operable status prior
Region: IV | River Bend | 31380 | 08/03/2017 08/03/2017 | 2017002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Single Component Failure Leads to Loss of Both Divisions of Control Building Air Conditioning |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to correctly translate the design basis into plant specifications. Specifically, the licensee implemen
Region: IV | River Bend | 31384 | 06/30/2017 08/14/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Extent of Condition for a Degraded 4.16 kV Magne Blast Safety-Related Circuit Breaker |  | H.14 - Conservative Bias | TE?: N | 05000458 River Bend Station 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or draw
Region: IV | River Bend | 31391 | 06/30/2017 08/14/2017 | 2017007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Determination for a Condition Identified During an NRC Walkdown |  | P.3 - Resolution | TE?: N | 05000458 River Bend Station 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficien
Region: IV | River Bend | 23228 | 06/09/2017 06/09/2017 | 2017009-01 | NRC | NOVIV | Initiating Events | Green | Failure to Obtain Prior NRC Approval for a Change in Reactor Core Isolation Cooling Injection Point |  | H.8 - Procedure Adherence | TE?: Y SL-NOVIV | 05000458 River Bend Station 1 |  | 71152B | The NRC identified a Severity Level IV violation for the licensee's failure to restore compliance for a non-cited violation (NCV) associated with failure to obtain NRC approval prior to making a change to the reactor core isolation cooling injection point
Region: IV | River Bend | 22373 | 03/31/2017 05/01/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Station Guidance on Control of Scaffolding |  | H.12 - Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 71111.04S | The inspectors identified a non-cited violation of Technical Specification 5.4, "Procedures," for the licensee's failure to follow station maintenance procedures related to the control of scaffolding in the reactor building. Specifically, the licensee ins
Region: IV | River Bend | 31376 | 03/31/2017 05/01/2017 | 2017001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Pre-Plan and Perform Maintenance on the Control Building Chilled Water System |  | H.11 - Challenge the Unknown | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors identified a non-cited violation of Technical Specification 5.4, "Procedures," for the licensee's failure to properly pre-plan and perform maintenance on safety-related components in accordance with documented instructions appropriate to th
Region: IV | River Bend | 22620 | 03/31/2017 05/01/2017 | 2017001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Applicable Technical Specification Action Statements When Control Building Chillers Were Out of Service |  | NPP | TE?: N | 05000458 River Bend Station 1 |  | 92701 | The inspectors identified a non-cited violation of Technical Specifications 3.8.4, "DC Sources - Operating," 3.8.7, "Inverters – Operating," and 3.8.9, "Distribution Systems – Operating," for the licensee’s failure to either restore inoperable electrical
Region: IV | River Bend | 31369 | 11/08/2016 12/20/2016 | 2016012-01 | NRC | NCV | Initiating Events | Green | Failure to Create Adequate Effectiveness Review Plans for Corrective Actions to Prevent the Recurrence of Significant Performance Issues |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 95001 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to create adequate effectiveness review
Region: IV | River Bend | 31353 | 10/12/2016 10/17/2016 | 2016301-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Plant Operating Procedures with Ten Examples |  | H.7 Documentation | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for ten examples of failing to provide appropriate qualitative and quantitative criteria in alarm response procedures, and abno
Region: IV | River Bend | 31359 | 09/30/2016 11/09/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design and Extent of Condition Review Leaves Circuit Breaker Failure Mechanism Uncorrected |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, after receiving a vendor nonconfor
Region: IV | River Bend | 31360 | 09/30/2016 11/09/2016 | 2016003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Criteria for Alternating Control Building Chilled Water System Chillers |  | P.5 Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed two examples of a self-revealing, non-cited violation of Technical Specification 5.4, "Procedures," for the licensee's failure to establish adequate instructions in the control building chilled water system operating procedures. Th
Region: IV | River Bend | 31346 | 06/30/2016 07/29/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Station Guidance on Use of Temporary Power Cables and Control of Transient Combustibles |  | H.5 Work Management | TE?: N | 05000458 River Bend Station 1 |  | 71111.05Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to follow station maintenance procedures related to the use of temporary power cables and storage of transient combustible materials in the auxi
Region: IV | River Bend | 31347 | 06/30/2016 07/29/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Conduct Common Cause Failure Evaluation in Response to Inoperable Emergency Diesel Generator |  | H.13 Consistent Process | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 3.8.1, "AC Sources - Operating," for the licensee's failure to take required actions for an inoperable emergency diesel generator. Specifically, after classifying the Division I em
Region: IV | River Bend | 31352 | 06/30/2016 07/29/2016 | 2016002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Improperly Stowed Transient Combustibles |  | H.4 Teamwork | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, after writing a condition report i
Region: IV | River Bend | 31328 | 04/29/2016 06/01/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Loop Flow Test Procedure |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(10) for the failure to implement and maintain in effect all provisions of their approved fire protection program. Specifically, the licensee's fire protection program surveillance testing
Region: IV | River Bend | 31335 | 04/29/2016 06/01/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Isolate Control Circuits for Safe Shutdown Equipment from the Effects of a Control Room Fire |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(10) for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified two examples where the licensee failed to
Region: IV | River Bend | 31336 | 04/29/2016 06/01/2016 | 2016007-03 | NRC | FIN | Mitigating Systems | Green | Failure to Demonstrate that Appendix R Emergency Lights Satisfied their Maintenance Rule Performance Criteria |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a finding for the failure to provide an adequate monitoring and testing program to demonstrate that the required Appendix R emergency lights satisfied the licensee's maintenance rule performance criteria. Specifically, the failure to p
Region: IV | River Bend | 30682 | 04/14/2016 05/12/2016 | 2016009-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure While Installing Jumpers for Shutdown Cooling |  | H.2 Field Presence | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing, non-cited violation of Technical Specification 5.4, "Procedures," for the licensee's failure to correctly implement Procedure SOP-0031, "Residual Heat Removal System," Revision 326. SOP-0031, Attachment 5, Step 5.4.1, r
Region: IV | River Bend | 30683 | 04/14/2016 05/12/2016 | 2016009-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedural Guidance |  |  | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing, non-cited violation of Technical Specification 5.4, "Procedures," for three examples of the licensee's failure to establish sufficient procedural guidance. Specifically, the licensee's operations and radiation protectio
Region: IV | River Bend | 30684 | 04/14/2016 05/12/2016 | 2016009-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Corrective Actions to Prevent the Recurrence of a Reactor Scram Due to Grid Disturbances |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to establish measures to assure that corrective action is taken to preclude repetition of a significant c
Region: IV | River Bend | 31327 | 04/14/2016 05/12/2016 | 2016009-04 | NRC | NCV | Initiating Events | Green | Failure to Adequately Assess Risk During Motor Generator Set Unavailability |  | H.14 Conservative Bias | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team identified a non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," for the licensee's failure to adequately assess the increase in risk that may result from proposed maintenan
Region: IV | River Bend | 30671 | 01/20/2016 02/16/2016 | 2015010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Assess Risk During Chiller Unavailability | EA Case: 2015140 | H.1 Resources | TE?: N | 05000458 River Bend Station 1 |  | 93812 | NRC INSPECTION REPORT 05000458/2016008 - FINAL SIGNIFICANCE DETERMINATION OF GREEN FINDING The preliminary significance was estimated to be White. After reviewing new information provided during the April 4, 2016, Regulatory Conference, the significanc
Region: IV | River Bend | 30672 | 01/20/2016 02/16/2016 | 2015010-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Identify and Correct Circuit Breakers Failure Mechanism |  | P.5 Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality related to Masterpact circuit breakers. Sp
Region: IV | River Bend | 30673 | 01/20/2016 02/16/2016 | 2015010-04 | NRC | NCV | Mitigating Systems | Green | Failure to Accomplish an Operability Determination In Accordance With Procedures |  | H.14 Conservative Bias | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to accomplish an operability determination in accordance with procedure EN-OP-104, "Operability Dete
Region: IV | River Bend | 30680 | 01/20/2016 02/16/2016 | 2015010-05 | NRC | FIN | Mitigating Systems | Green | Failure to Identify and Correct an Adverse Condition in a Timely Manner |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team identified a finding for the licensee's failure to identify and correct an adverse condition in a timely manner as required by plant procedures. Specifically, the licensee did not recognize degrading trends associated with incorrect racking of Ma
Region: IV | River Bend | 30652 | 12/31/2015 02/10/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Failure to Ensure Work Hours are Within Work Hour Limits |  | H.8 Procedure Adherence | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | The inspectors identified a non-cited violation of 10 CFR Part 26, "Fitness for Duty Programs," for the licensee's failure to ensure that the calculated hours for individuals subject to work hour controls included all time performing duties for the licens
Region: IV | River Bend | 30660 | 12/31/2015 02/10/2016 | 2015004-02 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Implement Surveillance Testing of Penetration Valve Leakage Control System Leads to Inoperability in Excess of Technical Specification Allowed Outage Time |  | H.3 Change Management | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification 3.6.1.9, "Main Steam-Positive Leakage Control System," for the licensee's failure to take required actions for an inoperable subsystem of the main steam positive leakage control sy
Region: IV | River Bend | 30661 | 12/31/2015 02/10/2016 | 2015004-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Conduct Operations and Control Work Practices to Minimize Residual Radioactivity into the Site, including the Subsurface |  | H.5 Work Management | TE?: N | 05000458 River Bend Station 1 |  | 71124.07 | The inspectors identified a non-cited violation of 10 CFR 20.1406(c) because the licensee failed to conduct operations to minimize the introduction of residual radioactivity into the site. Specifically, the licensee failed to implement procedural requirem
Region: IV | River Bend | 30666 | 12/31/2015 02/10/2016 | 2015004-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure Results in Inadvertent Draindown of Reactor Pressure Vessel |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4, "Procedures," for the licensee's failure to correctly implement procedure STP-200-0605, "Remote Shutdown System Control Circuit Operability Test," Revision 307.
Region: IV | River Bend | 30667 | 12/31/2015 02/10/2016 | 2015004-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Restore Main Steam Positive Leakage Control System to Operable Prior to Changing Modes |  | H.8 Procedure Adherence | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 3.0.4, "Limiting Condition for Operation Applicability," for the licensee's failure to restore safety-related equipment to operable status prior to changing modes. Sp
Region: IV | River Bend | 30637 | 10/08/2015 10/29/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Procedures for Severe Weather Operations |  | P.1 Identification | TE?: N | 05000458 River Bend Station 1 |  | 71111.17T | The team identified a Green, non-cited violation of Technical Specification 5.4.1, which states in part, "procedures recommended in Regulatory Guide 1.33, Revision 2, Appendix A, shall be established, implemented, and maintained for combating emergencies,
Region: IV | River Bend | 30638 | 10/08/2015 10/29/2015 | 2015007-02 | NRC | NCVIV | Mitigating Systems | Green | Failure to Obtain Prior NRC Approval for a Change in Reactor Core Isolation Cooling Injection Point |  |  | TE?: Y SL-IV-NCVIV | 05000458 River Bend Station 1 |  | 71111.17T | The team identified a Severity Level IV, Green, non-cited violation of 10 CFR 50.59, "Changes, Tests, and Experiments," Section (c)(2) which states, in part, "A licensee shall obtain a license amendment pursuant to Section 50.90 prior to implementing a pr
Region: IV | River Bend | 30651 | 09/30/2015 11/10/2015 | 2015003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Operate the Unit 1 Feedwater System in Accordance With Procedures |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to implement a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. Specifically, System Operating P
Region: IV | River Bend | 30639 | 07/02/2015 08/13/2015 | 2015008-01 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Recognize Violations of Contamination Control Requirements as Adverse Conditions |  | H.1 Resources | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The team identified a Green finding for a failure to document adverse conditions associated with radiological housekeeping or contamination controls in the corrective action program as required by procedure. The licensee's procedures did not adequately pr
Region: IV | River Bend | 30640 | 07/02/2015 08/13/2015 | 2015008-02 | NRC | FIN | Mitigating Systems | Green | Failure to Promptly Document Adverse Conditions in the Corrective Action Program |  | H.9 Training | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The team identified a Green finding for multiple examples of failures to timely document adverse conditions, as defined by corrective action program procedures, in condition reports. The team determined that these multiple failures, which were spread acro
Region: IV | River Bend | 30641 | 07/02/2015 08/13/2015 | 2015008-03 | NRC | NCV | Initiating Events | Green | Failure to Preclude Repetition of Consequential Gaps in Operator Performance |  | H.2 Field Presence | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50 Appendix B Criterion XVI, "Corrective Action," for the licensee's failure to preclude repetition of consequential gaps in operator performance. In August 2013, the licensee identified that
Region: IV | River Bend | 30642 | 07/02/2015 08/13/2015 | 2015008-04 | NRC | NCV | Initiating Events | Green | Failure to Identify an Adverse Trend in the Performance of Post Maintenance Testing on High Critical Components |  | H.1 Resources | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50 Appendix B Criterion XVI, "Corrective Action," for the failure to identify and correct a condition adverse to quality. Specifically, the licensee failed to identify an adverse trend in the
Region: IV | River Bend | 30618 | 06/30/2015 08/11/2015 | 2015002-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Operating Margin for Reactor Protection System A Motor Generator Set for Overvoltage Protection Results in Loss of Shutdown Cooling |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a finding for the licensee's failure to raise the overvoltage setpoint on the reactor protection system A motor generator set when the output of the generator was raised. This resulted in a reduction of the operating margin between
Region: IV | River Bend | 30619 | 06/30/2015 08/11/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for 18 Upgraded Hydraulic Control Unit Accumulators |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to verify the adequacy of the design of replacement accumulators, 18 of which were installed in the control rod driv
Region: IV | River Bend | 30620 | 06/29/2015 07/07/2015 | 2015009-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Adequate Procedures to Perform Maintenance on Equipment that can Affect Safety-Related Equipment |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to establish adequate procedures to properly preplan and perform maintenance that affected the performance of the B reactor protection
Region: IV | River Bend | 30621 | 06/29/2015 07/07/2015 | 2015009-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Procedures for Post-scram Recovery |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to establish, implement and maintain a procedure required by Regulatory Guide 1.33, Revision 2, Appendix A, February 1978. -3- Specif
Region: IV | River Bend | 30622 | 06/29/2015 07/07/2015 | 2015009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify High Reactor Water Level as a Condition Adverse to Quality |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to assure a condition adverse to quality was promptly identified. Specifically, the licensee failed to identify, that
Region: IV | River Bend | 30627 | 06/29/2015 07/07/2015 | 2015009-06 | NRC | FIN | Mitigating Systems | Green | Failure to Identify and Classify Operator Workarounds That Impacted Scram Recovery Actions |  | H.13 Consistent Process | TE?: N | 05000458 River Bend Station 1 |  | 93812 | The team identified a finding for the licensee's failure to follow written procedures for classifying deficient plant conditions as operator workarounds and providing compensatory measures or training in accordance with fleet Procedure EN-OP-117, "Opera
Region: IV | River Bend | 30599 | 03/31/2015 05/07/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Operability Evaluations on Degraded High Pressure Core Spray System |  | H.11 Challenge the Unknown | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform an adequate operability evaluation in accordance with Entergy Procedure EN-OP-104,
Region: IV | River Bend | 30603 | 03/31/2015 05/07/2015 | 2015001-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Engineering Change and Work Instruction Review Results in Reactor Recirculation Pump Trip |  | H.4 Teamwork | TE?: N | 05000458 River Bend Station 1 |  | 71111.18 | The inspectors reviewed a self-revealing finding for the licensee's failure to properly implement Procedure EN-DC-115, "Engineering Change Process," when developing engineering change notice ECN 39186, to ensure that no adverse impacts on the plant were w
Region: IV | River Bend | 30604 | 03/31/2015 05/07/2015 | 2015001-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Operate Condensate Demineralizer System Following Reactor Scram Results in Loss of All Feedwater |  | H.4 Teamwork | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing finding for the licensee's failure to follow Procedure SOP-0093, "Condensate Demineralizer System," Revision 033, following a reactor scram on October 17, 2014. Specifically, station operators inappropriately remov
Region: IV | River Bend | 30598 | 01/08/2015 01/12/2015 | 2014302-01 | NRC | NCV | Mitigating Systems | Green | Inadequate System Operating Procedures with Two Examples |  | H.7 Documentation | TE?: N | 05000458 River Bend Station 1 |  | NONE | Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," states, in part, "Instructions, procedures, or drawings shall include appropriate quantitative or qualitative acceptance criteria for determining that important activ
Region: IV | River Bend | 30591 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Retain Scenario-Based Testing Documentation |  | H.8 Procedure Adherence | TE?: N | 05000458 River Bend Station 1 |  | 71111.11B | The inspectors identified a non-cited violation of 10 CFR 55.46, "Simulation Facilities," for the failure of the licensee to retain the results of required performance tests for four years after completion, or until superseded by updated test results. T
Region: IV | River Bend | 30592 | 12/31/2014 02/10/2015 | 2014005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Lubricate Residual Heat Exchanger Bypass Valves |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, "Procedures," for the failure to develop lubrication schedules to ensure the reliability of safety-related motor operated valves (MOV). Specifically, the s
Region: IV | River Bend | 30563 | 09/30/2014 10/31/2014 | 2014004-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Provide Positive Exposure Control Within a Locked High Radiation Area |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 71124.01 | The inspectors identified a non-cited violation of Technical Specification 5.7.2 because a radiation protection technician did not provide positive exposure control to workers entering an area with dose rates greater than 1,000 millirem/hour. Radiation pr
Region: IV | River Bend | 30564 | 08/22/2014 11/05/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Improper Sequencing of Maintenance of 4160 Vac Circuit Breakers Prior to As-Found Tests |  | P.1 Identification | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems,
Region: IV | River Bend | 30566 | 08/22/2014 11/05/2014 | 2014007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Complete and Justify Extension of Preventative Maintenance on Division III 4160 Vac Safety Related Breakers |  | H.6 Design Margins | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The inspectors identified a Green, non-cited violation of Technical Specification 5.4.1, "Procedures," which states, in part, "Written procedures shall be established, implemented, and maintained, covering the following activities: The applicable procedur
Region: IV | River Bend | 30567 | 08/22/2014 11/05/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Determination for Missed Preventive Maintenance on Safety-Related Circuit Breakers |  | H.14 Conservative Bias | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," which states, "Activities affecting quality shall be prescribed by documented instructions, procedures, or drawings, o
Region: IV | River Bend | 30578 | 08/22/2014 11/05/2014 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Identified Negative Safety Margin in Design Documents for Reactor Core Isolation Cooling Valves under Postulated High Energy Line Break Conditions |  | P.3 Resolution | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criteria XVI, "Corrective Action," which states in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficien
Region: IV | River Bend | 30579 | 07/08/2014 11/05/2014 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Adverse Conditions associated with Non-cited Violation 05000458/2011008-06 |  | P.2 Evaluation | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, which states, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficiencies
Region: IV | River Bend | 30562 | 06/30/2014 08/14/2014 | 2014003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Tagging Clearance Instructions |  | H.12 Avoid Complacency | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.a., "Procedures," for the failure to adhere to procedural requirements to ensure that other fire suppression ring header valves are/are not correctly positioned.
Region: IV | River Bend | 30556 | 04/28/2014 05/12/2014 | 2014301-01 | NRC | NCV | Mitigating Systems | Green | Failure of the Plant Referenced Simulator to Demonstrate Expected Plant Response with Three Examples |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | Title 10 CFR Part 55.46(c)(1), "Plant-Referenced Simulators," states, in part, "A plant referenced simulator used for the administration of the operating test\x85must demonstrate expected plant response to operator input and to normal, transient, and emer
Region: IV | River Bend | 29796 | 03/31/2014 05/14/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control for Performance Testing of the Control Building Chillers |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.07A | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failing to verify acceptable performance of the control building chillers. Specifically, station personnel failed to evaluate the increase
Region: IV | River Bend | 29797 | 03/31/2014 05/14/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk for Electrical Switchyard Impacting Maintenance |  | H.3 Change Management | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants." Specifically, on February 12, 2014, the licensee failed to correctly assess and manage the incre
Region: IV | River Bend | 29807 | 03/31/2014 05/14/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Control Design Basis Documents for the Emergency Diesel Generators |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the licensee's failure to correctly translate the design basis for the diesel fuel oil transfer system into specifications, drawings,
Region: IV | River Bend | 29808 | 03/31/2014 05/14/2014 | 2014002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Degraded Emergency Diesel Generator Voltage Regulator |  | P.5 Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly correct a degraded voltage regulator in the Division 3 emergency diesel generator. Specifically, the station failed
Region: IV | River Bend | 29789 | 12/31/2013 02/13/2014 | 2013005-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Perform a Survey on Water Leak |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 71124.06 | IInspectors reviewed a self-revealing non-cited violation of 10 CFR 20.1501(a) because the licensee failed to perform radiation surveys to evaluate radiological conditions associated with a 5 gallons per minute water leak to ensure compliance with 10 CFR
Region: IV | River Bend | 29770 | 12/30/2013 01/02/2014 | 2013007-01 | NRC | VIO | Mitigating Systems | Green | Failure to Resolve Noncompliances Associated with Multiple Spurious Operations in a Timely Manner | EA Case: 2013110 | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The inspector's review confirmed that the licensee's actions were appropriate and complete. Therefore this violation is closed. (Section 4OA5) The team identified a Green violation of License Condition 2.C.(10) for the failure to implement and maintain
Region: IV | River Bend | 29777 | 12/30/2013 01/02/2014 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a Green non-cited violation of Technical Specification 5.4.1.d for the failure to implement and maintain adequate written procedures covering fire protection program implementation. Specifically, the licensee failed to maintain an alte
Region: IV | River Bend | 29778 | 12/30/2013 01/02/2014 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Calculate the Time Available for Operator Actions |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C.(10) for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to properly calculate the amount of
Region: IV | River Bend | 29780 | 12/30/2013 01/02/2014 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Communication Systems Required for Alternative Shutdown Scenarios |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C.(10) for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to ensure that the communications s
Region: IV | River Bend | 29788 | 12/30/2013 01/02/2014 | 2013007-06 | NRC | FIN | Mitigating Systems | Green | Failure to Implement the Engineering Change Process for Appendix R Lighting |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a Green finding for the failure to properly implement the engineering change process. Specifically, the licensee failed to update the Maintenance Rule program and perform the required preventive maintenance tasks after the addition of
Region: IV | River Bend | 29766 | 06/29/2013 08/09/2013 | 2013003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Establish Effective Preventive Maintenance for Components Used in High Critical Applications |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors reviewed a self-revealing finding for the failure to establish an adequate preventive maintenance strategy for the reactor feedwater regulating valves that resulted in several unplanned power changes due to packing steam leaks. In response,
Region: IV | River Bend | 29767 | 06/29/2013 08/09/2013 | 2013003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate and Correct Degraded 125 Vdc Fused Disconnect Switches |  | P.1(b) Trend Performance CAP | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for the failure to identify and take prompt and adequate corrective actions to address a condition adverse to quality specifically related to
Region: IV | River Bend | 29753 | 03/30/2013 05/08/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Performance of the Floor and Equipment Drains System |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(1) associated with the licensee's failure monitor the floor and equipment drains system against licensee-established goals. The licensee failed to properly classify two maintenance prevent
Region: IV | River Bend | 29754 | 03/30/2013 05/08/2013 | 2013002-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Request Briefings of the Dose Rates in High-Radiation Areas Before Entry |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71124.01 | The inspectors reviewed two examples of a self-revealing, non-cited violation of Technical Specification 5.7.1 that resulted because individuals failed to request briefings of the dose rates in high-radiation areas before entry. In response, the licensee
Region: IV | River Bend | 29755 | 03/30/2013 05/08/2013 | 2013002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure of a Radiation Protection Technician to Provide Adequate Job Coverage |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000458 River Bend Station 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.7.1 that resulted because a radiation protection technician failed to provide adequate job coverage. In response, the licensee coached the involved individuals invo
Region: IV | River Bend | 29763 | 03/30/2013 05/08/2013 | 2013002-04 | Self - Revealed | FIN | Occupational Radiation Safety | Green | Failure to Provide Adequate Work Instructions for Installing Reactor Water Cleanup Pump Seals |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71124.02 | The inspectors reviewed a self-revealing finding associated with the licensee's failure to provide adequate instructions for installing a new seal cartridge in the reactor water cleanup 'A' pump. The licensee entered this issue into their corrective actio
Region: IV | River Bend | 29745 | 12/31/2012 02/13/2013 | 2012005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Control Building Chilled Water System |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.01 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the failure to maintain temperature control of the safety-related battery rooms. An engineering evaluation to change a procedur
Region: IV | River Bend | 29746 | 12/31/2012 02/13/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Lubrication of the Standby Liquid Control Pump Motor Bearings |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a for not establishing appropriate lubrication procedures for the standby liquid control pump motor bearings. Specifically, the station incorrectly used the Electrical Power
Region: IV | River Bend | 29749 | 12/31/2012 02/13/2013 | 2012005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Implement Effective Corrective Actions for Defects in MasterPact Breakers |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to promptly correct a condition adverse to quality. Specifically, station personnel failed to implement repairs to the mechanism-op
Region: IV | River Bend | 29750 | 12/31/2012 02/13/2013 | 2012005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure for Lifting Leads Results in Inoperability of Standby Service Water Fan |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a due to a failure to follow work order instructions. Specifically, station personnel failed to follow the requirements of Procedure GMP-0042, "Lifted Leads and
Region: IV | River Bend | 29730 | 12/31/2012 12/28/2012 | 2012012-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspector documented a self-revealing finding associated with the licensee's failure to follow the requirements of Station Procedure EN-LI-102, "Corrective Action Process," and promptly identify and correct a condition adverse to quality. Specifically
Region: IV | River Bend | 29738 | 12/31/2012 12/28/2012 | 2012012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | P.1(b) Trend Performance CAP | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspector identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, following a turbine tri
Region: IV | River Bend | 29739 | 12/31/2012 12/28/2012 | 2012012-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of the Feedwater Control System |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspector identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with the licensee's failure to ensure that design requirements were correctly translated into installed plant equipment. Specifically
Region: IV | River Bend | 29740 | 12/31/2012 12/28/2012 | 2012012-04 | NRC | FIN | Mitigating Systems | Green | Failure to Correct an Identified Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspector identified a finding associated with the licensee's failure to follow the requirements of Station Procedure EN-LI-102, "Corrective Action Process," and correct a condition adverse to quality. Specifically, the licensee identified that both i
Region: IV | River Bend | 29744 | 12/31/2012 12/28/2012 | 2012012-05 | NRC | NCV | Mitigating Systems | Green | Failure to Correct the Maintenance Organizations Inadequate Procedure Use and Adherence |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspector identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, during a root cause eva
Region: IV | River Bend | 29705 | 10/11/2012 11/23/2012 | 2012010-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Correct Spurious Isolations of Reactor Core Isolation Cooling System |  |  | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed t
Region: IV | River Bend | 29706 | 10/11/2012 11/23/2012 | 2012010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Declare Reactor Core Isolation Cooling System Inoperable |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to declare the RCIC system inoperable when the system was unreliable for an automatic start fo
Region: IV | River Bend | 29707 | 10/11/2012 11/23/2012 | 2012010-03 | NRC | NCV | Initiating Events | Green | Failure to Establish an Adequate Controlling Procedure for Stroking Safety Relief Valves at Low Power |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a for the failure to develop adequate controls for low-power stroking of safety relief valves. In response to this finding, the licensee trained senior reactor operator
Region: IV | River Bend | 29717 | 10/11/2012 11/23/2012 | 2012010-04 | NRC | NCV | Initiating Events | Green | Failure to Implement Effective Corrective Actions for Lockout Relay Failures |  | H.3(a) Work Planning | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to identify and correct a condition adverse to quality. Specifically, after a lockout relay mechanically bound in 2011, causing a fire
Region: IV | River Bend | 29718 | 10/11/2012 11/23/2012 | 2012010-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to Test Lockout Relays in Accordance with Vendor Testing Practices |  |  | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for the licensee's failure to establish adequate preventative maintenance instructions for lockout relays in accordance with vendor recommendations fo
Region: IV | River Bend | 29719 | 10/11/2012 11/23/2012 | 2012010-06 | NRC | FIN | Initiating Events | Green | Failure to Establish An Adequate Cable Reliability Program |  | P.2(b) Implementing Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors reviewed a self-revealing finding for the licensee's failure to establish an effective cable reliability program, in that the licensee failed to distinguish between wetted and dry splices. In response, the licensee tested the high-risk-rank
Region: IV | River Bend | 29720 | 10/11/2012 11/23/2012 | 2012010-07 | NRC | NCV | MISC | Green | Loss of Onsite Safety Review Committee Independence |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, for several examples of failures to follow Procedure EN OM 119, "Onsite Safety Review Committee," Revision 8, which indicated that the onsite safety review committ
Region: IV | River Bend | 29721 | 10/11/2012 11/23/2012 | 2012010-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Prrevent Conflicts of Duty for Fire Brigade Members |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 93800 | The inspectors reviewed a self-revealing, non-cited violation of License Condition 2.C.(10) because the licensee failed to prevent conflict of duties for fire brigade members, which affected the timely response to fires. In response, the control room init
Region: IV | River Bend | 29702 | 09/28/2012 11/13/2012 | 2012004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Improper Hydrogen Igniter Breaker Trip Coil Setting |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to correctly translate the design bases for the power supply for the hydrogen igniter system into procedures used
Region: IV | River Bend | 29697 | 09/28/2012 11/13/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions to Ensure Reliability of the 480 VAC Molded Case Circuit Breakers and Unitized Motor Starters |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000458 River Bend Station 1 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to correct within a reasonable period conditions adverse to quality associated with testing safety-related molded-case circu
Region: IV | River Bend | 29703 | 09/28/2012 11/13/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Tune the Reactor Core Isolation Cooling Turbine Speed Controller |  | P.2(b) Implementing Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with inadequate instructions for tuning the reactor core isolation cooling (RCIC) terry turbine speed governor. The
Region: IV | River Bend | 29704 | 09/28/2012 11/13/2012 | 2012004-04 | NRC | FIN | Initiating Events | Green | Inadequate Verification of Leading Edge Flow Meter Functionality |  | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a finding for the licensee's failure to calibrate the feed water Leading Edge Flow Meter (LEFM) CheckPlus System following maintenance activities. This resulted in an error in reactor feed water flow rate data used to calculate r
Region: IV | River Bend | 29676 | 06/29/2012 08/08/2012 | 2012003-01 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure to Protect Sensitive Plant Areas |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | 71111.01 | The inspectors identified a finding for failure to follow Operating System Procedure OSP-0048, "Switchyard, Transformer Yard, and Sensitive Equipment Controls." Specifically, the licensee failed to appropriately consider the plant impact when planning and
Region: IV | River Bend | 29681 | 06/29/2012 08/08/2012 | 2012003-02 | NRC | FIN | Initiating Events | Green | Failure to Implement Severe Weather Operations Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000458 River Bend Station 1 |  | 71111.01 | The inspectors identified a finding that involved failure to implement a procedure to protect the plant during adverse weather conditions. Specifically, appropriate equipment walkdowns and corrective actions were not performed to protect equipment importa
Region: IV | River Bend | 29682 | 06/29/2012 08/08/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | High Pressure Core Spray Diesel Generator Bearing Lubrication Deficiencies |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, for failing to correct a condition adverse to quality for lubricating the high pressure core spray diesel generator bearings. The station docu
Region: IV | River Bend | 29683 | 06/29/2012 08/08/2012 | 2012003-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Properly Assemble Turbine Control Valve Push Rod-Spring Housing Coupling |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealing finding associated with main turbine control valve number 3 unexpectedly closing. In response, operators reduced reactor power to 90 percent. This issue was entered into the licensee's corrective action program as
Region: IV | River Bend | 29695 | 06/29/2012 08/08/2012 | 2012003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Specify Manual Actions for Safety Relief Valve Operations During a Station Blackout Event |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.63, "Loss of All Alternating Current," paragraph (a) (2), which states, in part, "The reactor core and associated coolant, control, and protection systems, including station batteries and any ot
Region: IV | River Bend | 29654 | 03/30/2012 05/14/2012 | 2012002-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Adequately Monitor the Performance of the Digital Radiation Monitoring System |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000458 River Bend Station 1 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(2) involving the failure to adequately monitor the performance of the digital radiation monitoring system. Specifically, the maintenance rule expert panel performed an inadequate analysis
Region: IV | River Bend | 29659 | 03/30/2012 05/14/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Assess and Manage Risk for Internal Flooding Events |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," due to the failure of work control and operations personnel to adequately assess the increase in
Region: IV | River Bend | 29660 | 03/30/2012 05/14/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Assumptions used in Standby Equipment Room Temperature Analysis |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.17T | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because, prior to February 7, 2012, the licensee did not verify that assumptions used in confirming that the safety-related battery inverter ro
Region: IV | River Bend | 29661 | 03/30/2012 05/14/2012 | 2012002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Appropriately Set Reactor Core Isolation Cooling Flow Controller High Output Limit |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Procedures," when the reactor core isolation cooling turbine tripped on mechanical over speed. Troubleshooting determined the cause was an improper
Region: IV | River Bend | 29665 | 03/30/2012 05/14/2012 | 2012002-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Relief Valve Configuration Control Results in a Reactor Downpower |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a self-revealing finding for failing to maintain configuration control of the gland seal header relief valves bonnet vent port. The configuration control failure lead to a subsequent decrease in condenser vacuum requiring an unpl
Region: IV | River Bend | 29666 | 03/30/2012 05/14/2012 | 2012002-06 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Maintenance Instructions used for Suppression Pool Cooling Isolation Valve Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | The inspectors identified a Green, self-revealing non-cited violation of Technical Specification 5.4.1.a, "Procedures," for inadequate maintenance procedures to properly assemble containment isolation valves on the suppression pool cooling system. This re
Region: IV | River Bend | 29667 | 03/30/2012 05/14/2012 | 2012002-07 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform a Radiation Survey |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 71124.02 | Inspectors reviewed a self-revealing non-cited violation of 10 CFR 20.1501(a) for the failure to perform a radiation survey. A survey was not completed after two contaminated valves were transferred from the 98-foot elevation of the main steam tunnel to t
Region: IV | River Bend | 29674 | 03/30/2012 05/14/2012 | 2012002-08 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Access to a High Radiation Area |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | 71124.02 | Inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.7.1(c), resulting from the licensee's failure to control access to a high radiation area. Specifically, a carpenter entered a high radiation area in the main steam tunne
Region: IV | River Bend | 29675 | 03/30/2012 05/14/2012 | 2012002-09 | Self - Revealed | FIN | Initiating Events | Green | Failure to Properly Fabricate and Install the mid-Standard Turbine Shaft Brush |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors reviewed a self-revealing finding regarding the improper fabrication of a turbine shaft grounding brush that resulted in turbine trip and subsequent reactor scram. The licensee identified the improper fabrication of a turbine shaft groundin
Region: IV | River Bend | 29652 | 12/31/2011 01/19/2012 | 2011005-01 | NRC | NCV | Mitigating Systems | Green | Standby Service Water Pump Motor Lubrication Deficiencies |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71111.04S | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a, because the station did not establish appropriate maintenance procedures to lubricate standby service water pump lower motor bearings. Specifically, the inspectors f
Region: IV | River Bend | 29653 | 12/31/2011 01/19/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Monitor the Performance of the Control Building Chiller System |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000458 River Bend Station 1 |  | 71111.12 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(2) involving the failure to adequately monitor the performance of the control building chilled water system. Specifically, the inspectors determined that the station had failed to tr
Region: IV | River Bend | 29610 | 10/27/2011 12/06/2011 | 2011008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing of Division I and Division III Standby Diesel Generators |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and compo
Region: IV | River Bend | 29611 | 10/27/2011 12/06/2011 | 2011008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Use Conservative Design Assumptions in the Ultimate Heat Sink Inventory Calculation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tran
Region: IV | River Bend | 29612 | 10/27/2011 12/06/2011 | 2011008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Residual Heat Removal Heat Exchanger Testing Frequency |  |  | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and compo
Region: IV | River Bend | 29623 | 10/27/2011 12/06/2011 | 2011008-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for Monitoring Standby Service Water System Leakage |  |  | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," which states, in part, "Instructions, procedures, or drawings shall include appropriate quantitative or qualitative acceptance
Region: IV | River Bend | 29634 | 10/27/2011 12/06/2011 | 2011008-07 | NRC | NCV | Mitigating Systems | Green | Inadequate Abnormal Procedure for Reducing Loads on Standby Diesel Generators |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Instructions, procedures, and drawings shall include appropriate quantitative or qualitative acce
Region: IV | River Bend | 29635 | 10/27/2011 12/06/2011 | 2011008-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency and Abnormal Procedures for Standby Diesel Generator Fail to Load Sequences |  | P.2(b) Implementing Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Instructions, procedures, and drawings shall include appropriate qualitative and quantitative cri
Region: IV | River Bend | 29641 | 10/27/2011 12/06/2011 | 2011008-09 | NRC | NCV | Mitigating Systems | Green | Inadequate Simulator Fidelity for Emergency Diesel Generator Loading |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a Green, noncited violation of 10 CFR 55.46(c)(1), "Simulation Facilities," which states, in part, that "a plant-referenced simulator used for the administration of the operating test must demonstrate expected plant response to operato
Region: IV | River Bend | 29608 | 09/30/2011 11/09/2011 | 2011004-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Standby Gas Treatment Electric Heater Power Output Calculation |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III "Design Control," for an inadequate calculation methodology used in determining standby gas treatment system operability. The inspectors found that the calculation
Region: IV | River Bend | 29609 | 09/30/2011 11/09/2011 | 2011004-02 | NRC | FIN | Initiating Events | Green | Ineffective Corrective Actions on the Main Steam Equalizing Header Drain Bypass Valve Results in an Unplanned Down Power |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000458 River Bend Station 1 |  | 71152 | The inspectors identified a self-revealing finding involving inadequate corrective actions in response to a failure in the main steam equalizing header drain bypass valve, resulting in a steam leak and an unplanned plant down power. Specifically, plant pe
Region: IV | River Bend | 29604 | 06/30/2011 08/09/2011 | 2011003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Track and Document Plant Equipment Oil Usage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a finding for the failure to properly document equipment oil additions in the oil lubrication accountability log per General Maintenance Procedure GMP-0015, "Lubrication Procedure." To correct the programmatic deficiencies, the s
Region: IV | River Bend | 29603 | 05/12/2011 06/23/2011 | 2011006-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Take Corrective Action for Service-Induced Failures of Gould J-series Relays |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The inspectors reviewed a self-revealing green noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to take corrective action to address service-induced failures of Gould J series relays. In response
Region: IV | River Bend | 29593 | 03/31/2011 05/12/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Repetitive Service Water Pressure Control Valves Diaphragm Failures Affecting Control Building Chillers Operability |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000458 River Bend Station 1 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify and correct adverse service water chemistry conditions to resolve repetitive service water pressure control
Region: IV | River Bend | 29594 | 03/31/2011 05/12/2011 | 2011002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Determine the Appropriate Preventive Maintenance Strategy and Task Frequency for the Reactor Core Isolation Cooling System Turbine Lube Oil Cooler Inlet Pressure Control Valve |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.12 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1 for the licensee's failure to determine the appropriate preventive maintenance strategy and task frequency for the reactor core isolation cooling system turbine l
Region: IV | River Bend | 29595 | 03/31/2011 05/12/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Control Rod Inspection Procedure |  | P.2(b) Implementing Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving an inadequate control rod inspection procedure. Specifically, the station's procedures only required inspection
Region: IV | River Bend | 29596 | 03/31/2011 05/12/2011 | 2011002-04 | Self - Revealed | FIN | Initiating Events | Green | Feedwater Control System Inadequate Corrective Actions Results in Power Transient |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | The inspectors reviewed a self-revealing finding involving failure to take adequate corrective actions on a degraded feedwater flow controller push-button, causing a recirculation flow control valve runback, reactor vessel level transient, and a resulting
Region: IV | River Bend | 29598 | 03/31/2011 05/12/2011 | 2011002-06 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Properly Control and Guard the Entrance to a Locked High Radiation Area |  | H.3(a) Work Planning | TE?: N | 05000458 River Bend Station 1 |  | 71124.01 | The inspectors identified a noncited violation of Technical Specification 5.7.2 for failure to properly control and guard a high radiation area with dose rates greater than or equal to 1000 mrem/hr. Specifically, on January 25, 2011, while touring the out
Region: IV | River Bend | 29599 | 03/31/2011 05/12/2011 | 2011002-07 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Procedure AOP-0027, "Fuel Handling Mishaps" |  | P.2(b) Implementing Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspector identified a Green noncited violation of Technical Specification 5.4.1.a, "Procedures" for River Bend Station fuel handling personnel failing to follow AOP-0027, "Fuel Handling Mishaps," when an actual fuel handling event occurred. Instead o
Region: IV | River Bend | 29601 | 03/31/2011 05/12/2011 | 2011002-08 | NRC | FIN | Barrier Integrity | Green | Failure to Follow Fuel Handling Guidelines |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspector identified a finding for failure to follow River Bend Station's "Fuel Handling Guideline." A fuel handling event occurred at River Bend Station on January 21, 2011, when a fuel assembly was grappled and raised approximately one foot rather t
Region: IV | River Bend | 28760 | 12/31/2010 02/14/2011 | 2010005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Develop a Preventive Maintenance Schedule to Specify Inspection or Replacement of the O-Ring in the High Pressure Core Spray Lower Motor Bearing Drain Plug |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1 for the licensee's failure to determine the appropriate preventive maintenance strategy and task frequency for the o-ring in the high pressure core spray lower mo
Region: IV | River Bend | 28761 | 12/31/2010 02/14/2011 | 2010005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Two Examples of Completing Maintenance that Affected the Performance of Safety-Related Equipment but Was Not Properly Preplanned |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors reviewed a two-example self-revealing green noncited violation of Technical Specification 5.4.1 for two occasions on which the licensee completed maintenance that affected the performance of safety-related equipment (high pressure core spra
Region: IV | River Bend | 28762 | 12/31/2010 02/14/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Required Quality Control Inspections |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000458 River Bend Station 1 |  | 71152 | Inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion X, "Inspection," for the failure to ensure that Quality Control verification inspections were consistently included and correctly specified in quality-affecting procedures
Region: IV | River Bend | 28765 | 12/31/2010 02/14/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71152 | Inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion II, "Quality Assurance Program," for the failure to implement the experience and qualification requirements of the Quality Assurance Program. As a result, the licensee fai
Region: IV | River Bend | 28766 | 12/31/2010 02/14/2011 | 2010005-05 | Self - Revealed | FIN | Initiating Events | Green | Failure to Plug a Main Condenser Tube in Accordance with an Approved Work Order |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | NONE | The inspectors reviewed a self-revealing finding for the licensee's failure to plug a main condenser tube in accordance with an approved work order. Specifically, a plastic tube plug was not replaced with the required brass plug causing a tube leak requir
Region: IV | River Bend | 28750 | 09/30/2010 11/10/2010 | 2010004-04 | NRC | NCV | Initiating Events | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.11B | The inspectors identified a noncited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of operations training personnel to ensure the integrity of an operating test administered to a licensed operations crew was mainta
Region: IV | River Bend | 28751 | 09/30/2010 11/10/2010 | 2010004-05 | NRC | NCV | Mitigating Systems | Green | Inadequate High Pressure Core Spray Pump Room Cooler Bearing Maintenance |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing, very low safety significance (Green) noncited violation 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings", was reviewed for the licensee's failure to prescribe lubrication and installation of bearings on the hi
Region: IV | River Bend | 28752 | 09/30/2010 11/10/2010 | 2010004-06 | NRC | FIN | Mitigating Systems | Green | Inadequate Maintenance Results in Unplanned Opening of Main Turbine Bypass Valve |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | A self-revealing finding of very low safety significance (Green) was identified when turbine bypass valve number 1 opened unexpectedly causing the reactor to exceed 100 percent core thermal power. Operators promptly lowered core thermal power to 90 percen
Region: IV | River Bend | 28743 | 06/30/2010 08/05/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for High Pressure Core Spray Room Unit Cooler Maintenance |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) involving the licensee's failure to perform an adequate risk assessment while the high pressure core spray room unit cooler was unavailable. Specifically, the licensee assumed that risk
Region: IV | River Bend | 28744 | 06/30/2010 08/05/2010 | 2010003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure Results in Loss of Offsite Power to a 4160 Vac Safety Bus |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | A self-revealing noncited violation of Technical Specification 5.4.1.a. was identified for inadequate procedural guidance when surveillance testing the Division III diesel generator. This resulted in a loss of offsite power to the Division III 4160 volt a
Region: IV | River Bend | 28745 | 06/30/2010 08/05/2010 | 2010003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71124.04 | NRC inspectors reviewed a self-revealing, noncited violation of Technical Specification 5.4.1 for failure to follow radiation work permit instructions. Specifically, a team technician made an unauthorized entry into a posted high radiation area on a radia
Region: IV | River Bend | 28732 | 06/02/2010 06/17/2010 | 2010006-01 | NRC | VIO | Mitigating Systems | Green | Failure to Ensure at Least One Train of Equipment Necessary to Achieve Hot Shutdown Conditions is Free of Fire Damage | EA Case: 2010095 | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | This violation closed in Inspection Report 05000458/2011005, Section 4OA5.1. The team identified a cited violation of License Condition 2.C.(10), "Fire Protection," for failing to ensure that the Division 1 standby service water support system to the D
Region: IV | River Bend | 28736 | 06/02/2010 06/17/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Alternative Shutdown Procedure Could be Implemented as Written |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a noncited violation of Technical Specification 5.4.1.d, "Fire Protection Program Implementation." Specifically, Procedure AOP-0031 "Shutdown from Outside the Main Control Room," Revision 307, had steps that could not be implemented as
Region: IV | River Bend | 28737 | 06/02/2010 06/17/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain in Effect all Provisions of the Approved Fire Protection Program |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a noncited violation of License Condition 2.C.(10), "Fire Protection," for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified, during a timed walkdo
Region: IV | River Bend | 28738 | 06/02/2010 06/17/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implement and Maintain in Effect all Provisions of the Approved Fire Protection Program |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05T | The team identified a noncited violation of License Condition 2.C.(10), "Fire Protection," related to the licensee's failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, during testing required
Region: IV | River Bend | 28723 | 03/31/2010 05/12/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Evaluate a Revised Equipment Tag Out |  | H.3(a) Work Planning | TE?: N | 05000458 River Bend Station 1 |  | 71111.04Q | A self-revealing noncited violation of Technical Specification 5.4.1.a. was identified for defeating the Division I emergency systems automatic start functions caused by the failure to follow a work implementation and closeout procedure when changing the
Region: IV | River Bend | 28730 | 03/31/2010 05/12/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Control Building Chiller Operability During Low Service Water Temperatures |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a Green noncited violation of Technical Specification 3.7.3 for exceeding the control room air conditioning system thirty day allowed outage time for one inoperable subsystem and the seven day allowed outage time for two inoperab
Region: IV | River Bend | 28731 | 03/31/2010 05/12/2010 | 2010002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Adequately Verify a Suitable Replacement Part Essential for Emergency Diesel Generator Operation |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to adequately verify suitable replacement parts essential to the operation of emergency diesel generator Division I. This re
Region: IV | River Bend | 28721 | 12/31/2009 02/09/2010 | 2009005-01 | Self - Revealed | NCV | Initiating Events | Green | Main Steam Line Plug Seal Failure Results in Loss of Reactor Cavity Inventory |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | A self-revealing noncited violation of 10CFR50 Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the failure to follow the procedure for making a permanent plant modification and provide adequate procedures for installat
Region: IV | River Bend | 28722 | 12/31/2009 02/09/2010 | 2009005-02 | NRC | NCV | Public Radiation Safety | Green | Failure to Ensure the Emergency Contact had Knowledge About a Shipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 7112202 | The inspectors identified a noncited violation of 10 CFR 71.5 and 49 CFR Part 172.604(a) for a failure to ensure that the shift manager, whose phone number was listed as the required 24-hour emergency phone number on shipping documents, was knowledgeable
Region: IV | River Bend | 28709 | 09/30/2009 11/12/2009 | 2009004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Containment Closure Procedure |  | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 71111.04Q | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to fully implement a station procedure to control obstructions in primary co
Region: IV | River Bend | 28710 | 09/30/2009 11/12/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Control Scaffold Construction |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a for the failure of maintenance personnel to control scaffold erection per procedure. This failure resulted in the licensee installing 31 scaffolds in safety related ar
Region: IV | River Bend | 28713 | 09/30/2009 11/12/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Reactor Core Isolation Cooling System Seismic Design |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to implement measures to ensure that the seismic design basis for the reactor core isolation cooling turbine governor hydrauli
Region: IV | River Bend | 28714 | 09/30/2009 11/12/2009 | 2009004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Standby Liquid Control System Test Tank Remained Drained |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a for the failure of operations personnel to provide adequate procedural guidance to preclude water intrusion into the nonseismically qualified standby liquid control sy
Region: IV | River Bend | 28707 | 06/30/2009 08/06/2009 | 2009003-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Identify and Formally Critique an Emergency Plan Weakness |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | 71114.06 | The inspectors identified a violation of 10 CFR 50.47(b)(14) for failure to identify and critique a nonrisk significant planning standard weakness demonstrated during a site emergency preparedness drill. Specifically, the licensee demonstrated a weakness
Region: IV | River Bend | 28708 | 05/15/2009 08/20/2009 | 2009008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determinations for a Degraded Diesel Exhaust Pipe |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings" for twice failing to perform an adequate operability evaluation on the Division II diesel generator after the number 8 cylin
Region: IV | River Bend | 28697 | 03/31/2009 05/08/2009 | 2009002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment While the Control Building Chilled Water System was Removed from Service |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(4) involving the failure of operators to perform an adequate risk assessment while the Division 1 control building chilled water was unavailable. Specifically, the inspectors identifi
Region: IV | River Bend | 28698 | 03/30/2009 04/20/2009 | 2009006-01 | NRC | NCV | Barrier Integrity | Green | Failure to promptly correct a condition adverse to quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 7112201 | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to implement required actions to ensure that conditions were promptly corrected. Specifically, on February 10, 2009, during a revi
Region: IV | River Bend | 28680 | 09/27/2008 11/06/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Staging the Station Blackout Diesel Generator during Severe Weather |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.01 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a involving the failure to have an adequate procedure to ensure the availability of on site emergency ac power sources following the four-hour coping period of a postulated st
Region: IV | River Bend | 28681 | 09/27/2008 11/06/2008 | 2008004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Corrective Actions Results in Multiple Failures of Standby Service Water Switchgear Room Ventilation Fans |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000458 River Bend Station 1 |  | 71111.12 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to take adequate corrective actions in response to a condition adverse to quality resulting in repetitive fail
Region: IV | River Bend | 28682 | 09/27/2008 11/06/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Transformer Yard Maintenance While Shut Down |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) involving the licensee's failure to assess and manage the increase in risk that may result from proposed maintenance activities. Specifically, while conducting maintenance in the transfo
Region: IV | River Bend | 27561 | 09/27/2008 11/06/2008 | 2008004-04 | Self - Revealed | FIN | Initiating Events | Green | Turbine Building Siding Failure Below Design Specifications |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing finding was identified for wind induced turbine building siding failure that occurred significantly below design specified stress levels as a result of design and installation deficiencies. This resulted in a forced outage to repair trans
Region: IV | River Bend | 28686 | 08/26/2008 10/27/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Eight Examples of a Failure to Meet 10 CFR Part 50, Appendix B, "Design Control" |  |  | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with eight examples. -Example 1: Non-conservative inputs and assumptions used without adequate
Region: IV | River Bend | 28687 | 08/26/2008 10/27/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Recalculate Suppression Pool Peak Temperature Rseponse |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, design control measures for verifying the adequacy of design were not implemented. Specif
Region: IV | River Bend | 28691 | 08/26/2008 10/27/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing Programs for 4-kV Circuit Breakers, Class 1E Molded Case Circuit Breakers, and the Emergency Diesel Generators |  |  | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," with three examples. Specifically, the team identified that the licensee failed to develop and implem
Region: IV | River Bend | 28692 | 08/26/2008 10/27/2008 | 2008006-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Temporary Installation Procedure |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for five examples of failure to follow the requirements of ADM-0073 "Tempora
Region: IV | River Bend | 28693 | 08/26/2008 10/27/2008 | 2008006-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Implementation of Operability Determination Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow procedures to evaluate conditions adverse to quali
Region: IV | River Bend | 28696 | 08/26/2008 10/27/2008 | 2008006-06 | NRC | NCV | Barrier Integrity | Green | Inadequate/Untimely Corrective Action for Failure of Magnesium-Rotor Motor-Operated Valves |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 7111121 | The team identified a finding of very low safety significance involving a noncited violation of 10 CFR Part 50 Appendix B, Criterion XVI, "Corrective Action," for failure to promptly identify magnesium-rotor motor-operated valve degradation. Specifically,
Region: IV | River Bend | 28673 | 06/28/2008 07/29/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Removing Control Building Chilled Water System from Service |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) when operators failed to perform an adequate risk assessment while the Division 1 control building chilled water and control building air conditioning systems were unavailable. Specifica
Region: IV | River Bend | 28674 | 06/28/2008 07/29/2008 | 2008003-02 | NRC | NCV | Initiating Events | Green | Inadequate Risk Assessment While Troubleshooting Results in Unanticipated Reactor Power Oscillations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) when operators failed to perform an adequate risk assessment associated with a reactor start-up while performing troubleshooting, and during maintenance activities on the main turbine el
Region: IV | River Bend | 28679 | 06/28/2008 07/29/2008 | 2008003-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow a Radiation Protection Procedure |  | H.3(a) Work Planning | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of Technical Specification 5.4.1 which resulted from workers failing to follow a radiation protection procedure. On January 13, 2008, three workers attempted to exit the radiologically controlled
Region: IV | River Bend | 28664 | 03/29/2008 05/09/2008 | 2008002-01 | NRC | NCV | Initiating Events | Green | Internal Operating Experience Not Used to Prevent Recurrence of Reactor Recirculation FCV Runbacks |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for an inadequate procedure for securing a reactor feedwater pump. Specifically, the licensee failed to incorporate internal operating experience into the procedure. As a re
Region: IV | River Bend | 28665 | 03/29/2008 05/09/2008 | 2008002-02 | Self - Revealed | FIN | Initiating Events | Green | Condensate Demineralizer Tank Liner Failure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing finding was identified for the failure to properly repair condensate Demineralizer 1E tank liner prior to returning it to service. As a result, failure of the liner resulted in approximately 20,000 gallons of radiological contaminated con
Region: IV | River Bend | 28671 | 03/29/2008 05/09/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Improper Design Control for Evaluating Emergency Diesel Generator Turbocharger Combustion Air Pipe Stresses |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | The inspectors identified a noncited violation of Title 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to incorporate accurate design information into a calculation to determine emergency diesel generator turbocharger discharge c
Region: IV | River Bend | 28672 | 03/29/2008 05/09/2008 | 2008002-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Reactor Startup Procedure Results in Six Control Rod Withdrawal Errors |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a occurred when River Bend Station reactor operators failed to comply with General Operating Procedure GOP 000-1, "Plant Start Up." Specifically operators withdrew six control rods two n
Region: IV | River Bend | 28656 | 12/31/2007 02/13/2008 | 2007005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Evaluate the Magnitude and Extent of Radiological Hazards Results in Personnel Contaminations |  | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | A self-revealing noncited violation of 10 CFR 20.1501(a) was identified for failure to evaluate the magnitude and extent of radiological hazards associated with performing inspections of equipment in the containment building after a reactor trip on May 4,
Region: IV | River Bend | 28657 | 12/31/2007 02/13/2008 | 2007005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit and Radiation Worker Expectations |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | A self-revealing noncited violation of Technical Specification 5.4.1 was identified for failure to follow radiation work permit instructions resulting in a worker entering a posted high radiation area without authorization. On April 20, 2007, an individua
Region: IV | River Bend | 28658 | 12/31/2007 02/13/2008 | 2007005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Post a Radiation Area |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | An NRC-identified noncited violation of 10 CFR 20.1902(a) was identified for failure to conspicuously post a radiation area. Specifically, the inspector identified an entrance to a radiation area on the 90-foot elevation of the radwaste building that was
Region: IV | River Bend | 28650 | 12/31/2007 02/13/2008 | 2007005-04 | Self - Revealed | NCV | Initiating Events | Green | RPS Terminal Board Loose Connection Results in a Reactor Scram |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50 Appendix B, Criterion V was identified involving the failure to adequately torque reactor protection system electrical terminal board connections during initial construction. This failure resulted in a
Region: IV | River Bend | 28662 | 12/31/2007 02/13/2008 | 2007005-05 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Preventive Maintenance Strategy Results in a Breaker's Failure to Promptly Open Due to Hardened Grease Results in a Complicated Reactor Scram |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing Green noncited violation of 10 CFR 50.65(A)(3) was identified for failure to incorporate internal and external operating experience into preventive maintenance activities to prevent industry known electrical circuit breaker deficiencies.
Region: IV | River Bend | 28663 | 12/31/2007 02/13/2008 | 2007005-06 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Preventative Maintenance Results in a Plant Down Power |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing finding was identified for failure to perform adequate preventive maintenance for control panels associated with providing make up water to the circulating water system. Adequate preventative maintenance was not performed on this system,
Region: IV | River Bend | 28654 | 09/29/2007 11/01/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Risk Assessment for Removing Control Building Chilled Water System from Service |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.13 | An NRC identified noncited violation of 10 CFR 50.65 (a)(4) was identified for the failure to assess and manage the increase in risk that may result from proposed maintenance activities on the control building chilled water system. This issue was entered
Region: IV | River Bend | 28655 | 09/29/2007 11/01/2007 | 2007004-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Survey Following Containment Atmosphere Radiation Monitor Particulate Channel Alarms |  | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 71152 | An NRC-identified noncited violation of 10 CFR 20.1501(a) was identified involving multiple failures to perform radiological surveys to evaluate radiological hazards following control room alarms of the Containment Atmosphere Radiation monitor particulate
Region: IV | River Bend | 28653 | 07/13/2007 08/21/2007 | 2007010-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post Radiation Areas |  | H.3(b) Work Activity Coordination | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The team identified a noncited violation of 10 CFR 20.1902(a) because the licensee failed to post radiation areas in the radwaste building with a conspicuous sign or signs bearing the radiation symbol and the words "Caution, Radiation Area." The licensee
Region: IV | River Bend | 28651 | 06/30/2007 08/07/2007 | 2007003-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Install Scram Discharge Instrument Volume Vent Plug |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified involving the failure to follow a surveillance procedure for scram discharge instrument volume water level channel calibration. Specifically, on February 9, 2007, an ins
Region: IV | River Bend | 28647 | 06/30/2007 08/07/2007 | 2007003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Vendor Recommendations |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing finding was identified involving the failure to implement 1998 vendor recommendations associated with the potential for vibration induced degradation of recirculation loop gate valves. This resulted in the failure to identify and implemen
Region: IV | River Bend | 28649 | 06/30/2007 08/07/2007 | 2007003-03 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Instructions Resulted in Exceeding Load Line Analysis Limit |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified involving the failure to follow procedure. Specifically, during control rod withdrawal a reactor engineer noted that reactor power, as calculated by a heat balance, was
Region: IV | River Bend | 28648 | 06/30/2007 08/07/2007 | 2007003-04 | NRC | FIN | Initiating Events | Green | Inadequate Work Instructions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors identified a finding involving inadequate maintenance instructions for opening a stuck closed feedwater regulating Valve A isolation valve. Specifically, the instructions failed to account for the system being pressurized resulting in unexp
Region: IV | River Bend | 28646 | 04/27/2007 06/11/2007 | 2007009-01 | NRC | FIN | Mitigating Systems | Green | Foreign Material Found in Residual Heat Removal Room Sump Pump Discharge Check Valve |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a finding because the licensee failed to address control of foreign material in the Train B residual heat removal room in June 2003. Consequently, on March 5, 2007, maintenance technicians found foreign material in one of the sump pump
Region: IV | River Bend | 28641 | 03/31/2007 05/07/2007 | 2007002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Implement Freeze Protection Compensatory Measures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | 71111.01 | The inspectors identified a finding involving the failure of operators to implement compensatory measures for cold weather conditions when a ventilation heater for a safety related standby cooling tower pipe chase was out of service during the winters fro
Region: IV | River Bend | 28642 | 03/31/2007 05/07/2007 | 2007002-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Maintenance Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing finding was identified involving the failure of maintenance personnel to follow maintenance instructions resulting in the failure to properly seal the desiccant retention strainer of an instrument air dryer. As a result, desiccant was rel
Region: IV | River Bend | 28643 | 03/31/2007 05/07/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Degraded Residual Heat Removal System Valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000458 River Bend Station 1 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to promptly identify and correct a condition adverse to quality. Specifically, on August 3, 2005, residual heat rem
Region: IV | River Bend | 28634 | 03/31/2007 05/07/2007 | 2007002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Maintenance Instructions for Installation of a Compression Fitting |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the licensee's failure to provide adequate work instructions for repairing a failed tubing compression fitting on the D
Region: IV | River Bend | 28627 | 02/28/2007 03/01/2007 | 2006013-01 | NRC | NCV | Initiating Events | Green | Failure to identify and correct discrepancies between the design function and observed response of the feedwater isolation valves prior to reactor restart |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 05000458 River Bend Station 1 |  | NONE | An NRC-identified noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of licensee personnel to identify and correct a condition adverse to quality in a timely manner. Specifically, followin
Region: IV | River Bend | 28631 | 02/28/2007 03/01/2007 | 2006013-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to place the reactor mode switch in the SHUTDOWN position following a reactor scram as required by abnormal operating procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | NONE | A self-revealing noncited violation of Technical Specification, Section 5.4, "Procedures," was identified for the failure of licensee personnel to accomplish activities affecting quality in accordance with prescribed procedures. Specifically, the at-the-c
Region: IV | River Bend | 28632 | 02/28/2007 03/01/2007 | 2006013-03 | NRC | NCV | Mitigating Systems | Green | Failure to verify that the reactor mode switch was in the SHUTDOWN position following a reactor scram as required by emergency operating procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | NONE | An NRC-identified noncited violation of Technical Specification, Section 5.4, "Procedures," was identified for the failure of licensee personnel to accomplish activities affecting quality in accordance with prescribed procedures. Specifically, the control
Region: IV | River Bend | 28633 | 02/28/2007 03/01/2007 | 2006013-04 | NRC | NCV | Mitigating Systems | Green | Operators failed to permit the safety/relief valves to cycle in automatic and to manually operate the safety/relief valves without driving level outside the prescribed level band as required by AOPs |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | NONE | An NRC-identified noncited violation of Technical Specification, Section 5.4, "Procedures," was identified for the failure of licensee personnel to accomplish activities affecting quality in accordance with prescribed procedures. Specifically, licensed op
Region: IV | River Bend | 28635 | 02/28/2007 03/01/2007 | 2006013-05 | Self - Revealed | NCV | Initiating Events | Green | Failure of reactor operators to perform an adequate control board walkdown resulting in failure to identify that feedwater isolation valves were closing |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | NONE | A self-revealing noncited violation of Technical Specification, Section 5.4, "Procedures," was identified for the failure of licensee personnel to accomplish activities affecting quality in accordance with prescribed conduct-of-operations procedures. Spec
Region: IV | River Bend | 28636 | 02/28/2007 03/01/2007 | 2006013-06 | NRC | FIN | Mitigating Systems | Green | Senior reactor operator relieved the watch during a transient without waiting for the plant to be in a stable condition, resulting in an inadvertent main steam isolation |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a finding for the failure of licensed operators to accomplish activities affecting quality in accordance with the standards established in the conduct-of-operations procedures. Specifically, on October 19, 2006, the on-coming control r
Region: IV | River Bend | 28637 | 02/28/2007 03/01/2007 | 2006013-07 | NRC | NCV | Initiating Events | Green | Licensee personnel failed to identify, place in the corrective action program, and correct deficiencies with Chart Recorder C33-R608 prior to restarting the reactor |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | NONE | An NRC-identified noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of licensee personnel to identify and correct a condition adverse to quality in a timely manner. Specifically, on Octob
Region: IV | River Bend | 28639 | 02/28/2007 03/01/2007 | 2006013-08 | NRC | NCV | Initiating Events | Green | Licensee personnel failed to provide complete corrective actions to address the probable cause of the October 19, 2006, scram, prior to restarting the reactor |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000458 River Bend Station 1 |  | NONE | An NRC-identified noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the failure of licensee personnel to correct a condition adverse to quality. Specifically, following the reactor scram on October 1
Region: IV | River Bend | 28619 | 12/31/2006 02/13/2007 | 2006005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to identify a degraded condition of steam leak detection system Transmitter E31-N084B |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | A self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified involving the failure to identify a degraded condition affecting the steam leak detection and Division II isolation logic for residual h
Region: IV | River Bend | 28620 | 12/31/2006 02/13/2007 | 2006005-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate work instructions result in isolation of annulus pressure control system and automatic start of the Division II standby gas treatment system |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing, noncited violation of Technical Specification 5.4.1.a was identified involving the failure to provide adequate maintenance instructions for replacement of relays in the Division I standby gas treatment system initiation logic. As a resul
Region: IV | River Bend | 28624 | 12/31/2006 02/13/2007 | 2006005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Licensee failed to perform a radiological survey in off-gas sample room after radiological conditions had changed |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | A self-revealing, noncited violation of 10 CFR 20.1501(a)(2) was identified involving the failure of radiation protection personnel to perform a survey in the off-gas sample room during main condenser leak testing. As a result, when a chemistry technician
Region: IV | River Bend | 28625 | 12/31/2006 02/13/2007 | 2006005-04 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to follow procedure resulted in loss of power to safety-related instrumentation bus and isolation of reactor water cleanup system |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing, noncited violation of Technical Specification 5.4.1.a was identified involving the failure to follow Procedure SOP-0048, "120 Vac System," Revision 303. Due to ineffective self- and peer-checking a procedure step was missed, resulting in
Region: IV | River Bend | 28626 | 12/31/2006 02/13/2007 | 2006005-05 | Self - Revealed | FIN | Barrier Integrity | Green | Newly installed reactor water cleanup pump coupling failed because it was beyond its expected service lifetime |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing finding was identified involving the installation of a pump coupling that exceeded vendor shelf- and service-life recommendations on November 15, 2006. As a result, the reactor water cleanup Pump A coupling failed on November 28, 2006, re
Region: IV | River Bend | 28612 | 09/30/2006 11/14/2006 | 2006004-02 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate procedure for reassembly of the turbine bypass valve hydraulic system filter cartridge |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing finding of very low safety significance was reviewed involving an inadequate procedure for conducting maintenance on the turbine bypass valve hydraulic system filter cartridge. This resulted in the improper reassembly of the filter. The r
Region: IV | River Bend | 28613 | 09/30/2006 11/14/2006 | 2006004-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to follow radiation work permit requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector reviewed a self-revealing, noncited violation of Technical Specification 5.4.1 resulting from workers' failure to follow radiation work permit requirements. Two workers performing a scaffolding modification in the inclined fuel transfer syst
Region: IV | River Bend | 28617 | 09/30/2006 11/14/2006 | 2006004-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to evaluate radiological conditions |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector reviewed a self-revealing, noncited violation of 10 CFR 20.1501(a) resulting from the licensee's failure to correctly measure the airborne radioactivity where personnel worked. The licensee's review of the January 26, 2006, contamination eve
Region: IV | River Bend | 28618 | 09/30/2006 11/14/2006 | 2006004-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to evaluate radiological conditions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector identified a noncited violation of 10 CFR 20.1501(a), resulting from the licensee's use of an inadequate alpha contamination survey technique. The inspector determined that the licensee's procedure for the use of the Eberline SAC-4 alpha sci
Region: IV | River Bend | 28604 | 06/30/2006 08/14/2006 | 2006003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to identify Division III ESF bus supply breaker not racked in |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 |  | 71111.15 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was reviewed involving the failure of the licensee to identify that the normal supply breaker to the Division III 4.16 kV engineered safety features bus
Region: IV | River Bend | 28605 | 06/30/2006 08/14/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Failure to adequately manage an increase in plant risk |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | An NRC identified noncited violation of 10 CFR 50.65 Maintenance Rule Section (a)(4) was identified for the failure of the licensee to provide prescribed compensatory measures for two Orange shutdown risk conditions during Refueling Outage 13. Specificall
Region: IV | River Bend | 28606 | 06/30/2006 08/14/2006 | 2006003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate procedure to verify required offsite power breaker alignment |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.22 | An NRC identified noncited violation of Technical Specification 5.4.1.a was identified for the failure of the licensee to provide an adequate surveillance test procedure to perform Technical Specification Surveillance Requirement 3.8.1.1. Specifically, ST
Region: IV | River Bend | 28610 | 06/30/2006 08/14/2006 | 2006003-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to control access to a high radiation area |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of Technical Specification 5.7.1, resulting from the licensee's failure to control access to a high radiation area. While transferring reverse osmosis system filters in the radwaste building, the
Region: IV | River Bend | 28611 | 06/30/2006 08/14/2006 | 2006003-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to perform airborne radiation survey |  | H.4(b) Procedural Compliance | TE?: N | 05000458 River Bend Station 1 |  | 7112101 | The inspector identified a noncited violation of 10 CFR 20.1501(a) because the licensee failed to survey airborne radioactivity. During the removal of local power range monitors, the licensee started collecting an air sample of the work area, but discarde
Region: IV | River Bend | 28603 | 05/10/2006 06/19/2006 | 2006011-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain a Standard Scheme of Emergency Classification and Action Levels in Use |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000458 River Bend Station 1 05000458 River Bend Station 1 |  | 71114.04 | The NRC has considered the information developed during the inspection, the EOI position on the issue which was attached to the inspection report, the information you provided at the Regulatory Conference, and the information provided by your staff in a J
Region: IV | River Bend | 28596 | 03/31/2006 05/05/2006 | 2006002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Installation of Incorrect Relief Valve Caused Leak in Standby Service Water System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000458 River Bend Station 1 |  | 71111.19 | A self-revealing noncited violation of Technical Specifications Section 5.4.1.a. was identified for the failure of procurement engineers to specify the correct replacement relief valve in a repetitive maintenance task to periodically replace thermal relie
Region: IV | River Bend | 28597 | 03/31/2006 05/05/2006 | 2006002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate maintenance results in a drywell steam leak from Low Pressure Coolant Injection Train A Testable Check Valve |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71111.2 | A self-revealing noncited violation of Technical Specification Section 5.4.1.a, was identified for the failure of mechanical maintenance technicians to correctly reassemble Low Pressure Coolant Injection Testable Check Valve E12-AOVF041A during Refueling
Region: IV | River Bend | 28598 | 03/31/2006 05/05/2006 | 2006002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadvertent Initiation of High Pressure Core Spray Caused by the Use of the Wrong Test Plug During Surveillance Testing |  | H.4(a) Human Error Prevention | TE?: N | 05000458 River Bend Station 1 |  | 71153 | A self-revealing noncited violation of Technical Specifications Section 5.4.1.a. was identified for the failure to provide adequate procedural guidance for the use of a test plug during the performance of a required surveillance test procedure. The use of
Region: IV | River Bend | 28591 | 01/19/2006 02/28/2006 | 2005008-01 | NRC | NCV | Mitigating Systems | Green | Unacceptable Preconditioning of a Safety-related Valve Prior to Surveillance Testing |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a non-cited violation of Technical Specification 5.4.1.a (Procedures) for unacceptable preconditioning of a low pressure core spray keepfill system check valve. The test procedure failed to prescribe testing the check valve in the as-f
Region: IV | River Bend | 28592 | 01/19/2006 02/28/2006 | 2005008-02 | NRC | NCV | Mitigating Systems | Green | Untimely Replacement of a Valve to Correct a Significant Condition Adverse to Quality |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI (Corrective Actions) for the failure to take prompt corrective measures to address a significant condition adverse to quality. Specifically, the low pressure core spray keep
Region: IV | River Bend | 28594 | 01/19/2006 02/28/2006 | 2005008-03 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain MCPR within Operating Limits |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified two examples of a Technical Specification 3.2.2, "Minimum Critical Power Ratio" (MCPR), non-cited violation for the failure to prevent transition boiling on the fuel during Operational Cycles 8 and 11. Fuel failures due to transition b
Region: IV | River Bend | 28593 | 01/19/2006 02/28/2006 | 2005008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Set MOV Limit Switches in Accordance with Design Documentation |  |  | TE?: N | 05000458 River Bend Station 1 |  | NONE | The team identified a 10 CFR 50, Appendix B, Criterion V (procedures) non-cited violation for the failure to set safety-related limit switches in accordance documents appropriate to the circumstances for 34 safety-related throttle valves. The licensee set
Region: IV | River Bend | 24038 | 07/12/2018 |  | Licensee - Identified | NCV |  | Green | Failure to Control Access to Critical Digital Asset Communication Paths Located Outside the Protected Area |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71130.10P | **OUO-Security Related Information** The licensee identified during a cyber security self-assessment that the data communication path associated with critical digital assets in the Meteorological Tower were not controlled as required by section E.5.6
Region: IV | River Bend | 125819 | 10/31/2019 |  |  | LIV |  | Green | Failure to Perform Hourly Fire Watches |  |  | TE?: N | 05000458 River Bend Station 1 |  | 71111.05Q
Region: IV | San Onofre | 10256 | 06/23/2013 08/06/2013 | 2013003-01 | NRC | FIN | Mitigating Systems | Green | Failure to Properly Scope All the Pertinent External Flood Protection Features into the Walkdown List in Accordance with Industry Guidance NEI 12-07 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The inspectors identified one finding of very low safety significance for the licensee's failure to follow procedures regarding the Fukushima event response for flood protection to comply with NRC endorsed NEI 12-07, "Guidelines for Performing Walkdowns o
Region: IV | San Onofre | 10250 | 03/24/2013 05/08/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Completely Inspect and Maintain PMF Berm |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.01 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to accomplish activities in accordance with procedures. Specifically, prior to March 4, 2013, the licen
Region: IV | San Onofre | 10251 | 03/24/2013 05/08/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Screen Nuclear Notifications Results in Missed Operability Determinations and Functionality Assessments |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000361 San Onofre 2 05000362 San Onofre 3 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure by operations personnel to implement procedures associated with evaluating the impact of degraded o
Region: IV | San Onofre | 10252 | 03/24/2013 05/08/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Write Nuclear Notifications for Degraded or Non-Conforming Conditions |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of licensee to implement procedures associated with entry of degraded or non-conforming issues into
Region: IV | San Onofre | 10253 | 03/24/2013 05/08/2013 | 2013002-04 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Actions for Nitrogen Gas Accumulation in the Auxiliary Feedwater System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," associated with the licensee's failure to take appropriate and prompt corrective actions regarding nitrogen gas accumulation in safety rel
Region: IV | San Onofre | 10254 | 03/24/2013 05/08/2013 | 2013002-05 | NRC | NCV | Initiating Events | Green | Two Examples of Failure to Follow Procedures for Control of Corrosion Related Maintenance |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The inspectors identified a Green non-cited violation of Technical Specification 5.5.1.1 for the failure by licensee personnel to follow Procedure SO23-XX-30, "Nuclear Maintenance Order (NMO) Generation, Screening and Classification," Revision 9 EC1, and
Region: IV | San Onofre | 10255 | 03/24/2013 05/08/2013 | 2013002-06 | NRC | FIN | Initiating Events | Green | Failure to Follow Procedure for Plant Preservation Rust Grading |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The inspectors identified a Green finding for failure to follow the requirements of the Plant Preservation Rust Grading and Budget Preparation Guide. Specifically, prior to February 28, 2013, licensee personnel failed to initiate nuclear notifications for
Region: IV | San Onofre | 10238 | 12/31/2012 02/14/2013 | 2012005-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Provide Complete and Accurate Information Regarding Auxiliary Feedwater Operation System Operability |  |  | TE?: Y SL-IV-NCVIV | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71153 | The inspectors identified a Severity Level IV noncited violation of 10 CFR 50.9, "Completeness and Accuracy of Information," for the failure of the licensee to provide complete and accurate information in all material respects in operability and reportabi
Region: IV | San Onofre | 10258 | 12/31/2012 09/20/2013 | 2012009-01 | NRC | NCV | Initiating Events | Green | Failure to Verify Adequacy of Thermal-Hydraulic and Flow-Induced Vibration Design for the Unit 2 Replacement Steam Generators |  |  | TE?: N | 05000361 San Onofre 2 |  | 92702 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify the adequacy of the thermal-hydraulic and flow-induced vibration design of the Unit 2 replacement steam generators, re
Region: IV | San Onofre | 10233 | 12/31/2012 11/09/2012 | 2012010-01 | NRC | NCV | Initiating Events | Green | Inadequate Trip/Transient and Event Review Procedure |  |  | TE?: N | 05000362 San Onofre 3 |  | 93800 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," because Operations Procedure SO123-0-A8, "Trip/Transient and Event Review," Revision 5, was not adequate in that it did not def
Region: IV | San Onofre | 10234 | 12/31/2012 11/09/2012 | 2012010-02 | NRC | NCV | Initiating Events | Green | Failure to Comply with Requirements for Handling, Storage, and Shipping |  |  | TE?: N | 05000362 San Onofre 3 |  | 93800 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XIII, "Handling, Storage, and Shipping," involving the licensee's failure to take appropriate measures to control preservation of safety-related equipment during shipping,
Region: IV | San Onofre | 10231 | 09/23/2012 11/07/2012 | 2012004-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Correct Drill Performance Weaknesses |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.47(b)(14) for failure to correct weakness or deficiencies that are identified in formal critiques of drills or exercises. The licensee did not take corrective actions for fourteen weaknesses in
Region: IV | San Onofre | 10232 | 09/23/2012 11/07/2012 | 2012004-02 | NRC | NCVIV | Public Radiation Safety | Green | Failure to Update the Final Safety Analysis Report for Solid Radioactive Waste |  |  | TE?: Y SL-IV-NCVIV | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71124.08 | The inspectors identified a Severity Level IV, non-cited violation of 10 CFR 50.71, "Maintenance of Records, Making of Reports," paragraph (e) which states, in part, "Each person licensed to operate a nuclear power reactor shall update periodically, the f
Region: IV | San Onofre | 10198 | 06/23/2012 08/07/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Barrier Separating Unit 2 Shutdown Cooling Heat Exchanger Rooms |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000361 San Onofre 2 |  | 71111.05Q | The inspectors identified a non-cited violation of License Condition 2.C.(14) and the Updated Fire Hazards Analysis for the failure of the licensee to maintain the 3-hour penetration fire seal that separated redundant post-fire safe shutdown equipment. Sp
Region: IV | San Onofre | 10210 | 06/23/2012 08/07/2012 | 2012003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Foreign Material Exclusion Controls in Safety Related Components |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 |  | 71111.12 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to implement procedures associated with foreign material exclusion
Region: IV | San Onofre | 10211 | 06/23/2012 08/07/2012 | 2012003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Foreign Material Exclusion Controls During Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to implement procedures associated with foreign material exclusion controls whil
Region: IV | San Onofre | 10212 | 06/23/2012 08/07/2012 | 2012003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Design Control Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.18 | The inspectors identified a non-cited violation 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to follow Procedure SO123-XXIV-10.1, "Engineering Design Change Process - NECPs," R
Region: IV | San Onofre | 10213 | 06/23/2012 08/07/2012 | 2012003-05 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Battery Testing Procedure for Battery Exceeding 85% Service Life |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71152 | The inspectors identified a finding for the failure to follow the battery testing procedure for non-class 1E batteries. Specifically, licensee personnel failed to implement the non-class 1E battery testing procedure, SO23-I-9.96, "Non-1E Battery Bank Perf
Region: IV | San Onofre | 10191 | 03/24/2012 05/08/2012 | 2012002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Seismic Controls in Safety-Related Areas |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow Procedure SO123-XV-1.20, "Seismic Controls," Revision 4. Specifically,
Region: IV | San Onofre | 10192 | 03/24/2012 05/08/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Timely Corrective Actions on a Safety-Related Pumps |  |  | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure of maintenance and engineering personnel to promptly correct a degraded condition associated with safety-related equipment.
Region: IV | San Onofre | 10193 | 03/24/2012 05/08/2012 | 2012002-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Control Work Activities and Prevent RCS Perturbations |  | H.3(b) Work Activity Coordination | TE?: N | 05000362 San Onofre 3 |  | 71111.2 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.5.1.1 for the failure of operations personnel to follow Procedure SO23-3-1.8, "Draining the Reactor Coolant System to a Reduced Inventory Condition," Revision 32, At
Region: IV | San Onofre | 10187 | 12/31/2011 02/09/2012 | 2011005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Work in a High Radiation Area |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000362 San Onofre 3 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 5.8.1 for the failure to control work in a high radiation area. On August 25, 2011, diving was performed in a high radiation area using stay time calculations instead
Region: IV | San Onofre | 10188 | 12/31/2011 02/09/2012 | 2011005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Required Compensatory Measures Resulted in Inoperable Condensate Storage Tank |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing non-cited violation of Technical Specification 5.5.1.1, "Procedures," was identified for the failure of operations personnel to adequately implement the appropriate compensatory measures per alarm response procedure to ensure equipment wa
Region: IV | San Onofre | 10189 | 12/31/2011 02/09/2012 | 2011005-03 | Self - Revealed | FIN | Mitigating Systems | Green | Failure to Correct Degraded Plant Equipment Results in Ammonia Spill |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing finding was identified for the failure to take adequate corrective actions for degraded equipment associated with the Unit 3 full flow condensate polishing demineralizer system. Specifically, on October 27, 2011, operations personnel fail
Region: IV | San Onofre | 10168 | 09/30/2011 11/03/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Emergency Core Cooling System Valves in Required Positions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 71111.04Q | The inspectors identified a noncited violation of Technical Specification 5.5.1.1.a for the failure of operations personnel to maintain valves in positions required by procedures. The inspectors observed a drain valve, required to be closed by procedure,
Region: IV | San Onofre | 10169 | 09/30/2011 11/03/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Flood Protection for the Auxiliary Feedwater Steam Supply Piping |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for failure to translate applicable regulatory requirements and the design basis into specifications, drawings, procedures, and instructions. Th
Region: IV | San Onofre | 10173 | 09/30/2011 11/03/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Calculation Results into Plant Procedures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 2515/177 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to ensure that procedures for preventing unacceptable gas accumulation included a
Region: IV | San Onofre | 10174 | 09/30/2011 11/03/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Plant Modification in Accordance with Applicable Specifications |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 2515/177 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of licensee personnel to perform a modification to the Unit 3 high pressure safety injection system in accordance with the seism
Region: IV | San Onofre | 10175 | 09/13/2011 10/14/2011 | 2011010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Assessment of Seismic Qualification of Emergency Diesel Generator Buried Fuel Oil Tanks |  |  | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states in part: "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translated
Region: IV | San Onofre | 10178 | 09/13/2011 10/14/2011 | 2011010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate that Sufficient Voltage would be Available at the Emergency Diesel Generator Air Start Solenoid |  |  | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states in part: "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly transl
Region: IV | San Onofre | 10179 | 09/13/2011 10/14/2011 | 2011010-03 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Requirements into Procedures and Instructions |  |  | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states in part: "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translated
Region: IV | San Onofre | 10180 | 09/13/2011 10/14/2011 | 2011010-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Effects of Fuse Resistance and High Energy Line Break Conditions on Control Circuit Voltage |  |  | TE?: N | 05000362 San Onofre 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states in part: "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translated
Region: IV | San Onofre | 10184 | 09/13/2011 10/14/2011 | 2011010-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Equipment Important to Safety |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR 50.65, "Requirements for monitoring the effectiveness of maintenance at nuclear power plants," which states in part: "Each holder of a license to operate a nuclear power plant shall monitor the perf
Region: IV | San Onofre | 10185 | 09/13/2011 10/14/2011 | 2011010-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Control Document Changes |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The team identified a Green non-cited violation, with multiple examples, of 10 CFR 50, Appendix B, Criterion VI, "Document Control," which states in part: "Measures shall be established to control the issuance of documents, such as instructions, procedure
Region: IV | San Onofre | 10154 | 06/30/2011 08/05/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Compensatory Measures for a Design Nonconformance |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.01 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure of operations personnel to establish adequate compensatory measures to restore or maintain operability as required by Procedure SO123-XV-52, "Operab
Region: IV | San Onofre | 10155 | 06/30/2011 08/05/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions to Ensure Environmentally Qualified Configuration |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.12 | The inspectors identified that work instructions to replace a safety-related steam generator differential pressure transmitter did not contain adequate instructions to ensure that the scope of work was defined and the installed configuration would satisfy
Region: IV | San Onofre | 10159 | 06/30/2011 08/05/2011 | 2011003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Appropriately Assess and Manage Risk for Work in Unit 3 Intake |  | H.1(c) Communication of Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | A self-revealing noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," was identified for the failure of work control and operations personnel to adequately assess and manage the
Region: IV | San Onofre | 10160 | 06/30/2011 08/05/2011 | 2011003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Long-Time Over-Current Protection for the Cables for Charging Pumps 2P190 and 2P191 |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The inspectors identified that the licensee did not provide adequate long-time over-current protection for charging pumps 2P190 and 2P191 feeder cables. The finding involved a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Contro
Region: IV | San Onofre | 10161 | 06/30/2011 08/05/2011 | 2011003-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Requirements for a Failed Surveillance |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.5.1.1, "Procedures," for the failure of operations personnel to follow the surveillance program requirements for control element assembly testing, when a satisfactory verification
Region: IV | San Onofre | 10167 | 06/30/2011 08/05/2011 | 2011003-06 | NRC | NCV | Mitigating Systems | Green | Lack of Adequate Procedures to Respond to the Inability to Drive Control Rods |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.5.1.1, "Procedures," for the licensee's failure to establish procedures for the inability to drive control rods. Specifically, from initial licensing to May 2011, Abnormal Operati
Region: IV | San Onofre | 10150 | 03/31/2011 05/05/2011 | 2011002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Station Procedures for Seasonal Readiness |  | H.3(b) Work Activity Coordination | TE?: N | 05000361 San Onofre 2 |  | 71111.01 | The inspectors identified a finding for the failure of license personnel to follow procedure SO23-XX-29.1, "Seasonal Readiness." Specifically, licensee personnel failed to implement, as seasonal weather conditions dictated, the appropriate preventative ma
Region: IV | San Onofre | 10151 | 03/31/2011 05/05/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures to Establish Compensatory Measures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The Inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawing," for the failure of operations personnel to follow the requirements of station procedure to perform an adequate operability d
Region: IV | San Onofre | 10152 | 03/31/2011 05/05/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specifications |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 3.5.4, "Refueling Water Storage Tank," for the failure of licensee personnel to enter the technical specification or complete the associated required action prior to the appropriate
Region: IV | San Onofre | 9935 | 12/31/2010 02/10/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Classify Conditions Adverse to Quality for Significance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | Between September 23 and November 15, 2010, the inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of licensee personnel to follow the requiremen
Region: IV | San Onofre | 9936 | 12/31/2010 02/10/2011 | 2010005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedure for Modifying Work Clearance Applications |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified for the failure of operations personnel to follow Procedure SO123-XX-5.1, "Work Clearance Management Issue, Release, and Tagging Modification," Revision 22, to prepare a
Region: IV | San Onofre | 9937 | 12/31/2010 02/10/2011 | 2010005-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Control of Foreign Material over the Spent Fuel Pool during Surveillance Testing |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for the failure of licensee personnel to follow procedures associated with foreign material exclusion controls, which
Region: IV | San Onofre | 9942 | 12/31/2010 02/10/2011 | 2010005-04 | NRC | NCV | Initiating Events | Green | Failure to Properly Store C-Panels in the Radwaste Building |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71152 | The team identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of plant personnel to follow site procedures that controlled equipment storage in the radwaste building. Specif
Region: IV | San Onofre | 9931 | 09/23/2010 11/03/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures While Implementing a Design Change |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to follow the requirements of station procedures while performing work on contain
Region: IV | San Onofre | 9933 | 09/23/2010 11/03/2010 | 2010004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Training Mandated by a Root Cause Evaluation |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure of electrical maintenance management personnel to adequately ensure that training was provided to electrical maintenance workers
Region: IV | San Onofre | 9947 | 08/16/2010 09/30/2010 | 2010007-01 | NRC | VIO | Mitigating Systems | Green | Failure to Ensure At Least One Train of Equipment Necessary to Achieve Hot Shutdown Conditions Is Free of Fire Damage | EA Case: 2010191 | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The team identified a cited violation of License Condition 2.C(14), "Fire Protection," for failure to correct a noncompliance. Specifically, Inspection Report 05000361;362/2007008 documented a noncompliance involving the failure to ensure that at least on
Region: IV | San Onofre | 9944 | 07/16/2010 08/30/2010 | 2010010-01 | NRC | NCV | Initiating Events | Green | Failure to Define Authorities and Responsibilities of Work Process Area Operator |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.5.1.1 for failure to provide a written procedure to define authorities and responsibilities of all work process area operators. Specifically, on July 13, 2010, the work process a
Region: IV | San Onofre | 9932 | 07/12/2010 11/03/2010 | 2010004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Safety-related Emergency Ventilation Fans |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the licensee's failure to promptly identify and correct a condition adverse to quality associated with safety-related emergency venti
Region: IV | San Onofre | 9865 | 06/23/2010 08/04/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Unavailability Time for Component Cooling Water Incorrectly Counted |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000362 San Onofre 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(1) and 50.65(a)(2) for the failure of engineering personnel to demonstrate that the performance or condition of the Unit 3 component cooling water system had been effectively controlled thr
Region: IV | San Onofre | 9868 | 06/23/2010 08/04/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage Risk for Maintenance on Emergency Diesel Generators |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," involving multiple instances where operations and work planning personnel failed to adequately as
Region: IV | San Onofre | 9869 | 06/23/2010 08/04/2010 | 2010003-03 | NRC | NCV | Initiating Events | Green | Improper Risk Assessment and Management for Emergent Work |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) for the failure of operations and planning personnel to appropriately characterize the potential impact of work activities on plant systems and to implement appropriate risk mitigating a
Region: IV | San Onofre | 9870 | 06/23/2010 08/04/2010 | 2010003-04 | NRC | NCV | Initiating Events | Green | Failure to Define the Control Room as Required by Technical Specifications |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of Technical Specification 5.1.3 for the failure of licensee management to appropriately define the Control Room Area as depicted in the Licensee Controlled Specifications. Specifically, prior to June 2010, l
Region: IV | San Onofre | 9874 | 06/23/2010 08/04/2010 | 2010003-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Work Control Procedures |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified for the failure of maintenance and construction services personnel to follow procedures for performing work on safety-related components. Specifically, between November
Region: IV | San Onofre | 9875 | 06/23/2010 08/04/2010 | 2010003-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Determination for Safety-Related Concrete Cracks |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations and engineering personnel to follow station procedures to determine the operability of a degr
Region: IV | San Onofre | 9876 | 06/23/2010 08/04/2010 | 2010003-07 | NRC | NCV | Mitigating Systems | Green | Inappropriate Control of Operator Aids |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a noncited violation of Technical Specification 5.5.1.1 for the failure of operations personnel to follow Procedure SO123-0-A1, "Conduct of Operations," Revision 27, to appropriately control operator aids. Specifically, between M
Region: IV | San Onofre | 9880 | 06/23/2010 08/04/2010 | 2010003-08 | Self - Revealed | NCV | Mitigating Systems | Green | Failure of Schedule 10S Piping |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for the licensee's failure to determine the cause and take corrective actions to preclude repetition of a significant condition adverse
Region: IV | San Onofre | 9881 | 06/23/2010 08/04/2010 | 2010003-09 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Identify and Classify Degraded Voltage on a Class 1E Battery |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to fully evaluate a degraded condition in accordance with its corrective action p
Region: IV | San Onofre | 9882 | 06/23/2010 08/04/2010 | 2010003-10 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assure Circuit Breakers Were Qualified for Installation |  |  | TE?: N | 05000361 San Onofre 2 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion VII, "Control of Purchased Material, Equipment, and Services," was identified for the failure of engineering personnel to assure that 4 kV vacuum circuit breakers supplied by NLI
Region: IV | San Onofre | 9884 | 06/23/2010 08/04/2010 | 2010003-11 | NRC | FIN | Initiating Events | Green | Failure to Follow Station Procedures on Written Instruction Use and Adherence |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71153 | The inspectors identified a finding for the failure of the licensee to follow its procedures for written instruction use and adherence during a test to determine the impact on main condenser vacuum of a damaged feedwater heater. Specifically, on May 5, 20
Region: IV | San Onofre | 9896 | 06/17/2010 07/30/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate operability determination of the turbine driven auxiliary feed water pump steam admission valves. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the failure to follow procedural requirements for performing operability determinations. Specifically, the licen
Region: IV | San Onofre | 9905 | 06/17/2010 07/30/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to translate design basis information into procedures for the turbine-driven auxiliary feed water pump steam admission valves |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 |  | 71152B | The team identified an NON-CITED VIOLATION of 10 CFR 50, Appendix B, Criterion III, "Design Control" in that the licensee failed to translate design basis information into procedures for the turbine-driven auxiliary feedwater pump steam admission valves.
Region: IV | San Onofre | 9906 | 06/17/2010 07/30/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Lack of preventive maintenance results in valve failure and inoperable condensate storage tank. |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000361 San Onofre 2 |  | 71152B | The inspectors identified a noncited violation of Technical Specification 3.7.6, which requires, in part, that Condensate Storage Tank T-120 be operable. Specifically, the tank isolation valve 2HV5715 had been inoperable for a period greater than the allo
Region: IV | San Onofre | 9886 | 06/17/2010 07/30/2010 | 2010006-05 | NRC | NCV | Initiating Events | Green | Control room operators failure to adhere to conduct of operations procedural requirements |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000362 San Onofre 3 |  | 71152B | The inspectors identified a noncited violation of Technical Specification 5.5.1.1.a involving the failure of control room operators to follow San Onofre Procedure SO123-0-A1, "Conduct of Operations." These included failures to: implement alarm response pr
Region: IV | San Onofre | 9894 | 06/17/2010 07/30/2010 | 2010006-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to provide adequate procedure for boron dilution activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 |  | 71152B | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.5.1.1.a involving the failure to maintain adequate instructions in San Onofre Procedure SO23-3-2.4, "RCS Purification and De-borating Ion Exchanger Operation," Revisi
Region: IV | San Onofre | 9924 | 06/17/2010 07/30/2010 | 2010006-07 | NRC | NCV | Public Radiation Safety | Green | Failure to establish component cooling water radiation monitoring procedures. |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a noncited violation of Technical Specification 5.5.1.1.a, "Scope," involving the failure to establish procedures for component cooling water system alignments such that leakage of radionuclides to the environment would be monito
Region: IV | San Onofre | 9916 | 06/17/2010 07/30/2010 | 2010006-08 | NRC | VIO | Mitigating Systems | Green | Failure to maintain written procedures covered in Regulatory Guide 1.33 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a cited violation of Technical Specification 5.5.1.1.a, involving the failure to maintain adequate written procedures. Specifically, as of April 23, 2010, the licensee's controls over its backlog of procedure change requests asso
Region: IV | San Onofre | 9917 | 06/17/2010 07/30/2010 | 2010006-09 | NRC | NCV | Mitigating Systems | Green | Failure to establish goals and monitor for Auxiliary Feedwater trains |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | Two examples of a noncited violation of 10 CFR 50.65(a)(1) were identified involving the failure to monitor the unavailability time associated with equipment failures which were maintenance induced. The first example involved maintenance inadvertently ben
Region: IV | San Onofre | 9918 | 06/17/2010 07/30/2010 | 2010006-10 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct the use of deficient relays. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," in that, from October 2008 to April 2010, the licensee failed to promptly identify and correct potentially degraded motor-driven relays in sa
Region: IV | San Onofre | 9895 | 06/17/2010 07/30/2010 | 2010006-11 | NRC | NCV | Initiating Events | Green | Failure to secure loose items in the electrical switchyard |  | H.3(a) Work Planning | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a noncitied violation of Technical Specification 5.5.1.1.a involving the failure to follow procedural guidance of SO123 XX-11, "Switchyard Work Performance." Specifically, the inspectors identified temporary equipment stored in t
Region: IV | San Onofre | 9923 | 06/17/2010 07/30/2010 | 2010006-12 | NRC | NCV | Mitigating Systems | Green | Failure to maintain design basis information |  | P.2(b) Implementing Operating Experience | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure to translate nonconservative errors in calculations and procedures identified during review of external operating experien
Region: IV | San Onofre | 9831 | 06/17/2010 07/30/2010 | 2010006-13 | NRC | FIN | MISC | Green | Failure to meet action plan for substantive crosscutting issues |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The inspectors identified a Green finding associated with the licensee's failure to meet the actions described to the NRC in letters dated April 21, 2009, and October 29 and 30, 2009, addressing corrective actions to improve site performance in the areas
Region: IV | San Onofre | 9863 | 02/26/2010 05/04/2010 | 2010002-13 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Station Work Order |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to follow Work Order 800195196 and provide appropriate oversight to transmission
Region: IV | San Onofre | 9847 | 02/18/2010 05/04/2010 | 2010002-04 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Electrical Switchyard Impacting Maintenance |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4), "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," involving multiple instances where operations and work control personnel failed to adequately ass
Region: IV | San Onofre | 9853 | 02/12/2010 05/04/2010 | 2010002-08 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Appropriately Control Access to a Locked High Radiation Area |  |  | TE?: N | 05000361 San Onofre 2 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specification 5.8.2 for the failure of radiation protection personnel to provide a locked door sufficient to prevent unauthorized entry into an area with radiation doses greater than 1.0 rem in 1
Region: IV | San Onofre | 9864 | 01/27/2010 05/04/2010 | 2010002-14 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Operations Procedure to Monitor Component Cooling Water Surge Tank pressure |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified for the failure of operations personnel to follow procedures for operating the component cooling water system. Specifically, on January 27, 2010, operations personnel fa
Region: IV | San Onofre | 9833 | 01/22/2010 03/02/2010 | 2009009-01 | NRC | NCV | Initiating Events | Green | Failure to Follow a Level 1 Quality Assurance Program Affecting Human Performance Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of training personnel to ensure activities affecting quality shall be prescribed by documented instructio
Region: IV | San Onofre | 9834 | 01/22/2010 03/02/2010 | 2009009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Written Procedures Covered in Regulatory Guide 1.33 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 5.5.1, "Procedures," for the failure of procedure writer personnel to maintain written procedures covered in Regulatory Guide 1.33. Specifically, from initial plant startup of Unit
Region: IV | San Onofre | 9845 | 01/21/2010 05/04/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Appropriately Scope Auxiliary Feedwater Pump Trench Eductors in the Maintenance Rule Monitoring Program |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(b)(2)(ii) for the licensee's failure to appropriately scope the steam driven auxiliary feedwater pump trench eductor in the maintenance rule monitoring program. Specifically, from the inceptio
Region: IV | San Onofre | 9848 | 01/15/2010 05/04/2010 | 2010002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in an Inadequate Operability Determination |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawing," for the failure of operations personnel to follow procedures to approve and document operability determinati
Region: IV | San Onofre | 9852 | 01/13/2010 05/04/2010 | 2010002-07 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Implement Foreign Material Exclusion Controls |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to adequately implement procedures SO123-I-3.7, "Refueling Foreign Material Exclusi
Region: IV | San Onofre | 9844 | 01/04/2010 05/04/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | Failure to Implement Fire Protection Plan Requirements Related to Hot Work Activities |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.05Q | The inspectors identified three examples of a noncited violation of Technical Specification 5.5.1.1.d, for the failure of contractor and station personnel to properly implement the requirements of a station fire protection procedure for control of hot wor
Region: IV | San Onofre | 9859 | 01/04/2010 05/04/2010 | 2010002-12 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Conditions Adverse to Quality into the Corrective Action Program |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of licensee personnel to follow procedure SO123-XV-50.CAP-1, "Writing Nuclear Notifications for Problem Id
Region: IV | San Onofre | 9840 | 12/31/2009 02/11/2010 | 2009005-10 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Safety-Related Electrical Connections |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | NONE | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with thirteen examples that occurred between June 2005 and July 2008, for the failure of the licensee to ensure that appropriate measures were i
Region: IV | San Onofre | 9838 | 12/31/2009 03/04/2010 | 2009007-01 | NRC | NCV | Barrier Integrity | Green | Failure to Adequately Store and Preserve Materials Used in Safety-Related Concrete |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 |  | 50001 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XIII, "Handling, Storage and Shipping," for the failure of contractor personnel to establish measures to ensure adequate controls for the storage and preservation of m
Region: IV | San Onofre | 9839 | 12/31/2009 03/04/2010 | 2009007-02 | NRC | NCV | Barrier Integrity | Green | Incorrect Mixing and Batching Associated with Concrete |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 |  | 50001 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," for the failure of contractor personnel to follow procedures to ensure proper mixing and batching of safety-related concret
Region: IV | San Onofre | 9846 | 12/17/2009 05/04/2010 | 2010002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Enter Operating Experience into Corrective Action Program for Timely Evaluation |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to properly implement procedure requirements to ensure that applicable risk significant operati
Region: IV | San Onofre | 9824 | 12/07/2009 02/11/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Identify Problems in Corrective Action Program |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure of engineering personnel to adequately identify for correction conditions adverse to quality between November 10 and December 1,
Region: IV | San Onofre | 9827 | 11/25/2009 02/11/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Operability Determination Process |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified three examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations and engineering personnel to follow procedures and adequately evaluate degr
Region: IV | San Onofre | 9823 | 11/10/2009 02/11/2010 | 2009005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Notification in a Timely Manner |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 |  | 71111.06 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," for the failure of operations personnel to initiate a nuclear notification within the required timeframe. Specifically, on Sep
Region: IV | San Onofre | 9826 | 10/27/2009 02/11/2010 | 2009005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Problems with Emergency Diesel Generator Train A |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000362 San Onofre 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions for conditions adverse to quality associated with Unit 3 emergency diesel gene
Region: IV | San Onofre | 9849 | 10/25/2009 05/04/2010 | 2010002-06 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Postmaintenance Test |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.19 | A self-revealing Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified for failure of maintenance planning personnel to develop and specify an adequate postmaintenance test in the wor
Region: IV | San Onofre | 9825 | 09/29/2009 02/11/2010 | 2009005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Problems with Emergency Diesel Generator Train B |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take adequate corrective actions for conditions adverse to quality associated with Unit 3 emergency diesel gene
Region: IV | San Onofre | 9815 | 09/28/2009 11/05/2009 | 2009004-02 | NRC | VIO | Initiating Events | Green | Failure to Assess and Manage Risk for Maintenance That Could Impact Offsite Power Components | EA Case: 2009270 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000361 San Onofre 2 |  | 71111.13 | The inspectors identified a cited violation of 10 CFR 50.65(a)(4) for the failure of work control and operations personnel to adequately assess and manage the increase in risk associated with maintenance activities. Specifically, on August 25-27, 2009, wo
Region: IV | San Onofre | 9829 | 09/13/2009 02/11/2010 | 2009005-07 | NRC | FIN | Initiating Events | Green | Inadequate Circulating Water System Maintenance Procedures Contribute to Unit 2 Inadvertent Reactor Trip |  | H.3(b) Work Activity Coordination | TE?: N | 05000361 San Onofre 2 |  | 71153 | The inspectors identified a finding for the failure of maintenance personnel to use the standards described in Procedure SO23-XV-2, "Troubleshooting Plant Equipment and Systems," in developing procedures and work plans to adequately perform, test, and com
Region: IV | San Onofre | 9828 | 09/09/2009 02/11/2010 | 2009005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement Compensatory Measures to Maintain Equipment Operable |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations personnel to follow procedures and adequately implement identified compensatory measures. Spe
Region: IV | San Onofre | 9830 | 09/01/2009 02/11/2010 | 2009005-08 | NRC | FIN | Initiating Events | Green | Unit 2 Heat Treat Pre-job Brief Not Performed in Accordance with Procedural Requirements |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 71153 | The inspectors identified a finding for the failure of operations personnel to perform an adequate pre-job brief in accordance with procedural requirements for a planned Unit 2 heat treat evolution. Specifically, on September 13, 2009, operations personne
Region: IV | San Onofre | 9813 | 06/05/2009 07/31/2009 | 2009003-09 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Written Procedures Covered in Regulatory Guide 1.33 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified 54 examples of a noncited violation of Technical Specification 5.5.1, "Procedures," for the failure of operations and maintenance personnel to maintain written procedures covered in Regulatory Guide 1.33. Specifically, from plant
Region: IV | San Onofre | 9798 | 06/02/2009 07/31/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Impact of Temporary Scaffolding on Installed Fire Protection Systems |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.05Q | The inspectors identified a noncited violation of License Condition 2.C.(14), "Fire Protection," for the failure of licensee personnel to evaluate scaffolding for its impact on fire protection systems. Specifically, the licensee failed either (1) to demon
Region: IV | San Onofre | 9818 | 06/02/2009 11/05/2009 | 2009004-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Specify Appropriate Requirements in Procurement Documents |  |  | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion IV, "Procurement Document Control," was identified for the failure of procurement engineering personnel to include requirements necessary to assure adequate quality in a safety-r
Region: IV | San Onofre | 9816 | 05/14/2009 11/05/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Process for an Inadequate Postmaintenance Test |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow corrective action program procedures to address deficiencies associated with postmain
Region: IV | San Onofre | 9809 | 05/06/2009 07/31/2009 | 2009003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Operability Determination in a Timely Manner on Safety-Related Equipment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to follow procedures to evaluate the operability of an identified nonconforming co
Region: IV | San Onofre | 9810 | 04/17/2009 07/31/2009 | 2009003-06 | NRC | NCV | Mitigating Systems | Green | Improper Controls for Electrical Test Equipment |  | H.4(b) Procedural Compliance | TE?: N | 05000362 San Onofre 3 |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance planning personnel to provide adequate work instructions to control the connection of elect
Region: IV | San Onofre | 9804 | 04/16/2009 07/31/2009 | 2009003-04 | NRC | NCV | Initiating Events | Green | Failure to Assess and Manage Risk for Electrical Switchyard Impacting Maintenance |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) for the failure of work control and operations personnel to include maintenance activities in or near the electrical switchyard and offsite power components in the on-line risk assessmen
Region: IV | San Onofre | 9803 | 04/13/2009 07/31/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Risk Assessment Performed Using Risk Assessment Tools with Known Errors |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) involving the failure of work control and operations personnel to assess and manage the increase in risk associated with planned maintenance activities. Specifically, the risk assessment
Region: IV | San Onofre | 9812 | 03/28/2009 07/31/2009 | 2009003-08 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Adequate Scaffolding Erection Procedures |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to establish adequate procedures for scaffolding erection in safety-related areas
Region: IV | San Onofre | 9794 | 03/17/2009 05/04/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Inspect Scaffolding in Safety-Related Areas |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.18 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of maintenance personnel to properly install and inspect scaffolding in safety-related areas in accordanc
Region: IV | San Onofre | 9802 | 03/11/2009 07/31/2009 | 2009003-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Corrective Actions to Prevent Repeat Safety-Related 480V Breaker Failures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.12 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to implement timely corrective actions to preclude repetition of a significant condition adverse to quality involving the
Region: IV | San Onofre | 9781 | 02/12/2009 05/04/2009 | 2009002-04 | NRC | NCV | Initiating Events | Green | Inadequate Procedure for Reactivity Manipulations |  | H.3(a) Work Planning | TE?: N | 05000361 San Onofre 2 |  | 71111.19 | The inspectors identified a non-cited violation of Technical Specification 5.5.1.1 for the failure of operations personnel to follow procedures for performing reactivity manipulations. Specifically, a procedure modification performed to Procedure SO23-3-2
Region: IV | San Onofre | 9796 | 02/07/2009 05/04/2009 | 2009002-06 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Follow Procedures to Reassemble a Reactor Coolant System Pressure Retaining Component |  | H.3(b) Work Activity Coordination | TE?: N | 05000361 San Onofre 2 |  | 71153 | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the failure of work control and maintenance personnel to follow the procedure requirements for work on a reactor c
Region: IV | San Onofre | 9782 | 02/07/2009 05/04/2009 | 2009002-07 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure for Aligning a Reactor Coolant System Ion Exchanger |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71153 | A self-revealing non-cited violation of Technical Specification 5.5.1.1 was identified for the failure of operations personnel to follow procedures to place Ion Exchanger ME074 in service which resulted in an interruption of letdown flow and diversion of
Region: IV | San Onofre | 9793 | 01/21/2009 05/04/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement the Operability Determination Process |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations and engineering personnel to follow procedures and adequately evaluate degraded conditions t
Region: IV | San Onofre | 9327 | 12/31/2008 02/12/2009 | 2008005-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Inspection of Stator Water Discharge Check Valve |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 |  | 71111.12 | A self-revealing finding was identified for the failure to perform an adequate inspection of a main generator stator water pump discharge check valve in accordance with maintenance procedures. The inadequate inspection allowed an unrecognized degraded con
Region: IV | San Onofre | 9328 | 12/31/2008 02/12/2009 | 2008005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Justify Longer Completion Schedule for Degraded Equipment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 71111.2 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of work control personnel to resolve degraded or nonconforming conditions at the first available opportuni
Region: IV | San Onofre | 9779 | 12/31/2008 02/12/2009 | 2008005-04 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Implementation for Corrective Action on Degraded Source Handling Tool |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 71153 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified because Nuclear Fuel Services personnel did not properly implement procedural controls to adequately evaluate o
Region: IV | San Onofre | 9792 | 12/09/2008 05/04/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures when Performing Maintenance on the Auxiliary Feedwater System |  | H.4(b) Procedural Compliance | TE?: N | 05000362 San Onofre 3 |  | 71111.12 | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," was identified for the failure of maintenance personnel to follow maintenance order instructions to fully remove fuses to establish c
Region: IV | San Onofre | 9811 | 11/04/2008 07/31/2009 | 2009003-07 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures for Safety-Related Painting Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000362 San Onofre 3 |  | 71152 | The inspectors identified two examples of a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of contract maintenance personnel to follow procedures while performing safety-related pai
Region: IV | San Onofre | 9317 | 10/22/2008 12/03/2008 | 2008012-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Maintenance Procedures Results in a Ground on the Safety-Related 125 VDC Distribution System |  | H.3(a) Work Planning | TE?: N | 05000361 San Onofre 2 |  | 71152B | A self-revealing noncited violation of Technical Specification 5.5.1, "Procedures," was identified for the failure of maintenance personnel to have adequate procedures. Specifically, on January 24, 2008, during maintenance on a flood detector switch, an i
Region: IV | San Onofre | 9318 | 10/22/2008 12/03/2008 | 2008012-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Operability Determination Process |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000362 San Onofre 3 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations personnel to follow procedures and adequately evaluate a degraded condition. Specifically, on Augus
Region: IV | San Onofre | 9325 | 10/22/2008 12/03/2008 | 2008012-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Auxiliary Feedwater Pump Room Heat Load Analysis |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of engineering personnel to ensure the auxiliary feedwater pump room heat load calculation was adequate. Specifically, since initial p
Region: IV | San Onofre | 9310 | 09/11/2008 10/24/2008 | 2008010-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Battery Performance Test Issues |  |  | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify, evaluate, or correct conditions adverse to quality. Specifically, in 2007 the licensee failed to recognize, evaluate, or write
Region: IV | San Onofre | 9308 | 09/11/2008 10/24/2008 | 2008010-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures During the Battery Performance Tests |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 7111121 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instruction, Procedures, and Drawings," for failure to follow procedures while performing the battery performance tests. Specifically, on four occasions, performance tests fo
Region: IV | San Onofre | 9309 | 09/11/2008 10/24/2008 | 2008010-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for 480 VAC System Grounds |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of Technical Specification 5.5.1.a for inadequate procedures for 480 Volts Alternating Current system grounds. Specifically, the procedures do not identify the deleterious effects of 480 Volts Alternating Current s
Region: IV | San Onofre | 9315 | 09/11/2008 10/24/2008 | 2008010-07 | NRC | NCV | Initiating Events | Green | Inadequate Corrective Actions for Reactivity Events |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure of operations management, operations training, and engineering to ensure that conditions adverse to quality are promptly identifie
Region: IV | San Onofre | 9300 | 09/03/2008 10/24/2008 | 2008010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for Design Basis of CCW/CWR Heat Exchangers |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for failure to ensure that plant conditions were consistent with design calculation inputs and assumptions (rate of established component cooling water hea
Region: IV | San Onofre | 9307 | 09/03/2008 10/24/2008 | 2008010-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control for 125VDC Control Circuits |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," for failure to properly analyze voltage drop in 125 Volts Direct Current control circuits. Specifically, the licensee failed to consider and analyze the vo
Region: IV | San Onofre | 9283 | 08/26/2008 10/30/2008 | 2008004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Procedure to Move Nuclear Fuel in the Spent Fuel Pool |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71153 | Two examples of a self-revealing noncited violation of 10 CFR 50, Appendix B, Criterion V, were identified for the failure of engineering personnel to follow procedures for the movement of nuclear fuel in the spent fuel pool. Specifically, on July 3, 2008
Region: IV | San Onofre | 9275 | 06/18/2008 08/08/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Air Supply Equalizing Valve Not Secured Closed Due To Failure To Follow Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.04Q | The inspectors identified a noncited violation of Technical Specification 5.5.1.1 for the failure of operations personnel to follow Procedure SO23-2-8.1,"Saltwater Cooling System Alignments," Revision 7. Specifically, on June 17, 2008, inspectors identifi
Region: IV | San Onofre | 9277 | 06/03/2008 08/08/2008 | 2008003-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Properly Monitor and Execute a Unit 2 Reactivity Manipulation. |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71111.13 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, (Procedures) was identified for the failure of operations personnel to understand, monitor and perform a Unit 2 reactivity manipulation in accordance with procedural requireme
Region: IV | San Onofre | 9280 | 06/03/2008 08/08/2008 | 2008003-04 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement the Operability Determination Process. |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure of operations and engineering personnel to follow procedures and adequately evaluate degraded, nonconformin
Region: IV | San Onofre | 9281 | 06/03/2008 08/08/2008 | 2008003-05 | NRC | NCV | Mitigating Systems | Green | Component Cooling Water heat exchanger not operable due to Inadequate Maintenance Procedure. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000362 San Onofre 3 |  | 71111.19 | The inspectors identified a noncited violation of Technical Specification 5.5.1.1 for the failure of maintenance personnel to have adequate procedures in place to ensure maintenance associated with a saltwater cooling isolation butterfly valve would not a
Region: IV | San Onofre | 9795 | 06/01/2008 05/04/2009 | 2009002-05 | NRC | NCV | Initiating Events | Green | Failure to Properly Evaluate Boric Acid Leakage from the Reactor Coolant Pump Vapor Seal |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000361 San Onofre 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of engineering personnel to properly perform an evaluation of reactor coolant pump vapor seal boric acid
Region: IV | San Onofre | 9282 | 04/10/2008 08/08/2008 | 2008003-06 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement Procedural Requirements for Planned Unit 2 Power Reduction. |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000361 San Onofre 2 |  | 71152 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified associated with the failure to implement procedural guidance to ensure a Unit 2 power reduction was properly performed. Lack of supervisory oversight resulted in an unco
Region: IV | San Onofre | 9276 | 04/03/2008 08/08/2008 | 2008003-02 | Self - Revealed | NCV | Initiating Events | Green | Pressurizer Pressure Transient due to Inadequate Maintenance Procedure. |  | H.3(b) Work Activity Coordination | TE?: N | 05000362 San Onofre 3 |  | 71111.13 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified for the failure of maintenance personnel to have adequate procedures in place to ensure troubleshooting associated with proportional heater Bank 3E123 would not adversel
Region: IV | San Onofre | 9297 | 04/01/2008 12/19/2008 | 2008013-08 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 93812 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to establish measures to assure that deficient electrical connections were promptly identified and corrected. The
Region: IV | San Onofre | 9286 | 03/25/2008 12/19/2008 | 2008013-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Delays Entry Into Technical Specification Condition |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 |  | 93812 | The team identified a Green noncited violation of Technical Specification 5.5.1.1 involving the failure of an electrical maintenance supervisor to follow procedures after notification that Battery 2B008 terminal voltage was less than the TS required value
Region: IV | San Onofre | 9287 | 03/25/2008 12/19/2008 | 2008013-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Work Control Process to Perform Troubleshooting |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000361 San Onofre 2 |  | 93812 | The team identified a Green noncited violation of Technical Specification 5.5.1.1, for the failure of electrical maintenance personnel to follow Procedure SO123-XX-1, "Action Request/Maintenance Order Initiation and Processing," Revision 20. Specifically,
Region: IV | San Onofre | 9288 | 03/25/2008 12/19/2008 | 2008013-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Work Control Process |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | NONE | The team identified a Green noncited violation of Technical Specification 5.5.1.1, for the failure of electrical maintenance personnel to follow Procedure SO123-XX-5, "Work Authorizations," Revision 17. Specifically, work to correct the identified degrade
Region: IV | San Onofre | 9240 | 03/25/2008 12/19/2008 | 2008013-04 | NRC | NCV | Initiating Events | Green | Inadequate Implementation of Risk Assessment and Risk Management Actions for Emergent Work Activities |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The team identified a Green noncited violation of 10 CFR Part 50.65(a)(4) involving the failure to adequately assess the increase in risk and effectively implement risk mitigation actions for emergent maintenance activities. Specifically, on March 25 and
Region: IV | San Onofre | 9298 | 03/25/2008 12/19/2008 | 2008013-09 | NRC | NCV | Mitigating Systems | Green | Lack of Written Procedures for a Loss of 125 Vdc Bus |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The team identified a Green noncited violation of Technical Specification 5.5.1.1 for the failure to establish written procedures for a loss or degradation of a safety-related electrical power source. Specifically, no procedural guidance was provided to o
Region: IV | San Onofre | 9269 | 03/24/2008 05/06/2008 | 2008002-01 | Self - Revealed | FIN | Initiating Events | Green | Unit 2 Main Feedwater Pump Trip Results in Inadvertent Power Reduction |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 |  | 71111.22 | The inspectors identified a Green self-revealing finding for the failure of maintenance personnel to adequately adjust bearing oil pressure to a Unit 2 main feedwater pump. This caused the main feedwater pump to trip, which subsequently caused an unplanne
Region: IV | San Onofre | 9270 | 01/12/2008 05/22/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Operability Procedure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000362 San Onofre 3 |  | 93812 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure of operations personnel to meet operability determination procedural requirements following unexplai
Region: IV | San Onofre | 9274 | 01/12/2008 05/22/2008 | 2008006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Test Procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000362 San Onofre 3 |  | 93812 | The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 for an inadequate monthly Surveillance Test Procedure SO23-3-3.23, "Diesel Generator Monthly and Semi-Annual Testing," Revision 30. The licensee failed to provide adeq
Region: IV | San Onofre | 9263 | 12/31/2007 02/13/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Implement Maintenance Rule Requirements for EDG AVRs |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.12 | Green. The inspectors identified a Green noncited violation of 10 CFR 50.65(a)(1) for the failure to include Units 2 and 3 emergency diesel generator automatic voltage regulator deficiencies as functional failures in the maintenance rule program. The insp
Region: IV | San Onofre | 9264 | 12/31/2007 02/13/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedural Requirements for Draining the Auxiliary Feedwater Steam Supply Trench |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | Green. The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 for the failure of operations personnel to have adequate procedural guidance in place to ensure the proper application for use of a submersible pump to prevent
Region: IV | San Onofre | 9265 | 12/31/2007 02/13/2008 | 2007005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow a Radiation Exposure Permit Requirement |  | H.4(a) Human Error Prevention | TE?: N | 05000362 San Onofre 3 |  | 7112101 | Green. The inspector reviewed a self-revealing noncited violation of Technical Specification 5.5.1.1 when a worker failed to follow radiation work permit instructions. On July 14, 2007, after completing a pre-job site review, a worker proceeded to verify
Region: IV | San Onofre | 9268 | 12/31/2007 02/13/2008 | 2007005-04 | NRC | VIO | Mitigating Systems | Green | Failure to Prevent Recurrence of Premature Tripping of Square D Thermal Overloads |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | Green. A self revealing Green violation of 10 CFR Part 50, Appendix B, Criterion XVI, was identified for the failure to prevent recurrence of premature tripping of Square D thermal overloads used for equipment protection on safety-related equipment. The l
Region: IV | San Onofre | 9242 | 10/11/2007 10/19/2007 | 2007013-01 | Self - Revealed | FIN | Initiating Events | Green | Ineffective Corrective Actions for Instrument Air Header Ruptures |  | P.2(b) Implementing Operating Experience | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The inspectors reviewed a self-revealing Green finding involving ineffective corrective actions taken in response to site and industry operating experience with instrument air header ruptures. Specifically, contrary to Section 6.2.3 of Procedure SO-123-I-
Region: IV | San Onofre | 9243 | 10/11/2007 10/19/2007 | 2007013-02 | NRC | NCV | Initiating Events | Green | Failured to Follow Abnormal Operating Instruction in Response to a Loss of Instrument Air |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 involving the failure to meet procedural requirements following a loss of instrument air. Specifically, operators failed to monitor nitrogen tank levels or take precau
Region: IV | San Onofre | 9248 | 10/11/2007 10/19/2007 | 2007013-03 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Evaluation Results in CCW Pump Runout |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | A self-revealing, Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified when Unit 2 experienced a loss of instrument air due to the failure of a soldered joint. Specifically, the loss of instrument air res
Region: IV | San Onofre | 9249 | 10/11/2007 10/19/2007 | 2007013-04 | Self - Revealed | FIN | Mitigating Systems | Green | Ineffective Corrective Actions for a Failed Control Room Annunciator |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000361 San Onofre 2 05000362 San Onofre 3 05000362 San Onofre 3 |  | 93812 | The inspectors reviewed a self-revealing Green finding involving the failure to take effective corrective actions for a failed control room annunciator. Specifically, after the annunciator for actuation of the backup nitrogen supply to the instrument air
Region: IV | San Onofre | 9250 | 10/11/2007 10/19/2007 | 2007013-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Loss of Instrument Air |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 involving the failure to maintain an adequate abnormal operating instruction for a loss of instrument air event. The licensee entered this issue in their corrective ac
Region: IV | San Onofre | 9251 | 10/11/2007 10/19/2007 | 2007013-06 | Self - Revealed | NCV | Mitigating Systems | Green | Simulator Incorrectly Modeled Plant Response to Loss of Instrument Air |  | H.2(d) Facilities & Equipment | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | A self-revealing, Green noncited violation of 10 CFR Part 55.46(c)(1) was identified involving the licensee's failure to incorporate a design change in modeling plant response for the plant-referenced simulator. Specifically, during operator training in t
Region: IV | San Onofre | 9254 | 10/11/2007 10/19/2007 | 2007013-07 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for an Impaired Annunciator |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 involving the failure to meet procedural requirements governing impaired annunciators. Specifically, after the identification of a failed annunciator, operators did no
Region: IV | San Onofre | 9255 | 10/11/2007 10/19/2007 | 2007013-08 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate Implementation of Corrective Actions for Air Operated Valve Regulators |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 93812 | A Green self-revealing finding was identified associated with the failure of the reactor coolant pump controlled bleed off valve to shut during a loss of instrument air event. The licensee failed to adequately implement corrective actions from previously
Region: IV | San Onofre | 9256 | 09/27/2007 11/09/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Operating Experience for Missing Nuts in 4kV Electrical Breakers |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion V (Procedures) for the failure to follow requirements for evaluating applicable 4 kV breaker operating experience. Engineers had inappropriately determined that operating e
Region: IV | San Onofre | 9257 | 09/27/2007 11/09/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate corrective Actions to Prevent Water Intrusion into auxiliary Feedwater Valve Cabinet 3MS4706 |  |  | TE?: N | 05000362 San Onofre 3 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Actions) for the failure to prevent the recurrence of a significant condition adverse to quality, water intrusion into auxiliary feedwater electrical C
Region: IV | San Onofre | 9262 | 09/27/2007 11/09/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Main Feedwater Isolation Valve Hydraulic Leak due to Inadequte Maintenance Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 71111.19 | The inspectors identified a Green noncited violation of Technical Specification 5.5.1.1 (Procedures) for the failure of maintenance personnel to have adequate procedures in place to ensure a feedwater isolation valve hydraulic pump discharge filter housin
Region: IV | San Onofre | 9237 | 06/26/2007 08/09/2007 | 2007003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Gas Accumulation in the Units 2 and 3 Component Cooling Water Systems |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and correct the formation of gas pockets in the piping of the Units 2 and 3 component cooling water systems from
Region: IV | San Onofre | 9238 | 06/26/2007 08/09/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Deficient Emergency Diesel Generator Potentiometers |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly correct a common cause problem associated with debris intrusion into potentiometers in the automatic voltag
Region: IV | San Onofre | 9239 | 06/15/2007 07/24/2007 | 2007008-01 | NRC | URI | Mitigating Systems | Green | Review Adequacy of Manual Action Completion Times for Control Room Evacuation |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.05T
Region: IV | San Onofre | 9241 | 06/15/2007 07/24/2007 | 2007008-02 | NRC | NCV | Mitigating Systems | Green | Fire Separation in Fire Area 2/3-AC-50-29 Did Not Comply With Deviation Request. |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.05T | A noncited violation of License Condition 2.C.(14), "Fire Protection," was identified for failure to ensure that redundant trains of safe shutdown equipment would remain free of fire damage in Fire Area 2-AC-50-29. Specifically, the cables for redundant t
Region: IV | San Onofre | 9234 | 03/31/2007 04/27/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow an Abnormal Operating Instruction in Response to High Offsite Power Grid Voltage |  | H.2(d) Facilities & Equipment | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification 5.5.1.1 for the failure of operations personnel to enter and implement abnormal operating Instruction SO23-13-4, "Operation During Major System Disturbances," on multiple occasions from 2004
Region: IV | San Onofre | 9236 | 03/31/2007 04/27/2007 | 2007002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Instructions Results in Dose Rate Alarm |  | H.4(a) Human Error Prevention | TE?: N | 05000362 San Onofre 3 |  | 7112101 | A self-revealing, noncited violation of Technical Specification 5.5.1 was processed regarding the failure to follow written instructions in a radiation exposure permit. A worker received an electronic dosimeter alarm on dose rate when the worker entered a
Region: IV | San Onofre | 9235 | 02/13/2007 04/27/2007 | 2007002-02 | NRC | NCV | Barrier Integrity | Green | Loss of Spent Fuel Pool Cooling due to Inadequate Temporary Ventilation Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 71111.15 | The inspectors identified a Green NCV of Technical Specification 5.5.1.1 for the failure of operations personnel to have adequate procedures in place to establish temporary ventilation in the safety-related switchgear rooms when the normal ventilation sys
Region: IV | San Onofre | 9225 | 12/31/2006 02/06/2007 | 2006005-01 | NRC | NCV | Occupational Radiation Safety | Green | INADEQUATE CONTAINMENT AIRBORNE RADIOACTIVITY BRIEFING |  | H.4(a) Human Error Prevention | TE?: N | 05000362 San Onofre 3 05000362 San Onofre 3 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR 19.12 for the failure of health physics personnel to adequately inform workers of the radiological conditions of the Unit 3 containment on October 23, 2006. A contract health physics technician and
Region: IV | San Onofre | 9226 | 12/31/2006 02/06/2007 | 2006005-02 | Self - Revealed | NCV | Initiating Events | Green | UNPLANNED POWER INCREASE RESULTS IN VIOLATION OF TECHNICAL SPECIFICATIONS |  | H.4(b) Procedural Compliance | TE?: N | 05000362 San Onofre 3 05000362 San Onofre 3 |  | 71111.22 | A self-revealing noncited violation of Technical Specification 5.5.1.1 was identified for the failure of operations personnel to follow procedures while diluting the reactor coolant system. This resulted in the Technical Specification required surveillanc
Region: IV | San Onofre | 9232 | 12/31/2006 02/06/2007 | 2006005-03 | NRC | NCV | Occupational Radiation Safety | Green | FAILURE TO ADEQUATELY LABEL A CONTAINER OF RADIOACTIVE MATERIAL |  | H.4(a) Human Error Prevention | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7112101 | The inspector identified a noncited violation of 10 CFR 20.1904(a) because the licensee failed to adequately label a container of radioactive material. On August 4, 2006, a vial of spent resin that had a dose rate of 5 millirem per hour on contact and con
Region: IV | San Onofre | 9233 | 12/31/2006 02/06/2007 | 2006005-04 | NRC | NCV | Mitigating Systems | Green | FAILURE TO PREVENT RECURRENCE OF PREMATURE TRIPPING OF SQUARE D THERMAL OVERLOADS |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to prevent recurrence of a significant condition adverse to quality involving the premature tripping of Square D therma
Region: IV | San Onofre | 9220 | 11/30/2006 12/08/2006 | 2006009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Diesel Ground Alarm Procedure |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of Technical Specification 5.5.1.a for an inadequate emergency diesel generator ground fault alarm response procedure. Specifically, the procedure had operators check for grounds associated with the emergency diese
Region: IV | San Onofre | 9221 | 11/30/2006 12/08/2006 | 2006009-03 | NRC | NCV | Mitigating Systems | Green | Incorrect Methodology for 125VDC Calculations |  |  | TE?: N | 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of Part 50 of Title 10 of the Code of Federal Regulations, Appendix B, Criterion III, Design Control, for the failure to properly calculate control circuit voltages associated with the Unit 3 motor-driven auxiliary
Region: IV | San Onofre | 9222 | 11/30/2006 12/08/2006 | 2006009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Air Voids in Safeety Injection Suction Piping |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of the Code of Federal Regulations, Title 10, Part 50, Appendix B, Criterion XVI, Corrective Actions, for the failure to promptly identify a condition adverse to quality (trapped air in the safety injection suction
Region: IV | San Onofre | 9224 | 11/30/2006 12/08/2006 | 2006009-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Diesel Generator Seismic Nonconformance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a Code of Federal Regulations, Title 10, Part 50, Appendix B, Criterion XVI, Corrective Actions, violation for the failure to promptly identify a condition adverse to quality (Train A emergency diesel generators lost seismic qualificat
Region: IV | San Onofre | 9219 | 07/12/2006 12/08/2006 | 2006009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Addressing Foreign Material Exclusion |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 7111121 | The team identified a noncited violation of Part 50 of Title 10 of the Code of Federal Regulations, Appendix B, Criterion V, Procedures, for the failure to follow procedural requirements and establish the Units 2 and 3 CST-120 condensate storage tank encl
Region: IV | San Onofre | 9203 | 03/25/2006 07/14/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Safety Injection Tank Manway Gaskets |  |  | TE?: N | 05000361 San Onofre 2 05000362 San Onofre 3 |  | 71111.12 | A self-revealing, noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified for the failure to select an appropriate replacement gasket for the Units 2 and 3 safety injection tank manways. The inadequate gaskets buc
Region: IV | San Onofre | 9202 | 03/19/2006 07/14/2006 | 2006003-01 | Self - Revealed | NCV | Initiating Events | Green | Inadvertent Reactor Coolant System Drainage while in Mode 5 |  | H.4(b) Procedural Compliance | TE?: N | 05000361 San Onofre 2 |  | 71111.04Q | A self revealing, noncited violation of Technical Specification 5.5.1.1 was identified for the failure of operations personnel to operate reactor coolant pump system vent valves with the use of approved procedures. This failure resulted in the inadvertent
Region: IV | San Onofre | 9213 | 03/12/2006 11/01/2006 | 2006004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Evaluate Radiological Conditions |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000361 San Onofre 2 |  | 7112102 | The inspectors reviewed a self-revealing, noncited violation of 10 CFR Part 20.1501(a), resulting from the licensee's failure to adequately evaluate radiological conditions in a work area. While assisting in decontaminating the reactor cavity on March 12,
Region: IV | South Texas Project | 126620 | 12/31/2019 01/29/2020 | 2019004-02 | NRC | NCV | Initiating Events | Green | Failure to Perform a Risk Assessment Prior to Performing Maintenance |  | H.5 - Work Management | TE?: N | 05000498 South Texas 1 | Human Performance | 71152 | The inspectors identified Green finding and associated non-cited violation of 10 CFR 50.65(a)(4) when the licensee failed to perform a risk assessment prior to performing maintenance. Specifically, inspectors identified breaker relay calibrations being pe
Region: IV | South Texas Project | 126621 | 12/31/2019 01/29/2020 | 2019004-03 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Work Instruction Results in Loss of Spent Fuel Pool Cooling |  | H.8 - Procedure Adherence | TE?: N | 05000499 South Texas 2 | SSC Performance | 71152 | A self-revealed Green finding and associated non-cited violation of Technical Specification 6.8.1.a, Regulatory Guide 1.33, Section 9, was identified for the failure to provide adequate work instruction for maintenance associated with an engineered safety
Region: IV | South Texas Project | 126629 | 12/31/2019 01/29/2020 | 2019004-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Work Instructions Result in Reactor Coolant System Leaks |  | H.5 - Work Management | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Equipment Performance | 71152 | A self-revealed Green finding and associated non-cited violation of Technical Specification 6.8.1.a was identified for the failure to provide adequate work instruction for compression fitting connections that resulted in reactor coolant system leakage. S
Region: IV | South Texas Project | 126630 | 12/31/2019 01/29/2020 | 2019004-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Two Inoperable Emergency Diesel Generators |  | H.11 - Challenge the Unknown | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Equipment Performance | 71152 | A self-revealed, Green finding and associated non-cited violation of Technical Specification 6.8.1.a, Regulatory Guide 1.33, Section 3.s.2.a, was identified for the failure to follow emergency diesel generator (EDG) testing procedure, which resulted in tw
Region: IV | South Texas Project | 125959 | 09/30/2019 10/30/2019 | 2019003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Maintenance Rule (a)(1) Goals for Safety-Related Chillers |  | P.2 - Evaluation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Equipment Performance | 71111.12 | The inspectors identified a Green, non-cited violation (NCV) of 10 CFR 50.65(a)(1) for the licensee’s failure to establish goals commensurate with safety for equipment subject to the Maintenance Rule. Specifically, once the essential chilled water system
Region: IV | South Texas Project | 125958 | 09/30/2019 10/30/2019 | 2019003-02 | Self - Revealed | FIN | Initiating Events | Green | Failure to Follow Procedure Results in Load Rejection |  | H.4 - Teamwork | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Human Performance | 71152 | The inspectors reviewed a Green, self-revealed finding for the licensee’s failure to implement procedures for a surveillance resulting in a change in reactivity. Specifically, a licensed operator failed to adjust limits on the main steam governor valves d
Region: IV | South Texas Project | 125370 | 06/30/2019 08/08/2019 | 2019002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Operability Determination Procedure Results in a Technical Specification Violation |  | H.11 - Challenge the Unknown | TE?: N | 05000499 South Texas 2 | Human Performance | 71153 | The inspectors identified a Green non-cited violation of 10 CFR 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings” associated with the licensee’s failure to follow the operability procedure, 0POP01-ZO-0011, “Operability, Functionality,
Region: IV | South Texas Project | 125374 | 06/30/2019 08/08/2019 | 2019002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedural Guidance for Essential Cooling Water Pump Shaft Seal Leak Off Results in Technical Specification Violation |  | H.11 - Challenge the Unknown | TE?: N | 05000498 South Texas 1 | Equipment Performance | 71153 | A self-revealed Green finding and associated non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33, Revision 2, when the licensee failed to provide adequate procedures for maintenance on safety-related equipment. Specifically, m
Region: IV | South Texas Project | 124935 | 04/11/2019 05/23/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions for Distribution Panel Molded Case Circuit Breaker Testing |  | H.4 - Teamwork | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Design Control | 71111.21M | The inspectors identified a Green non-cited violation for the failure to assure that conditions adverse to quality, such as failures, malfunctions, deficiencies, deviations, defective material and equipment, and nonconformances are promptly identifi
Region: IV | South Texas Project | 124936 | 04/11/2019 05/23/2019 | 2019010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Design Changes into Emergency Procedures and the Updated Final Safety Analysis |  | H.4 - Teamwork | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 | Design Control | 71111.21M | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, “Design Control,” for the licensee’s failure to incorporate design changes into the plant design bases documentation and associated operating procedures.
Region: IV | South Texas Project | 124763 | 03/31/2019 05/08/2019 | 2019001-01 | NRC | FIN | Initiating Events | Green | Failure to Implement the Procedure for Equipment Failures |  | H.12 - Avoid Complacency | TE?: N | 05000499 South Texas 2 | Human Performance | 71152 | The inspectors identified a Green finding for the licensee’s failure to implement the procedure for the failure of a plant generation risk (PGR) high risk component. Specifically, the licensee failed to implement and follow Procedure WCG-0008, “Preventing
Region: IV | South Texas Project | 124764 | 03/31/2019 05/08/2019 | 2019001-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide Adequate Procedural Guidance for a Surveillance Test |  | H.12 - Avoid Complacency | TE?: N | 05000499 South Texas 2 | Procedure Quality | 71152 | The inspectors documented a Green self-revealed NCV for the failure to provide an adequate procedure for a Unit 2 qualified display processing system (QDPS) surveillance procedure that resulted in unnecessary troubleshooting, unnecessary replacement of pr
Region: IV | South Texas Project | 124768 | 10/02/2018 05/08/2019 |  |  | LIV |  | Green | LER 05000498/2018-001-00 for South Texas Project, Unit 1, Main Steam Safety Valve As Left Settings Outside of Required Range Contrary to Technical Specifications Due to Inadequate Procedure. |  |  | TE?: N | 05000498 South Texas 1 |  | 71153
Region: IV | South Texas Project | 24002 | 05/14/2018 05/14/2018 | 2018001-01 | NRC | NCV | Initiating Events | Green | Failure to Perform a Maintenance Risk Assessment Prior to Conducting Maintenance |  | H.1 - Resources | TE?: N | 05000498 South Texas 1 |  | 71111.13 | The inspectors identified Green, non-cited violation of 10 CFR 50.65(a)(4) for the failure to perform a maintenance risk assessment prior to performing maintenance that could have resulted in a reactor shutdown. Specifically, maintenance performed to inst
Region: IV | South Texas Project | 24003 | 05/14/2018 05/14/2018 | 2018001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality Associated with Reactor Containment Fan Coolers |  | H.1 - Resources | TE?: N | 05000499 South Texas 2 |  | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI for the failure to promptly identify and correct a condition adverse to quality. Specifically, the backdraft damper of the Unit 2, train B reactor containm
Region: IV | South Texas Project | 22680 | 12/31/2017 02/05/2018 | 2017004-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Control Equipment Configuration in Accordance with Procedures |  | H.4 - Teamwork | TE?: N | 05000499 South Texas 2 |  | 71152 | A self-revealed, Green, non-cited violation of Technical Specification 6.8.1.a, “Procedures,” was documented for the licensee’s failure to follow a procedure for equipment configuration control which resulted in a plant transient. Specifically, fro
Region: IV | South Texas Project | 23229 | 11/14/2017 12/13/2017 | 2017301-01 | NRC | NCV | Barrier Integrity | Green | Failure to Maintain the Plant Procedure for Control Room Logs |  | H.7 - Documentation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The team identified a non-cited violation of Technical Specification 6.8.1.a, due to the licensee’s failure to maintain the procedure for reactivity manipulation entries for the main control room logs. The "Conduct of Operations" Procedure, Revision 71, i
Region: IV | South Texas Project | 15926 | 09/07/2017 09/13/2017 | 2017010-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Conduct Drills In Accordance with the Site Emergency Plan |  | H.1 Resources | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) associated with the licensee's failure to conduct correctly scoped drills as required by the site emergency plan in 2015 and 2016. Annually, the licensee was required to conduct a radio
Region: IV | South Texas Project | 15914 | 06/30/2017 08/14/2017 | 2017002-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Establish Procedures to Remove Reactor Vessel Head Vent Rig Results In Loss of Reactor Coolant System Inventory |  | H.5 Work Management | TE?: N | 05000498 South Texas 1 |  | 71111.2 | The inspectors documented a self-revealed, non-cited violation of Technical Specification 6.8.1.a, Regulatory Guide 1.33, Revision 2, February 1978, Appendix A, Section 9.d.(4). Specifically, inadequate written work instructions to remove the reactor vess
Region: IV | South Texas Project | 15915 | 06/30/2017 08/14/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedures for Control of High-Energy Line Break Barriers |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to establish adequate procedures for the control of high-energy line break barriers. Specifically, on July 21
Region: IV | South Texas Project | 15925 | 06/30/2017 08/14/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Failure To Establish Adequate Procedures To Ensure Emergency Diesel Generator Access Flood Panels Would Meet Their Safety Function |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to provide adequate written instructions for performing preventative maintenance to ensure the emergency diese
Region: IV | South Texas Project | 15907 | 02/09/2017 03/20/2017 | 2017007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide 8-hour Emergency Lighting for All Alternative Shutdown Manual Actions |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.E for the failure to provide 8-hour emergency lighting in all areas where operators perform manual actions required during an alternative shutdown. As a compensatory measure, the licensee ad
Region: IV | South Texas Project | 15900 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Emergency Preparedness | Green | Implementation of a Protective Action Recommendation Strategy That Can Recommend Unnecessary Protective Actions for the Public |  | H.12 Avoid Complacency | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71114.05 | The inspectors identified a Green non-cited violation of 10 CFR 50.47(b)(10) for the failure between July 16, 2015, and September 8, 2016, to develop a range of protective actions for the plume exposure emergency planning zone for the public, considering
Region: IV | South Texas Project | 15901 | 08/26/2016 11/18/2016 | 2016009-01 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Update Procedure Reference Leads to Non-functional Unit 1 Technical Support Center Diesel Generator |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152B | The team is documenting a self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow Procedure 0PGP04-ZE-0309, "Design Change Package," Revision 2. Sp
Region: IV | South Texas Project | 15886 | 06/30/2016 08/11/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Scaffold Procedure to Ensure Safety-Related Equipment Not Impacted |  | P.6 Self Assessment | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to provide an adequate scaffold procedure to ensure that safety-related equipment would not be impacted.
Region: IV | South Texas Project | 15891 | 06/30/2016 08/11/2016 | 2016002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Control Steam Generator Water Levels at Low Power |  | H.9 Training | TE?: N | 05000498 South Texas 1 |  | 71152 | The inspectors documented a self-revealed, non-cited violation of Technical Specification 6.8.1.a, "Procedures," for failure to implement procedures for power operation as described in Regulatory Guide 1.33, Revision 2, Appendix A, Section 2.g, dated Febr
Region: IV | South Texas Project | 15861 | 03/31/2016 05/09/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Faulty NI-36 Channel |  | H.14 Conservative Bias | TE?: N | 05000498 South Texas 1 |  | 71152 | Inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to identify a condition adverse to quality. Specifically, the licensee failed to identify that a faulty logarithmic amplifier was producin
Region: IV | South Texas Project | 15862 | 03/09/2016 04/22/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Periodic Testing of Molded Case Circuit Breakers |  | H.13 Consistent Process | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "a test program shall assure that all testing required to demonstrate that structures, systems, and components will perfor
Region: IV | South Texas Project | 15863 | 03/09/2016 04/22/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequacy Calculations Associated with Direct Current Circuit Breakers |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified two examples of a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "the design control measures shall provide for verifying or checking the adequacy of design, such as by
Region: IV | South Texas Project | 15868 | 03/09/2016 04/22/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate On-going Class 1E Qualification for the Qualified Display Processing System |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR 50.55a(h)(2) "Protection Systems," which requires, in part, for nuclear power plants with construction permits issued after January 1, 1971, but before May 13, 1999, protection systems must meet t
Region: IV | South Texas Project | 15869 | 03/09/2016 04/22/2016 | 2016007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Control Software Tools Commensurate with the Importance to Safety |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XII, "Control of Measuring and Test Equipment," which states, "Measures shall be established to assure that tools, gages, instruments, and other measuring and testin
Region: IV | South Texas Project | 15870 | 03/09/2016 04/22/2016 | 2016007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Conditions Adverse to Quality Associated with the Eagle 21 System |  | H.14 Conservative Bias | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficie
Region: IV | South Texas Project | 15871 | 03/09/2016 04/22/2016 | 2016007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Administrative Controls for a Nonconservative Technical Specification of Standby Diesel Generator Frequency Variation |  | H.3 Change Management | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, defici
Region: IV | South Texas Project | 15876 | 03/09/2016 04/22/2016 | 2016007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Sufficient Capacity and Capability of Mitigating Systems during a Station Blackout Event |  | H.8 Procedure Adherence | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR 50.63(a)(2) which states, in part, "The reactor core and associated coolant, control, and protection systems, including station batteries and any other necessary support systems, must provide suff
Region: IV | South Texas Project | 15877 | 03/09/2016 04/22/2016 | 2016007-09 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Design Control Measures in Place to Mitigate a Loss of Normal Feedwater Flow Event |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "Measures shall be established to assure that applicable regulatory requirements and the design basis\x85for those
Region: IV | South Texas Project | 15885 | 03/09/2016 04/22/2016 | 2016007-10 | NRC | NCV | Initiating Events | Green | Failure to Correct Procedure Deficiencies Allowing Cooling Restoration to RCP Seals |  | P.2 Evaluation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.21M | The team identified a Green, non-cited violation of Technical Specification 6.8.1.a., "Procedures," which requires that written procedures shall be established, implemented, and maintained for procedures in Appendix A of Regulatory Guide 1.33, Revision 2,
Region: IV | South Texas Project | 15859 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | FIN | Mitigating Systems | Green | Failure to Track and Incorporate Actual Plant Data into Simulator Operability Testing |  | H.8 Procedure Adherence | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.11B | The inspectors identified a finding, associated with simulator operability testing, for the failure of the licensee to track and incorporate actual plant data into their cyclic operability tests, as required by American National Standards Institute-3.5-20
Region: IV | South Texas Project | 15860 | 12/31/2015 02/11/2016 | 2015004-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain the Emergency Plan Up to Date With the Safety Evaluation Report |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2) for failure to maintain the emergency plan in accordance with the approved safety evaluation report. Specifically, the licensee failed to meet 10 CFR 50.47(b)(2) requirements for timely
Region: IV | South Texas Project | 15852 | 06/30/2015 08/14/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Hurricane Plan Procedure to Secure Missile Hazards During Tropical Storm Bill |  | P.3 Resolution | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.01 | Inspectors identified a non-cited violation of Technical Specification 6.8.1.a for failure to follow Procedure 0PGP03-ZV-0002, "Hurricane Plan," Revision 7. Specifically, on June 15 through 16, 2015, the licensee failed to remove loose trash and materials
Region: IV | South Texas Project | 15853 | 06/30/2015 08/14/2015 | 2015002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Properly Check Design and Test Chiller Purge Check Valves |  | P.3 Resolution | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors documented a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to have adequate measures for the selection and review for suitability of application of parts that are essenti
Region: IV | South Texas Project | 15647 | 12/31/2014 02/10/2015 | 2014005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failue to Identify a Condition Adverse to Quality on Emergency Diesel Generator |  | P.2 Evaluation | TE?: N | 05000498 South Texas 1 |  | 71111.15 | The inspectors documented a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality following an unexpected alarm on t
Region: IV | South Texas Project | 15649 | 12/18/2014 01/30/2015 | 2014010-01 | NRC | NCV | MISC | Green | Failure to Perform Proper Material Package Searches to Ensure Identification Prior to Entry into Protected Area |  | H.12 Avoid Complacency | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152B | The team identified a non-cited violation of 10 CFR 73.55(h)(3)(i) for the failure to properly search personnel items (lunch boxes, briefcases, packages) before granting access to protected areas. Specifically, security personnel did not follow Security I
Region: IV | South Texas Project | 15640 | 09/28/2014 11/10/2014 | 2014004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Identify a Condition Adverse to Quality for the Control Room Envelope |  | P.2 Evaluation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, following the identifi
Region: IV | South Texas Project | 15639 | 09/25/2014 10/21/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Loop Flow Test |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 6.8.1.d for the failure to implement and maintain written procedures for fire protection program implementation. Specifically, the licensee failed to have procedures for and to flow test
Region: IV | South Texas Project | 15637 | 04/04/2014 05/19/2014 | 2014002-01 | NRC | NCV | Initiating Events | Green | Failure to Establish Adequate Screening Criteria in the Boric Acid Corrosion Control Program |  | H.14 Conservative Bias | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.08P | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for an inadequate procedure associated with the boric acid corrosion control program (BACCP). Specifically, Procedure 0PG
Region: IV | South Texas Project | 15638 | 04/04/2014 05/19/2014 | 2014002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Fill and Vent Results in an Inoperable Essential Chilled Water Train |  | H.1 Resources | TE?: N | 05000498 South Texas 1 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for an inadequate procedure because train C essential chilled water system was rendered inoperable by failing to remove a
Region: IV | South Texas Project | 15597 | 03/28/2014 03/18/2014 | 2014007-01 | NRC | VIO | Initiating Events | Green | Failure to Accurately Document Completion of a Maintenance Activity | EA Case: 2013213 |  | TE?: Y SL-V-VIO | 05000499 South Texas 2 |  | 71152 | The inspectors identified a violation of 10 CFR 50.9; 10 CFR 50, Appendix B, Criterion XVII; and Technical Specification 6.8.1.a, for failure to accurately document completion of a maintenance activity. Specifically, on November 7, 2011, a maintenance sup
Region: IV | South Texas Project | 15600 | 02/06/2014 03/28/2014 | 2013007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Evaluate Safety-Related Equipment Electrical Load Requirements when Verifying the Adequacy of Voltage from the Nuclear Steam Supply System Inverter/Rectifier |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, for those struct
Region: IV | South Texas Project | 15601 | 02/06/2014 03/28/2014 | 2013007-02 | NRC | NCV | Mitigating Systems | Green | Improper Sequencing of Maintenance of 4160 VAC Circuit Breakers Prior to As-Found Tests |  | H.7 Documentation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and comp
Region: IV | South Texas Project | 15612 | 02/06/2014 03/28/2014 | 2013007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Adequate Test Program for Safety-Related 480 VAC Circuit Breakers |  | P.2 Evaluation | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and comp
Region: IV | South Texas Project | 15613 | 02/06/2014 03/28/2014 | 2013007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Preventative Maintenance Procedure for Reactor Containment Fan Cooler |  | H.1 Resources | TE?: N | 05000498 South Texas 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented procedures of a type appropriate
Region: IV | South Texas Project | 15624 | 02/06/2014 03/28/2014 | 2013007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Design Control of Safety Injection Pump Room Cooler |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tra
Region: IV | South Texas Project | 15625 | 02/06/2014 03/28/2014 | 2013007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate the Adequacy of Voltage Available at AF-19 Valve Motor to Close the Valve During Postulated High Energy Line Break Conditions |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis, for those struct
Region: IV | South Texas Project | 15636 | 02/06/2014 03/28/2014 | 2013007-07 | NRC | NCV | Initiating Events | Green | Failure to Develop Adequate Procedures for Loss of All Seal Cooling to a Reactor Coolant Pump |  | H.9 Training | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Instructions, procedures, or drawings shall include appropriate qualitative and quantitative acc
Region: IV | South Texas Project | 15595 | 12/31/2013 02/06/2014 | 2013005-01 | NRC | NCV | Initiating Events | Green | Failure to Include Appropriate Acceptance Criteria in a Quality Procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.11B | The inspectors identified a non-cited violation of Title 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to include appropriate quantitative or qualitative acceptance criteria for determining that important a
Region: IV | South Texas Project | 15596 | 12/31/2013 02/06/2014 | 2013005-02 | NRC | FIN | Initiating Events | Green | Flawed Job Performance Measures |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.11B | The inspectors identified a finding of very low safety significance for developing and administering an excessive number of flawed job performance measures during the 2012 and 2013 NRC annual operating tests, which resulted in invalidating several operato
Region: IV | South Texas Project | 15589 | 12/31/2013 12/03/2013 | 2013301-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | NONE | A self revealing Green noncited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," was identified for the failure of operations training personnel to ensure the integrity of an operating test scheduled for administration for an initial
Region: IV | South Texas Project | 15588 | 06/29/2013 07/30/2013 | 2013003-01 | NRC | FIN | Barrier Integrity | Green | Inadequate Design Calculations for Spent Fuel Pool Mitigation Strategies |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a Green finding for the licensee's failure to follow Procedure 0PGP04-ZA-0307, "Preparation of Calculations," Revision 4. Specifically, two parts were not followed, step 3.1.5.4 states all design calculations SHALL be identified
Region: IV | South Texas Project | 15582 | 03/30/2013 05/06/2013 | 2013002-01 | NRC | FIN | Barrier Integrity | Green | Failure to Initiate a Condition Report for Spent Fuel Pool Cooling Low Flow Alarms |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 |  | 71111.15 | The inspectors identified a Green finding for the failure to follow Procedure 0PGP03-ZX-0002, "Condition Reporting Process," Revision 43, step 4.2.1, which required initiation of a condition report for an abnormal or unexpected condition on a structure, s
Region: IV | South Texas Project | 15587 | 03/30/2013 05/06/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Use of Non-Conservative Values in Reportability Evaluation |  | H.4(a) Human Error Prevention | TE?: N | 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criteron V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure 0PGP04-ZA-0002, "Condition Report Engineering Evaluation," Revision 18. On February 25
Region: IV | South Texas Project | 15576 | 12/31/2012 02/05/2013 | 2012005-01 | NRC | NCV | Initiating Events | Green | Failure to Perform Pressure Testing of the Reactor Vessel Flange Leak-Off Lines |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.08P | Inspectors identified a non-cited violation of 10CFR50.55a(g)(4) involving the licensee's failure to perform a system pressure test of the reactor vessel flange leak-off line of Units 1 and 2, in accordance with the applicable edition of Section XI of the
Region: IV | South Texas Project | 15577 | 12/31/2012 02/05/2013 | 2012005-02 | NRC | NCV | Initiating Events | Green | Failure to Follow Procedure for the Control of Tools for Use on Stainless Steel |  | H.4(b) Procedural Compliance | TE?: N | 05000498 South Texas 1 |  | 71111.08P | Inspectors identified a non-cited violation of very low safety significance of Technical Specification 6.8.1.a and Regulatory Guide 1.33, for the failure to follow procedures that ensured abrasive tools for use on stainless steel systems were not contamin
Region: IV | South Texas Project | 15578 | 12/31/2012 02/05/2013 | 2012005-03 | NRC | NCV | Initiating Events | Green | Failure to Maintain Adequate Fire Penetration Seal Material Thickness |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 6.8.1.d, "Fire Protection Program Implementation," for the failure to follow work order package instructions requiring the use of Drawing C012- 00081-F7F, "Detail "E-1" Silicone El
Region: IV | South Texas Project | 15570 | 10/31/2012 11/20/2012 | 2012007-01 | NRC | VIO | Mitigating Systems | Green | Failure to Timely Correct Conditions Adverse to Fire Protection | EA Case: 2012227 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152B | The team identified a violation of License Condition 2.E for the failure to correct a noncompliance. Procedure 0POP04-ZO-0001, "Control Room Evacuation," Revision 35, was not consistent with the post-fire safe shutdown analysis in that it failed to ensure
Region: IV | South Texas Project | 15564 | 09/28/2012 11/08/2012 | 2012004-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Procedure Results in Stator Cooling Water Coil Damage and Main Generator Trip |  |  | TE?: N | 05000499 South Texas 2 |  | 71152 | The inspectors reviewed a self-revealing finding for the failure to follow Procedure 0POP02-GG-0001, "Generator Hydrogen and Carbon Dioxide Gas System," Revision 43, for a verified alarm on the Unit 2 main generator. On November 26, 2011, the Unit 2 contr
Region: IV | South Texas Project | 15565 | 09/28/2012 11/08/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct a Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly identify and correct a condition adverse to quality. Specifically, the licensee failed to correct a l
Region: IV | South Texas Project | 15559 | 06/29/2012 08/02/2012 | 2012003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow ASME Code Requirements |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000498 South Texas 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50.55a(g)(4) for the failure to follow in-service inspection requirements of Section XI of the 2004 ASME Boiler and Pressure Vessel Code. Specifically, the inspectors determined that the licensee h
Region: IV | South Texas Project | 15560 | 06/29/2012 08/02/2012 | 2012003-02 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify Conditions Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to promptly identify conditions adverse to quality. Specifically, on May 21, 2012, the inspectors observed water was dripping from the isolation
Region: IV | South Texas Project | 15561 | 06/29/2012 08/02/2012 | 2012003-03 | NRC | NCVIV | Initiating Events | Green | Failure to Report a Condition Prohibited by Technical Specifications |  |  | TE?: Y SL-IV-NCVIV | 05000499 South Texas 2 |  | 71153 | The inspectors identified a non-cited violation of 10 CFR 50.73(a)(2)(i)(B) for the failure to report a condition prohibited by technical specifications to the NRC within 60 days. Specifically, on March 6, 2012, after reviewing licensee records, the inspe
Region: IV | South Texas Project | 15544 | 12/31/2011 02/13/2012 | 2011005-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedural Requirements (Section 2RS01) |  | H.4(b) Procedural Compliance | TE?: N | 05000498 South Texas 1 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 6.8.1.a, for the failure to follow procedural and radiation work permit requirements. On April 22, 2011, work was performed in the Unit 1 reactor cavity and the health
Region: IV | South Texas Project | 15545 | 12/31/2011 02/13/2012 | 2011005-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Procedures and Maintain Doses ALARA |  | H.3(a) Work Planning | TE?: N | 05000499 South Texas 2 |  | 71124.02 | On November 1, 2011, the inspectors identified a non-cited violation of Technical Specification 6.8.1.a, for the failure to follow procedures and minimize occupational doses during an outage maintenance activity for the disassembly of the Unit 2 reactor h
Region: IV | South Texas Project | 15546 | 12/31/2011 02/13/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Change on Class 1E 4160 Vac ESF Transformers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criteria III, "Design Control," for the failure to ensure that design standards were correctly translated into drawings, procedures, and instructions. Specifically, the design
Region: IV | South Texas Project | 15530 | 09/30/2011 11/09/2011 | 2011004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Standby Diesel Generator Maintenance Procedures |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 |  | 71111.15 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 6.8.1.a, for the failure to follow maintenance work authorization number 416904. Specifically on January 27, 2011, mechanics incorrectly aligned the fuel oil delivery v
Region: IV | South Texas Project | 15536 | 09/30/2011 11/09/2011 | 2011004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Corrective Actions from an Inadequate Extent of Condition Review |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, "Corrective Action," for the failure to assure that conditions adverse to quality were promptly identified and corrected. Specifically, the licensee did not prompt
Region: IV | South Texas Project | 15537 | 09/30/2011 11/09/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action to Correct an Inadequate Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, "Corrective Action," for the failure to assure that conditions adverse to quality were promptly identified and corrected. Specifically, the inspectors determined t
Region: IV | South Texas Project | 15529 | 07/01/2011 08/10/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Timely Correct Conditions Adverse to Fire Protection |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05T | The team identified a noncited violation of License Condition 2.E for the failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the team identified two examples of failure to implement timely cor
Region: IV | South Texas Project | 15524 | 06/30/2011 08/04/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Protection System Functionality Procedure Results in Failure to Establish Fire Watches |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05Q | The inspectors identified a noncited violation of license condition 2.E, "Fire Protection Program," because of an inadequate procedure that resulted in the licensee failing to establish compensatory fire watches in eight fire zones with degraded fire dete
Region: IV | South Texas Project | 15525 | 06/30/2011 08/04/2011 | 2011003-02 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Risk Assessment for Switchyard Activities |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000498 South Texas 1 |  | 71111.13 | The inspectors reviewed a self-revealing noncited violation of 10 CFR 50.65(a)(4) for the failure to perform an adequate risk assessment to manage the increase in risk of performing activities in the switchyard. On September 26, 2010, the licensee removed
Region: IV | South Texas Project | 15515 | 03/31/2011 05/09/2011 | 2011002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Restoration Results in Void in High Head Safety Injection Pump 2C |  | H.3(b) Work Activity Coordination | TE?: N | 05000499 South Texas 2 |  | 71111.15 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure 0POP11-SI-0001, "Safety Injection/Containment Spray Pump Online Isolation
Region: IV | South Texas Project | 15516 | 03/31/2011 05/09/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Immediate Operability Determination |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure 0PGP03-ZX-0002, "Condition Reporting Process," Revision 38. On January 13, 2011,
Region: IV | South Texas Project | 15517 | 03/31/2011 05/09/2011 | 2011002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Action to Correct Nonconforming Steam Generator Power Operated Relief Valve Condition |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.22 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria XVI, "Corrective Action," for the failure to assure that conditions adverse to quality were corrected in a timely manner, or that an evaluation to justify
Region: IV | South Texas Project | 15518 | 03/31/2011 05/09/2011 | 2011002-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Follow Reactor Protection System Procedure Results in Automatic Reactor Trip |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 |  | 71111.22 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 6.8.1.a, for the failure to follow surveillance test Procedure 0PSP03-SP-0006R, "Train R Reactor Trip Breaker TADOT," Revision 21, because operators did not block a rea
Region: IV | South Texas Project | 15509 | 01/11/2011 02/15/2011 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Nonconservative Modeling of Engineered Safety Feature Transformer Load Tap Changer Controller Dead Band |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly transla
Region: IV | South Texas Project | 15510 | 01/11/2011 02/15/2011 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations for Degraded Voltage Relay Voltage Setpoint |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly transla
Region: IV | South Texas Project | 15512 | 01/11/2011 02/15/2011 | 2010007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Emergency Core Cooling System Transfer to Containment Sump |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | South Texas Project | 15513 | 01/11/2011 02/15/2011 | 2010007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis and Procedures for Offsite Power Availability |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly transla
Region: IV | South Texas Project | 15502 | 12/31/2010 01/24/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Review Removes Safety Injection Flush Line Valves from Locked Valve Program |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.04Q | On October 21, 2010, the inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria III, "Design Control," for the failure to properly ensure that design standards were correctly translated into drawings; procedures; and instructio
Region: IV | South Texas Project | 15507 | 12/31/2010 01/24/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Install the Required Number of Smoke Detectors (4) in the Auxiliary Shutdown Rooms |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05Q | The inspectors identified a noncited violation of license condition 2.E, Fire Protection Program, for the failure to install the required number of smoke detectors (four) in the auxiliary shutdown room per the National Fire Protection Association Standard
Region: IV | South Texas Project | 15508 | 12/31/2010 01/24/2011 | 2010005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Protective Relay Trip of Residual Heat Removal Pump |  | H.4(a) Human Error Prevention | TE?: N | 05000499 South Texas 2 |  | 71111.22 | On October 17, 2010, the inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure 0PSP03-RH-0003, "Residual Heat Removal Pump 1C(2C) In
Region: IV | South Texas Project | 15496 | 09/30/2010 11/02/2010 | 2010004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Repair Essential Cooling Water System Leak within the Technical Specification Allowed Outage Time |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a Green noncited violation of Technical Specification 3.7.4 because the licensee had one independent loop of essential cooling water inoperable for longer than the allowed outage time of 7 days. Specifically, on October 27, 2009,
Region: IV | South Texas Project | 15501 | 09/30/2010 11/02/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Adequate Operability Review of High Temperatures in Isolation Valve Cubicle Room |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure 0PGP03-ZO-9900, "Operability Determinations and Functionality Assessments," Revis
Region: IV | South Texas Project | 15495 | 06/30/2010 08/04/2010 | 2010003-03 | NRC | FIN | Mitigating Systems | Green | Inadequate Design Change Review of AMSAC |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified a Green finding for the failure to identify specific design parameters and the impact of changes on the anticipated transient without scram mitigation system actuation circuitry (AMSAC) in accordance with station Procedure 0PGP04
Region: IV | South Texas Project | 15485 | 03/31/2010 05/10/2010 | 2010002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Follow Procedures Results in Repetitive Malfunction of Electrical Auxiliary Building Air Handling Unit 21B Smoke Purge Inlet Damper |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000499 South Texas 2 |  | 71111.22 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow procedures and enter a malfunction of the Unit 2 smoke purge damper 21B into the corrective action program. Specifically, the
Region: IV | South Texas Project | 15486 | 03/31/2010 05/10/2010 | 2010002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Engineering Evaluation Causes an Inoperable Essential Chilled Water Train |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000499 South Texas 2 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 3.7.14 because the licensee had one independent loop of essential chilled water inoperable for longer than the allowed outage time of 7 days. Specifically, the licensee
Region: IV | South Texas Project | 15483 | 12/31/2009 01/28/2010 | 2009005-01 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Procedure Degrades Cold Overpressure Mitigation System |  | P.2(b) Implementing Operating Experience | TE?: N | 05000499 South Texas 2 |  | 71111.15 | The inspectors reviewed a self-revealing noncited violation of 10CFR Part 50, Appendix B, Criterion V, "instructions, Procedures, and Drawings," for an inadequate maintenance procedure that failed to describe the steps for correctly restoring auxiliary pr
Region: IV | South Texas Project | 15484 | 12/31/2009 01/27/2010 | 2009301-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Implement Emergency Operating Procedures |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | NONE | A self-revealing non-cited violation of Technical Specification 6.8.1 was identified for failing to properly implement Emergency Operating Procedures required by section 6.8.1a. Specifically, four crews out of five did not take actions as directed in 0POP
Region: IV | South Texas Project | 15474 | 10/03/2009 11/05/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Reportability Results in Two Trains of the Essential Chilled Water System Being Inoperable |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 |  | 71111.15 | The inspectors identified an inadequate reportability review that resulted in a Green noncited violation of Technical Specification 3.7.14 because the licensee had two independent loops of essential chilled water system inoperable for longer than the allo
Region: IV | South Texas Project | 15457 | 07/04/2009 08/10/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify Maintenance Rule A1 Condition |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(2) for the licensee's failure to effectively monitor the performance of the Unit 2 4160Vac Class 1E system. On August 30, 2007, an undervoltage Agastat relay on the Unit 2 4160Vac Train A b
Region: IV | South Texas Project | 15458 | 07/04/2009 08/10/2009 | 2009003-02 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Perform Radiation Surveys |  | H.3(a) Work Planning | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7112101 | A self-revealing noncited violation of 10 CFR 20.1501(a) was identified for failure to perform a radiological survey to determine the potential radiological hazards present when deposting a high contamination area. On October 25, 2008, decontamination tec
Region: IV | South Texas Project | 15459 | 07/04/2009 08/10/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure a Reliable Fire Suppression Water Supply System |  |  | TE?: N | 05000498 South Texas 1 |  | NONE | The inspectors identified a noncited violation of License Condition 2.E, "Fire Protection," for the failure to ensure that a fire pump would automatically start upon low pressure in the fire main in the event of a fire in the electrical auxiliary building
Region: IV | South Texas Project | 15460 | 07/04/2009 08/10/2009 | 2009003-04 | NRC | NCV | Mitigating Systems | Green | Potential Loss of Centrifugal Charging Pump Suction Due to Fire Damage |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | NONE | The inspectors identified a noncited violation of License Condition 2.E, "Fire Protection," for failure to ensure that equipment required for post-fire safe shutdown system remains free of fire damage. Specifically, the licensee credited manual actions to
Region: IV | South Texas Project | 15450 | 04/09/2009 04/24/2009 | 2009002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Assess and Manage Outage Maintenance Risk Activities Resulting in the Loss of the Residual Heat Removal System |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000499 South Texas 2 |  | 71111.13 | The inspectors reviewed a self-revealing noncited violation of 10 CFR 50.65(a)(4), for the failure to assess and manage risk from an emergent maintenance work activity on the solid state protection system during the Unit 2 refueling outage that resulted i
Region: IV | South Texas Project | 15451 | 04/09/2009 04/24/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Reportability Misses an Inoperable Component Cooling Water Train |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000499 South Texas 2 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 3.7.3 for an inadequate reportability review on the Train A component cooling water low-level actuation switch which failed during surveillance testing. On October 14, 2008, during
Region: IV | South Texas Project | 15456 | 04/09/2009 04/24/2009 | 2009002-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Surveillance Test for Component Cooling Water |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for the inadequate surveillance Procedure 0PSP05-CC-0001, "FCI CCW Surge Tank Compartment Level Switch Calibration," Revisi
Region: IV | South Texas Project | 15449 | 12/31/2008 02/11/2009 | 2008005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Perform Routine Operator Rounds Results in the Creation of Fire Hazards |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.22 | The inspectors identified two examples of a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V (Procedures), for the failure to adequately perform routine operator rounds in accordance with station procedures. Plant operators had failed to obs
Region: IV | South Texas Project | 15445 | 09/27/2008 11/06/2008 | 2008004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedures Resulted in Isolation of Majority of Fire Water |  | H.3(b) Work Activity Coordination | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 6.8.1.d for the failure to follow Procedure 0PGP03-ZF-0018, "Fire Protection System Operability Requirements," Revision 14. As a result the licensee unintentionally iso
Region: IV | South Texas Project | 15446 | 08/14/2008 09/26/2008 | 2008009-01 | NRC | FIN | Initiating Events | Green | Ineffective Corrective Actions on the Equipment Clearance Order Process |  | H.4(b) Procedural Compliance | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152B | The team identified a finding involving ineffective corrective actions for the equipment clearance order process. Despite the identification of numerous related failures of the equipment clearance order process in various significant conditions adverse to
Region: IV | South Texas Project | 15426 | 06/28/2008 08/12/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Motor Operated Valve Motor Damage |  | H.4(b) Procedural Compliance | TE?: N | 05000498 South Texas 1 |  | 71111.19 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for the failure to follow Work Order 452133, "Terminate Replacement Cables for MCC E1C3 in Accordance with Design Change Package 05-1437-4 during 1RE14
Region: IV | South Texas Project | 15427 | 06/28/2008 08/12/2008 | 2008003-02 | NRC | NCV | Initiating Events | Green | Failure to evaluate and/or Document Multiple Boric Acid Leaks with Changed Conditions |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to follow Procedure 0PGP03-ZE-0133, "Boric Acid Corrosion Control Program," Revision 0 and Revision 1, which resulted in the licensee not re-evaluating
Region: IV | South Texas Project | 15430 | 06/28/2008 08/12/2008 | 2008003-03 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conduct Adequate Radiation Surveys in the Pressurizer Cubicle |  | H.3(b) Work Activity Coordination | TE?: N | 05000498 South Texas 1 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of 10 CFR 20.1501 because radiation protection staff failed to perform an adequate survey to evaluate and determine the radiological hazards in the pressurizer cubicle on March 31, 2008. Conseque
Region: IV | South Texas Project | 15425 | 04/08/2008 05/02/2008 | 2008002-01 | NRC | NCV | Barrier Integrity | Green | CRE HVAC Makeup Fan 11B Failure to Start |  |  | TE?: N | 05000498 South Texas 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria III, for an inadequate design control package that resulted in incorrect instantaneous over current breaker trip point settings. On September 11, 2006, con
Region: IV | South Texas Project | 15433 | 01/22/2008 02/13/2008 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Specify Setpoint Calibration Limits in Relay Setpoint Calculations |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to specify in a design calculation allowable relay setpoint tolerances. Specifically, the licensee
Region: IV | South Texas Project | 15434 | 01/22/2008 02/13/2008 | 2007007-02 | NRC | NCV | Mitigating Systems | Green | Manual Loads not Considered for Fuel Oil Storage Tank Sizing Calculation |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the failure to include all potential loads in the standby diesel generator fuel oil sizing calculation. Specif
Region: IV | South Texas Project | 15435 | 01/22/2008 02/13/2008 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Use Correct Design Inputs in Determination of the Weak Link for the Auxiliary Feedwater System Outside Containment Isolation Motor Operated Valves |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria III, "Design Control," of very low safety significance for the failure to translate design basis information into specifications and procedures. Specifically, a non-conservat
Region: IV | South Texas Project | 15438 | 01/22/2008 02/13/2008 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Surveillance Procedure Lacked Check for Timing of Chiller Loading on the Bus |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of Technical Specification Surveillance Requirement 4.8.1.1.2.E.11, having very low safety significance for the licensee's failure to adequately perform the technical specification surveillance requirement. Specifi
Region: IV | South Texas Project | 15439 | 01/22/2008 02/13/2008 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Test Program for 125V DC Molded Case Circuit Breakers |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," having very low safety significance for the licensee's failure to implement a test program to assure that all installed safety-related molded case circui
Region: IV | South Texas Project | 15440 | 01/22/2008 02/13/2008 | 2007007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Instrument Uncertainties into Surveillance Requirements for Technical Specification Limiting Condition for Operation 3.5.2 (Specifically Surveillance Requirement 4.5.2.f) |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria III, "Design Control," of very low safety significance for the failure to adequately translate design basis information into specifications and procedures. Specifically, meas
Region: IV | South Texas Project | 15441 | 01/17/2008 02/07/2008 | 2008006-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Conspicuously Post a Radiation Area |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000498 South Texas 1 |  | 7112101 | The team identified a noncited violation of 10 CFR 20.1902(a) because the licensee failed to conspicuously post a radiation area in the radwaste storage yard with a sign or signs bearing the radiation symbol and the words "Caution, Radiation Area." The li
Region: IV | South Texas Project | 15422 | 12/31/2007 02/11/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Incorrect Count Rate Board Installed in Extended Range Nuclear Instrument Channel |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 |  | 71111.12 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria V, for the failure to follow Procedure STI 32174927, "Conduct of Maintenance," Revision 5. On April 6, 2007, operations declared extended range nuclear ins
Region: IV | South Texas Project | 15423 | 12/31/2007 02/11/2008 | 2007005-02 | NRC | NCV | MISC | Green | Inadequate Reportability Review Results in Missed Reporting Requirement |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000498 South Texas 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criteria V, for the failure to follow Procedure 0POP03-ZX-0002, "Condition Reporting Process," Revision 31. On April 14, 2007, operations recognized that the extended range nucl
Region: IV | South Texas Project | 15424 | 12/31/2007 02/11/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Incorrectly Installed Safety-Related Solenoid Valve Results in Unexpected Steam Dump Valve Operation |  |  | TE?: N | 05000498 South Texas 1 |  | 71152 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria V, for an inadequate procedure for testing safety-related solenoid valves that operate the steam dump valves. On December 18, 2006, during troubleshooting
Region: IV | South Texas Project | 15417 | 10/11/2007 11/14/2007 | 2007004-01 | NRC | FIN | MISC | Green | Loss of Control Room Annunciators due to Poor Worker Material Control for ERFDADS Inverter Upgrade |  | H.3(a) Work Planning | TE?: N | 05000498 South Texas 1 |  | 71111.13 | The inspectors reviewed a self-revealing finding for an inadequate procedure, STI 32174927, "Conduct of Maintenance," Revision 5, for work associated with the Unit 1 emergency response facility data acquisition and display systems inverter modification ac
Region: IV | South Texas Project | 15418 | 10/11/2007 11/14/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Leads to Inoperable Turbine-Driven AFW Pump for Longer than TSs Allowed Outage Time |  | P.2(b) Implementing Operating Experience | TE?: N | 05000498 South Texas 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criteria V, "Instructions, Procedures, and Drawings," for an inadequate surveillance test procedure on the turbine-driven auxiliary feedwater pump, due to inadequat
Region: IV | South Texas Project | 15410 | 07/06/2007 08/17/2007 | 2007003-01 | Self - Revealed | NCV | Initiating Events | Green | Improper Turbine Load Rate Manipulation Results in Unexpected Power Reduction |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000499 South Texas 2 |  | 71111.2 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 6.8.1.a for the failure to follow Procedure 0POP03-ZG-0006, "Plant Shutdown from 100% to Hot Standby," Revision 28. As part of the shutdown, operations personnel are di
Region: IV | South Texas Project | 15411 | 07/06/2007 08/17/2007 | 2007003-02 | NRC | NCV | Occupational Radiation Safety | Green | Two Examples of a Failure to Conspicuously Post and Barricade a High Radiation Area |  | H.4(b) Procedural Compliance | TE?: N | 05000499 South Texas 2 |  | 7112101 | The inspector identified two examples of a noncited violation of Technical Specification 6.12.1 because the licensee failed to conspicuously post and barricade two separate high radiation areas. On April 19, 2007, during a tour of the reactor containment
Region: IV | South Texas Project | 15416 | 07/06/2007 08/17/2007 | 2007003-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Obtain Authorization to Enter a High Radiation Area |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000499 South Texas 2 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of Technical Specification 6.8.1 because of a failure to follow procedural and radiation work permit requirements. On April 4, 2007, a worker entered a high radiation area without authorization, d
Region: IV | South Texas Project | 15405 | 04/06/2007 05/18/2007 | 2007002-01 | Self - Revealed | FIN | Initiating Events | Green | Human Performance Error Hanging an Equipment Clearance Order |  | H.4(a) Human Error Prevention | TE?: N | 05000499 South Texas 2 |  | 71111.13 | The inspectors reviewed a self-revealing finding for a failure to follow procedure, which resulted in losing power to Load Center 2G2 and subsequently the running stator cooling water pump, which would have resulted in a main turbine/reactor trip had the
Region: IV | South Texas Project | 15409 | 04/06/2007 05/18/2007 | 2007002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Improper Maintenance Results in Damage to a HHSI Pump Resulting in NOED | EA Case: 2007068 | H.4(b) Procedural Compliance | TE?: N | 05000499 South Texas 2 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 6.8.1.a for failure to follow Procedures STI 32013741, "Conduct of Maintenance," dated May 15, 2006, and 0PMP04-SI-0002, "High Head Safety Injection Pump Maintenance."
Region: IV | South Texas Project | 15401 | 12/31/2006 02/14/2007 | 2006005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Monitor and Control Workers' Exposure in a High Radiation Area. |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 |  | 7112101 | The inspector reviewed a self revealing, non-cited violation of Technical Specification 6.12.1.b. for failure to monitor and control workers' dose in a high radiation area. Two contract support workers for nozzle dam removal were not able to read their el
Region: IV | South Texas Project | 15398 | 10/12/2006 11/20/2006 | 2006004-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Comply with a Radiation Work Permit Requirement |  | H.4(a) Human Error Prevention | TE?: N | 05000498 South Texas 1 |  | 71111.22 | A self-revealing noncited violation was identified for the failure to comply with a radiation work permit requirement. On July 13, 2006, a maintenance technician alarmed the personnel contamination monitors upon exiting the radiologically area, due to con
Region: IV | South Texas Project | 15399 | 10/12/2006 11/20/2006 | 2006004-02 | NRC | NCV | Barrier Integrity | Green | Inadequate Procedural Guidance for Verifying Control Room Ventilation Doors are Secured |  | P.1(b) Trend Performance CAP | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71152 | The inspectors identified three examples and the licensee identified one example of a noncited violation of Technical Specification 6.8.1.a for the failure to provide an adequate procedure to ensure that doors, which provide access through the control roo
Region: IV | South Texas Project | 15397 | 07/07/2006 08/10/2006 | 2006003-01 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Main Generator Reactive Power Test Procedure |  |  | TE?: N | 05000499 South Texas 2 |  | 71153 | A self-revealing finding was identified for the failure to provide an adequate procedure, which resulted in an unexpected initiation of a "Generator U/F (Under-Frequency) Loss of Field Voltage" alarm. This alarm would have caused a generator/turbine/react
Region: IV | South Texas Project | 15387 | 04/07/2006 05/18/2006 | 2006002-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Motor-Operated Valve Operation Method |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05A | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix R, Section III.L.3, in that the method used to position motor-operated valves ("hot-sticking") following a fire in the control room was not independent of the fire area. Specifical
Region: IV | South Texas Project | 15388 | 04/07/2006 05/18/2006 | 2006002-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternate Shutdown Analysis |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05A | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix R, Section III.L.1 because the thermohydraulic analysis was inconsistent with actions allowed in the South Texas Project licensing basis for a control room evacuation. Specifically
Region: IV | South Texas Project | 15385 | 01/26/2006 02/27/2006 | 2006008-01 | NRC | NCV | Public Radiation Safety | Green | Failure to Confine Radioactive Material to A Radiologically Controlled Area |  | H.3(a) Work Planning | TE?: N | 05000498 South Texas 1 05000498 South Texas 1 05000499 South Texas 2 05000499 South Texas 2 |  | 7112203 | The team reviewed two examples of a self-revealing non-cited violation of Technical Specification 6.8.1, resulting from the licensee's failure to prevent radioactive material from being unconditionally released from a radiologically controlled area. The f
Region: IV | South Texas Project | 24004 | 05/14/2018 |  | Licensee - Identified | NCV |  | Green | Willful Failure of Fire Watches to Conduct Complete Tours |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05Q | Violation: Title 10 CFR 50.48, “Fire Protection,” requires, in part, that licensees have a fire protection plan that outlines the plans for fire protection, fire detection, suppression capability, and limitation of damage. STP Nuclear Operating
Region: IV | South Texas Project | 24005 | 05/14/2018 |  | Licensee - Identified | NCV |  | Green | Willful Failure to Accurately Document Fire Watch Tours |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71111.05Q | Violation: Title 10 CFR 50.9, “Completeness and accuracy of information,” requires, in part, that information required by the Commission’s regulations, orders, or license conditions to be maintained by the licensee shall be complete and accurate in all ma
Region: IV | South Texas Project | 126347 | 11/04/2019 |  | Licensee - Identified | LIV |  | Green | (OUO-SRI) The licensee identified seven examples of an individual who did not have a psychological assessment that included a clinical interview prior the individuals performing job functions that are critical to the safe and secure operation of the licen |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71130.02
Region: IV | South Texas Project | 126348 | 11/04/2019 |  | Licensee - Identified | LIV |  | Green | (OUO-SRI) The licensee identified an on-duty security force person who was not capable of maintaining continuous communication with an individual in each alarm station. |  |  | TE?: N | 05000498 South Texas 1 05000499 South Texas 2 |  | 71130.02
Region: IV | Waterford | 126572 | 12/31/2019 01/30/2020 | 2019004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Implement the Operability Determination Process When Applied to the Auxiliary Component Cooling Water System |  | H.6 - Design Margins | TE?: N | 05000382 Waterford 3 | Equipment Performance | 71111.15 | The inspectors identified a Green non-cited violation of Title 10 of the Code of Federal Regulations (CFR), Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” which occurred because the licensee did not perform an operability dete
Region: IV | Waterford | 125986 | 09/30/2019 11/05/2019 | 2019003-01 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Periodically Calibrate Radiation Monitoring Equipment |  | H.3 - Change Management | TE?: N | 05000382 Waterford 3 | Plant Facilities/Equipment and Instrumentation | 71124.05 | The inspectors identified a Green non-cited (NCV) of 10 CFR 20.1501(c) for failure to periodically calibrate area radiation monitoring equipment used to perform dose rate measurements. Specifically, on or around January 18, 2012, the licensee began changi
Region: IV | Waterford | 125746 | 09/30/2019 11/05/2019 | 2019003-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Procedures for Main Generator Exciter Maintenance |  | H.5 - Work Management | TE?: N | 05000382 Waterford 3 | Equipment Performance | 71153 | The inspectors reviewed a self-revealing Green finding because the licensee did not follow procedure requirements when performing periodic maintenance on the main generator exciter. Specifically, the licensee did not implement the preventative maintenance
Region: IV | Waterford | 125172 | 05/23/2019 06/28/2019 | 2019010-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate Storage and Shelf-Life Requirements |  | NPP | TE?: N | 05000382 Waterford 3 |  | 71111.21N | The inspectors identified a Green finding and associated Non-Cited Violation (NCV) of Title 10 of the Code of Federal Regulations (10 CFR) Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” for the licensee’s failure to identify a
Region: IV | Waterford | 124680 | 03/31/2019 04/30/2019 | 2019001-01 | NRC | NCV | Initiating Events | Green | Failure to Lock an Reactor Coolant System Drain Valve Results in Loss of Inventory during Lowered Inventory Conditions |  | H.12 - Avoid Complacency | TE?: N | 05000382 Waterford 3 | Configuration Control | 71111.13 | The inspectors identified Green non-cited violation of Technical Specification 6.8.1.a associated with the licensee’s failure to implement procedures for equipment control. Specifically, on January 7, 2019, the licensee failed to lock the boron managemen
Region: IV | Waterford | 124603 | 03/31/2019 04/30/2019 | 2019001-02 | Self - Revealed | NCV | Barrier Integrity | Green | Inadequate Procedure Contributed to Damage to a Fuel Assembly |  | P.3 - Resolution | TE?: N | 05000382 Waterford 3 | Procedure Quality | 71111.2 | The inspectors reviewed a self-revealed, Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” which occurred because the licensee did not prescribe procedures for handling spent fuel in the spent
Region: IV | Waterford | 25958 | 12/31/2018 02/05/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Control and Document Traceability for Quality Lubricating Oil for Safety-Related Components |  | H.1 - Resources | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion II, “Quality Assurance Program,” for the licensee’s failure to ensure that identification of quality items be maintained throughout fabrication, erection, inst
Region: IV | Waterford | 24712 | 10/05/2018 11/15/2018 | 2018008-01 | NRC | NOV | Mitigating Systems | Green | Failure to Control Nonconforming Parts |  | P.2 - Evaluation | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green cited violation of 10 CFR Part 50, Appendix B, Criterion XV, “Nonconforming Materials, Parts, or Components,” when the licensee failed to dedicate commercial-grade relays for use in safety-related applications. After receiving
Region: IV | Waterford | 24713 | 10/05/2018 11/15/2018 | 2018008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality |  | P.2 - Evaluation | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, “Corrective Action,” associated with the licensee’s failure to identify and correct condition adverse to quality associated with the breeching of hazard barriers
Region: IV | Waterford | 24056 | 06/30/2018 07/18/2018 | 2018002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure Appropriate Chemistry Controls on the Component Cooling Water Heat Exchangers |  | H.12 - Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71111.07A | The inspectors reviewed a self-revealed, Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” which occurred because the licensee did not prescribe procedures for preventing fouling of the compone
Region: IV | Waterford | 24103 | 06/07/2018 07/20/2018 | 2017009-02 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Consider the Impacts on FLEX Phase 2 Equipment from Large Internal Flooding Sources Which Were Not Seismically Robust |  | P.2 - Evaluation | TE?: N | 05000382 Waterford 3 |  | 2515/191 | The NRC inspection team identified a Green finding related to the licensee’s failure to adequately consider the impacts from large internal flooding sources that are not seismically robust on the design, protection, and staging of the FLEX core cooling pu
Region: IV | Waterford | 23174 | 12/31/2017 02/07/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Testing Requirements for the Containment Spray Pump A |  | H.9 - Training | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee’s failure to assure that all testing required to demonstrate that structures, systems, and components will perform satisfactorily
Region: IV | Waterford | 23175 | 12/31/2017 02/07/2018 | 2017004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Adequate Maintenance on a Reactor Trip Circuit Breaker |  | H.12 - Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 6.8, "Procedures and Programs," and Regulatory Guide 1.33 for the licensee’s failure to properly perform maintenance on a safety-related component in accordance with s
Region: IV | Waterford | 22363 | 12/14/2017 12/28/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Three examples of Failure to Establish and Maintain Preventive Maintenance Procedures for Safety-Related Electrical Equipment |  | NPP | TE?: N | 05000382 Waterford 3 |  | 71111.21M | The team identified three examples of a Green non-cited violation of Technical Specification 6.8.1.a, for failure to establish, implement, and maintain written procedures for activities referenced in Appendix A of Regulatory Guide 1.33, Revision 2, dated
Region: IV | Waterford | 22364 | 12/14/2017 12/28/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Meet RG 1.9 Emergency Diesel Testing Requirements during Surveillance Test Results in Missed Surveillance |  | H.11 - Challenge the Unknown | TE?: N | 05000382 Waterford 3 |  | 71111.21M | The team identified a Green non-cited violation of Waterford Steam Electric Station, Unit 3, Technical Specification Limiting Condition for Operation 3.8.1.1 for failure to maintain operability of two separate independent diesel generators. Specifically,
Region: IV | Waterford | 22354 | 11/09/2017 12/20/2017 | 2017011-01 | NRC | NCV | Barrier Integrity | Green | Failure to Implement Off-normal Procedure for Low Spent Fuel Pool Inventory |  | H.11 - Challenge the Unknown | TE?: N | 05000382 Waterford 3 |  | 93812 | The inspectors identified a non-cited violation of Technical Specification 6.8, "Procedures and Programs," associated with the licensee’s failure to implement procedures for abnormal, off-normal, or alarm conditions. Specifically, on July 17, 2017, the li
Region: IV | Waterford | 22355 | 11/09/2017 12/20/2017 | 2017011-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Implement an Adequate Design Change for the Fast Bus Transfer System |  |  | TE?: N | 05000382 Waterford 3 |  | 93812 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 3.0.1 involving the failure to maintain at least two physically independent circuits between the offsite transmission network and the onsite Class 1E distribution syst
Region: IV | Waterford | 22356 | 11/09/2017 12/20/2017 | 2017011-03 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Procedures for Isophase Bus Maintenance |  | H.14 - Conservative Bias | TE?: N | 05000382 Waterford 3 |  | 93812 | The inspectors reviewed a self-revealed finding that occurred because the licensee did not follow procedural guidance when performing periodic maintenance on the main transformer isophase buses. Specifically, the licensee did not implement portions of the
Region: IV | Waterford | 22357 | 11/09/2017 12/20/2017 | 2017011-04 | NRC | NCV | Barrier Integrity | Green | Failure to Demonstrate that the Performance of Fuel Pool Purification Valves is Effectively Controlled through Preventive Maintenance |  | P.2 - Evaluation | TE?: N | 05000382 Waterford 3 |  | 93812 | The inspectors identified a non-cited violation of 10 CFR 50.65, paragraph (a)(2), "Requirements for Monitoring the Effectiveness of Maintenance of Nuclear Power Plants," because the licensee did not demonstrate that performance of components were being e
Region: IV | Waterford | 23493 | 06/30/2017 08/08/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Prepare the Site for Impending Adverse Weather |  | H.5 - Work Management | TE?: N | 05000382 Waterford 3 |  | 71111.01 | Green. The inspectors identified multiple examples of a non-cited violation of Technical Specification 6.8, "Procedures and Programs," and Regulatory Guide 1.33, "Quality Assurance Program Requirements," for the licensee’s failure to follow Licensee Proce
Region: IV | Waterford | 3877 | 06/30/2017 08/08/2017 | 2017002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Ensure Containment Equipment Hatch Closure Prior to RCS Time to Boil |  | H.4 - Teamwork | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 6.8, "Procedures and Programs," and Regulatory Guide 1.33, "Quality Assurance Program Requirements," which occurred because the licensee did not implement instructions
Region: IV | Waterford | 3878 | 06/30/2017 08/08/2017 | 2017002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Appropriate Testing of TSP Baskets Inside Containment |  | H.3 - Change Management | TE?: N | 05000382 Waterford 3 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to assure that testing required to demonstrate that structures, systems, and components will perform satisfactorily whi
Region: IV | Waterford | 3882 | 06/30/2017 08/08/2017 | 2017002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Perform a Post Maintenance Test on a Main Steam Isolation Valve Solenoid Valve |  | H.14 - Conservative Bias | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors identified a non-cited violation of Technical Specification 6.8, "Procedures and Programs," and Regulatory Guide 1.33, "Quality Assurance Program Requirements," for the licensee's failure to perform operability testing on a safety-related c
Region: IV | Waterford | 3883 | 06/30/2017 08/08/2017 | 2017002-05 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Perform Maintenance on the Correct Safety-Related Component |  | H.12 - Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71153 | The inspectors reviewed a self-revealed, non-cited violation of Technical Specification 6.8, "Procedures and Programs," and Regulatory Guide 1.33, "Quality Assurance Program Requirements," which occurred due to the licensee's failure to perform field work
Region: IV | Waterford | 23492 | 03/31/2017 05/01/2017 | 2017001-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Perform Field Changes in Accordance with Design Control Measures |  | NPP | TE?: N | 05000382 Waterford 3 |  | 71152 | Green. The inspectors reviewed a self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because the licensee failed to perform field changes in accordance with design control measures. Specifically, following ma
Region: IV | Waterford | 3855 | 12/31/2016 01/20/2017 | 2016004-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Ensure Appropriate Post-Maintenance Testing on Essential Chiller B |  | H.4 Teamwork | TE?: N | 05000382 Waterford 3 |  | 71111.12 | A self-revealed, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," occurred because the licensee did not assure that the procedures for post-maintenance testing of activities affecting quality includ
Region: IV | Waterford | 3861 | 12/16/2016 01/26/2017 | 2016008-01 | NRC | NCVIV | Mitigating Systems | Green | Failure to Control Nonconforming Parts |  | H.14 Conservative Bias | TE?: Y SL-IV-NCVIV | 05000382 Waterford 3 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XV, "Nonconforming Materials, Parts, or Components," which occurred when the licensee failed to dedicate commercial-grade relays for use in safety related application
Region: IV | Waterford | 3862 | 12/16/2016 01/26/2017 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Operability Determinations for Nonconforming Conditions |  | P.1 Identification | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," that occurred when the licensee failed on two occasions to perform an operability determination for a nonconforming condi
Region: IV | Waterford | 3868 | 12/16/2016 01/26/2017 | 2016008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Include Appropriate Quantitative Acceptance Criteria for the Reconstituted Feedwater/Emergency Feedwater Monitoring Plan Associated with Steam Generator Replacement Induced Vibration |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to include appropriate quantitative acceptanc
Region: IV | Waterford | 3844 | 09/30/2016 11/10/2016 | 2016003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Assembling a Safety-Related Valve Actuator |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors reviewed a self-revealing, Green, non-cited violation of Technical Specification 6.8, "Procedures and Programs," associated with the licensee's failure to perform maintenance that could affect the performance of safety-related equipment in
Region: IV | Waterford | 3838 | 06/30/2016 08/05/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Pre-Plan and Perform Maintenance on the Cable Vault and Switchgear Ventilation System |  | P.1 Identification | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 6.8, "Procedures and Programs," associated with the licensee's failure to properly pre-plan and perform maintenance on safety-related components in accordance with EN-DC-335, "Prev
Region: IV | Waterford | 3839 | 06/30/2016 08/05/2016 | 2016002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Assess and Manage Risk When Performing Dry Cooling Tower Maintenance |  | H.8 Procedure Adherence | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," section (a)(4) because the licensee did not properly assess and manage risk associated with maintenanc
Region: IV | Waterford | 3840 | 06/30/2016 08/05/2016 | 2016002-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Perform Drills Required by the Site Emergency Plan |  | H.5 Work Management | TE?: N | 05000382 Waterford 3 |  | 71114.05 | The inspectors identified a non-cited violation of 10 CFR 50.54(q)(2), which requires a power reactor licensee to follow and maintain the effectiveness of the site emergency plan. Specifically, Waterford Steam Electric Station, Unit 3, failed to conduct t
Region: IV | Waterford | 3843 | 06/30/2016 08/05/2016 | 2016002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Account for Starting Air Design Features in Emergency Diesel Operating Procedures |  | P.2 Evaluation | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing, Green, non-cited violation of Technical Specification 6.8, "Procedures and Programs," occurred because the licensee did not establish adequate procedures for the operation of the emergency diesel generators. Specifically, prior to July 7
Region: IV | Waterford | 3833 | 03/31/2016 04/25/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assess and Manage the Increase in Risk from Emergent Maintenance Activities |  | H.8 Procedure Adherence | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65, "Requirements for Monitoring the Effectiveness of Maintenance at Nuclear Power Plants," section a(4), for the licensee's failure to assess and manage the increase in risk during an auxiliary
Region: IV | Waterford | 3824 | 10/03/2015 01/21/2016 | 2015004-01 | NRC | NCV | Initiating Events | Green | Failure to Properly Pre-Plan and Perform Maintenance on the Core Element Assembly Calculators |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors reviewed a self-revealing, Green, non-cited violation of Technical Specification 6.8.1.a associated with the licensee's failure to properly pre-plan and perform maintenance in accordance with EN-DC-153, "Preventative Maintenance Component C
Region: IV | Waterford | 3818 | 09/30/2015 11/12/2015 | 2015003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Design Control Measures for Safety-Related Emergency Feedwater System Valves |  |  | TE?: N | 05000382 Waterford 3 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," because the licensee failed to verify the adequacy of the design of the emergency feedwater system. As a result, on June 3, 2015,
Region: IV | Waterford | 3819 | 09/30/2015 11/12/2015 | 2015003-02 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Procedures when Changing Materials Used for Feedwater Heater Level Control Valves |  |  | TE?: N | 05000382 Waterford 3 |  | 71153 | The inspectors reviewed a self-revealing finding of very low safety significance that occurred because the licensee did not follow procedural guidance when changing materials used for feedwater heater level control valves. As a result, a feedwater heater
Region: IV | Waterford | 3823 | 09/17/2015 09/30/2015 | 2015008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedures for a Design Basis Tornado Event |  | P.2 Evaluation | TE?: N | 05000382 Waterford 3 |  | 71111.17T | Green. The team identified two examples of a Green, non-cited violation of Technical Specification 6.8.1, which states, in part, "Written procedures shall be established, implemented, and maintained, covering the activities including procedures recommende
Region: IV | Waterford | 3813 | 04/24/2015 07/30/2015 | 2015002-01 | NRC | NCV | Initiating Events | Green | Failure to Identify and Secure Potential Tornado-Borne Missile Hazards |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71111.01 | The inspectors identified a non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33, Revision 2, Appendix A, for the licensee's failure to follow procedure OP-901-521, "Severe Weather and Flooding," Revision 313. Specifically, o
Region: IV | Waterford | 3817 | 03/02/2015 07/30/2015 | 2015002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Instructions in Painting Procedure while Painting on Safety-Related Equipment |  | H.2 Field Presence | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to follow procedure PMC-002-007, "Maintenance and Construction Painting," while
Region: IV | Waterford | 3502 | 02/21/2015 05/14/2015 | 2015001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Perform Testing of Safety-Related Dry Cooling Tower Tube Bundle Isolation Valves |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.04Q | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee did not identify and perform testing for safety-related components to demonstrate that they would perform satisfactorily in
Region: IV | Waterford | 3532 | 02/13/2015 05/27/2015 | 2015007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Fire Area Boundary |  | H.1 Resources | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(9), "Fire Protection," for the failure to ensure the required separation between fire areas. Specifically, the licensee installed fire barriers on two ventilation ducts which were not in
Region: IV | Waterford | 3808 | 02/13/2015 05/27/2015 | 2015007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide a Bounding Calculation for Time Critical Actions |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9, "Fire Protection," for the failure to adequately correct a previous violation. Specifically, the licensee failed to provide a bounding calculation for the amount of time available for o
Region: IV | Waterford | 3811 | 02/13/2015 05/27/2015 | 2015007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Periodically Test Emergency Lighting Units |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9, "Fire Protection," for the failure to periodically test and demonstrate the 8-hour capacity of the Appendix R emergency lighting units. The licensee entered this issue into their correc
Region: IV | Waterford | 3812 | 02/13/2015 05/27/2015 | 2015007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Long Standing Deficiencies with the Appendix R Emergency Lighting Units |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9, "Fire Protection," for the failure to correct adverse conditions associated with fire protection. Specifically, the licensee failed to correct longstanding deficiencies with the Appendi
Region: IV | Waterford | 3513 | 01/14/2015 05/14/2015 | 2015001-03 | NRC | NCV | Public Radiation Safety | Green | Failure to Develop the Transportation Security Plan |  | H.1 Resources | TE?: N | 05000382 Waterford 3 |  | 71124.08 | The inspectors identified a non-cited violation of 10 CFR 71.5, "Transportation of Licensed Material," and 49 CFR 172, Subpart I, "Safety and Security Plans." Specifically, licensee personnel failed to adequately develop their transportation security pl
Region: IV | Waterford | 3486 | 01/12/2015 01/22/2015 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Evaluate Elevated Bus Voltages |  | P.4 Trending | TE?: N | 05000382 Waterford 3 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions,
Region: IV | Waterford | 3487 | 01/12/2015 01/22/2015 | 2014007-02 | NRC | FIN | Mitigating Systems | Green | Inadequate Station Procedures for Temporary Emergency Diesel Generator |  | H.4 Teamwork | TE?: N | 05000382 Waterford 3 |  | 7111121 | Green. The team identified a Green finding for inadequate station procedures for the temporary emergency diesel generators. Specifically, the licensee failed to ensure that Procedures OP-TEM-008, "Emergency Diesel Generator A(B) Backup Temporary Diesel Ge
Region: IV | Waterford | 3488 | 01/12/2015 01/22/2015 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Condition Report for a Condition Adverse to Quality |  | H.5 Work Management | TE?: N | 05000382 Waterford 3 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions,
Region: IV | Waterford | 3496 | 01/12/2015 01/22/2015 | 2014007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Missile Protection Requirements for Emergency Diesel Generator Day and Storage Tank Vents |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Waterford | 3497 | 01/12/2015 01/22/2015 | 2014007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Through Wall Corrosion on Emergency Diesel Generator A and B Day Tank Vents | EA Case: 2014228 | H.8 Procedure Adherence | TE?: N | 05000382 Waterford 3 |  | 7111121 | -TBD. The team identified an apparent violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficien
Region: IV | Waterford | 3499 | 01/12/2015 01/22/2015 | 2014007-06 | NRC | NCV | Barrier Integrity | Green | Failure to Properly Evaluate Main Feedwater Isolation Valve Required Thrust |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | Green. The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "design control measures shall provide for verifying or checking the adequacy of design, such as by the performa
Region: IV | Waterford | 3500 | 01/12/2015 01/22/2015 | 2014007-07 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Properly Evaluate Main Steam Isolation Valve Weak Link |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states in part, that design control measures shall provide for verifying or checking the adequacy of design, such as by the performance o
Region: IV | Waterford | 3524 | 01/09/2015 05/14/2015 | 2015001-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Tightening Thermal Overload Connections for Safety-Related Components |  |  | TE?: N | 05000382 Waterford 3 |  | 71153 | A self-revealing, non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33, Revision 2, Appendix A, was identified for the failure to perform maintenance that could affect the performance of safety-related equipment in accordance
Region: IV | Waterford | 3512 | 01/08/2015 05/14/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Fire Protection |  | H.12 Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71111.05Q | The inspectors identified a finding of very low safety significance and an associated non-cited violation of Waterford Steam Electric Station, Unit 3, License Condition 2.C.9, and the fire protection program for the licensee's failure to identify and co
Region: IV | Waterford | 3476 | 12/31/2014 02/12/2015 | 2014005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Control Potential Tornado-Borne Missile Hazards |  | H.2 Field Presence | TE?: N | 05000382 Waterford 3 |  | 71111.01 | The inspectors identified a non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33, Revision 2, Appendix A, for the licensee's failure to follow procedure OP-901-521, "Severe Weather and Flooding," Revision 312, on two separate i
Region: IV | Waterford | 3477 | 12/31/2014 02/12/2015 | 2014005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow the Operability Determination Process |  | H.13 Consistent Process | TE?: N | 05000382 Waterford 3 |  | 71111.15 | TThe inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to assess immediate operability of safety-related systems in accordance with site procedures,
Region: IV | Waterford | 3478 | 12/31/2014 02/12/2015 | 2014005-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish an Inspection Schedule of the Dry Cooling Towers |  | P.1 Identification | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 6.8.1.a and Regulatory Guide 1.33, Revision 2, Appendix A, for failure of the licensee to develop a preventative maintenance schedule for inspections of safety-relate
Region: IV | Waterford | 3479 | 12/31/2014 02/12/2015 | 2014005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Design Control Measures for the Suitability of Safety-Related Relays |  | H.11 Challenge the Unknown | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to establish measures for the selection and review for suitability of application of materials, parts,
Region: IV | Waterford | 3484 | 12/31/2014 02/12/2015 | 2014005-05 | NRC | FIN | Occupational Radiation Safety | Green | Failure to Adequately Plan and Control Work Activities Related to Alloy 600 Pipe Weld Inspections to Ensure Doses were ALARA. |  | H.5 Work Management | TE?: N | 05000382 Waterford 3 |  | 71124.02 | The inspectors identified a finding associated with the licensee's failure to adequately plan and control work activities associated with Alloy 600 ultrasonic examinations during Refueling Outage 19. Specifically, the inspectors concluded that, had the
Region: IV | Waterford | 3485 | 12/31/2014 02/12/2015 | 2014005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Correct a Condition Adverse to Quality in a Timely Manner |  | H.14 Conservative Bias | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a finding of very low safety significance and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the licensee's failure to correct a condition adverse to quality in a time comme
Region: IV | Waterford | 3444 | 06/30/2014 08/08/2014 | 2014003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to Control Entry into a High Radiation Area |  | H.12 Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 6.12.1 because a worker entered a high radiation area, but was not on a radiation work permit that authorized entry and was not knowledgeable of the dose rates in the
Region: IV | Waterford | 3449 | 06/30/2014 08/08/2014 | 2014003-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Adequate Public Address System to Implement Onsite Protective Actions. |  | P.2 Evaluation | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50.54(q)(2) for a failure to maintain the effectiveness of an emergency plan that meets the planning standards of 10 CFR Part 50.47(b). Specifically, the licensee failed to maintain the public
Region: IV | Waterford | 3450 | 06/06/2014 07/24/2014 | 2014008-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedures for Securing Dry Cooling Tower Fans |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71152B | A self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion III occurred when the licensee did not assure that design basis information was translated into specifications, drawings, procedures, and instructions. Specifically, after a fai
Region: IV | Waterford | 3456 | 06/06/2014 07/24/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Condition Adversely Affecting Flooding Mitigation Design |  | P.3 Resolution | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the licensee's failure to identify and correct a condition adverse to quality. On May 19, 2014, the team identified a significant amount of debris on the floor of
Region: IV | Waterford | 3457 | 06/06/2014 07/24/2014 | 2014008-03 | NRC | NCV | Initiating Events | Green | Failure to Identify a Cause and Implement Corrective Actions to Prevent Recurrence for a Significant Condition Adverse to Quality |  | H.1 Resources | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for a failure to identify a cause and take corrective actions to prevent recurrence. Specifically, the licensee did not identify a cause or corrective actions to preve
Region: IV | Waterford | 3463 | 06/06/2014 07/24/2014 | 2014008-04 | NRC | FIN | Initiating Events | Green | Failure to Evaluate Operating Experience as Directed in Station Procedure |  | H.14 Conservative Bias | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a finding for the licensee's failure to evaluate industry operating experience as directed in the station operating experience program procedure. Specifically, a vendor supplied Technical Bulletin TB-13-1 "Steam Generator and Pressuriz
Region: IV | Waterford | 3464 | 06/06/2014 07/24/2014 | 2014008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Multiple Degraded or Nonconforming Conditions |  | P.2 Evaluation | TE?: N | 05000382 Waterford 3 |  | 71152B | The inspectors identified multiple instances of the licensee's failure to promptly correct degraded or nonconforming conditions as required by 10 CFR Part 50, Appendix B, Criterion XVI. At the conclusion of the inspection, the licensee had one structure,
Region: IV | Waterford | 3443 | 02/20/2014 05/08/2014 | 2014002-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Establish Adequate Design Control Measures for the Selection and Review for the Suitability of Application of Molded Case Circuit Breakers |  | H.12 Avoid Complacency | TE?: N | 05000382 Waterford 3 05000382 Waterford 3 |  | 71152 | A self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," occurred because the licensee did not establish design control measures for the selection and review for the suitability of application of a molded case
Region: IV | Waterford | 3430 | 01/08/2014 05/08/2014 | 2014002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Replace an Essential Chiller Oil Pump prior to the End of Duty Life. |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.12 | A Green self-revealing, non-cited violation of Technical Specification 6.8.1.a, occurred because the licensee did not establish preventative maintenance schedule to inspect or replace an item that have a specific lifetime. Specifically, the licensee did n
Region: IV | Waterford | 3428 | 01/06/2014 05/08/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Procedures for Using the Alternate Emergency Fuel Oil Storage Tank Fill Line. |  | H.12 Avoid Complacency | TE?: N | 05000382 Waterford 3 |  | 71111.04Q | An NRC-identified Green, non-cited violation of Technical Specification 6.8.1.a, occurred because the licensee did not establish written procedures for filling emergency power sources. Specifically, the licensee did not establish procedures to fill the fu
Region: IV | Waterford | 3431 | 01/03/2014 05/08/2014 | 2014002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Evaluation for Transient Combustibles. |  | H.14 Conservative Bias | TE?: N | 05000382 Waterford 3 |  | 71111.15 | An NRC-identified Green, non-cited violation of Waterford's Facility Operating License Number NPF-38, License Condition 2.C.9 and the Fire Protection Program occurred because the licensee failed to follow procedures. Specifically, the licensee did not per
Region: IV | Waterford | 3417 | 12/06/2013 02/07/2014 | 2013005-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique Weaknesses During an Evaluated Exercise |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71114.01 | The inspectors identified a non-cited violation of 10 CFR Part 50.47(b)(14) for the failure to identify deficiencies resulting from the licensee's 2013 biennial evaluated exercise. Specifically, the licensee did not identify as part of the critique proces
Region: IV | Waterford | 3407 | 09/30/2013 11/20/2013 | 2013004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Fire Protection Program Procedure Requirements When Securing from a Fire Watch |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000382 Waterford 3 |  | 71111.05Q | The inspectors identified a non-cited violation of Waterford's Facility Operating License Number NPF-38, License Condition 2.C.9, because the licensee did not implement fire protection procedure FP-001-014, "Duties of a Fire Watch." Specifically, the lice
Region: IV | Waterford | 3408 | 09/30/2013 11/20/2013 | 2013004-03 | NRC | NCV | Mitigating Systems | Green | Failure to accomplish activities affecting quality on a degraded safety-related solenoid valve in accordance with procedure requirements |  | H.3(b) Work Activity Coordination | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee did not accomplish activities affecting quality on a degraded safety-related train B component cooli
Region: IV | Waterford | 3386 | 06/30/2013 08/13/2013 | 2013003-01 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate design control measures for verifying or checking the adequacy of the effects of a PMP flooding event on the reactor auxiliary building roof areas that contained safety-rea |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000382 Waterford 3 |  | 71111.01 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, because the licensee did not provide design control measures for verifying or checking the adequacy of the features designed to withstand the effects of a probab
Region: IV | Waterford | 3394 | 06/30/2013 08/13/2013 | 2013003-03 | NRC | NCV | Barrier Integrity | Green | Failure to comply with Action 4 of TS 3.3.1 during shutdown with the protective system trip breakers in the open position for Modes 4 and 5 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000382 Waterford 3 |  | 71111.2 | The inspectors identified a non-cited violation of Waterford Steam Electric Station, Unit 3, Technical Specification (TS) Limiting Condition of Operation (LCO) 3.3.1 because the licensee did not take action to suspend operations that involved reactivity c
Region: IV | Waterford | 3398 | 06/30/2013 08/13/2013 | 2013003-05 | Self - Revealed | NCV | Initiating Events | Green | Failure to provide adequate post modification testing instructions for vibration monitoring on the feedwater piping system following steam generator replacement |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71111.01 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, because the licensee did not provide adequate post modification testing instructions for activities affecting quality to the circumstances that includ
Region: IV | Waterford | 3382 | 03/31/2013 05/14/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Control Potential Tornado Borne Missile Hazards |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.01 | The inspectors identified a Green, NCV of Technical Specification 6.8.1.a for failure to follow Procedure OP-901-521, "Severe Weather and Flooding," Revision 307. Specifically, on February 25, 2013, the licensee entered the off-normal procedure due to a t
Region: IV | Waterford | 3383 | 03/31/2013 05/14/2013 | 2013002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Determination for Nitrogen Leak in MSIV |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.15 | The inspectors identified a Green NCV of 10 CFR Part 50, Appendix B, Criterion V "Instructions, Procedures, and Drawings," for the failure of the licensee to accomplish activities affecting quality in accordance with written procedures. Specifically, oper
Region: IV | Waterford | 3385 | 03/31/2013 05/14/2013 | 2013002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Perform Testing to Demonstrate Local Manual Operation Action on Safety-Related Air-Operated Valves |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a NCV of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee failed to identify and perform testing on safety-related components to demonstrate that they would perform satisfactorily in service in accor
Region: IV | Waterford | 3371 | 12/31/2012 02/14/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to promptly identify and correct the cause of repetitive failures associated with train A component cooling water radiation monitor |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, because the licensee did not promptly identify and correct a condition adverse to quality associated with the train A safety-related component cooling water (CCW
Region: IV | Waterford | 3357 | 10/23/2012 02/14/2013 | 2012005-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to implement control measures to ensure that activated materials were not raised above or brought near the surface of the refueling pool, causing a locked high radiation area |  | H.3(a) Work Planning | TE?: N | 05000382 Waterford 3 |  | 71124.01 | The inspectors reviewed a self-revealing non-cited violation of Technical Specification 6.12.2 which resulted because licensee representatives failed to implement control measures to ensure that activated materials were not raised above or brought near th
Region: IV | Waterford | 3094 | 09/30/2012 11/14/2012 | 2012004-01 | NRC | NCV | Mitigating Systems | Green | Failure to establish procedural controls to ensure that licensed operators could perform immediate and time critical operator actions associated with security and fire events |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71111.11Q | The inspectors identified a non-cited violation of Waterford Steam Electric Station, Unit 3, Technical Specification 6.8.1.a because the licensee did not establish procedural controls to ensure that the assigned minimum staff of licensed operators could p
Region: IV | Waterford | 3100 | 09/30/2012 11/14/2012 | 2012004-02 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct degraded conditions associated with the auxiliary component cooling water heat exchanger outlet temperature control valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI because the licensee did not promptly identify and correct conditions adverse to quality related to the header A auxiliary component cooling water heat exchanger
Region: IV | Waterford | 3101 | 09/30/2012 11/14/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Failure to identify and correct a torn diaphragm of a safety-related air operated valve associated with the emergency feedwater system |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI because the licensee did not promptly identify and correct a condition adverse to quality associated with the B emergency feedwater backup control valve EFW-223B.
Region: IV | Waterford | 3318 | 09/30/2012 11/14/2012 | 2012004-04 | NRC | NCV | Initiating Events | Green | Failure to adequately access and manage risk before performing maintenance activities associated with non-standard lifts |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(4) because the licensee did not assess and manage the overall on line risk involved with maintenance activities that lifted heavy loads over safety related equipment. Specifically, the lic
Region: IV | Waterford | 3340 | 09/24/2012 11/05/2012 | 2012008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Determine the Operability of the Emergency Diesel Generators |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a failure to follow the Operability Determination Process. Specifically, the licensee failed to determine the operabi
Region: IV | Waterford | 3341 | 09/24/2012 11/05/2012 | 2012008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Take Corrective Action Associated with Emergency Feedwater Pump AB |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to take timely corrective action for a condition adverse to quality. Specifically, from May 2011, through August 2012, the license
Region: IV | Waterford | 3348 | 09/24/2012 11/05/2012 | 2012008-03 | NRC | VIO | Mitigating Systems | Green | Failure to Take Timely Corrective Action to Establish a Basis for Flood Control Measures | EA Case: 2012198 | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control", for the failure to establish measures to assure that applicable regulatory requirements and the design basis as defined in 10 CFR 50.2 are correctly tr
Region: IV | Waterford | 3349 | 09/24/2012 11/05/2012 | 2012008-04 | NRC | NCV | Initiating Events | Green | Failure to Ensure Operator Knowledge of Equipment Status |  | H.4(b) Procedural Compliance | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a failure to follow Procedure EN-OP-115, "Conduct of Operations". Specifically, the licensee failed to ensure that control
Region: IV | Waterford | 3356 | 09/24/2012 11/05/2012 | 2012008-05 | NRC | NCV | Initiating Events | Green | Failure to Develop Effective Corrective Actions to Preclude Repetition |  | H.4(b) Procedural Compliance | TE?: N | 05000382 Waterford 3 |  | 71152B | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," because the licensee failed to determine the cause of a significant condition adverse to quality and take corrective actions to preclude re
Region: IV | Waterford | 3085 | 06/30/2012 06/30/2012 | 2012003-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to establish adequate procedural guidance to control feedwater heater level control valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.12 | A self-revealing finding occurred because the licensee did not establish adequate procedural guidance to control feedwater heater level control valves. Specifically, the procedures used to control the settings for the valves did not contain guidance that
Region: IV | Waterford | 3093 | 06/30/2012 06/30/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Failure to provide adequate design control measures for verifying or checking the adequacy of the ultimate heat sink thermal performance analysis |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III because the licensee did not provide adequate design control measures for verifying or checking the adequacy of the ultimate heat sink thermal performance analysi
Region: IV | Waterford | 3079 | 03/31/2012 04/26/2012 | 2012002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Develop Preventive Maintenance Tasks for Critical Limit Switches on Component Cooling Water Inlet Isolation Valves |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.19 | A Green self-revealing, non-cited violation of Waterford Steam Electric Station, Unit 3, Technical Specification 6.8.1.a occurred because the licensee did not establish procedures for performing preventive maintenance tasks on the dry cooling tower compon
Region: IV | Waterford | 3082 | 03/31/2012 04/26/2012 | 2012002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Perform Testing to Demonstrate Performance of Safety-Related Valves |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, because the licensee did not identify and perform testing on a safety-related component to demonstrate that it would perform satisfactorily in service in ac
Region: IV | Waterford | 3077 | 02/17/2012 03/12/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate the Impact of Fire Damage on the Dry Cooling Tower Fans |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9 and Appendix R, Section III.G for the failure to adequately evaluate the impact of fire damage on the dry cooling tower fans. Specifically, the failure to adequately evaluate fire damage
Region: IV | Waterford | 3078 | 02/17/2012 03/12/2012 | 2012007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Calculate Adequate Cooling Provided to Diesel Generator B within Required Time |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9 and the fire protection program for the failure to perform a post-fire safe shutdown analysis design calculation. Specifically, the team determined that the licensee had not calculated t
Region: IV | Waterford | 3044 | 12/31/2011 02/08/2012 | 2011005-01 | NRC | NCV | Barrier Integrity | Green | Inoperable Train of Containment Cooling System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.07T | The inspectors identified a non-cited violation of Technical Specification Limiting Condition for Operation 3.6.2.2, "Containment Cooling System", which requires in Modes 1, 2, 3, and 4 that "Two independent trains of containment cooling shall be OPERABLE
Region: IV | Waterford | 3013 | 12/31/2011 02/08/2012 | 2011005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Quality Associated with the Main Feedwater Isolation Valves |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10CFR50, Appendix B, Criterion XVI because the licensee failed to identify and correct a condition adverse to quality associated with the main feedwater isolation valve. Specifically, the licensee did not
Region: IV | Waterford | 3053 | 12/31/2011 02/08/2012 | 2011005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Tornado Impact on the Ultimate Heat Sink During a Refueling Outage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71151 | The inspectors identified a non-cited violation of 10CFR50, Appendix B, Criterion III because the licensee did not translate applicable regulatory requirements and the design basis into specifications and instructions. Specifically, the licensee did no
Region: IV | Waterford | 3054 | 12/31/2011 02/08/2012 | 2011005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Work Order Instructions to Install a Swagelok Fitting on a Main Feedwater Isolation Valve Tube Connection |  |  | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a non-cited violation of Technical Specification 6.8.1.a because the licensee did not follow work order instructions to install a pressure gage in an air line used to measure and maintain pressure for the hydraulic accumulator
Region: IV | Waterford | 3055 | 10/07/2011 12/14/2011 | 2011007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Assure Design Basis Input was Correctly Translated into Design Basis Calculations |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly
Region: IV | Waterford | 3056 | 10/07/2011 12/14/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Adequate Containment Spray Pump Design Basis Verification Surveillance Test |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A program shall be established to assure that all testing required to demonstrate that structures, systems, and components
Region: IV | Waterford | 3057 | 10/07/2011 12/14/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Basis for Extrapolation of Vendor Supplied Pump Net Positive Suction Head Values |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design bases are correctly
Region: IV | Waterford | 3062 | 10/07/2011 12/14/2011 | 2011007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Preventive Maintenance Procedures for Aluminum/Copper Electrical Connections to the Ultimate Heat Sink Transformers |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, "Activities affecting quality shall be prescribed by documented instructions, procedures, or drawings, of a
Region: IV | Waterford | 3063 | 10/07/2011 12/14/2011 | 2011007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Analysis to Support the Adequacy of the Four Inch Bulkhead Drain to Protect the Ultimate Heat Sink During Flood Events |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design bases are correctly
Region: IV | Waterford | 3074 | 10/07/2011 12/14/2011 | 2011007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Establish an Analysis of the Effects of Reverse Rotation of Dry Cooling Tower Fan Motors Resulting from a Tornado Event |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translate
Region: IV | Waterford | 3075 | 10/07/2011 12/14/2011 | 2011007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Provide an Adequate Basis for Temperature Limits of Auxiliary Component Cooling Water Pump Motor Bearings |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly
Region: IV | Waterford | 3076 | 10/07/2011 12/14/2011 | 2011007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Manage the Risk Involved with a Maintenance Window for the Turbine Driven Essential Feedwater Pump |  | P.3(a) Self-Assessment | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a Green noncited violation of 10 CFR 50.65(a)(4), which states, in part, that "the licensee shall assess and manage the increase in risk that may result from the proposed maintenance activities." Specifically, on October 28, 2010 the t
Region: IV | Waterford | 3029 | 09/30/2011 11/14/2011 | 2011004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate and Adequately Perform Preventive Maintenance Activities Assiocated with the Dry Cooling Tower Process Analog Control Cards |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65 (a)(3) because the licensee did not adequately evaluate and take into account, where practical, industry operating experience related to preventive maintenance activities for the dry cooling
Region: IV | Waterford | 3030 | 09/30/2011 11/14/2011 | 2011004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Implement a Reactor Coolant System Drain Down Procedure |  | H.3(b) Work Activity Coordination | TE?: N | 05000382 Waterford 3 |  | NONE | The inspectors documented a self-revealing non-cited violation of Technical Specification 6.8.1.a because the licensee did not adequately implement Operating Procedure OP-001-003, "Reactor Coolant System Drain Down," during the installation of the incore
Region: IV | Waterford | 3035 | 09/30/2011 11/14/2011 | 2011004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide Adequate Testing for a Shutdown Cooling Heat Exchanger Outlet Stop Check Valve |  |  | TE?: N | 05000382 Waterford 3 |  | NONE | The inspectors documented a self-revealing non-cited violation of 10 CFR 50.55a, "Codes and Standards," because the licensee did not establish and maintain an adequate testing program for a shutdown cooling heat exchanger outlet stop check valve (CS-117A)
Region: IV | Waterford | 3036 | 09/30/2011 11/14/2011 | 2011004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Work Order Instructions used for Technical Specification Surveillance Procedures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee did not promptly identify and correct work order instructions used to perform technical specification surveillance requ
Region: IV | Waterford | 3040 | 09/30/2011 11/14/2011 | 2011004-05 | NRC | NCV | Mitigating Systems | Green | Failure to Comply with Technical Specification Surveillance Requirement 4.0.3 and the Limiting Conditions for Operation for Technical Specifications 3.0.3 |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification (TS) because the licensee did not enter or comply with the technical specification action requirements. Specifically, the licensee did not enter or comply with Technical Specificat
Region: IV | Waterford | 3041 | 09/30/2011 11/14/2011 | 2011004-06 | NRC | NCV | Mitigating Systems | Green | Untimely Actions to Correct Repetitive Dry Cooling Tower Fan Failures |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee did not promptly correct a condition adverse to quality related to repetitive failures of the dry cooling tower fans to star
Region: IV | Waterford | 3042 | 09/30/2011 11/14/2011 | 2011004-07 | NRC | FIN | Initiating Events | Green | Failure to Follow Apparent Cause Evaluation Process Procedure |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a finding because the licensee did not implement procedure EN-LI-119, "Apparent Cause Evaluation Process." Specifically, the licensee did not follow the requirements provided in procedure EN-LI-119, Section 5.3.3 (k), to complete
Region: IV | Waterford | 3006 | 06/30/2011 08/11/2011 | 2011003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate and Adequately Monitor Activities Associated with the Internal Conditions of the Condensate and Refueling Water Storage Pool Structures. |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR 50.65(a)(3) because the licensee did not evaluate or adequately monitor activities associated with the condition of the condensate and refueling water storage pools structures. Specifically, the li
Region: IV | Waterford | 3008 | 06/30/2011 08/11/2011 | 2011003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Implement Written Procedures for Restoring a Time Delay Relay Associated with the 'A' Emergency Diesel Generator Output Breaker. |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71111.19 | A self-revealing non-cited violation of Technical Specification 6.8.1.a occurred because the licensee did not implement written procedures and instructions. Specifically, maintenance personnel did not follow procedure ME-007-005, "Time Delay Relay Setting
Region: IV | Waterford | 3009 | 06/30/2011 08/11/2011 | 2011003-04 | Self - Revealed | FIN | Initiating Events | Green | Failure to Implement Work Order Instructions to Restore a Feedwater Heater Drain Valve. |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing finding occurred because maintenance personnel did not follow written procedures during the calibration of a level switch that controls feedwater heater drain valve FHD703A. Specifically, the licensee did not perform concurrent verificati
Region: IV | Waterford | 3003 | 03/31/2011 05/13/2011 | 2011002-01 | NRC | NCV | Barrier Integrity | Green | Control Room Envelope Preconditioning |  | H.3(a) Work Planning | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," because the licensee did not conduct required technical specification surveillance testing on equipment in an as-found condition. Specifically, th
Region: IV | Waterford | 3004 | 03/31/2011 05/13/2011 | 2011002-02 | NRC | NCV | Initiating Events | Green | Failure to follow Operability Determination Process for a Degraded and Non-Conforming condition Related to Reactor Coolant Pump N9000 Seals |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.12 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee did not adequately implement the operability determination process requirements in accordance with E
Region: IV | Waterford | 2996 | 12/31/2010 01/11/2011 | 2010005-04 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Conduct Timely Corrective Actions to Replace Degraded Diodes in Safety Related Inverters |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing non-cited violation (NCV) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," occurred because the licensee did not promptly correct a condition adverse to quality that affected static uninterruptible power supply inverters
Region: IV | Waterford | 2978 | 06/30/2010 08/13/2010 | 2010003-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Conduct Timely Corrective Actions to Replace Faulty Relays |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," occurred because the licensee did not conduct timely corrective actions to preclude repetition of a significant condition adverse to quality that involv
Region: IV | Waterford | 3005 | 06/14/2010 01/11/2011 | 2010005-05 | NRC | NCV | Mitigating Systems | Green | Failure to Implement the Experience and Qualification Requirements of the Quality Assurance Program |  |  | TE?: N | 05000382 Waterford 3 |  | 71152
Region: IV | Waterford | 2983 | 05/28/2010 07/12/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Repetitive Voiding in the Low Pressure Safety Injection System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to preclude repetition of a significant condition adverse to quality. Specifically, licensee corrective actions to prevent recurren
Region: IV | Waterford | 2984 | 05/28/2010 07/12/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Failure to Derive Technical Specifications from Analysis |  |  | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a noncited violation of 10 CFR 50.36 (b), "Technical Specifications," for failure to derive technical specifications from the analyses and evaluation included in the safety analysis report. Specifically, the licensee failed to derive a
Region: IV | Waterford | 2985 | 05/28/2010 07/12/2010 | 2010006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Multiple Conditions Adverse to Quality |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to ensure that conditions adverse to quality are promptly corrected. Specifically, multiple examples of boric acid leaks were ident
Region: IV | Waterford | 2971 | 03/31/2010 05/10/2010 | 2010002-01 | NRC | NCV | Initiating Events | Green | Failure to Control Transient Combustibles |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71111.05Q | The inspectors identified five examples of a green noncited violation of Waterford Steam Electric Station, Unit 3's license condition 2.C.9 for the failure to perform a transient combustible evaluation prior to introducing transient combustibles into proc
Region: IV | Waterford | 2955 | 12/31/2009 02/05/2010 | 2009005-01 | Self - Revealed | NCV | Initiating Events | Green | Reactor Coolant Pump Vapor Seal Leakage |  | H.3(a) Work Planning | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, was identified for the licensee's failure to promptly correct a condition adverse to quality. Specifically, the licensee did not promptly correct reactor coolant pump
Region: IV | Waterford | 2954 | 12/31/2009 02/05/2010 | 2009005-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Update Drawings after Design Change |  | P.2(b) Implementing Operating Experience | TE?: N | 05000382 Waterford 3 |  | 71152 | A self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, was identified for the licensee's failure to prescribe an activity affecting quality by documented instructions, procedures, or drawings appropriate to the circumstance
Region: IV | Waterford | 2956 | 12/31/2009 02/05/2010 | 2009005-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to follow radiation protection procedural requirements |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 7112101 | The inspectors reviewed a self-revealing, noncited violation of Technical Specification 6.8.1 which resulted from a worker failing to follow radiation protection procedures. A contract radiation worker went to work near steam generator 1 rather than the a
Region: IV | Waterford | 2967 | 10/19/2009 11/05/2009 | 2009010-02 | NRC | NCV | Mitigating Systems | Green | Failure to identify an adverse trend in failures of time-delay relays |  | P.1(b) Trend Performance CAP | TE?: N | 05000382 Waterford 3 |  | 93812 | The team identified a violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee failed to perform a root cause analysis and implement corrective actions to prevent repetition of a significant condition adverse to quality
Region: IV | Waterford | 2968 | 10/19/2009 11/05/2009 | 2009010-03 | NRC | NCV | Mitigating Systems | Green | Inappropriate extension of qualified service life of Agastat relays |  |  | TE?: N | 05000382 Waterford 3 |  | 93812 | The team identified a violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which occurred when the licensee inappropriately extended the service life of 322 safety-related Tyco/Agastat series E7000 time-delay relays without having an adequ
Region: IV | Waterford | 2948 | 10/07/2009 11/18/2009 | 2009004-01 | NRC | NCV | Mitigating Systems | Green | Failure to follow technical specification requirements for Reactor Protective Instrumentation. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors identified a Green non-cited violation of technical specification 3.3.1, Reactor Protective Instrumentation. The technical specifications require all four channels (A, B, C, and D) of local power density, departure from nucleate boiling rat
Region: IV | Waterford | 2932 | 09/18/2009 11/02/2009 | 2009009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Reduction of Flow from the Emergency Feedwater System to the Steam Generators |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee did not account for reduction of flow from the emergency feedwater system when analyzing the flow rate to the steam generat
Region: IV | Waterford | 2933 | 09/18/2009 11/02/2009 | 2009009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Proper Design Control Measures to Assure Adequate Design and to Properly Translate the Design into Test Procedures. |  | P.3(a) Self-Assessment | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," with three examples. Example 1: The licensee did not use the correct size emergency feedwater system suction piping in calculation MNQ10-12 "Net Po
Region: IV | Waterford | 2938 | 09/18/2009 11/02/2009 | 2009009-03 | NRC | NCV | Mitigating Systems | Green | Failure to have an Operating Procedure for Executing an Evolution Credited in the UFSAR and in an Request for a License Amendment |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings" pertaining to the emergency diesel generator fuel oil transfer pump. Criterion V states, in part, "activities affecting quality s
Region: IV | Waterford | 2939 | 09/18/2009 11/02/2009 | 2009009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Analyze the Effect of Acceptable Reverse Flow through Emergency Feedwater Check Valves |  | P.3(a) Self-Assessment | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." Specifically, the licensee failed to analyze the effects of the acceptable back leakage of 25 gpm from the emergency feedwater pump discharge check va
Region: IV | Waterford | 2946 | 09/18/2009 11/02/2009 | 2009009-06 | NRC | FIN | Initiating Events | Green | Failure to Incorporate Start-Up Transformer Protective Relay Design Basis into Instructions, Procedures, or Drawings. |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a finding for failure to translate design basis criteria into a design basis document for the start-up transformer '3A' 51G relay to support the settings listed in Calculation EC E90 012, "Protective Relays Settings for Main Generator
Region: IV | Waterford | 2947 | 09/18/2009 11/02/2009 | 2009009-07 | NRC | NCV | Mitigating Systems | Green | Failure to Verify or Check the adequacy of Design Changes for the Emergency Diesel Generator Protective Relay IGVC-51V |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." The calculation EE2 14 3 "Diesel Generator Overcurrent Protection," Revision 1, does not document sufficient design bases for the setting of the IGCV
Region: IV | Waterford | 2911 | 06/30/2009 08/12/2009 | 2009003-01 | NRC | NCV | Emergency Preparedness | Green | Licensee Practices Result in Protective Actions Recommendations for Areas Where Protective Action Guides Are Not Exceeded |  |  | TE?: N | 05000382 Waterford 3 |  | 71114.01 | Green. The inspectors identified a noncited violation of 10 CFR 50.47(b)(10), for the licensee's failure to develop and have in place guidelines for the choice of protective actions during an emergency that were consistent with federal guidance. Specifica
Region: IV | Waterford | 2910 | 06/30/2009 08/12/2009 | 2009003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Several Conditions Adverse to Quality |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Action) for the failure to promptly correct conditions adverse to quality. The licensee had documented several conditions adverse to quality and
Region: IV | Waterford | 2901 | 06/30/2009 08/12/2009 | 2009003-03 | NRC | NCV | Mitigating Systems | Green | Failure to Determine the Cause of a 125 Vdc Battery Failure |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion VXI (Corrective Actions) because the licensee failed to identify the cause for a significant condition adverse to quality. The Train B 125 Vdc battery bank failed to
Region: IV | Waterford | 2912 | 05/22/2009 07/01/2009 | 2009006-01 | NRC | NCV | Mitigating Systems | Green | Failure to identify conditions adverse to fire protection. |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.9 for the failure to identify conditions adverse to the fire protection program, as required by Procedure UNT-005-013, "Fire Protection Program," Revision 10. Specifically, during required
Region: IV | Waterford | 2630 | 04/07/2009 05/18/2009 | 2009002-01 | NRC | FIN | Mitigating Systems | Green | Failure to Follow Commitment Tracking Procedures |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors identified a finding because the licensee inadvertently deleted procedural steps to recover an emergency diesel generator during a severe accident. The steps were part of a formal commitment to the NRC. The licensee had failed to follow the
Region: IV | Waterford | 2900 | 04/07/2009 05/18/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Obtain Voltage Readings Following a Single Cell Battery Charge |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000382 Waterford 3 |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion V (Instructions, Procedures and Drawings) because the licensee failed to implement instructions that were intended to help troubleshoot a defective 125 Vdc battery cell. In
Region: IV | Waterford | 2617 | 12/31/2008 02/11/2009 | 2008005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Untimely Corrective Actions |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000382 Waterford 3 |  | 71152 | -Green. The inspectors reviewed a self revealing noncited violation of 10 CFR 50, Appendix B, Criterion XVI due to the failure by the licensee to take prompt corrective actions following the identification of an inadequate testing method used for determin
Region: IV | Waterford | 2618 | 12/31/2008 02/11/2009 | 2008005-02 | Self - Revealed | NCV | Mitigating Systems | Green | Essential Chiller AB Component Failure Due to Inadequate Procedural Guidance |  |  | TE?: N | 05000382 Waterford 3 |  | 71152 | -Green. The inspectors reviewed a self revealing noncited violation of Technical Specification 6.8.1.a for failure to provide documented instructions appropriate to the circumstances as recommended in Appendix A of Regulatory Guide 1.33. The failure by th
Region: IV | Waterford | 2619 | 12/31/2008 02/11/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculations Used for Operability determination of SI-405 A(B) |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71152 | Green. The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion III to address three examples of inadequate calculations involving shutdown cooling Valves SI-405A and SI-405B. The calculations were also used, in part, to support
Region: IV | Waterford | 2624 | 12/31/2008 02/11/2009 | 2008005-04 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Test Procedure for Safety Injection Valves S1-405A(B) Post Modification Testing |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000382 Waterford 3 |  | 71152 | Green. The inspectors reviewed a self revealing noncited violation of 10 CFR 50, Appendix B, Criterion III due to the failure by the licensee to perform adequate post modification testing to evaluate the adequacy of design modifications made to the actuat
Region: IV | Waterford | 2615 | 10/31/2008 12/11/2008 | 2008007-01 | NRC | NCV | Barrier Integrity | Green | Failure to promptly identify and correct a condition adverse to quality. |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to promptly identify and correct a condition adverse to quality. Specifically, from March 20, 2007, through October 27, 2008, personnel failed to iden
Region: IV | Waterford | 2616 | 10/31/2008 12/11/2008 | 2008007-02 | NRC | NCV | Barrier Integrity | Green | Inadequate operability determination of a pressure boundary valve |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71152B | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for a failure to follow procedure, when the licensee failed to complete an adequate operability evaluation for Valve SI 142A. Specifically, on August 21, 2008, the
Region: IV | Waterford | 2625 | 09/16/2008 10/31/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Inadequate pressure locking calculation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.15 | Green. The inspectors identified a noncited violation of 10 CFR 50, Appendix B, Criterion III (Design Control) for an inadequate "pressure locking" design calculation for shutdown cooling Valves SI-405A and SI-405B. Plant engineers also used the calculati
Region: IV | Waterford | 2626 | 09/16/2008 10/31/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | Failure to follow integrated EDG test procedure |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.22 | Green. The inspectors identified a noncited violation of Technical Specification 6.8.1.c (Procedures) for the failure to open the Train A low pressure safety injection pump suction valve prior to pump operation during a surveillance. The butterfly valve w
Region: IV | Waterford | 2614 | 05/14/2008 08/14/2008 | 2008003-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to conspicuously post a radiation area |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 7112101 | The inspectors identified a NCV of 10 CFR 20.1902 because the licensee failed to post a radiation area conspicuously. On May 14, 2008, the inspectors toured the hot machine shop and noted a box with high radiation area signs attached. Dose rates around th
Region: IV | Waterford | 2613 | 04/30/2008 08/14/2008 | 2008003-01 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to follow procedure when entering the radiological controlled area |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 7112101 | The inspectors reviewed two examples of a self-revealing, noncited violation of Technical Specification 6.8.1 because workers failed to follow procedural requirements when preparing to enter the radiological controlled area. The first example, on April
Region: IV | Waterford | 2606 | 04/07/2008 05/13/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to re-evaluate previously identified boric acid leaks |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71111.04Q | The inspectors identified a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to implement corrective actions for a condition adverse to quality. Specifically, the licensee developed a corrective action to evalu
Region: IV | Waterford | 2607 | 04/07/2008 05/13/2008 | 2008002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to correct "Fuel Oil Receipt and Transfer" procedure |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to implement adequate corrective actions for a deficient emergency diesel generator fuel tank filling procedure (a condition adve
Region: IV | Waterford | 2608 | 04/07/2008 05/13/2008 | 2008002-03 | NRC | NCV | Mitigating Systems | Green | Essential chiller AB return Header B Isolation Valve CHW 786B Misposition |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71111.19 | The inspectors documented a self revealing noncited violation of Technical Specification 6.8.1.c (Procedures) for the failure to correctly position a valve during a surveillance. The procedure required operators to position the essential Chiller AB return
Region: IV | Waterford | 2609 | 04/07/2008 05/13/2008 | 2008002-04 | NRC | NCV | Mitigating Systems | Green | ACCW pump failure due to inaccurate operator aid |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee failed to correct a condition adverse to quality (inadequate instructions that led to low fuel oil and the failure of au
Region: IV | Waterford | 2595 | 12/31/2007 02/01/2008 | 2007005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Review Process |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.05Q | Green. The inspectors identified a Green noncited violation of Technical Specification 6.8.1.a (Procedures) for failure to correctly implement a procedure recommended in Appendix A of Regulatory Guide 1.33. Specifically, the failure to follow Site Procedu
Region: IV | Waterford | 2596 | 12/31/2007 02/01/2008 | 2007005-02 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.19 | Green. A self-revealing Green noncited violation of 10 CFR 50, Appendix B, Criterion V was identified for an inadequate maintenance procedure. Specifically, MM-006-054, "Check Valve Inspection (Tilting Disc)", lacked sufficient detail to prevent poor work
Region: IV | Waterford | 2600 | 12/31/2007 02/01/2008 | 2007005-03 | NRC | NCV | Initiating Events | Green | Reactor Coolant Pump 1A Seal Leak |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000382 Waterford 3 |  | 71111.2 | Green. A self-revealing Green noncited violation of 10 CFR 50, Appendix B, Criterion XVI was identified for the licensee's failure to promptly identify and correct a significant condition adverse to quality. Specifically, the licensee did not identify a s
Region: IV | Waterford | 2601 | 12/31/2007 02/01/2008 | 2007005-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Obtain Current Radiological Information Prior to Entering a High Radiation Area |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 7112101 | Green. The inspector reviewed a self-revealing, noncited violation of Technical Specification 6.12.1.b that resulted when workers did not obtain current radiological information before entering a high radiation area as required by the Technical Specificat
Region: IV | Waterford | 2602 | 12/31/2007 02/01/2008 | 2007005-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 7112101 | Green. The inspector reviewed two examples of a self-revealing, noncited violation of Technical Specification 5.4.1 that resulted when workers failed to follow their radiation work permit instructions. The first example occurred on October 11, 2007, when
Region: IV | Waterford | 2592 | 10/07/2007 11/09/2007 | 2007004-02 | NRC | NCV | Barrier Integrity | Green | Missed Reactor Coolant System Chemistry Samples |  | H.4(a) Human Error Prevention | TE?: N | 05000382 Waterford 3 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification (TS) 3.4.7 for multiple failures to complete a radiochemical analysis for EBAR (Average Disintegration Energy) determination within the required periodicity. Specifically, on thirte
Region: IV | Waterford | 2593 | 10/07/2007 11/09/2007 | 2007004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for a Fire in Vital Switchgear Room B |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified two examples of a noncited violation of Waterford Steam Electric Station, Unit 3 Facility Operating License Condition 2.C.9 for failure to implement and maintain in effect all provisions of the approved fire protection program as
Region: IV | Waterford | 2589 | 09/12/2007 11/09/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Boric Acid Leak Evaluation |  | H.4(b) Procedural Compliance | TE?: N | 05000382 Waterford 3 |  | 71111.13 | The inspectors identified a noncited violation of Technical Specification 6.8.1.a (Procedures) for an inadequate boric acid evaluation procedure and for the failure to follow the same procedure. Specifically, the procedure noted that small amounts of bori
Region: IV | Waterford | 2582 | 05/31/2007 07/13/2007 | 2007007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Meet Maintenance Rule Requirements for Dry Cooling Tower Sump Pumps Failure to Meet Maintenance Rule Requirements for Dry Cooling Tower Sump Pumps |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | DRAFT - Green. The team identified a non-cited violation of 10 CFR 50.65(a)(2) for the failure to adequately demonstrate the performance or condition of the dry cooling tower motor-driven sump pumps. Specifically, the licensee failed to periodically verif
Region: IV | Waterford | 2583 | 05/31/2007 07/13/2007 | 2007007-02 | NRC | FIN | Mitigating Systems | Green | Failure to Implement FME Procedure for Dry Cooling Tower Sumps |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | DRAFT - The team identified a finding for the failure to properly implement the site foreign material exclusion procedure for the dry cooling tower sumps. Specifically, the procedure required the establishment of a foreign material exclusion area if forei
Region: IV | Waterford | 2586 | 05/31/2007 07/13/2007 | 2007007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Restoring Power to Dry Cooling Tower Sump Pumps |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | DRAFT - The team identified a non-cited violation of Technical Specification 6.8.1.a, Procedures, for inadequate procedural guidance for operators to respond to a postulated loss of offsite power event coincident with a design basis rain event. The design
Region: IV | Waterford | 2587 | 05/31/2007 07/13/2007 | 2007007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate Acceptance Criteria for Battery Cell-to-Cell and Terminal Connection Resistance Value |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | DRAFT - The Team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the failure to ensure that the 125 Vdc safety-related batteries would remain operable if all the intercell and terminal connections were at
Region: IV | Waterford | 2588 | 05/31/2007 07/13/2007 | 2007007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Take Prompt Corrective Measures to Address Degraded Dry Cooling Towers |  |  | TE?: N | 05000382 Waterford 3 |  | 7111121 | DRAFT - The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion XVI, Corrective Actions, for the failure to promptly correct a condition adverse to quality (dirt and debris in the dry cooling tower heat exchanger fins). The condition
Region: IV | Waterford | 2580 | 04/07/2007 05/15/2007 | 2007002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis into Drawings |  |  | TE?: N | 05000382 Waterford 3 |  | 7111112B | The inspectors identified a Green noncited violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," for failure to assure that the design basis, as specified in the license application, was correctly translated into drawings and the actual plan
Region: IV | Waterford | 2581 | 04/07/2007 05/15/2007 | 2007002-02 | NRC | FIN | Mitigating Systems | Green | Failure to Ensure that Written Procedures Adequately Incorporate Regulatory Requirements and Design Basis |  |  | TE?: N | 05000382 Waterford 3 |  | NONE | The inspectors identified a finding of very low safety significance for failure to assure that the design basis for the dry cooling tower diesel-driven sump pumps was properly implemented. Specifically, the Train B dry cooling tower diesel-driven sump pum
Region: IV | Waterford | 2579 | 02/12/2007 03/05/2007 | 2006012-01 | NRC | NCV | Barrier Integrity | Green | Failure to Promptly Identify and Correct an Adverse Condition (Welds Not In Accordance With Design) |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000382 Waterford 3 |  | 71111.08P | A noncited violation of Criterion XVI of Appendix B to 10 CFR Part 50 was identified for the failure to promptly identify and correct an adverse condition (i.e., steam generator batwing-to-wrapper bar welds not in accordance with design). Specifically, in
Region: IV | Waterford | 2576 | 12/31/2006 02/13/2007 | 2006005-01 | Self - Revealed | NCV | Mitigating Systems | Green | Recurring Failure of Valve SI-405B to Open |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000382 Waterford 3 |  | 71111.19 | A self-revealing violation of very low safety significance (Green) of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was identified for the failure to implement effective corrective actions to prevent recurrence of a significant condition
Region: IV | Waterford | 2577 | 12/31/2006 02/13/2007 | 2006005-02 | NRC | NCV | Initiating Events | Green | Excess Torque Resulting in Pressurizer Skirt Bolt Failures |  |  | TE?: N | 05000382 Waterford 3 |  | 71111.2 | A self-revealing violation of very low safety significance of Technical Specification 6.8.1.a was identified for an inadequate procedure for installing a bolted joint that provided structural support for the pressurizer. Specifically, the installation pro
Region: IV | Waterford | 2578 | 12/20/2006 02/13/2007 | 2006005-03 | NRC | NCV | Emergency Preparedness | Green | Failure to Conduct a Required Offsite medical Drill in 2005 |  |  | TE?: N | 05000382 Waterford 3 |  | 71114.05 | The inspector identified a noncited violation of 10 CFR 50.54(q) for failure to conduct during 2005 an offsite drill involving a simulated contaminated individual with provision for participation by local medical support services as required by the licens
Region: IV | Waterford | 2572 | 10/07/2006 11/16/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Inspection of Essential Chiller Condenser Tubing |  | H.4(b) Procedural Compliance | TE?: N | 05000382 Waterford 3 |  | 71111.19 | A self-revealing noncited violation of Technical Specification 6.8.1.a was identified for failing to follow a maintenance procedure during performance of eddy current testing on the safety-related essential chiller Train A condenser tubing. The performanc
Region: IV | Waterford | 2575 | 10/07/2006 11/16/2006 | 2006004-02 | NRC | NCV | Initiating Events | Green | Inadequate Maintenance Procedure for ESFAS Relay Replacement |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000382 Waterford 3 |  | 71111.19 | A self-revealing noncited violation of Technical Specification 6.8.1.a was identified for an inadequate procedure that resulted in the unintentional actuation of five engineered safety features actuation system Train B relays and the loss of a 480 Vac mot
Region: IV | Waterford | 2570 | 07/07/2006 08/18/2006 | 2006003-01 | NRC | VIO | Mitigating Systems | Green | Untimely Actions to Reestablish Full Qualification of the Emergency Diesel Generator Starting Air System | EA Case: 06 192 |  | TE?: N | 05000382 Waterford 3 |  | 71152 | The inspectors identified a Green violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control." In September 2003, the NRC identified that the emergency diesel generator starting air system was incapable of supplying sufficient air to start it
Region: IV | Waterford | 125772 | 11/05/2019 |  | Licensee - Identified | LIV |  | Green | Boron Dilution Alarm (Startup Channel High Neutron Flux) Inoperable Resulting in Operation or Condition Prohibited by Technical Specifications |  |  | TE?: N | 05000382 Waterford 3 |  | 71153
Region: IV | Wolf Creek | 25914 | 12/31/2018 02/07/2019 | 2018004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Perform Required Design Basis Testing of the Class 1E Electrical Equipment Air Conditioning Recirculation Subsystem |  | H.3 - Change Management | TE?: N | 05000482 Wolf Creek 1 | Procedure Quality | 71111.22 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Criterion XI, “Test Control,” for the licensee’s failure to perform testing in accordance with written test procedures incorporating design basis requirements and acceptance limits.
Region: IV | Wolf Creek | 25916 | 12/31/2018 02/07/2019 | 2018004-02 | NRC | NCV | Initiating Events | Green | Programmatic Deficiencies in the Control and Separation of Stainless Steel Tools |  | H.9 - Training | TE?: N | 05000482 Wolf Creek 1 | Human Performance | 71152 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Criterion V, “Instructions, Procedures, and Drawings,” which requires, in part, that activities affecting quality shall be accomplished in accordance with instructions, procedures,
Region: IV | Wolf Creek | 24640 | 09/30/2018 11/07/2018 | 2018003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Degraded Performance of a Safety-Related Tornado Damper |  | H.14 - Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Criterion XVI, “Corrective Action,” for the licensee’s failure to promptly correct a condition adverse to quality associated with a safety-related tornado damper. Specifically, dampe
Region: IV | Wolf Creek | 25862 | 08/03/2018 11/14/2018 | 2018010-01 | NRC | UNKN | Mitigating Systems | Green | Failure to Follow Procedures |  | NPP | TE?: N | 05000482 Wolf Creek 1 |  | 71111.21M | The team identified two examples of a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to follow procedures. Performance Deficiency: The team determined that the licensee’s f
Region: IV | Wolf Creek | 25863 | 08/03/2018 11/14/2018 | 2018010-02 | NRC | UNKN | Mitigating Systems | Green | Failure to Establish an Adequate Procedure for Operator Time Critical Actions Validation |  | NPP | TE?: N | 05000482 Wolf Creek 1 | Procedure Quality | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to have an adequate Procedure. Procedure AI 21-016, "Operator Time Critical Actions Validation," Revision 14
Region: IV | Wolf Creek | 25864 | 08/03/2018 11/14/2018 | 2018010-03 | NRC | UNKN | Mitigating Systems | Green | Failure to Correct Reoccurring Problems with Time Critical/Sensitive Action Activities |  | P.4 - Trending | TE?: N | 05000482 Wolf Creek 1 |  | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee’s failure to correct reoccurring problems with completing Time Critical/Time Sensitive Action issues. Performance Defici
Region: IV | Wolf Creek | 25865 | 08/03/2018 11/14/2018 | 2018010-04 | NRC | UNKN | Mitigating Systems | Green | Failure to Identify 125 VDC Equalizing Voltage Exceeded Design Requirements |  | H.13 - Consistent Process | TE?: N | 05000482 Wolf Creek 1 | Procedure Quality | 71111.21M | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to verify or check the adequacy of design calculation NK-E-001, "125 Volt Direct-Current (VDC) Class 1E Battery System Sizing,
Region: IV | Wolf Creek | 24378 | 06/30/2018 08/12/2018 | 2018002-02 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Adequate Pressurization of the Control Room Envelope |  | H.3 - Change Management | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A self-revealed Green NCV of 10 CFR Part 50, Criterion III, “Design Control,” was identified when the licensee failed to adequately recognize that the cable spreading room floor was a control building ventilation isolation boundary. Specifically, the lice
Region: IV | Wolf Creek | 24379 | 06/30/2018 08/12/2018 | 2018002-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Implement Instrumentation and Controls Surveillance Procedures |  | H.2 - Field Presence | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A self-revealed Green NCV of 10 CFR Part 50, Criterion V, “Instructions, Procedures, and Drawings,” was identified when the licensee failed to adequately implement surveillance procedures that affected safety-related equipment and plant stability. Specifi
Region: IV | Wolf Creek | 24365 | 06/28/2018 08/08/2018 | 2018007-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Provide Adequate Work Instructions for Preventive Maintenance on Safety-Related Equipment |  | P.2 - Evaluation | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors reviewed a Green, self-revealed non-cited violation of Technical Specification 5.4.1.a to establish, implement, and maintain written procedures recommended by Regulatory Guide 1.33, Appendix A, Revision 2. Specifically, work instructions fo
Region: IV | Wolf Creek | 23528 | 03/31/2018 05/14/2018 | 2018001-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Functionality Assessment Associated with the Emergency Excess Letdown Flowpath |  | H.14 - Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a Green finding and associated non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, “Instructions, Procedures, and Drawings,” when the licensee failed to adequately implement the operability determination and functiona
Region: IV | Wolf Creek | 22648 | 12/31/2017 02/12/2018 | 2017004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Work Instructions for Preventive Maintenance |  | NPP | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a, for the licensee’s failure to provide adequate work instructions for preventive maintenance on safety-related equipment. Specifically, preventive maintenance work in
Region: IV | Wolf Creek | 22652 | 12/31/2017 02/12/2018 | 2017004-02 | NRC | NCV | Emergency Preparedness | Green | Failure to Critique TSC and OSC Performance During a Biennial Exercise |  | P.2 - Evaluation | TE?: N | 05000482 Wolf Creek 1 |  | 71114.01 | The inspectors identified that the licensee failed to correct a deficiency in emergency response organization performance identified as a result of an exercise in accordance with the requirements of 10 CFR 50.47(b)(14). The failure to identify and correct
Region: IV | Wolf Creek | 22650 | 12/31/2017 02/12/2018 | 2017004-03 | NRC | NCV | Initiating Events | Green | Failure to Initiate a Condition Report for Boric Acid Evaluations |  | S.1 - SCWE Policy | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to implement the operability and functionality assessment procedure. Specifically, as of October 12, 20
Region: IV | Wolf Creek | 22306 | 10/20/2017 11/20/2017 | 2017008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Spurious Valve Operation |  | NPP | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(5) for failure to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to adequately evaluate the potential impacts o
Region: IV | Wolf Creek | 22307 | 10/20/2017 11/20/2017 | 2017008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Emergency Lighting |  | H.9 - Training | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(5) for failure to provide emergency lighting along alternate routes plant operators are allowed to take during implementation of the procedure for control room evacuation due to fire.
Region: IV | Wolf Creek | 21647 | 09/30/2017 11/07/2017 | 2017003-01 | NRC | NCV | Mitigating Systems | Green | Programmatic Failure to Scope Floor Drain Function within the Maintenance Rule Monitoring Program |  | NPP | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(b)(2)(ii), because the licensee did not adequately include nonsafety-related SSC functions within the scope of the maintenance rule monitoring program. Specifically, the licensee failed
Region: IV | Wolf Creek | 21689 | 09/30/2017 11/07/2017 | 2017003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure the Design Basis was Adequately Represented in the Technical Specification Bases |  | P.2 - Evaluation | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the licensee’s failure to establish adequate measures to ensure that the design bases are correctly translated into specifications, dra
Region: IV | Wolf Creek | 21690 | 09/30/2017 11/07/2017 | 2017003-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Verify Equipment or Systems are Capable of Performing Their Intended Design Function Following Maintenance |  | H.1 - Resources | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a Green, self-revealed non-cited violation of Technical Specification 5.4.1.a for the licensee’s failure to ensure that maintenance that can affect the performance of safety-related equipment was properly pre-planned and performed
Region: IV | Wolf Creek | 5759 | 07/12/2017 08/01/2017 | 2017007-01 | NRC | NCV | Emergency Preparedness | Green | Failure to Maintain Effectiveness of the Emergency Plan upon Loss of Containment High Radiation Monitoring |  | H.14 Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71111.21N | Green. The inspectors identified a Green, non-cited violation of 10 CFR 50.54(q)(2) which requires that a holder of a nuclear power plant operating license follow and maintain the effectiveness of an emergency plan that meets the requirements in Appendix
Region: IV | Wolf Creek | 5754 | 06/30/2017 08/10/2017 | 2017002-01 | NRC | NCV | Barrier Integrity | Green | Failure to Ensure Safety-Related Valves were Adequately Protected from Internal Flooding Hazards |  | P.1 Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.06 | The inspectors identified a Green non-cited violation of 10 Code of Federal Regulations Part 50, Appendix B, Criterion III, Design Control, for the licensee's failure to establish adequate measures to ensure that safety-related components remained capable
Region: IV | Wolf Creek | 5755 | 06/30/2017 08/10/2017 | 2017002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Declare Train A Component Cooling Water Inoperable |  | H.11 Challenge the Unknown | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a Green non-cited violation of Technical Specification Limiting Condition for Operation 3.7.7 for the licensee's failure to place the unit in MODE 3 within 78 hours with the train A component cooling water system inoperable. Spec
Region: IV | Wolf Creek | 5753 | 03/31/2017 05/12/2017 | 2017001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Adequate Work Instructions for Preventive Maintenance |  | P.3 Resolution | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors reviewed a Green, self-revealed non-cited violation (NCV) of Technical Specification 5.4.1.a and Regulatory Guide 1.33 for the licensee's failure to provide adequate work instructions for preventive maintenance on safety-related equipment.
Region: IV | Wolf Creek | 5752 | 12/31/2016 02/13/2017 | 2016004-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Establish and Adjust Preventive Maintenance for Emergency Diesel Generator Excitation System Diodes |  | P.5 Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | Green. The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to adequately develop and adjust preventive maintenance activities in accordance with Procedure AP 16B-003, "Planning and Scheduling Prev
Region: IV | Wolf Creek | 5739 | 09/30/2016 11/08/2016 | 2016003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Adjust Testing and Preventive Maintenance for Safey-Related Lockout Relays |  | P.5 Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a, for the licensee's failure to adequately adjust testing and preventive maintenance activities in accordance with Procedure AP 16B-003, "Planning and Scheduling Preve
Region: IV | Wolf Creek | 5688 | 06/30/2016 08/03/2016 | 2016002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Establish Control Room Air Conditioning System Testing Flow Rate Acceptance Criteria |  | H.3 Change Management | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green non-cited violation of Technical Specification Limiting Condition for Operation 3.7.11 and 3.0.3 for the licensee's failure to place the unit in mode 3 within 7 hours, mode 4 within 13 hours, and mode 5 within 37 hours wi
Region: IV | Wolf Creek | 5722 | 06/30/2016 08/09/2016 | 2016009-01 | NRC | FIN | Initiating Events | Green | Failure to evaluate and address failures of prior corrective actions to prevent repeat events |  | P.2 Evaluation | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified several examples in which multiple station events had occurred due to similar programmatic or organizational-behavior causes (i.e., potential gaps in nuclear safety culture). The licensee's evaluations for these repeat events and issue
Region: IV | Wolf Creek | 5723 | 06/30/2016 08/09/2016 | 2016009-02 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Negative Trend in Breach Permit Corrective Actions |  | P.4 Trending | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," associated with the licensee's failure to identify and correct a condition adverse to quality. Specifically, between October 2012 and June 2016, the li
Region: IV | Wolf Creek | 5717 | 06/29/2016 07/19/2016 | 2016008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Significant Condition Adverse to Quality Associated with the Emergency Diesel Generator B Excitation System Diodes |  | H.14 Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to assure that conditions adverse to quality, such as failures, malfunctions, and deficiencies are promptly
Region: IV | Wolf Creek | 5687 | 04/28/2016 06/10/2016 | 2016007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Degraded Voltage Analyses of Class 1E Systems |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the use of alte
Region: IV | Wolf Creek | 5696 | 04/28/2016 06/10/2016 | 2016007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify the Adequancy of Design of the Control Circuitry of the Fuel Oil Transfer Pumps |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the use of alte
Region: IV | Wolf Creek | 5708 | 04/28/2016 06/10/2016 | 2016007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Analysis of Essential Service Water Piping |  | P.5 Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," which states, in part, "The design control measures shall provide for verifying or checking the adequacy of design, such as by the use of alte
Region: IV | Wolf Creek | 5709 | 04/28/2016 06/10/2016 | 2016007-04 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Correct Deficiencies With Operator Time Critical Actions |  | H.9 Training | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficie
Region: IV | Wolf Creek | 5683 | 03/31/2016 04/25/2016 | 2016001-01 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Establish and Adjust Preventive Maintenance Activities for Control Room Air Conditioning Unit SGK04A Sensing lines and Fittings |  | H.1 Resources | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a for the licensee's failure to adequately develop and adjust preventive maintenance activities in accordance with Procedure AP 16B-003, "Planning and Scheduling Preven
Region: IV | Wolf Creek | 5659 | 12/31/2015 02/11/2016 | 2015004-01 | NRC | VIO | Mitigating Systems | Green | Inadequate Measures to Assure SGK05A Issues Were Promptly Corrected |  | H.1 Resources | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's inadequate measures to assure that corrective action was taken to preclude repetition of a significant condition advers
Region: IV | Wolf Creek | 5673 | 12/31/2015 02/11/2016 | 2015004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Essential Service Water Valves were Adequately Protected from External Flooding Hazards |  | H.11 Challenge the Unknown | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to establish measures to assure that applicable regulatory requirements and the design basis, for applicable s
Region: IV | Wolf Creek | 5682 | 12/31/2015 02/11/2016 | 2015004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Determination and Consider Design Basis Events |  | H.14 Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to accomplish activities affecting quality in accordance with Procedure AP 26C-004, "Ope
Region: IV | Wolf Creek | 5430 | 11/24/2015 12/08/2015 | 2015009-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Provide Adequate Instructions for Control of Feedwater Flow in Startup Procedures |  | H.12 Avoid Complacency | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," because the licensee did not assure the procedures for reactor startup were appropriate to the circums
Region: IV | Wolf Creek | 5431 | 11/24/2015 12/08/2015 | 2015009-02 | Self - Revealed | NCV | Initiating Events | Green | Failure of the Plant Referenced Simulator to Demonstrate Expected Plant Response |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing Green non-cited violation of 10 CFR 55.46(c)(1), "Plant-referenced Simulators," due to the licensee's failure to maintain a plant-referenced simulator used for the administration of the operating test such that it
Region: IV | Wolf Creek | 5417 | 09/26/2015 11/10/2015 | 2015003-01 | NRC | NCV | Barrier Integrity | Green | Inadequate Implementation of the Breach Authorization Procedure |  | H.11 Challenge the Unknown | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a non cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's inadequate implementation of Procedure AP 10 104, "Breach Authorization," Revision 34. Spe
Region: IV | Wolf Creek | 5416 | 06/30/2015 08/06/2015 | 2015002-01 | NRC | NCV | Mitigating Systems | Green | Class 1E 4kV Feeder Breakers from Station Blackout Diesel Generators Current Transfomrer Wiring not Installed per Design Drawings |  | H.4 Teamwork | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, for not installing the current transformer wiring in the Class 1E 4kV alternate feeder breaker cubicles from the station blackout diesel generators per
Region: IV | Wolf Creek | 5406 | 03/28/2015 05/07/2015 | 2015001-02 | NRC | NCV | Mitigating Systems | Green | Failure to Assess the Operability of Emergency Diesel Generator B during Emergent Work Activities |  | H.5 Work Management | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, associated with the failure to properly preplan maintenance such that it would not affect safety-related equipment. Specifically, during emergent work activities on Januar
Region: IV | Wolf Creek | 5407 | 03/28/2015 05/07/2015 | 2015001-03 | NRC | NCV | Mitigating Systems | Green | Failure to Complete an Adequate Operability Evaluation for Declaring the Train A Control Room Air Conditioning Unit Operable |  | H.14 Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," associated with the licensee's failure to complete an adequate operability evaluation in accordance with procedure AP-28001,"Ope
Region: IV | Wolf Creek | 5408 | 03/28/2015 05/07/2015 | 2015001-04 | NRC | NCV | Barrier Integrity | Green | Failure to Station Boundary Watch for Opening Auxiliary Building Emergency Exhaust System Boundary Door |  | H.5 Work Management | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, Drawings," associated with the licensee's failure to follow the requirements of Station Procedure AP 10-104, "Breach Authorization," Revision
Region: IV | Wolf Creek | 5396 | 12/31/2014 02/10/2015 | 2014005-01 | NRC | FIN | Mitigating Systems | Green | Failure to Conduct and Evaluate Simulator Testing in Accordance with ANSI/ANS 3.5-2009 (1998) |  | P.1 Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.11B | The inspectors identified a Green finding for WCNOC inadequately conducting and evaluating simulator performance testing in accordance with the standards of ANSI/ANS 3.5-2009 and ANSI/ANS 3.5-1998, "Nuclear Power Plant Simulators for Use in Operator Train
Region: IV | Wolf Creek | 5394 | 11/07/2014 12/18/2014 | 2014008-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.4.1.d for the failure to implement and maintain adequate written procedures covering fire protection program implementation. Specifically, the licensee failed to maintain an alternativ
Region: IV | Wolf Creek | 5395 | 11/07/2014 12/18/2014 | 2014008-02 | NRC | NCV | Mitigating Systems | Green | Procedure Inadequacies Related to Cold Shutdown Repairs |  | H.7 Documentation | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of Technical Specification 5.4.1.d for the failure to implement and maintain adequate written procedures covering fire protection program implementation. Specifically, the licensee failed to adequately label equip
Region: IV | Wolf Creek | 5398 | 10/09/2014 10/10/2014 | 2014007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Operability Determinations on Degraded Boundaries |  | H.1 Resources | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to perform operability determinations on degraded boundaries with credited compensatory measur
Region: IV | Wolf Creek | 5405 | 10/09/2014 10/10/2014 | 2014007-02 | NRC | NCV | Barrier Integrity | Green | Failure to Preclude Repetition of a Significant Condition Adverse to Quality to Prevent Reactor Coolant System Leak |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors reviewed a self-revealing violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Actions," for failure to prevent repetition of a significant condition adverse to quality related to reactor coolant system boundary leakage on Ap
Region: IV | Wolf Creek | 5399 | 10/09/2014 10/10/2014 | 2014007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Include the Containment Coolers in a Test Program |  | P.1 Identification | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for the licensee's failure to include the containment coolers in the heat exchanger inspection program that would demonstrate their leak tight integrity and
Region: IV | Wolf Creek | 5404 | 10/09/2014 10/10/2014 | 2014007-04 | NRC | FIN | Mitigating Systems | Green | Failure to Incorporate LERs in OE Program |  | H.12 Avoid Complacency | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a finding for the licensee's failure to follow the operating experience program's requirement to review external licensee event reports, and initiate a condition report for those potentially applicable to Wolf Creek. The licensee
Region: IV | Wolf Creek | 5384 | 09/30/2014 10/30/2014 | 2014004-01 | Self - Revealed | FIN | Initiating Events | Green | Failure to Maintain Control and Cognizance of Activities with the Potential to Impact Plant Conditions |  | H.4 Teamwork | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | A self-revealing finding was identified for failure to recognize the potential effects on supported plant equipment while manipulating electrical power distribution components. The finding resulted in an unplanned reactor pressure transient during solid p
Region: IV | Wolf Creek | 5385 | 09/30/2014 10/30/2014 | 2014004-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Ensure that Outage Work Could be Safely Performed During the Existing Plant Conditions |  | H.4 Teamwork | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | A Green self-revealing non-cited violation of Technical Specification 5.4.1.a was identified for the failure to analyze the effects of performing motor operated valve testing on the plant being aligned to support alternate decay heat removal. The activity
Region: IV | Wolf Creek | 5367 | 03/28/2014 05/12/2014 | 2014002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Work Instructions for Reinstallation of ESW Expansion Joints |  | H.1 Resources | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for maintenance instructions inappropriate to the circumstances. Specifically, Work Orders 11-341986-005 and 11-342065-002 did not contain adequate instructi
Region: IV | Wolf Creek | 5374 | 03/28/2014 05/12/2014 | 2014002-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to Maintain Licensed Power Limits During Planned Evolutions Affecting Reactivity |  | H.14 Conservative Bias | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | A self-revealing non-cited violation, with two examples, of Technical Specification 5.4.1.a, "Procedures," was identified for the failure to follow the reactivity management procedures. On two occasions, operators failed to take prudent actions to ensure
Region: IV | Wolf Creek | 5375 | 03/28/2014 05/12/2014 | 2014002-03 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to Maintain Seismic and Missile Protection Design Basis Requirements During Essential Service Water Construction |  | H.5 Work Management | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," was identified for the failure to conduct excavation work such that it would ensure that design basis requirements for tornado missile protection and seismic q
Region: IV | Wolf Creek | 5361 | 12/31/2013 02/10/2014 | 2013005-01 | NRC | FIN | Mitigating Systems | Green | Failure Rates Exceed Twenty Percent for Annual Requalification Operating Tests |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspector reviewed a self-revealing finding associated with licensed operator performance on the annual requalification operating tests. Specifically, 2 of 8 crews (25 percent) failed the simulator scenario portion of the operating test; and 11 of 46
Region: IV | Wolf Creek | 5337 | 12/31/2013 02/10/2014 | 2013005-02 | NRC | NCV | Initiating Events | Green | Failure to Assess Risk Prior to Performing Online Maintenance to an Offsite Power Circuit Component |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | The inspectors identified a Green non-cited violation of 10 CFR 50.65(a)(4) for the failure to assess risk associated with an emergent maintenance activity performed on one of the offsite power circuit components inside the Wolf Creek switchyard. Specific
Region: IV | Wolf Creek | 5338 | 12/31/2013 02/10/2014 | 2013005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Preclude Repetition of a Significant Condition Adverse to Quality Affecting Class 1E Air Conditioning Unit |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A Green self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," was identified for failure to identify the underlying causes of the train A Class 1E air conditioner slug flow in the refrigerant prior to a recurren
Region: IV | Wolf Creek | 5342 | 10/28/2013 11/22/2013 | 2013008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure When Making Changes to Off-Normal Operating Procedure OFN NB-042 |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "Activities affecting quality shall be prescribed by documented instructions, procedures, or drawings,
Region: IV | Wolf Creek | 5343 | 10/28/2013 11/22/2013 | 2013008-02 | NRC | NCV | Mitigating Systems | Green | Failure to Verify or Check the Adequacy of Design Calculations |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation, with three examples, of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis
Region: IV | Wolf Creek | 5346 | 10/28/2013 11/22/2013 | 2013008-03 | NRC | NCV | Initiating Events | Green | Failure to Ensure that Degraded Voltage Relay Minimum Allowable Time Delay Value is Bounded by Analyzed Value |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5347 | 10/28/2013 11/22/2013 | 2013008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Over Voltages on the 480 Vac System During Emergency Diesel Generator Training |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficiencies
Region: IV | Wolf Creek | 5348 | 10/28/2013 11/22/2013 | 2013008-05 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Motors are Operated Within Their Thermal Limits |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5349 | 10/28/2013 11/22/2013 | 2013008-06 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Implement Electrical Protection Criteria for Containment Penetrations |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5350 | 10/28/2013 11/22/2013 | 2013008-07 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Flow Measurement Uncertainty when Operating the Residual Heat Removal Pumps in the Low Flow Regime |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5352 | 10/28/2013 11/22/2013 | 2013008-08 | NRC | NCV | Barrier Integrity | Green | Failure to Account for Containment Temperature Measurement Uncertainty |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5353 | 10/28/2013 11/22/2013 | 2013008-09 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Assess Problems with Component Cooling Water Valve EGHV102 |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficie
Region: IV | Wolf Creek | 5354 | 10/28/2013 11/22/2013 | 2013008-10 | NRC | NCV | Mitigating Systems | Green | Failure to Provide Procedure Instructions to Remove Thermal Overload Bypass Jumpers |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5355 | 10/28/2013 11/22/2013 | 2013008-11 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Adequacy of Electrical Protective Devices to Isolate Fire-Damaged Associated Circuits |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion III, "Design Control," which states, in part, "Measures shall be established to assure that applicable regulatory requirements and the design basis are correctly translat
Region: IV | Wolf Creek | 5358 | 10/28/2013 11/22/2013 | 2013008-12 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Basis Performance Requirements into Pump Surveillance Tests |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green, non-cited violation of 10 CFR 50, Appendix B, Criterion XI, "Test Control," which states, in part, "A test program shall be established to assure that all testing required to demonstrate that structures, systems, and component
Region: IV | Wolf Creek | 5359 | 10/28/2013 11/22/2013 | 2013008-13 | NRC | NCV | Mitigating Systems | Green | Failure to Fully Establish Design Control Measures for Vital Essential Chillers SGK05 A/B Air Conditioning Units |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a Green, non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action", which states, in part, "Measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, deficie
Region: IV | Wolf Creek | 5336 | 07/24/2013 11/04/2013 | 2013004-01 | NRC | NCV | Initiating Events | Green | Failure to Analyze Erected Scaffolding for Fire Impairment and Transient Combustible Loading |  | H.3(a) Work Planning | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a non-cited violation of Technical Specification 5.4.1.d "Fire Protection Program Procedures" for the failure to analyze scaffolding for fire protection impairments and transient combustible loading. The cause of the finding was
Region: IV | Wolf Creek | 5323 | 06/30/2013 08/14/2013 | 2013003-01 | NRC | NCV | Initiating Events | Green | Failure to Follow Station Procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," which states, in part, "activities affecting quality shall be prescribed by procedures of a type appropriate to the
Region: IV | Wolf Creek | 5324 | 06/30/2013 08/14/2013 | 2013003-02 | NRC | NCV | Initiating Events | Green | Failure to Identify Leakage at Refueling Pool Cavity |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," which states, in part, "Measures shall be established to assure that conditions adverse to quality are promptly identified and correct
Region: IV | Wolf Creek | 5325 | 06/30/2013 08/14/2013 | 2013003-03 | NRC | NCV | Mitigating Systems | Green | Diesel Generator Pressure Switch Failed Due to Instrument Line Pressure Oscillations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing non-cited violation of 10 CFR 50 Appendix B, Criterion XVI, Corrective Action, was identified on March 13, 2013. Specifically, the licensee replaced a jacket water pressure transmitter ten times, but failed to correct pressure oscillation
Region: IV | Wolf Creek | 5328 | 06/30/2013 08/14/2013 | 2013003-04 | Self - Revealed | NCV | Initiating Events | Green | Failure to Update Station Procedures and Train Operators Regarding the Effects of Implemented Design Changes to the Turbine Control System |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A Green self-revealing non-cited violation of Technical Specification 5.4.1.a was identified for failure to properly update operating procedures and train operators on the effects of a recently installed modification. Specifically, procedures were not ade
Region: IV | Wolf Creek | 5329 | 06/30/2013 08/14/2013 | 2013003-05 | NRC | NCV | Initiating Events | Green | Failure to Properly Manage Reactivity Changes when Swapping Turbine Steam Admission Modes from Full to Partial Arc |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | Inspectors identified a Green non-cited violation of Technical Specification 5.4.1.a for the failure to follow Conduct of Operations and Reactivity Management procedures. The inspectors reviewed an unplanned 11 percent power increase during a shift in tur
Region: IV | Wolf Creek | 5318 | 04/29/2013 05/06/2013 | 2013009-01 | NRC | NCV | Mitigating Systems | Green | Failure to Identify the Cause and Take Corrective Action to Preclude Repetition of a Diesel Generator Functional Failure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 95001 | The inspector identified a NCV of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to determine the cause of a significant condition adverse to quality and take corrective action to preclude repetition. On October 22, 2009, the
Region: IV | Wolf Creek | 5314 | 03/30/2013 05/06/2013 | 2013002-01 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate a Condition Report and Determine Extent of Condition for Emergency Diesel Generator Head Stud Failure |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green, NCV of 10 CFR 50 Appendix B, Criterion XVI, "Corrective Actions." The licensee did not initiate a condition report (CR) for a hardware failure of an emergency diesel generator structural component identified in October 2
Region: IV | Wolf Creek | 5315 | 03/30/2013 05/06/2013 | 2013002-02 | Self - Revealed | NCV | Initiating Events | Green | Failure to Promptly Identify and Correct Reactor Coolant System Pressure Boundary Leakage |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing non-cited violation (NCV) of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Actions," for the failure to promptly identify and correct the source of a reactor coolant system pressure boundary leak from about Aug
Region: IV | Wolf Creek | 5306 | 12/31/2012 02/13/2013 | 2012005-01 | Self - Revealed | FIN | Mitigating Systems | Green | Failure Rates Exceed Twenty Percent for Biennial Requalification Exam |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors reviewed a self-revealing finding associated with licensed operator performance on the biennial requalification exam. Specifically, 19 of 52 operators failed at least one portion of the biennial requalification examinations. As an immediate
Region: IV | Wolf Creek | 5310 | 12/31/2012 02/13/2013 | 2012005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure that All License Conditions are Met for Licensed Operators |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR 55.53, "Conditions of License," for the failure of the licensee to ensure that licensed operators met all the conditions of their licenses in order to be considered an active watch stander. Specifi
Region: IV | Wolf Creek | 5312 | 12/31/2012 02/13/2013 | 2012005-04 | NRC | NCV | Barrier Integrity | Green | Failure to Perform Control Room Air Conditioning Technical Specification Surveillance Requirements |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a non-cited violation for failure to perform surveillance testing specified in Technical Specification 3.7.11, "Control Room Air Conditioning System." The activities the licensee was crediting to meet the requirement to verify he
Region: IV | Wolf Creek | 5313 | 12/31/2012 02/13/2013 | 2012005-05 | NRC | NCV | Initiating Events | Green | Inadequate Bases Change Causes Violation of Low Temperature Overpressure Protection Technical Specification |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a non-cited violation of Technical Specification 3.4.12, "Low Temperature Overpressure Protection System," for exceeding the maximum allowed number of centrifugal charging pumps capable of injecting to the reactor coolant system
Region: IV | Wolf Creek | 5302 | 09/28/2012 11/09/2012 | 2012004-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Operability Evaluations for a Single A/C Cooling its Associated Train |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | On August 30, 2012, inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for an operability evaluation that failed to adequately evaluate the operability of safety-related electr
Region: IV | Wolf Creek | 5304 | 09/28/2012 11/09/2012 | 2012004-05 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow ALARA Planning Procedures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000482 Wolf Creek 1 |  | 71124.02 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, resulting from the licensee's failure to follow ALARA planning procedures. Nonsafety-related gaskets were used, inadequate walkdowns were conducted, and work
Region: IV | Wolf Creek | 5303 | 09/27/2012 11/09/2012 | 2012004-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Protection Procedures |  | H.2(d) Facilities & Equipment | TE?: N | 05000482 Wolf Creek 1 |  | 71124.01 | The inspectors reviewed a self-revealing, non-cited violation of Technical Specification 5.4.1.a, which resulted from a worker failing to follow radiation protection procedures. A radiation worker, in a high noise area, received an electronic alarming dos
Region: IV | Wolf Creek | 5301 | 07/09/2012 11/09/2012 | 2012004-03 | NRC | NCV | Mitigating Systems | Green | Safety-Related Fan Flow Rate Acceptance Criteria Reduced Below Design Basis |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | On July 9, 2012, the inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for inappropriately reducing the vital air conditioning unit fan flow rate test acceptance criteria to a value less than that use
Region: IV | Wolf Creek | 5285 | 06/29/2012 07/05/2012 | 2012003-01 | NRC | NCV | Initiating Events | Green | Incorrect Leak Seal Injection Port Installation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.18 | A self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Inspections, Procedures, and Drawings," was identified as a result of a leaking watertight door that was observed on January 13, 2012. Station procedure MPM XX-002, "Watertight D
Region: IV | Wolf Creek | 5286 | 06/29/2012 07/05/2012 | 2012003-02 | NRC | NCV | Mitigating Systems | Green | Unacceptable Leakage through Safety-Related Watertight Door during Loss of Offsite Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.06 | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a work order that did not accomplish a leak seal repair in accordance with its engineering evaluation. Valve BMV0037
Region: IV | Wolf Creek | 5297 | 06/01/2012 08/06/2012 | 2012009-02 | NRC | NCV | Mitigating Systems | Green | Inadequte Preventative Maintenance Procedure on Turbine Driven Auxiliary Feedwater Pump |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team reviewed a self-revealing non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to have an adequate preventative maintenance procedure, PM 28129, "Refueling Inspection of the Tri
Region: IV | Wolf Creek | 5296 | 06/01/2012 08/06/2012 | 2012009-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Temporary Fire Pump |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team reviewed a self-revealing non-cited violation of Technical Specification 5.4.1.d for the failure to have procedures appropriate for the implementation of fire protection compensatory measures. Specifically, Procedure SYS FP-290, "Temporary Fire P
Region: IV | Wolf Creek | 5290 | 06/01/2012 08/06/2012 | 2012009-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct a Condition Adverse to Fire Protection |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a non-cited violation of License Condition 2.C.5.a for the failure of the licensee to identify and correct a condition adverse to fire protection. Specifically, the licensee failed to identify an adverse trend in the diesel driven fire
Region: IV | Wolf Creek | 5260 | 05/26/2012 07/05/2012 | 2012007-01 | NRC | NCV | Mitigating Systems | Green | Inadequte Procedure to Implement Compensatory Measures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to adequately translate design information into procedures and requirements. Specifically, the
Region: IV | Wolf Creek | 5259 | 05/26/2012 07/05/2012 | 2012007-03 | NRC | VIO | Mitigating Systems | Green | Failure to Take Timely corrective Action to Preclude Repetition | EA Case: 2012135 | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a violation of 10 CFR 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to take corrective action to preclude repetition of system leaks due to water hammer events in the essential service water syste
Region: IV | Wolf Creek | 5266 | 05/26/2012 07/05/2012 | 2012007-04 | NRC | NCV | Mitigating Systems | Green | Untimely Corrective Action |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to effectively correct deficient procedures regarding the use of clearance orders. A number of clearance-related proble
Region: IV | Wolf Creek | 5267 | 05/26/2012 07/05/2012 | 2012007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Complete Corrective Actions |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to establish adequate procedures for resolution of corrective actions. Specifically, the licensee failed to esta
Region: IV | Wolf Creek | 5268 | 05/26/2012 07/05/2012 | 2012007-06 | NRC | VIO | Mitigating Systems | Green | Failure to Implement Procedures to Test Safety-Related Equipment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to perform testing of safety-related spring-loaded tornado dampers in the emergency diesel generator and essential service water
Region: IV | Wolf Creek | 5276 | 05/26/2012 07/05/2012 | 2012007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Prevent Recurrent of Component Cooling Water System Voiding |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | NONE | On February 23, 2011, a non-cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," was revealed when an anomalous start of component cooling water pump B indicated gas voiding in the component cooling water piping. This violati
Region: IV | Wolf Creek | 5277 | 05/26/2012 07/05/2012 | 2012007-08 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Evaluate the Suitability of Nonsafety-related Gaskets, O-Rings, and Seals Installed in Safety-Related Equipment and to Identify Extent of the Condition |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the licensee's failure to evaluate the suitability of nonsafety-related gaskets, o-rings, and seals installed in safety-related components. These
Region: IV | Wolf Creek | 5278 | 05/26/2012 07/05/2012 | 2012007-09 | NRC | FIN | Mitigating Systems | Green | Inappropriately High Threshold for Condition Report Initiation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The team identified a finding for the licensee's failure to ensure that condition reports were initiated as required by procedure. The licensee's implementing procedure for its corrective action program did not contain clear guidance as to what conditions
Region: IV | Wolf Creek | 5245 | 03/26/2012 05/09/2012 | 2012002-02 | NRC | NCV | Barrier Integrity | Green | Failure to Test ASME O&M Code Category A Valves in Post-LOCA Flow Path |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a non-cited violation of 10 CFR Part 50.55a(f)(4), "Codes and Standards," for failure to adequately demonstrate that the seat leakage for 12 emergency core cooling system and containment spray valves remained within acceptable li
Region: IV | Wolf Creek | 5244 | 02/12/2012 05/09/2012 | 2012002-01 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Procedure Causes Lift of Relief Valve and Reactor Coolant Leak During Shutdown |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors reviewed a self-revealing non-cited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for a procedure that failed to restore the reactor coolant pump seal return flow path prior to raising reactor co
Region: IV | Wolf Creek | 5247 | 01/24/2012 05/09/2012 | 2012002-03 | NRC | NCV | Mitigating Systems | Green | Loss of Configuration Control Causes Loss of All Non-Vital Power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | Inspectors identified a non-cited violation of Technical Specification 5.4.1.a, "Procedures," for implementation of an unauthorized modification by using a clearance order and a temporary procedure. This left the power source to a temporary protective re
Region: IV | Wolf Creek | 5211 | 12/31/2011 02/14/2012 | 2011005-01 | Self - Revealed | NCV | Initiating Events | Green | Failure to Evaluate Gasket Compatibility |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors reviewed a self-revealing, non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," associated with an improperly selected essential service water gasket that sprayed safety-related electrical equipment. On August
Region: IV | Wolf Creek | 5212 | 12/31/2011 02/14/2012 | 2011005-02 | NRC | NCV | Initiating Events | Green | Failure to Account for RCP Seal Injection in Safety Analysis for Inadvertent Safety Injection |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.18 | On June 13, 2011, the inspectors identified a non-cited violation of 10 CFR, Part 50, Appendix B, Criterion XVI, for an inadequate safety analysis of inadvertent operation of the emergency core cooling system. The inspectors identified that Updated Safety
Region: IV | Wolf Creek | 5213 | 12/31/2011 02/14/2012 | 2011005-03 | NRC | NCV | Barrier Integrity | Green | Preconditioning of 480 Vac Breakers Prior to Required Surveillance Testing |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | On November 14, 2011, the inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion XI, "Test Control," for pre-conditioning of the 480 Vac breaker for the containment cooling fan D prior to performance of the periodic fun
Region: IV | Wolf Creek | 5214 | 12/31/2011 02/14/2012 | 2011005-04 | NRC | NCV | Initiating Events | Green | Inadequate Evaluation of Effects of Emergency Diesel Generator Frequency Variation on Supplied Equipment |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green non-cited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, for the licensee's failure to adequately evaluate the effects of allowed technical specification frequency variations on plant equipment in
Region: IV | Wolf Creek | 5215 | 12/31/2011 02/14/2012 | 2011005-05 | NRC | NCV | Mitigating Systems | Green | Incorrect Retraction of an Event that Could Have Prevented Fulfillment of a Safety Function |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Severity Level IV noncited violation of 10 CFR 50.73 because the licensee inappropriately retracted a licensee event report. On September 29, 2011, Wolf Creek issued Licensee Event Report 2011-004-01 which retracted the 10 CFR
Region: IV | Wolf Creek | 5207 | 12/12/2011 12/27/2011 | 2011007-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Alternative Shutdown Procedure |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a Green non-cited violation of Technical Specification 5.4.1.d for the failure to implement and maintain adequate written procedures covering fire protection program implementation. Specifically, the team identified two examples where
Region: IV | Wolf Creek | 5208 | 12/12/2011 12/27/2011 | 2011007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Post-Fire Safe Shutdown Components Remain Free of Fire Damage |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C(5) because the licensee failed to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to properly analyze for f
Region: IV | Wolf Creek | 5206 | 11/04/2011 12/27/2011 | 2011007-01 | NRC | FIN | Mitigating Systems | Green | Failure to Verify Isolation of Associated Circuits on Isolation Switches |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a finding because the licensee was not fully testing the isolation function of local transfer switches located at motor control center breakers for individual components. As a result, the licensee was not performing periodic verificati
Region: IV | Wolf Creek | 5209 | 11/04/2011 12/27/2011 | 2011007-04 | NRC | NCV | Mitigating Systems | Green | Procedure Inadequacies Related to Cold Shutdown Repairs |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a Green non-cited violation of License Condition 2.C(5) because the licensee failed to implement and maintain in effect all provisions of the approved fire protection program. Specifically, the licensee failed to provide an adequate pr
Region: IV | Wolf Creek | 5203 | 09/30/2011 11/10/2011 | 2011004-03 | NRC | NCV | Mitigating Systems | Green | Failure to Follow ASME Code Cas OMN-1 for Butterfly Valves |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR 50.55a, "Codes and Standards," when the licensee failed to correctly test a series of butterfly valves. The licensee installed seven Crane butterfly valves in the essential service water system in 2
Region: IV | Wolf Creek | 5205 | 09/30/2011 11/10/2011 | 2011004-05 | NRC | NCV | Initiating Events | Green | Failure to Maintain Steam Generator Level Above Lo Lo Level Setpoint |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a noncited violation of Technical Specification 5.4.1.a, "Procedures," for failure of operators to follow procedure to maintain steam generator water level. This failure resulted in level in steam generator B level lowering such th
Region: IV | Wolf Creek | 5196 | 09/22/2011 10/18/2011 | 2011301-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Emergency Operating Procedure for Steam Generator Tube Rupture |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a, "Procedures," due to insufficient procedural direction to operations personnel to perform a subcooled recovery of a steam generator tube rupture if the ruptured steam
Region: IV | Wolf Creek | 5225 | 09/01/2011 03/01/2012 | 2011009-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing Of Emergency Diesel Generator A |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The inspector identified a noncited violation of 10 CFR 50, Appendix B, Criterion XI, Test Control, with two examples, because the licensee failed to ensure that all testing required to demonstrate that the emergency diesel generators would perform satisf
Region: IV | Wolf Creek | 5195 | 08/10/2011 11/10/2011 | 2011004-02 | NRC | NCV | Emergency Preparedness | Green | Technical Support Center External Door Propped Open without Impairment |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a noncited violation of 10 CFR 50.47, "Emergency Plans," for the failure to maintain an adequate emergency facility. The technical support center doors were propped open during maintenance for 82 days without a breach permit, lea
Region: IV | Wolf Creek | 5194 | 07/21/2011 11/10/2011 | 2011004-01 | NRC | FIN | Initiating Events | Green | Switchyard component Failures Cause Loss of Ring Bus and Loss of Offsite Power |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | On July 21, 2011, the inspectors identified a finding for degraded switchyard equipment that caused a loss of offsite power. Updated Safety Analysis Report (USAR), Section 8.2.1.3.g.1, states that: "Any transmission line can be cleared under normal or fau
Region: IV | Wolf Creek | 5174 | 06/16/2011 08/12/2011 | 2011003-01 | NRC | NCV | Initiating Events | Green | No Procedure for Debris in Transformer an Tank Yards Propr to Severe Weather |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.01 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Administrative Procedures," for having no procedure to address onsite debris impacting plant equipment during severe weather. The inspectors walked down external areas of
Region: IV | Wolf Creek | 5182 | 06/16/2011 08/12/2011 | 2011003-03 | NRC | NCV | Initiating Events | Green | Undersized Weld Failure on Charging Header |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors documented a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion IX, "Control of Special Processes." Specifically, in October 2009, welders failed to ensure the fillet weld between the train B charging header and the
Region: IV | Wolf Creek | 5186 | 06/16/2011 08/12/2011 | 2011003-04 | NRC | NCV | Initiating Events | Green | Failure to Ensure Separation of Stainless Steel and Carbon Steel Grinding and Cutting Tools |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50 involving the failure of the licensee to ensure that weld preparation was protected from deleterious contamination in that drawers (located in the hot tool room) containing files, grinding w
Region: IV | Wolf Creek | 5187 | 06/16/2011 08/12/2011 | 2011003-05 | NRC | NCV | Initiating Events | Green | Failure to Ensure Configuration Control of Safety-Related Systems |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving the failure of the licensee to review the suitability of installing brass fittings and leaving test fittings on pressure, differential
Region: IV | Wolf Creek | 5216 | 05/23/2011 03/01/2012 | 2011009-01 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure to Adjust the Compensation in Emergency Diesel Generator Governor |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | A self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," was identified for the failure to include essential information needed to correctly adjust the emergency diesel generator governor actuator compensation potentiometer in
Region: IV | Wolf Creek | 5188 | 05/06/2011 08/12/2011 | 2011003-10 | NRC | NCV | Mitigating Systems | Green | Failure to Analyze for Vortexing in Containment Spray Additive Tank |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 2515/177 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to translate the design basis into instructions, procedures, and drawings. The inspectors found that the licensee failed to asse
Region: IV | Wolf Creek | 5180 | 04/05/2011 08/12/2011 | 2011003-09 | Self - Revealed | NCV | Initiating Events | Green | Inadequate Fire Watch Defeats Halon Fire Suppression in Vital Switchgear Rooms During Fire |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of License Condition 2.C.5 for failure to implement adequate fire watches which affected both trains of vital ac and dc switchgear. The inadequate fire watches occurred during an actual fire whic
Region: IV | Wolf Creek | 5149 | 03/31/2011 05/09/2011 | 2011002-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control of the Fuel Oil Storage Tank Fill System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, for the failure to assure that applicable regulatory requirements and the design basis were met. Specifically, the licensee failed to ensure that the fuel oil sto
Region: IV | Wolf Creek | 5155 | 03/31/2011 05/09/2011 | 2011002-02 | NRC | NCV | Mitigating Systems | Green | Isolated Cooling to Inservice Safety-Related Equipment |  | H.3(a) Work Planning | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a involving the failure to properly implement the clearance order procedure resulting in a failure to provide adequate cooling to inservice safety-related equipme
Region: IV | Wolf Creek | 5156 | 03/31/2011 05/09/2011 | 2011002-03 | NRC | NCV | Mitigating Systems | Green | Failure to Monitor the Performance of Nonsafety Related Systems and Components Used in the Plant Emergency Operating Procedures under 10 CFR 50.65 Programs |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(1) with three examples involving the failure to monitor the performance of stand by nonsafety-related systems and components that exceeded performance criteria against goals. First, the ins
Region: IV | Wolf Creek | 5157 | 03/31/2011 05/09/2011 | 2011002-04 | NRC | NCV | Mitigating Systems | Green | Failure to Follow 10 CFR 50.65 a(2) for Main Control Board Annunciator Power Supply Failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65 a(2), involving the failure to demonstrate that the performance of main control board annunciator power supplies was effectively controlled through preventive maintenance such that the annunci
Region: IV | Wolf Creek | 4866 | 03/31/2011 05/09/2011 | 2011002-05 | NRC | NCV | Mitigating Systems | Green | Inadequate Calculation for Vital Switchgear Cooling |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, involving an inadequate calculation supporting vital switchgear room temperatures with only one vital switchgear cooler operable. The licensee entered this issue
Region: IV | Wolf Creek | 5158 | 03/31/2011 05/09/2011 | 2011002-06 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Determination for Degradation of the Fuel Oil Storage Tank |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, involving the failure to follow plant procedures. Specifically, the licensee failed to follow procedure and perform an operability determination when a nonconformin
Region: IV | Wolf Creek | 5159 | 03/31/2011 05/09/2011 | 2011002-07 | NRC | NCV | Mitigating Systems | Green | Failure to Verify Ultimate Heat Sink Sedimentation Levels within Design Bases |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR Part 50 Appendix B, Criterion III, involving a failure to perform periodic testing to verify that ultimate heat sink sedimentation remained within design basis limits. The licensee subsequently veri
Region: IV | Wolf Creek | 5160 | 03/31/2011 05/09/2011 | 2011002-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Fill and Vent of Component Cooling Water |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," involving the failure to perform an adequate fill and vent of the component cooling water system which resulted in voiding of the system. The lic
Region: IV | Wolf Creek | 5164 | 03/31/2011 05/09/2011 | 2011002-09 | NRC | NCV | Initiating Events | Green | Inadequate Clearance Order Disables Power Operated Relief Valve Low Temperature Overpressure Function |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," involving the failure to follow the requirements of Procedure AP 21E-001, "Clearance Orders." This procedure violation resulted in an inadequate
Region: IV | Wolf Creek | 5165 | 03/31/2011 05/09/2011 | 2011002-10 | NRC | NCV | Mitigating Systems | Green | Repetitive Failure to Enter Technical Specifications for Auxiliary Feedwater Suction Valve Testing |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," involving the failure to follow Procedure AP 21-001, "Conduct of Operations." Specifically, the licensee failed to enter into technical specification limiting
Region: IV | Wolf Creek | 5166 | 03/31/2011 05/09/2011 | 2011002-11 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Follow Radiation Work Permit Instructions |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71124.01 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for the failure to follow procedure requirements related to adding work to existing radiation work permits. On January 4, 2011, welding was performed in a locked high radiat
Region: IV | Wolf Creek | 5176 | 03/21/2011 08/12/2011 | 2011003-08 | NRC | NCV | Initiating Events | Green | Failure to Maintain RCS Pressure Below Relief Valve Setpoint |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a, "Administrative Procedures," for failure to follow procedural requirements to maintain reactor coolant system pressure below 350 psig. Control room operators i
Region: IV | Wolf Creek | 5171 | 03/19/2011 08/12/2011 | 2011003-07 | Self - Revealed | VIO | Initiating Events | Green | Failure to Correct Procedure for Opening Main Steam Isolation Valves (EA-11-149) | EA Case: 2011149 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a cited violation of Technical Specification 5.4.1.a, "Administrative Procedures," involving Wolf Creek's failure to correct Procedure SYS AB-120 for main steam isolation valve operation. Specifically, between March 3, 2010, and
Region: IV | Wolf Creek | 5175 | 03/08/2011 08/12/2011 | 2011003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Establish Clearance Order Boundary Isolation Resulting in Loss of Component Cooling Water Inventory |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1a, "Administrative Procedures," for a loss of component cooling water train B inventory caused by inadequate clearance order verification. Valve HBV110 was stuck i
Region: IV | Wolf Creek | 5181 | 03/08/2011 08/12/2011 | 2011003-06 | NRC | FIN | Mitigating Systems | Green | Inadequate Acceptance Criteria for Postmaintenance Testing of the Startup Feedwater Pump |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a finding involving the failure to follow the requirements of Procedure AP 16E-002, "Post Maintenance Testing Development," for the startup feedwater pump. On November 4-6, 2010, Wolf Creek workers disassembled the startup feedwa
Region: IV | Wolf Creek | 5169 | 02/25/2011 05/20/2011 | 2011006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Trend Emergency Diesel Generator Chemistry Paameters Results in an Unplanned Technical Specification Entry |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | 95002 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow Procedure AP 28A-0100, "Condition Reports," Revision 13. On February 17, 2011, the licensee rece
Region: IV | Wolf Creek | 5114 | 12/31/2010 02/11/2011 | 2010005-01 | NRC | NCV | Mitigating Systems | Green | Failure to Properly Identify and Evaluate Degraded Piping in the Train A Essential Service Water System |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | The inspector identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the licensee's failure to properly evaluate a condition adverse to quality involving train A of the essential service
Region: IV | Wolf Creek | 5107 | 12/31/2010 02/11/2011 | 2010005-02 | NRC | NCV | Mitigating Systems | Green | Failure to Account for Water Hammer Stresses in Essential Service Water System Calculations |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | The inspector identified a Green noncited violation of 10 CFR 50, Appendix B, Criterion III, having very low safety significance for the licensee's failure to ensure that applicable regulatory requirements and the design basis were correctly translated in
Region: IV | Wolf Creek | 5108 | 12/31/2010 02/11/2011 | 2010005-03 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain Licensed Operator Examination Integrity |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.11B | The inspectors identified a Green noncited violation of 10 CFR Part 55.49, "Integrity of Examinations and Tests," for the failure of the licensee to ensure that the integrity of the written examinations and the operating tests administered to licensed ope
Region: IV | Wolf Creek | 5116 | 12/31/2010 02/11/2011 | 2010005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Corrosion Mechanism in Accordance with Code Case N513 |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | On September 15, 2010, the inspectors identified a Green noncited violation of 10 CFR 50.55a(b)(5) for failing to implement the requirements of Code Case N513-2, Section 2.0(e). On June 29, 2010, Wolf Creek discovered a through-wall leak of a 30 inch esse
Region: IV | Wolf Creek | 5115 | 12/31/2010 02/11/2011 | 2010005-05 | NRC | NCV | Initiating Events | Green | Failure to Identify Boric Acid Leak on Instrument Lines to Reactor Coolant System |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to identify, document, and evaluate sources of boric acid leakage. During a boric acid wa
Region: IV | Wolf Creek | 5120 | 12/31/2010 02/11/2011 | 2010005-06 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Have Procedures to Prevent Draining Radioactive Systems into Nonradioactive Systems |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71124.06 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a for failure to implement written procedures to prevent draining and venting radioactive systems into nonradioactive systems and prevent unplanned releases of ra
Region: IV | Wolf Creek | 5146 | 12/31/2010 02/11/2011 | 2010005-07 | NRC | NCV | Public Radiation Safety | Green | Failure to Have Adequate Procedures for Meteorological Monitoring |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71124.07 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for failure to have adequate procedures for maintaining meteorological monitoring systems functional. The inspectors determined that procedures did not exist for maintaining
Region: IV | Wolf Creek | 5147 | 12/31/2010 02/11/2011 | 2010005-08 | NRC | NCV | Initiating Events | Green | Inadequate Procedures for Establishing Feedwater Preheat |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for Wolf Creek Procedures GEN 00-003, "Hot Standby to Minimum Load," and SYS AE-200, "Feedwater Preheating During Plant Startup and Shutdown," being inadequat
Region: IV | Wolf Creek | 5148 | 12/31/2010 02/11/2011 | 2010005-09 | NRC | NCV | Initiating Events | Green | Inadequate Procedures to Ensure Proper Main Feed Pump Speed During Startup |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for Wolf Creek Procedures GEN 00-003, "Hot Standby to Minimum Load," and SYS AE-121, "Turbine Driven Main Feedwater Pump Startup," being inadequate by failing
Region: IV | Wolf Creek | 5118 | 12/31/2010 02/11/2011 | 2010005-10 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Steam Generator Hi-Hi Turbine Trip |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for Wolf Creek Procedure ALR 00-112A, "Steam Generator Level Hi-Hi Turbine Trip," being inadequate when reactor power exceeds the capabilities for the auxilia
Region: IV | Wolf Creek | 5119 | 12/31/2010 02/11/2011 | 2010005-11 | NRC | NCV | Mitigating Systems | Green | Inadequate Simulation Facility Fidelity |  | H.2(d) Facilities & Equipment | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR 55.46(c)(1)(i), "Simulator Fidelity," in that the licensee's simulation facility did not have adequate fidelity to simulate steam generator level oscillations that occur during startup and shutdown
Region: IV | Wolf Creek | 4873 | 11/24/2010 01/07/2011 | 2010008-01 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct a Condition Adverse to Quality |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify voiding conditions in the component cooling water and residual heat removal system piping. The licensee
Region: IV | Wolf Creek | 4874 | 11/24/2010 01/07/2011 | 2010008-02 | Self - Revealed | NCV | Mitigating Systems | Green | Inadequate Procedure for Fill and Vent of the Component Cooling Water System |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The inspectors identified a self-revealing noncited violation of Technical Specification 5.4.1, "Procedures," for failure to maintain procedures required for filling and venting of the component cooling water system. The licensee failed to ensure that the
Region: IV | Wolf Creek | 4875 | 11/24/2010 01/07/2011 | 2010008-03 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Adequate Operability Evaluation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the failure to follow the requirements of Procedures AP 28-001, "Operability Evaluations," and AP 26C-004, "Tech
Region: IV | Wolf Creek | 4876 | 11/24/2010 01/07/2011 | 2010008-04 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Inadequate RHR Fill and Vent |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to promptly identify and take corrective actions to address inadequacies in the residual heat removal system fill and vent pr
Region: IV | Wolf Creek | 4881 | 10/01/2010 01/10/2011 | 2010007-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Design of Component Cooling Water Safety/Nonsafety Isolation |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tr
Region: IV | Wolf Creek | 4882 | 10/01/2010 01/10/2011 | 2010007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform Tornado Damper Testing |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, Corrective Action, which states, in part, that "measures shall be established to assure that conditions adverse to quality, such as failures, malfunctions, defici
Region: IV | Wolf Creek | 4889 | 10/01/2010 01/10/2011 | 2010007-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Auxiliary Feedwater Pump Suction Line Break Analysis and Design |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tr
Region: IV | Wolf Creek | 4890 | 10/01/2010 01/10/2011 | 2010007-04 | NRC | NCV | Mitigating Systems | Green | Emergency Diesel Generator Specified Rating did not Address Engine Operation at Design Basis Extreme Meteorological Temperature Conditions |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states, in part, that "measures shall be established to assure that applicable regulatory requirements and the design basis are correctly tr
Region: IV | Wolf Creek | 4891 | 10/01/2010 01/10/2011 | 2010007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Requirements to Operating Procedures for the Transfer of Residual Heat Removal and Containment Spray Suction to the Containment Recirculation Sumps |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, Design Control, which states in part, that "measures shall be established to assure that applicable regulatory requirements and the design bases are correctly tra
Region: IV | Wolf Creek | 4868 | 09/30/2010 11/10/2010 | 2010004-01 | NRC | NCV | Initiating Events | Green | Failure to Establish Conditons to Open a Main Steam Isolation Valve that Resulted in a Feedwater Isolation |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | A self-revealing noncited violation of Technical Specification 5.4.1.a, Procedures, was identified for the failure to provide a procedure to establish appropriate conditions to open a main steam isolation valve in Mode 4 which resulted in an excessive ste
Region: IV | Wolf Creek | 4869 | 09/30/2010 11/10/2010 | 2010004-02 | NRC | NCV | Mitigating Systems | Green | Failure to Correct Degraded Vital Switchgear Cooler Wiring |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Conditions Adverse to Quality," involving Wolf Creek's failure to identify and correct degraded wiring in the train A vital switchgear air conditioning unit. On
Region: IV | Wolf Creek | 5127 | 07/30/2010 09/13/2010 | 2010006-01 | NRC | NCV | Mitigating Systems | Green | Failure to Resolve Degraded Conditions in a Timely Manner |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the licensee's failure to promptly correct degraded or nonconforming conditions in that the conditions were not corrected at the first av
Region: IV | Wolf Creek | 5128 | 07/30/2010 09/13/2010 | 2010006-02 | NRC | NCV | Mitigating Systems | Green | Unqualified Scaffolding Erected Near Safety-Related Equipment |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for failure to properly implement Procedure AP 14A-003, "Scaffold Construction and Use," Revision 17, when scaffolding was erected near operable safety-related equipment. On
Region: IV | Wolf Creek | 5129 | 07/30/2010 09/13/2010 | 2010006-03 | NRC | FIN | Mitigating Systems | Green | Failure to Adequately Monitor Control Room Deficiencies |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a finding for the failure to follow Procedure AI 22A-001, "Operator Work Arounds/Burdens/Control Room Deficiencies," Revision 8, to adequately identify, document, and track control room deficiencies associated with instruments an
Region: IV | Wolf Creek | 5135 | 07/30/2010 09/13/2010 | 2010006-04 | NRC | NCV | Mitigating Systems | Green | Failure to Update an Operability Evaluation |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures and Drawings," for the failure to implement Procedure AP 26C-004, "Technical Specification Operability," Revision 20, to adequately evalua
Region: IV | Wolf Creek | 5136 | 07/30/2010 09/13/2010 | 2010006-05 | NRC | VIO | Mitigating Systems | Green | Failure to Perform Adequate Evaluation for Significant Conditions | EA Case: 2010160 | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a cited violation 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," because the licensee failed to perform an adequate evaluation to determine the cause of loss of offsite power induced water hammers and internal co
Region: IV | Wolf Creek | 5137 | 07/30/2010 09/13/2010 | 2010006-07 | NRC | NCV | Mitigating Systems | Green | Failure to Determine if a Deficiency Existed in the Ultimate Heat Sink |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to follow the requirements of Procedure AP 26C-004, "Technical Specification Operability," Revision 20. Specific
Region: IV | Wolf Creek | 5143 | 07/30/2010 09/13/2010 | 2010006-08 | Self - Revealed | NCV | Mitigating Systems | Green | Notice of Unusual Event Due to Loss of Both Emergency Diesel Generators |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors reviewed a self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to identify a degraded equipment condition in December 2006. As a result, the emergency diesel generator system expe
Region: IV | Wolf Creek | 5144 | 07/30/2010 09/13/2010 | 2010006-09 | NRC | NCV | Mitigating Systems | Green | Failure to Translate Design Information into a Procedure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure to translate criteria from the atmospheric relief valve accumulator leakage calculation into proceduralized leakage criteria. Sp
Region: IV | Wolf Creek | 4864 | 06/30/2010 08/11/2010 | 2010003-01 | NRC | NCV | Mitigating Systems | Green | Failure to Maintain an Adequate Flooding Analysis for Auxiliary Feedwater Trains |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.06 | The inspectors identified a green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," after Wolf Creek failed to provide adequate design control measures for verifying the adequacy of the flooding analysis for the auxiliary
Region: IV | Wolf Creek | 4865 | 06/30/2010 08/11/2010 | 2010003-02 | NRC | NCV | Mitigating Systems | Green | Lack of Acceptance Criteria Allows Degraded EDG Power Supply to Remain in Service |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a violation of Technical Specification 5.4.1.a, "Procedures," for the failure of maintenance personnel to provide an adequate work order that included critical acceptance criteria for the emergency diesel generator B. On October
Region: IV | Wolf Creek | 4867 | 06/30/2010 08/11/2010 | 2010003-03 | NRC | NCV | Mitigating Systems | Green | Nonsafety Power Supply Causes Failure of Emergency Diesel Generator A |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a Green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to ensure the design of the emergency diesel local annunciator power supply circuit such that its failure
Region: IV | Wolf Creek | 4859 | 03/31/2010 05/04/2010 | 2010002-01 | NRC | NCV | Mitigating Systems | Green | Degraded Fire Barriers for Auxiliary Feedwater |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a noncited violation of License Condition 2.C(5)(a) for degraded fire seals that separated redundant safe shutdown equipment. Specifically, silicone foam and ceramic fiber board seals separating the auxiliary feedwater trains fro
Region: IV | Wolf Creek | 4860 | 03/31/2010 05/04/2010 | 2010002-02 | NRC | NCV | Mitigating Systems | Green | Failure to Establish Goals and Monitor for a(1) Offgas Radiation Monitor GERE0092 |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | The inspectors identified a noncited violation of 10 CFR 50.65 for failure to establish goals per paragraph (a)(1) to monitor the performance of the main condenser offgas radiation Monitor GERE0092. Multiple failures occurred which exceeded the monitoring
Region: IV | Wolf Creek | 4863 | 03/31/2010 05/04/2010 | 2010002-03 | NRC | NCV | Barrier Integrity | Green | Inoperable Containment Cooler Condensate Monitoring System |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, due to all containment cooler drip pans being degraded such that the containment cooler condensate monitoring system could not perform its design basis safety fun
Region: IV | Wolf Creek | 4861 | 03/31/2010 05/04/2010 | 2010002-04 | NRC | FIN | Mitigating Systems | Green | Failure to Perform Adequate Posttrip Review |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green finding for the failure to adequately implement the posttrip review procedure following a reactor trip caused by low steam generator water levels on March 2, 2010. Specifically, Wolf Creek's posttrip evaluation was not ad
Region: IV | Wolf Creek | 4862 | 03/31/2010 05/04/2010 | 2010002-05 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure for a Main Feed Pump Trip |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.a, "Procedures," for the failure of Wolf Creek control room personnel to follow procedures for a main feedwater pump trip. During a review of the posttrip data and opera
Region: IV | Wolf Creek | 4842 | 12/31/2009 02/11/2010 | 2009005-01 | NRC | VIO | Mitigating Systems | Green | Failure to Correct Discolored Boric Acid Deposits | EA Case: 2010004 | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for failure to take action to stop leakage from the base of the refueling water storage tank or evaluate the leakage and wastage for acceptabili
Region: IV | Wolf Creek | 4840 | 12/31/2009 02/11/2010 | 2009005-02 | NRC | NCV | Mitigating Systems | Green | Control of Transient Ignition Sources |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, for an inadequate Procedure AP-10-101, "Control of Transient Ignition Sources." On October 21, 2009, the inspectors observed maintenance personnel performing weld preparati
Region: IV | Wolf Creek | 4841 | 12/31/2009 02/11/2010 | 2009005-03 | NRC | NCV | Initiating Events | Green | Failure to Identify Sources of Boron Leakage |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71111.08P | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to identify sources of boron leakage and document them in a corrective action document. S
Region: IV | Wolf Creek | 4843 | 12/31/2009 02/11/2010 | 2009005-04 | NRC | NCV | Mitigating Systems | Green | Failure to Incorporate Requirements of Regulatory Guide 1.182 into Shutdown Risk |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | The inspectors identified a noncited violation of 10 CFR 50.65(a)(4) involving the failure to adequately perform shutdown risk assessments during Refueling Outage 17. Between October 10 and November 17, 2009, Wolf Creek did not appropriately consider elec
Region: IV | Wolf Creek | 4844 | 12/31/2009 02/11/2010 | 2009005-05 | NRC | NCV | Mitigating Systems | Green | Mode Change Under Technical Specification 3.0.4.b without Required Risk Management Actions |  | H.1(c) Communication of Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | On November 18, 2009, the inspectors identified a noncited violation of Technical Specification 3.0.4.b for ascension from Mode 4 to Mode 3 without establishing required risk management actions. Wolf Creek used technical specification Limiting Condition f
Region: IV | Wolf Creek | 4845 | 12/31/2009 02/11/2010 | 2009005-06 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Corrective Action Procedure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | On October 15, 2009, the inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to follow Procedure AP 28A-100, "Condition Reports." Wolf Creek failed to initiate a cond
Region: IV | Wolf Creek | 4846 | 12/31/2009 02/11/2010 | 2009005-07 | NRC | NCV | Mitigating Systems | Green | Failure to Follow Procedure Results in Draining of Emergency Core Cooling System Pump Oil |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | On November 23, 2009, a self-revealing violation of Technical Specification 5.4.1.a was identified when a technician failed to follow procedure and emptied 45 gallons of oil from centrifugal charging Pump A. The technician was supposed to remove the tempe
Region: IV | Wolf Creek | 4847 | 12/31/2009 02/11/2010 | 2009005-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Operability Evaluation of Essential Service Water Pumps |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | On November 5, 2009, inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for the failure to perform an adequate operability evaluation required by procedure. The inspectors ident
Region: IV | Wolf Creek | 4848 | 12/31/2009 02/11/2010 | 2009005-09 | NRC | NCV | Barrier Integrity | Green | Positive Reactivity Addition Prohibited by Technical Specifications while in Mode 2 |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 3.3.1, Condition I, for making positive reactivity addition prohibited by technical specifications in Mode 2 because one source range nuclear instrument channel was inoperable. Foll
Region: IV | Wolf Creek | 4849 | 12/31/2009 02/11/2010 | 2009005-10 | NRC | NCV | Initiating Events | Green | Failure to Obtain Vendor Data Necessary for Plant Modification |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71111.18 | On December 16, 2009, inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," involving failure to obtain vendor design data for a modification. In August 2009, a component cooling water modification was
Region: IV | Wolf Creek | 4850 | 12/31/2009 02/11/2010 | 2009005-11 | NRC | VIO | Initiating Events | Green | Failure to Correct Vessel Head Vent Path |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," due to an inadequate vent path for the reactor vessel head. The inadequate vent path resulted in the formation of voids in the reactor vessel head
Region: IV | Wolf Creek | 4851 | 12/31/2009 02/11/2010 | 2009005-12 | NRC | NCV | Mitigating Systems | Green | Unevaluated Scaffold Against Component Cooling Water Piping |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a for failure to properly implement Procedure AP 14A-003, "Scaffold Construction and Use," when scaffolding was erected against operable safety-related equipment. On October 1
Region: IV | Wolf Creek | 4852 | 12/31/2009 02/11/2010 | 2009005-13 | NRC | NCV | Occupational Radiation Safety | Green | Failure to Maintain Administrative Control of Keys to Locked High Radiation Areas |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 7112101 | The inspector identified a noncited violation of Technical Specification 5.7.2.a.1 for failure to maintain administrative control of door and gate keys to high radiation areas with dose rates greater than 1 rem per hour but less than 500 rads per hour (re
Region: IV | Wolf Creek | 4853 | 12/31/2009 02/11/2010 | 2009005-14 | NRC | NCV | Barrier Integrity | Green | Failure to Identify Inoperable P-6 Interlock and Intermediate Range Detector |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | On December 30, 2009, the inspectors identified a noncited violation of Technical Specification Table 3.3.1-1, Function 18.a, when Wolf Creek restarted on May 18, 2005. During a reactor shutdown on October 7, 2006, intermediate range neutron detector Nucl
Region: IV | Wolf Creek | 4855 | 12/31/2009 02/11/2010 | 2009005-16 | NRC | NCV | Initiating Events | Green | Operator Actions Disable Circuit Breaker Coordination and Could Initiate Secondary Fires |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a noncited violation of License Condition 2.C.(5), "Fire Protection," for the failure to implement and maintain the approved fire protection program. Specifically, the licensee prescribed mitigating actions in response to certain
Region: IV | Wolf Creek | 4824 | 12/22/2009 02/02/2010 | 2009007-01 | NRC | FIN | Initiating Events | Green | Failure to Enter Adverse Conditions into the Corrrective Action Program |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a finding associated with the licensee's failure to recognize the adverse conditions related to their offsite power system as prescribed by Procedure AP 28A-100, "Condition Reports." Specifically, the licensee failed to enter pertinent
Region: IV | Wolf Creek | 4829 | 12/22/2009 02/02/2010 | 2009007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Perform an Operability Evaluation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure AP 26C-004, "Technical Specification Operability." Spec
Region: IV | Wolf Creek | 4830 | 12/22/2009 02/02/2010 | 2009007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Correctly Screen Essential Service Water Piping Leaks for Significance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to follow the requirements of Procedure AI 28A-010, "Screening Condition Reports." Specifically
Region: IV | Wolf Creek | 4832 | 12/22/2009 02/02/2010 | 2009007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure Adequate Acceptance Criteria and Extent of Condition Guidance in Lake Water and Corrective Action Program Procedures |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to provide adequate guidance to identify and address pitting, corrosion, and surface indication
Region: IV | Wolf Creek | 4833 | 12/22/2009 02/02/2010 | 2009007-06 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure Resulted in Failure to Discover Essential Service Water System Leakage Following a Water Hammer Event |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," regarding the licensee's failure to provide adequate guidance to address the impact of a loss of offsite power event on the esse
Region: IV | Wolf Creek | 4834 | 12/22/2009 02/02/2010 | 2009007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Initiate Timely Fire Protection Impairment Control Permit and Implement Compensatory Measures |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of License Condition 2.C.(5), "Fire Protection," for the failure to establish a compensatory fire watch in a timely manner per the station fire protection program. On August 19, 2009, a complete loss of offsite pow
Region: IV | Wolf Creek | 4836 | 12/22/2009 02/02/2010 | 2009007-09 | Self - Revealed | NCV | Initiating Events | Green | Failure to Adequately Control Steam Generator Water Levels |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a self-revealing noncited violation of Technical Specification 5.4.1.a, "Procedures," after operator's failure to monitor and maintain steam generator water levels resulted in an unanticipated turbine trip signal and feedwater isolatio
Region: IV | Wolf Creek | 4858 | 12/15/2009 02/11/2010 | 2009302-01 | NRC | NCV | Barrier Integrity | Green | Inadequately Analyzed Emergency Operating Procedure Change |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The NRC examiners identified a Green noncited violation of Technical Specification 5.4.1.b for failure to validate changes made to Emergency Operating Procedures. Specifically, the licensee failed to validate a change made to Emergency Operating Procedure
Region: IV | Wolf Creek | 4816 | 09/30/2009 11/10/2009 | 2009004-01 | NRC | NCV | Barrier Integrity | Green | Failure to Log Foreign Material in Spent Fuel Pool After Extent of Condition Evaluation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, "Procedures," for failure to follow Procedure AP 12-003, "Foreign Material Exclusion." On August 12, 2009, the inspectors conducted a walkdown of the spent fuel pool area a
Region: IV | Wolf Creek | 4817 | 09/30/2009 11/10/2009 | 2009004-02 | NRC | NCV | Mitigating Systems | Green | Inability to perform manual actions for risk assessment |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | The inspector identified a noncited violation of 10 CFR 50.65(a)(4) for failure to adequately assess and manage the increase in risk during fuse inspection of component cooling water valves supplying cooling loads inside containment. On March 18, 2009, co
Region: IV | Wolf Creek | 4818 | 09/30/2009 11/10/2009 | 2009004-03 | NRC | NCV | Mitigating Systems | Green | Inadequate Evaluation of Emergency Diesel Generator for Common Cause Failure in the Supporting Essential Service Water System |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | On June 30, 2009, the inspectors identified a noncited violation of Technical Specification 3.8.1 for failure to perform an adequate common cause evaluation within 24 hours to demonstrate no common cause failure mechanism existed between the emergency die
Region: IV | Wolf Creek | 4819 | 09/30/2009 11/10/2009 | 2009004-04 | NRC | NCV | Mitigating Systems | Green | Failure to Implelment Engineered Safety Features Actuation System Technical Specification Results in Missed Mode Change |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | On August 22, 2009, the inspectors identified a noncited violation of Technical Specification 3.0.3 in which both trains of Technical Specification 3.3.2 engineered safety features actuation system interlock function 8.a were bypassed with jumper wires in
Region: IV | Wolf Creek | 4820 | 09/30/2009 11/10/2009 | 2009004-05 | NRC | NCV | Mitigating Systems | Green | Use of Nonsafety Related Power to Ensure Operability of Safety Related Boric Acid System |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.18 | The inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion III, "Design Control," for failing to translate the boric acid design basis into procedures that ensure time sensitive operator actions are completed to achieve the core shu
Region: IV | Wolf Creek | 4821 | 09/30/2009 11/10/2009 | 2009004-06 | NRC | NCV | Mitigating Systems | Green | Performing Prohibited Elective Maintenance on Safety Bus NB02 Channel 4 During Emergency Diesel Generator Maintenance |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a noncited violation of Technical Specification 3.8.1, Required Action B.4.2.2 on March 24, 2009 when the licensee performed elective maintenance on safety bus relays and removed equipment from service that was required by the te
Region: IV | Wolf Creek | 4809 | 06/30/2009 08/05/2009 | 2009003-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Testing Equipment Used for Alignment Verification of Emergency Diesel Lube Oil Piping |  | H.3(a) Work Planning | TE?: N | 05000482 Wolf Creek 1 |  | 71111.18 | The inspectors identified a noncited violation for an inadequate control of measuring and test equipment used to verify the design basis of a safety related system. On June 2, 2009, Wolf Creek measured pipe gaps and angles of deflection associated with Sm
Region: IV | Wolf Creek | 4811 | 06/30/2009 08/05/2009 | 2009003-02 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Fuse Thermography Procedure Resulted in Blown Fuses and Unplanned Reactor Trip |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding was identified for an inadequate thermography maintenance procedure. Inadequate procedural guidance resulted in thermography failing to identify an overheated fues which resulted in a reactor trip due a loss of power to a main fee
Region: IV | Wolf Creek | 4812 | 06/30/2009 08/05/2009 | 2009003-03 | NRC | NCV | Barrier Integrity | Green | Inadequate Testing Results in P-6 Interlock Failure to Energize Source Range on Reactor Trip |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | On April 28, 2009, the inspectors identified a Green noncited violation of Technical Specification, Table 3.3.1-1, Function 18.a, when Wolf Creek tripped from 100 percent reactor power. During the trip, intermediate range neutron Detector NI-36 did not de
Region: IV | Wolf Creek | 4857 | 06/30/2009 08/12/2009 | 2009006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate instructions for changing modes of operation of the residual heat removal system |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of Technical Specification 5.4.1, "Procedures," associated with the licensee's failure to ensure that adequate procedures were available for changing modes of operation of the residual heat removal system fro
Region: IV | Wolf Creek | 4796 | 03/31/2009 05/13/2009 | 2009002-01 | NRC | FIN | Mitigating Systems | Green | Untimely corrective actions result in room temperature below boric acid solubility limit |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 71111.01 | The inspectors identified a finding for allowing low room temperature to cause a boric acid flow path to be inoperable. The inspectors reviewed a performance improvement request from 2005, which identified that boric acid could decrease below its limits i
Region: IV | Wolf Creek | 4803 | 03/31/2009 05/13/2009 | 2009002-02 | NRC | NCV | Mitigating Systems | Green | Degraded fire barrier for auxiliary feedwater |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05A | The inspectors identified a noncited violation of License Condition 2.C(5)(a) for a degraded fire seal that separated redundant safe shutdown equipment. Specifically, a silicone foam seal and ceramic fiber board separating redundant motor driven auxiliary
Region: IV | Wolf Creek | 4807 | 03/31/2009 05/13/2009 | 2009002-03 | NRC | NCV | Barrier Integrity | Green | Failure to implement foreign material exclusion control procedure for spent fuel pool |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, Procedures, for failure to follow Procedure AP 12-003, Foreign Material Exclusion. On January 17, 2009, inspectors conducted a walkdown of the spent fuel pool area and foun
Region: IV | Wolf Creek | 4801 | 03/31/2009 05/13/2009 | 2009002-04 | NRC | NCV | Barrier Integrity | Green | Failure to follow 10 CFR 50.65a(2) for containment isolation valve failures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | On February 25, 2009, the inspectors identified a noncited violation of 10 CFR 50.65 a(2), the Maintenance Rule, for failure to demonstrate that the performance of a containment isolation valve was effectively controlled through the performance of prevent
Region: IV | Wolf Creek | 4795 | 03/31/2009 05/13/2009 | 2009002-06 | NRC | NCV | Mitigating Systems | Green | Unacceptable preconditioning of control rods prior to surveillance testing |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.22 | On February 6, 2009, the inspectors identified a noncited violation of 10 CFR 50 Appendix B, Criterion XI, "Test Control" for a procedure that allowed unacceptable preconditioning of the control rods prior to Technical Specification Surveillance 3.1.4.2.
Region: IV | Wolf Creek | 4802 | 03/31/2009 05/13/2009 | 2009002-07 | NRC | VIO | Initiating Events | Green | Failure to correct component cooling water valve closures | EA Case: 2009110 | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a cited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," involving Wolf Creek's failure to correct the cause of the reactor coolant pump thermal barrier component cooling water heat exchanger outlet va
Region: IV | Wolf Creek | 4813 | 03/31/2009 05/13/2009 | 2009002-08 | Self - Revealed | NCV | Mitigating Systems | Green | Inattentive on-duty senior reactor operator |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | A self-revealing noncited violation of Technical Specification 5.4.1(a) was identified when an on-duty operations shift manager was observed to be inattentive on multiple occasions in 2004 and 2005. This limited his ability to monitor the safe operation o
Region: IV | Wolf Creek | 4794 | 11/25/2008 02/11/2009 | 2008005-03 | NRC | NCV | Mitigating Systems | Green | Equipment out of service log definitions redefined outside of procedure change process |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a, procedures, for changing the equipment out of service log outside of the procedure change process. On November 25, 2008, the inspectors questioned the status of excess letd
Region: IV | Wolf Creek | 4787 | 10/24/2008 01/02/2009 | 2008010-02 | NRC | NCV | Mitigating Systems | Green | Failure to Ensure a Fire Pump Would Automatically Start for One Fire Area |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(5), "Fire Protection," for the failure to ensure that a water supply for the manual fire suppression system credited by the fire protection program would be promptly available in the even
Region: IV | Wolf Creek | 4790 | 10/24/2008 01/02/2009 | 2008010-05 | NRC | NCV | Mitigating Systems | Green | Operator Actions Affect the Ability to Operate Post Fire Safe Shutdown Equipment |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a non-cited violation of License Condition 2.C.(5), "Fire Protection," for operator actions taken in response to a fire in Fire Area A-27 (Reactor Trip Switchgear Room 1403) that remove the ability to remotely operate equipment require
Region: IV | Wolf Creek | 4791 | 10/24/2008 01/02/2009 | 2008010-06 | NRC | NCV | Mitigating Systems | Green | Failure to Evaluate Changes to the Approved Fire Protection Program |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05T | The team identified a Severity Level IV non-cited violation for making changes to the approved fire protection program in a manner contrary to the requirements of License Condition 2.C.(5).(b). Prior to 2005, the licensee made multiple revisions to Proced
Region: IV | Wolf Creek | 4773 | 09/27/2008 11/07/2008 | 2008004-01 | Self - Revealed | NCV | Barrier Integrity | Green | Incompatible Procedures Result in 6400 gallon Drain of SFP |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.04Q | A self-revealing noncited violation of 10 CFR Part 50 Appendix B, Criterion V, "Instructions, Procedures, and Drawings," was identified after the licensee followed two incompatible procedures simultaneously resulting in the inadvertent partial draining of
Region: IV | Wolf Creek | 4774 | 09/27/2008 11/07/2008 | 2008004-02 | NRC | NCV | Mitigating Systems | Green | Use of hammer to reduce accumulator check valve leakage |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | Inspectors identified a green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," when Wolf Creek hammered the side of check Valve EP8818D such that the body of the valve was dented numerous times. This
Region: IV | Wolf Creek | 4775 | 09/27/2008 11/07/2008 | 2008004-03 | NRC | NCV | Mitigating Systems | Green | Failure to adequately evaluate submerged safety-related cables |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a green noncited violation of 10 CFR, Part 50, Appendix B, Criterion III, "Design Control," because Wolf Creek failed to adequately demonstrate that 4160v cables that are under water are qualified for such service, and that they
Region: IV | Wolf Creek | 4776 | 09/27/2008 11/07/2008 | 2008004-04 | NRC | NCV | Mitigating Systems | Green | EDG lube oil heat exchanger leak due water hammer |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | On April 7, 2008, the inspectors identified a green noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," due to an approximately 10 to 15 gpm leak on the Emergency Diesel Generator B lubricating oil heat
Region: IV | Wolf Creek | 4779 | 09/27/2008 11/07/2008 | 2008004-05 | NRC | NCV | Mitigating Systems | Green | Waterhammer caused by loss of offsite power exceeds heat exchanger bolt yield strength |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A self-revealing noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," occurred on April 7, 2008, when a loss of offsite power caused the service water pumps to shutdown and the essential service water pump to start. As a resu
Region: IV | Wolf Creek | 4780 | 09/27/2008 11/07/2008 | 2008004-06 | NRC | NCV | Barrier Integrity | Green | Failure to completely close the SFP valve resulted in a loss of SFP water inventory |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A self-revealing green noncited violation of Technical Specification 5.4.1.a was identified for the failure to close Valve EC-V025 during a lineup to recirculate the refueling water storage tank through the spent fuel pool cleanup system. These two system
Region: IV | Wolf Creek | 4781 | 09/27/2008 11/07/2008 | 2008004-07 | Self - Revealed | NCV | Initiating Events | Green | Inadequate reactor vessel vent path |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing green noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," was identified due to an inadequate vent path for the reactor vessel head. The inadequate vent path resulted in the formation of a maximum void size
Region: IV | Wolf Creek | 4782 | 09/27/2008 11/07/2008 | 2008004-08 | NRC | NCV | Mitigating Systems | Green | Diesel generator low frequency and voltage variation not considered in calculations |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 2515/176 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to account for the effect of emergency diesel generator frequency variation at
Region: IV | Wolf Creek | 4792 | 09/24/2008 02/11/2009 | 2008005-01 | Self - Revealed | NCV | Barrier Integrity | Green | Maintenance causes unplanned increase in reactor power |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | On September 24, 2008, inspectors identified a noncited violation of 10 CFR 50.54(j) in which the fix it now team manipulated limit switches for Valve ACPV186C that caused the reactor to exceed the licensed thermal power limit of 3565 MWt for 27 minutes u
Region: IV | Wolf Creek | 4785 | 09/12/2008 10/20/2008 | 2008009-01 | Self - Revealed | NCV | Public Radiation Safety | Green | Failure to Provide an Accuratge Shipping Manifest |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 7112202 | The team reviewed a self-revealing, noncited violation of 10 CFR 20.2006(b) resulting from the licensee's failure to provide an accurate shipping manifest. On May 16, 2008, the licensee shipped used radioactive resin to a waste processor. The shipment con
Region: IV | Wolf Creek | 4742 | 06/28/2008 08/07/2008 | 2008003-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement transient combustible control permit requirements for a propane tank |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | A noncited violation (NCV) TS 5.4.1.d was identified for failing to control combustible materials in an area of the plant that contained safety related equipment. During a walkdown on May 1, 2008, inspectors noted that a temporary propane cylinder for a g
Region: IV | Wolf Creek | 4755 | 06/28/2008 08/07/2008 | 2008003-02 | NRC | NCV | Mitigating Systems | Green | Failure to establish goals and monitor for a(1) ECCS room |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.12 | An NCV of 10 CFR 50.65(a)(1) was identified by the inspectors for failure to establish a(1) goals for the safety-related room coolers and monitor room cooler performance against those goals. On May 5, 2005, the Train A residual heat removal pump accumulat
Region: IV | Wolf Creek | 4756 | 06/28/2008 08/07/2008 | 2008003-03 | NRC | NCV | Mitigating Systems | Green | Inadequate containment sump inspection procedure |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion V, "Procedures, Instructions, and Drawings," for Wolf Creek's failure to specify acceptance criteria in its containment sump inspection procedure which led to unidentified gaps in c
Region: IV | Wolf Creek | 4761 | 06/28/2008 08/07/2008 | 2008003-04 | NRC | NCV | Barrier Integrity | Green | Troubleshooting activities bypass design control for the fuel transfer system |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors identified a violation of TS 5.4.1.a in which Wolf Creek raised the winch load setpoint for its fuel transfer system to avoid trips without knowing the cause. During core reload, Wolf Creek experienced repeated trips of the fuel handling sy
Region: IV | Wolf Creek | 4762 | 06/28/2008 08/07/2008 | 2008003-05 | Self - Revealed | FIN | Mitigating Systems | Green | Inadequate switchyard work procedure resulted in a loss of offsite power |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding was identified for an inadequate Wolf Creek switchyard maintenance work instruction which resulted in the loss of offsite power. On April 7, 2008, offsite power was lost to the NB02 4 kV safety-related bus when switchyard workers
Region: IV | Wolf Creek | 4767 | 06/28/2008 08/07/2008 | 2008003-06 | NRC | NCV | Mitigating Systems | Green | Failure to verify engineering design calculation prior to use |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified an NCV of 10 CFR Part 50, Appendix B, Criterion III (Design Control) for failure to implement engineering procedures and approve a third party calculation prior to use at Wolf Creek. Specifically, the calculation review failed to
Region: IV | Wolf Creek | 4768 | 06/28/2008 08/07/2008 | 2008003-07 | Self - Revealed | FIN | Initiating Events | Green | Inadequate transformer procedure resulted in an unplanned reactor trip and forced outage |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding was identified for an inadequate maintenance procedure that resulted in a reactor trip due a loss of all condensate pumps. On March 17, 2008, plant operators observed that steam generator water level was lowering and main feed pum
Region: IV | Wolf Creek | 4706 | 04/07/2008 07/24/2008 | 2008002-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement fire protection impairment control permit requirements and compensatory measures |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a noncited violation of Technical Specification 5.4.1.d for failure to implement fire protection impairment control permit requirements and compensatory measures when operators received a trouble alarm on a fire detector in the a
Region: IV | Wolf Creek | 4707 | 04/07/2008 07/24/2008 | 2008002-02 | NRC | NCV | Mitigating Systems | Green | Performing prohibited elective maintenance on offsite power during EDG maintenance |  | H.3(b) Work Activity Coordination | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | -An NRC identified a noncited violation of Technical Specification 3.8.1.B.4 resulted from Wolf Creek removing equipment from service that was prohibited by the TS. Inspectors reviewed Technical Specification Bases 3.8.1.B.4 which prohibits elective maint
Region: IV | Wolf Creek | 4712 | 04/07/2008 07/24/2008 | 2008002-04 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to control area as a locked high radiation area |  | H.3(a) Work Planning | TE?: N | 05000482 Wolf Creek 1 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.7.2.a for failure to evaluate changing radiological conditions and control an area as a locked high radiation area. Specifically, on October 17, 2007, dose rates in R
Region: IV | Wolf Creek | 4713 | 04/07/2008 07/24/2008 | 2008002-05 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to follow procedure |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 7112101 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1 for failure to follow a licensee procedure. Specifically, on March 29, 2008, one of two radiographers conducting radiography operations in the quality control vau
Region: IV | Wolf Creek | 4714 | 04/07/2008 07/24/2008 | 2008002-06 | NRC | NCV | Mitigating Systems | Green | Failure to establish reasonable expectation of operability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | -An NRC identified NCV of Technical Specification 5.4.1 for failure to follow the operability process on discovery of the CCP A room cooler leak. Wolf Creek made no log entries at 2:20 p.m. stating its basis for immediate operability. At 3:50 p.m., Wolf
Region: IV | Wolf Creek | 4719 | 04/07/2008 07/24/2008 | 2008002-07 | NRC | NCV | Mitigating Systems | Green | Untimely corrective actions for CCP room cooler leads to NOED |  | H.2(a) Maintaining Long Term Plant Safety | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors identified a noncited violation of 10 CFR Part 50 Appendix B Criterion XVI, "Corrective Action," because Wolf Creek failed to take timely corrective actions to prevent failure of the centrifugal charging pump A room cooler which resulted in
Region: IV | Wolf Creek | 4721 | 04/07/2008 07/24/2008 | 2008002-09 | NRC | NCV | Mitigating Systems | Green | Failure to reestablish timely seal cooling for the reactor coolant pumps |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | -An NRC identified violation of Technical Specification 5.4.1.d resulted because Procedure OFN RP 017, "Control Room Evacuation," Revision 21, failed to account for the needed actions to reestablish reactor coolant pump seal cooling. Failure to reestablis
Region: IV | Wolf Creek | 4722 | 04/07/2008 07/24/2008 | 2008002-10 | NRC | NCV | Mitigating Systems | Green | Failure to analyze motor operated valuve circuits |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | -The inspectors identified a noncited violation of License Condition 2.c(5) because the licensee failed to evaluate the impact of a motor operated valve failure mechanism on their ability to implement postfire safe shutdown following a control room evacua
Region: IV | Wolf Creek | 4725 | 03/13/2008 04/24/2008 | 2008007-01 | NRC | NCV | Mitigating Systems | Green | Failure to Vent ECCS Piping Every 31 days |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified two examples of a noncited violation of Technical Specification Surveillance Requirements 3.5.2.3 for the failure to vent emergency core cooling system discharge piping. In the first example, the licensee had inappropriately concluded
Region: IV | Wolf Creek | 4733 | 03/13/2008 04/24/2008 | 2008007-02 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Voiding in the Safety Injection System |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Actions), with five examples, for the failure to promptly identify and correct voids in safety injection system. In some cases, significant changes in the sa
Region: IV | Wolf Creek | 4734 | 03/13/2008 04/24/2008 | 2008007-03 | NRC | NCV | Mitigating Systems | Green | Failure to Promptly Identify and Correct Voids in ECCS Suction Piping |  | P.2(b) Implementing Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Actions), because the licensee failed to promptly identify and correct voids in emergency core cooling systme suction piping. After NRC concerns were raised,
Region: IV | Wolf Creek | 4735 | 03/13/2008 04/24/2008 | 2008007-04 | NRC | NCV | Mitigating Systems | Green | Inadequate RHR and CS Void Calculations |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III (Design Control), for an inadequate calculation involving previously identified voids in the residual heat removal and containment spray containment suction piping. A co
Region: IV | Wolf Creek | 4736 | 03/13/2008 04/24/2008 | 2008007-05 | NRC | NCV | Mitigating Systems | Green | Failure to Adequately Correct Voiding Design Control Violation |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI (Corrective Actions), because the licensee took inadequate corrective measures to address NRC identified deficiencies involving the calculation for voids in the residual
Region: IV | Wolf Creek | 4737 | 03/13/2008 04/24/2008 | 2008007-06 | NRC | NCV | Mitigating Systems | Green | Failure to Approve Engineering Calculations Prior to Use at Wolf Creek and Inadequate Work Instructions |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III (Design Control), with two examples for: (1) the failure to implement engineering procedures and approve a third party calculation prior to use at Wolf Creek, and (2) th
Region: IV | Wolf Creek | 4738 | 03/13/2008 04/24/2008 | 2008007-07 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Piping Design Procedure and ASME Code Requirements |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR 50, Appendix B, Criterion V (Procedures), for the failure to implement piping design procedure requirements. The procedure required that piping systems be designed for normal component service (filling an
Region: IV | Wolf Creek | 4741 | 03/13/2008 04/24/2008 | 2008007-08 | NRC | NCV | Mitigating Systems | Green | Inadequate Root Cause Assessment |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 93812 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, because the licensee failed to follow the site procedure when performing a root cause assessment for the emergency core cooling system voiding issues and, subsequently, c
Region: IV | Wolf Creek | 4726 | 02/29/2008 05/14/2008 | 2008006-01 | NRC | NCV | Mitigating Systems | Green | Failure to correct procedure deviations to demonstrate seismic acceptability |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, for failure to follow Procedure AP 14A-003, "Scaffold Construction and Use," Revision 14. From November 13, 2003, to February 4, 2008, the licensee did not construct 21 s
Region: IV | Wolf Creek | 4727 | 02/29/2008 05/14/2008 | 2008006-02 | NRC | FIN | Mitigating Systems | Green | Failure to implement corrective actions to correct a finding associated with logging the sequence of events following main annuciator failure |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a finding for the failure to establish appropriate corrective actions as required by Procedure AP 28A-100, "Condition Reports," Revision 4, for a previous noncited violation associated with the failure to log the sequence of events whe
Region: IV | Wolf Creek | 4728 | 02/29/2008 05/14/2008 | 2008006-03 | NRC | NCV | Mitigating Systems | Green | Failure to implement corrective action for missed operability assessment |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to take corrective actions. Specifically, from June 13, 2007, to February 29, 2008, the licensee failed to take corrective actions for noncited Violation 20
Region: IV | Wolf Creek | 4723 | 02/29/2008 05/14/2008 | 2008006-04 | NRC | NCV | Barrier Integrity | Green | Failure to correct finding associated with auxiliary feedwater pump governor null setting |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to take corrective actions. Specifically, from June 2005 to February 29, 2008, the licensee failed to take actions to monitor the turbine driven auxiliary f
Region: IV | Wolf Creek | 4731 | 02/29/2008 05/14/2008 | 2008006-05 | NRC | NCV | Mitigating Systems | Green | Failure to take corrective actions for Barton transmitter defects |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for failure to take corrective actions. Specifically, from January 16, 2007, to February 29, 2008, the licensee failed to take corrective actions to address the failure
Region: IV | Wolf Creek | 4732 | 02/29/2008 05/14/2008 | 2008006-06 | NRC | FIN | Mitigating Systems | Green | Failure to take corrective actions to correct annunciator deficiencies |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a finding for failure to update the plant annunciator system wiring drawing when a modification to the design of the wiring was made during the decommissioning of the sewage treatment process plant. The plant annunciator system was c
Region: IV | Wolf Creek | 4696 | 12/31/2007 02/12/2008 | 2007005-02 | NRC | NCV | Mitigating Systems | Green | Failure to evaluate ESW valve corrosion |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation (NCV) of 10 CFR Appendix B, Criterion V, "Instructions, Procedures, and Drawings," for failure to follow a procedure which required an evaluation of the Train B of ESW traveling screen wash valve and identica
Region: IV | Wolf Creek | 4702 | 12/31/2007 02/12/2008 | 2007005-03 | NRC | NCV | Mitigating Systems | Green | Inadequate evaluation of EDG for common cause failure |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a noncited violation of Technical Specification 3.8.1 for failure to perform an adequate common cause evaluation within 24 hours to demonstrate no common cause failure mechanism existed between the emergency diesel generators. Wo
Region: IV | Wolf Creek | 4703 | 12/31/2007 02/12/2008 | 2007005-04 | NRC | FIN | Mitigating Systems | Green | Failure to enter and evaluate EDG operating experience in CAP |  | P.2(a) Evaluating & Communicating Operating Experience | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a finding for failure to enter into corrective action program evaluate relevant emergency diesel generator operating experience which allowed a manufacturing defect to exist resulting in a testing failure. Procedure AP 20E-001, S
Region: IV | Wolf Creek | 4704 | 12/31/2007 02/12/2008 | 2007005-05 | Self - Revealed | FIN | Initiating Events | Green | Inadequate work instructions resulted in condensate pump trip |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding was identified for inadequate work instructions and poor work practices associated with trip circuit verification on the Central Chiller B resulted in the Condensate Pump B trip and steam generator level transient. Procedure RNM C
Region: IV | Wolf Creek | 4705 | 12/31/2007 02/12/2008 | 2007005-06 | NRC | FIN | Mitigating Systems | Green | Clogged drains cause circulating water roof loads to exceed design |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | The inspectors identified a Green finding for exceeding the calculated roof loading for the circulating water screen house. In May 2007, Wolf Creek received heavy rains and water leaks from the circulating water screen house roof were observed. On May 8,
Region: IV | Wolf Creek | 4679 | 10/06/2007 11/16/2007 | 2007004-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement transient combustible material control permit requirements |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05Q | The inspectors identified a Green noncited violation of Technical Specification 5.4.1.d for failing to control combustible materials in an area of the plant that contained safety-related equipment. During a walkdown, inspectors noted that temporary scaffo
Region: IV | Wolf Creek | 4680 | 10/06/2007 11/16/2007 | 2007004-02 | NRC | NCV | Mitigating Systems | Green | Failure to collor EDG assembly procedure resulting in NOED |  | H.2(b) Personnel Training & Qualifications | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing noncited violation was identified regarding failure to follow a procedure used to reassemble the intercooler and jacketwater pumps to the Train A emergency diesel generator resulting in the Emergency Diesel Generator A being inoperable. D
Region: IV | Wolf Creek | 4681 | 10/06/2007 11/16/2007 | 2007004-03 | NRC | FIN | Mitigating Systems | Green | Failure to use appropriate guidance for valve operation |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | A self-revealing finding was identified when a nonlicensed plant operator failed to utilize appropriate guidance and used excessive torque on service water Valves 1WS0002A and 1WS0004 resulting in damage to the valves and unavailability of service water P
Region: IV | Wolf Creek | 4682 | 07/20/2007 10/15/2007 | 2007006-01 | NRC | NCV | Mitigating Systems | Green | Inadequate Procedure for Restoration of the Emergency Diesel Generator Fuel Oil Transfer Pump Control Circuit Following a Fire Requiring Control Room Evacuation |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of Technical Specification 5.4.1.a, for the licensee's inadequate procedure for remotely starting the emergency diesel generator fuel oil transfer pump following a fire in the control room. Specifically, the govern
Region: IV | Wolf Creek | 4683 | 07/20/2007 10/15/2007 | 2007006-02 | NRC | NCV | Mitigating Systems | Green | Inadequate Design Control Associated with Vortexing Calculation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," in that, the licensee did not ensure adequate suction submergence for the containment spray pumps by not properly translating vortex design parameters
Region: IV | Wolf Creek | 4684 | 07/20/2007 10/15/2007 | 2007006-03 | NRC | NCV | Mitigating Systems | Green | Failure to Identify and Correct Discolored Boric Acid Deposits |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Corrective Action," for the failure to identify and take timely corrective action to correct indications of material wastage at the base of the Refueling Water Storage
Region: IV | Wolf Creek | 4688 | 07/20/2007 10/15/2007 | 2007006-04 | NRC | NCV | Mitigating Systems | Green | Nonconservative Battery Intercell Connection Resistance Value Specified in Design Calculation |  | P.1(a) Corrective Action Program Issue Identification | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," for the failure of the licensee to ensure that the 125 Vdc safety-related batteries would remain operable if all the intercell and terminal connection
Region: IV | Wolf Creek | 4689 | 07/20/2007 10/15/2007 | 2007006-05 | NRC | NCV | Mitigating Systems | Green | Battery Surfaces Not Cleaned as Required by Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of Technical Specification 5.4.1.a, for the licensee's failure to clean electrolyte from the outside surfaces of the 125 Vdc safety-related batteries in accordance with procedures. Specifically, surveillance proced
Region: IV | Wolf Creek | 4690 | 07/20/2007 10/15/2007 | 2007006-06 | NRC | FIN | Mitigating Systems | Green | Normal Charging Pump Balance Line Crack |  | P.1(d) Implementation of Corrective Actions | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team reviewed a self-revealing finding associated with the licensee's failure to correct normal charging pump balance line vibrations in a timely manner. Because the licensee did not address the extended time and periodically increased magnitude of th
Region: IV | Wolf Creek | 4691 | 07/20/2007 10/15/2007 | 2007006-07 | NRC | FIN | Mitigating Systems | Green | Inadequate Procedure for Maintaining Drains Capable of Functioning |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a finding associated with the licensee's failure to maintain a procedure which ensured that control building room drains remained available to pass their design flows for postulated flooding events. As a result of the licensee's proced
Region: IV | Wolf Creek | 4692 | 07/20/2007 10/15/2007 | 2007006-08 | NRC | NCV | Mitigating Systems | Green | Diesel Generator Frequency Variation Not Considered in Loading Calculations |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion III, "Design Control," having very low safety significance for the licensee's failure to account for the effect of emergency diesel generator frequency variation in the dies
Region: IV | Wolf Creek | 4693 | 07/20/2007 10/15/2007 | 2007006-09 | NRC | URI | Mitigating Systems | Green | Potential for Damage to TDAFW Pump and ESW System During CST Unavailability |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team reviewed the pertinent design calculations concerning the automatic swapover of the suction source for the auxilary feedwater (AFW) pumps from the condensate storage tank (CST) to the emergency service water (ESW) system. In responding to a loss
Region: IV | Wolf Creek | 4694 | 07/20/2007 10/15/2007 | 2007006-10 | NRC | URI | Mitigating Systems | Green | Effect of Emergency Diesel Generator Frequency Variation on Supplied Equipment |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111121 | The team identified that during a LOOP event with the EDGs supplying plant loads, the output frequency of the supplied power would be allowed to vary from 58.8 hertz to 61.2 hertz by Technical Specification 3.8.1. The licensee had already begun to address
Region: IV | Wolf Creek | 4668 | 07/07/2007 08/16/2007 | 2007003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Implement Manual Actions |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13 | A noncited violation of 10 CFR 50.65(a)(4) was identified for failure to adequately assess and manage the increase in risk during observation of a scheduled emergency diesel generator surveillance. On January 4, 2007, inspectors observed the emergency die
Region: IV | Wolf Creek | 4669 | 07/07/2007 08/16/2007 | 2007003-03 | NRC | NCV | Initiating Events | Green | Failure to Identify Cause of Component Cooling Water Valve Closures |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, "Conditions Adverse to Quality," involving Wolf Creek's failure to identify and correct the cause of the reactor coolant pump (RCP) thermal barrier component cool
Region: IV | Wolf Creek | 4670 | 07/07/2007 08/16/2007 | 2007003-04 | NRC | NCV | Barrier Integrity | Green | Failure to Establish an Adequate Preventive Maintenance Program |  | P.1(c) Evaluation of Identified Problems | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.4.1.a in which Wolf Creek did not implement a preventive maintenance procedure to mitigate Train B emergency exhaust system fan bearing vibrations which resulted in a degraded con
Region: IV | Wolf Creek | 4677 | 07/07/2007 08/16/2007 | 2007003-05 | NRC | NCV | Barrier Integrity | Green | Failure to Follow Test Control Procedures to Demonstrate Operability |  | H.1(a) Systematic Process for Decisions | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a noncited violation of 10 CFR, Part 50, Appendix B, Criterion XI, "Test Control," in which Wolf Creek did not implement controlled testing of the Train B emergency exhaust system fan to demonstrate operability prior to returning
Region: IV | Wolf Creek | 4678 | 07/07/2007 08/16/2007 | 2007003-06 | Self - Revealed | FIN | Initiating Events | Green | Inadequate Inspections of Circulating Water Pump Auto Transformers |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding for failing to identify degraded circulating water pump auto transformers during inspections in April 2007. Specifically, Wolf Creek failed to adequately inspect and identify signs of overheating and degradation during inspection
Region: IV | Wolf Creek | 4655 | 04/07/2007 05/11/2007 | 2007002-01 | Self - Revealed | NCV | Mitigating Systems | Green | Failure to implement fire protection impairment control permit requirements and compensatory measures |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71111.05A | A self-revealing noncited violation of Technical Specification 5.4.1.d was identified for failure to implement fire protection impairment control permit requirements and compensatory measures when operators incorrectly disabled three fire detectors in the
Region: IV | Wolf Creek | 4656 | 04/07/2007 05/11/2007 | 2007002-02 | NRC | URI | Public Radiation Safety | Green | Use of wrench on manual service water valve handwheel |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.13
Region: IV | Wolf Creek | 4657 | 04/07/2007 05/11/2007 | 2007002-03 | Self - Revealed | NCV | Occupational Radiation Safety | Green | Failure to perform an adequate survey in a high radiation area |  | H.3(a) Work Planning | TE?: N | 05000482 Wolf Creek 1 |  | 7112101 | The inspector reviewed a self-revealing noncited violation of 10 CFR 20.1501(a) because the licensee failed to perform an adequate survey in a high radiation area. On March 7, 2007, a health physics technician performed a survey of Floor Drain Tank Room 7
Region: IV | Wolf Creek | 4658 | 04/07/2007 05/11/2007 | 2007002-04 | NRC | NCV | MISC | Green | Failure to maintain sufficient records to furnish evidence of events significant to plant safety |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A noncited violation of Technical Specification 5.4.1.a was identified for failure to maintain sufficient records (logs) to furnish evidence of events significant to plant safety. On January 26, 2007, electrical maintenance commenced a scheduled replaceme
Region: IV | Wolf Creek | 4662 | 04/07/2007 05/11/2007 | 2007002-05 | Self - Revealed | FIN | MISC | Green | Failure to maintain drawings technically accurate |  | H.2(c) Documentation, Procedures & Component Labeling | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing finding was identified regarding inadequate engineering drawings used as guidance to replace main control board annunciator power supplies resulting in a loss of all main control board annunciators. During de-termination of the power supp
Region: IV | Wolf Creek | 4663 | 04/07/2007 05/11/2007 | 2007002-06 | NRC | NCV | Barrier Integrity | Green | Failure to maintain steady state reactor power at or below the licensed thermal power limit |  | H.1(b) Conservative Assumptions & Safe Actions | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A noncited violation of Technical Specification 5.4.1.a occurred when operators did not take timely action to lower power below the licensed thermal limit of 3565 MWt. During an incore to excore neutron detector calibration, the power level exceeded the l
Region: IV | Wolf Creek | 4664 | 04/07/2007 05/11/2007 | 2007002-07 | NRC | NCV | Barrier Integrity | Green | Failure to remove the correct containment radiation monitor from service |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | A self-revealing noncited violation of Technical Specification 5.4.1 occurred on February 20, 2007, when a chemistry technician inadvertently removed both containment purge radiation Monitors GTRE22 and GTRE33 from service at the same time. During planned
Region: IV | Wolf Creek | 4648 | 12/31/2006 02/06/2007 | 2006005-01 | NRC | NCV | Mitigating Systems | Green | Failure to implement the reactor vessel closure head installation procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 05000482 Wolf Creek 1 |  | 71111.2 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, "Instructions, Procedures, and Drawings," involving the licensee's failure to properly implement the reactor vessel closure head installation procedure during Refue
Region: IV | Wolf Creek | 4649 | 12/31/2006 02/06/2007 | 2006005-02 | NRC | NCV | Occupational Radiation Safety | Green | Failure to provide instructions to workers |  | H.4(c) Supervisory & Management Oversight | TE?: N | 05000482 Wolf Creek 1 |  | 7112101 | The inspector identified a noncited violation of 10 CFR 19.12(a)(2) because the licensee failed to provide instructions to a worker on how to minimize exposure while working with radioactive material and contaminated equipment. Specifically, on October 18
Region: IV | Wolf Creek | 4638 | 10/07/2006 11/09/2006 | 2006004-01 | NRC | NCV | Mitigating Systems | Green | Inadequate inspections of potentially defective pressure transmitter |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion V, regarding the failure to implement Administrative Procedure AP 28-011, "Resolving Deficiencies Impacting SSC's," Revision 1. Procedure AP 28-011 requires that, duri
Region: IV | Wolf Creek | 4639 | 10/07/2006 11/09/2006 | 2006004-02 | Self - Revealed | NCV | Barrier Integrity | Green | Failure to completely close SFP valves resulted in a loss of SFP water inventory |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152 | A self-revealing noncited violation of Technical Specification 5.4.1.a was identified for the failure to close Valves EC-V025 and -V033 during a lineup to recirculate the refueling water storage tank through the spent fuel pool cleanup system. These two s
Region: IV | Wolf Creek | 4640 | 10/07/2006 11/09/2006 | 2006004-03 | Self - Revealed | NCV | Initiating Events | Green | Failure to follow procedure results in loss of coolant charging flow |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | The inspectors reviewed a self-revealing noncited violation of Technical Specification 5.4.1.a involving the licensee's failure to follow a procedure that resulted in a loss of coolant charging flow during a planned surveillance. The licensee entered this
Region: IV | Wolf Creek | 4632 | 06/23/2006 08/21/2006 | 2006003-01 | NRC | NCV | MISC | Green | Failure to Follow Station Procedures for Clearance Orders |  | H.4(b) Procedural Compliance | TE?: N | 05000482 Wolf Creek 1 05000482 Wolf Creek 1 |  | 71152 | An NRC-identified noncited violation of Technical Specifications 5.4.1 for failing to follow procedures was identified when electricians removed terminal leads that were still energized with 500 volt ac. During work under Clearance Orders C15-D-LF-005 and
Region: IV | Wolf Creek | 4633 | 06/23/2006 08/21/2006 | 2006003-02 | NRC | NCV | Mitigating Systems | Green | Failure to Follow System Operating Procedure |  | H.4(a) Human Error Prevention | TE?: N | 05000482 Wolf Creek 1 |  | 71153 | An NRC-identified noncited violation of Technical Specification 5.4.1 was identified for failing to follow system operating procedures for the Class 1E electrical equipment air conditioning units. On May 4, 2006, a planned maintenance evolution was schedu
Region: IV | Wolf Creek | 4615 | 05/10/2006 05/26/2006 | 2006010-01 | NRC | FIN | Mitigating Systems | Green | Inadequate Procedure to Address a 10 CFR Part 21 Notification of a Potential Safety-Related Component Defect |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a finding for the licensee's failure to establish appropriate testing procedures for the operation of the turbine-driven auxiliary feedwater pump following notification (10 CFR Part 21 report issued April 12, 2005) of a component defec
Region: IV | Wolf Creek | 4616 | 05/10/2006 05/26/2006 | 2006010-02 | NRC | FIN | Mitigating Systems | Green | Inadequate procedure for long-standing component cooling water pump problems |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a finding for the failure to establish appropriate procedures for the operation of the component cooling water pump. Specifically, the licensee did not establish procedures to include appropriate acceptance criteria for component cooli
Region: IV | Wolf Creek | 4617 | 05/10/2006 05/26/2006 | 2006010-03 | NRC | NCV | Barrier Integrity | Green | Inadequate corrective actions to address spent fuel pool foreign material. |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a noncited violation of 10 CFR Part 50, Appendix B, Criterion XVI, for the failure to take adequate corrective actions to address spent fuel pool foreign material issues. Specifically, the licensee did not determine the source of the f
Region: IV | Wolf Creek | 4618 | 05/10/2006 05/26/2006 | 2006010-04 | NRC | FIN | Mitigating Systems | Green | Inadequate procedure to address industry operating experience regarding submerged cables |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152B | The team identified a finding for the failure to establish appropriate procedures for the inspection of buried safety-related electrical cables. Specifically, the licensee did not establish procedures to include acceptance criteria to determine if buried
Region: IV | Wolf Creek | 4603 | 04/07/2006 05/22/2006 | 2006002-01 | NRC | NCV | Initiating Events | Green | Failure to provide adequate fire detection in the diesel generator rooms |  |  | TE?: N | 05000482 Wolf Creek 1 |  | NONE | An NRC identified Green noncited violation of Facility Operating License Condition 2.C.5, Fire Protection, was identified for inadequate fire detection in the emergency diesel generator rooms. The infrared detectors' view of some combustibles in the rooms
Region: IV | Wolf Creek | 4604 | 04/07/2006 05/22/2006 | 2006002-02 | Self - Revealed | FIN | Initiating Events | Green | INADEQUATE PROCEDURE FOR THE OPERATION OF LIMITORQUE MOTOR-OPERATED VALVES |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 7111114 | A self-revealing Green finding was identified for the failure to provide adequate instructions for the operation of Limitorque motor-operated valves. The instructions were inadequate because they failed to provide guidance on declutching Limitorque motor-
Region: IV | Wolf Creek | 4605 | 04/07/2006 05/22/2006 | 2006002-03 | NRC | NCV | Barrier Integrity | Green | Failure to follow administrative procedure for operability determination |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.15 | The inspectors identified a noncited violation of Technical Specification 5.4.1 for failure to follow Administrative Procedure AP28-011, "Resolving Deficiencies Impacting SSC's [structures, systems and components]," Revision 1. The inspectors identified a
Region: IV | Wolf Creek | 4606 | 04/07/2006 05/22/2006 | 2006002-04 | NRC | NCV | Occupational Radiation Safety | Green | Failure to follow a station procedure for the operation of the incore detector drive system |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71111.19 | The inspectors identified a noncited violation of Technical Specification 5.4.1(a) for the failure to follow licensee Procedure SYS SR-200, "Movable Incore Detector Operation," Revision 18. Contrary to this procedure, during troubleshooting activities on
Region: IV | Wolf Creek | 124710 | 05/08/2019 |  |  | LIV |  | Green | Failure to Maintain the Effectiveness of the Emergency Plan |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71152
Region: IV | Wolf Creek | 125650 | 09/24/2019 |  |  | LIV |  | Green | Failure to Implement Audit and Accountability Controls for the Main Fire Panel |  |  | TE?: N | 05000482 Wolf Creek 1 |  | 71130.10P